## sysconfig
configuration switches |  |  | Hydrogen Microgrid Energy Model
solar PV | 1 |  | Reference: R.P. van Leeuwen, Determining the optimal capacity of hydrogen storage and conversion, Saxion, 2020 | [7 empty] | CAPEX & OPEX parameters
wind turbine | 0 | [9 empty] | Parameter | Value | Unit | Capacity | CAPEX | energy flows | OPEX | TOTAL COST/y
electric storage | 0 | [8 empty] | De,g,max | c1 | 348 | €/kW.y | 3000 | 1044000 |  |  | 1044000
electricity import | 1 | [8 empty] | compr cap |  | 2400 | €/(kg/hr) | 52.5 | 126000 |  |  | 126000
electricity demand supply | 0 | [8 empty] | Smax | c2 | 50 | €/kg.y | 1500 | 75000 |  |  | 75000
hydrogen gas demand supply | 1 | [8 empty] | Ppv | c3 | 60 | €/kWp.y | 1779.0429 | 106742.574 |  |  | 106742.574
heat demand supply | 0 | [8 empty] | Pw | c4 | 108 | €/kW.y | 0 | 0 |  |  | 0
[10 empty] | Ing | o1 | 0.2 | €/kWh |  |  | 0 | 0 | 0
solar PV | [9 empty] | Ie | o2 | var | €/kWh |  |  | 20911385.2905 | 1130581.8099 | 1130581.8099
kWp/m2 | 0.1779 | [8 empty] | Ig | o3 | 2.5 | €/kg |  |  | 71518.3462 | 178795.8656 | 0
panel area | 10000 | m2 | [7 empty] | Ee | o4 | 0.07 | €/kWh |  |  | -47853.835 | -3349.7685 | -3349.7685
maximum power | 1779.0429 | kWp | [14 empty] | objective: | 2478974.6154
wind turbine
axle height | 89 | m | [8 empty] | Capacity constraints |  |  |  | Hydrogen price level for gas produced
rotor diameter | 92 | m | [8 empty] | lower limit | upper limit | Unit |  | Total costs | 2478974.6154 | euro
maximum power | 2350 | kW | [7 empty] | De,g,max | 100 | 1500 | kW |  | production | 399220.0918 | kg
power production | 0 | kW | [7 empty] | Smax | 50 | 400 | kg |  | kg price | 6.2095 | euro/kg
split factor | 0.5 | [8 empty] | PV_area | 500 | 10000 | m2 |  | m3AE price | 1.3648 | euro/m3AE
[10 empty] | W_split | 1 | 5 |  |  | note: compressor CAPEX included
hydrogen elektrolyzer
conversion efficiency | 0.7
max. electric power | 3000 | kW | [8 empty] | Grid export price based on SDE
min. production factor | 0.1 | [9 empty] | SDE tariff | full load hrs | av prd
min. electric power | 300 | kW | storages | [6 empty] | PV | 0.07 | 950 | 1690090.755 | kWh/yr
max. hydrogen production | 2100 | kW |  | capacity | value |  | C-value | max. (dis)charge rate |  | wind | 0.048 | 2500 | 0 | kWh/yr
max. mass flow production | 52.5 | kg/h | electric storage | 180 | 0 | kWh | 0.7 | 0 | kW |  |  | total | 1690090.755 | kWh/yr
min. hydrogen production | 210 | kW | hydrogen storage | 1500 | 1500 | kg | 0.5 | 750 | kg/h |  |  | av SDE grid export price | 0.07 | €/kWh
min. mass flow production | 5.25 | kg/h | initial value SC |  | 750 | kg
hydrogen compressor |  |  | electricity import for hydrogen |  |  |  | conditions hydrogen electricity pool
isentropic efficiency | 0.7 |  | P1 | 0.07 | euro/kWh |  | Ce,g,max | 3093.8105 | kW
electrolyzer pressure | 20 | bar | P2 | 0.07 | euro/kWh |  | Ce,g,min | 300 | kW
storage pressure | 200 | bar | penalty for CO2 emission | 0.015 | euro/kWh
inlet temperature | 60 | °C
number of compressor stages | 1 |  | boilers |  |  |  |  | user defined
spec. energy consumption | 1.7869 | kWh/kg | thermal efficiency hydrogen | 0.95 |  |  |  | optimization variable (don't change)
max. electric power | 93.8105 | kW | thermal efficiency natural gas | 1 |  |  |  | dependent variable (don't change)
Note on O4: Annelies Boerman: zie log over kosten; 348 betreft PEM 129 voor Alkaline
Note on U11: Annelies Boerman: dit zouden de kosten van aanvullend ingekocht gas zijn: niet zo logisch om dat als kosten aan het geproduceerde gas toe te rekenen, daarom op 0 gezet
Note on E33: Annelies Boerman: P>P1: alleen gridafname voor elektriciteitsvoorziening P>P2: ook voor H2 productie, maar niet voor opslag.

## graph
graph 1 | Dg;Dg*
graph 2 | Dh;Ph,g;Ph,ng
graph 3 | Pg;St;Sg;Dg*;Dg,h*
graph 4 | Ppv;Pw;Ie;Ee;De;De*;De,g;De,c

## graphs for pub
figure 2a - mei
figure 3a - mei
figure 4a - mei
figure 5a - mei
figure 2b - augustus
figure 3b - augustus
figure 4b - augustus
figure 5b - augustus

## results
Yearly totals local energy sources + import
final demand |  |  |  |  | realised demand supply
De | Dh | Dg |  |  | De* | Ph,g | Ph,ng | Dg*
kWh | kWh | kg |  |  | kWh | kWh | kWh | kg
0 | 0 | 469988.438 |  |  | 0 | 0 | 0 | 398470.0918
[5 empty] | #DIV/0! | #DIV/0! | #DIV/0! | 84.78% | % of demand
[5 empty] | De | Dh | Dh | Dg
electricity production |  |  |  |  | internal electricity consumption |  |  |  |  | hydrogen production
Ppv | Pw | Ee | Ie | self consumption | De,g | De,c | total consumption + supply |  |  | Pg | Dg* | Dg,h* | Send-Sinit
kWh | kWh | kWh | kWh | kWh | kWh | kWh | kWh |  |  | kg | kg | kg | kg
2115060.3037 | 0 | -47853.835 | 20911385.2905 | 2067206.4687 | 22812576.6722 | 166015.0869 | 22978591.7592 |  |  | 399220.0918 | 398470.0918 | 0 | 778.9376
|  |  |  | 97.74% |  |  | should match Ppv+Pw+Ee+Ie |  |  | 86.81% | 86.64% | 0% | 0.1694% | %'s of max production | 459900
obv t-1
Send-Sinit
kg
750
0.1631%
Note on P14: Annelies Boerman: gerekend obv St; moet obv S(t-1)
Note on P24: Annelies Boerman: gerekend obv St; moet obv S(t-1)

## modifications
modifications from v0.10
2021-02-02 | change plots to xy-scatter
change plots to fill one screen
change plot data to full year range (change by changing x=axis!)
2021-02-04 | sheet GROHW_demand, waterstof gebruiksprofielen, toegevoegd.
door verschillende maxima, factoren in te stellen kunnen leverafspraken ingebouwd worden.
kolommen gebundeld voor wegvervoer berekenen afname indien per tubetrailer geleverd wordt, capaciteit in te stellen bovenin
in kolom z kan eenvoudig het toepasselijke totaalgebruik gedefinieerd worden, dit wordt overgenomen in de verdere berekening
2021-06-24 | update in Grohw 3 overleg over afname: Auping en Nefit doen niet mee; Vos en Westfalen wel.
Westfalen is een gasleverancier, afname nog onbekend
Vos is een transportbedrijf: nemen zij zelf af of via tankstation? Hoeveel?
voorlopig deze data nog niet toegevoegd. Wordt de komende tijd door westfalen/engie/hve geinventariseerd.
div data tables toegevoegd op sysconfig pagina (aparte pagina werkt om onduidelijke reden niet :(
2021-06-29 | optie calculation automatic except for data tables aangezet
2021-07-08 | data voor 2019 ingevoerd:
weerdata windsnelheid en zoninstraling van KNMI (uurdata)
day-ahead price en CO2eq/MWh door uurgemiddelden uit kwartierdata van Entsoe
prijzen waterstof systeemcomponenten obv waterstofcursus, compressor ook toegevoegd
prijzen wind en zon berekend obv SDE voorjaar 2020 met 11% winstmarge
SDE op gridexport toegevoegd: exportprijs is gewogen gemiddelde van PV en wind tarief
sysconfig U11: op 0 gezet: hier werden de kosten van aanvullend ingekocht gas toegerekend aan het geproduceerde gas
Als je dat al wilt meerekenen dan voor kg-prijsberekening niet delen door geproduceerd gas maar door totaal gasvraag
2021-08-06 | (tijdellijke aanpassing) Cap voor ACS levering op sysconfig-pagina toegevoegd
2021-10-08 | tabs graph en result direct rechts van sysconfig geplaatst
in graph/ grafiek Hydrogen gas balance de grafiek production groen gemaakt, duidelijker te onderscheiden van storage charge

## consumption
day | date | hour | De | Dg | Dh | De, Dh and Dg to be defined by user as input in tab "profiles"
|  |  | kWh | kg | kWh
1 | 1899-12-31 | 1 | 0 | 28.9376 | 0
1 | 1899-12-31 | 2 | 0 | 29.1815 | 0
1 | 1899-12-31 | 3 | 0 | 35.9061 | 0
1 | 1899-12-31 | 4 | 0 | 30.1971 | 0
1 | 1899-12-31 | 5 | 0 | 39.6806 | 0
1 | 1899-12-31 | 6 | 0 | 28.9379 | 0
1 | 1899-12-31 | 7 | 0 | 34.4637 | 0
1 | 1899-12-31 | 8 | 0 | 49.7149 | 0
1 | 1899-12-31 | 9 | 0 | 52.0359 | 0
1 | 1899-12-31 | 10 | 0 | 39.1974 | 0
1 | 1899-12-31 | 11 | 0 | 42.405 | 0
1 | 1899-12-31 | 12 | 0 | 52.6496 | 0
1 | 1899-12-31 | 13 | 0 | 44.2398 | 0
1 | 1899-12-31 | 14 | 0 | 49.0333 | 0
1 | 1899-12-31 | 15 | 0 | 46.7205 | 0
1 | 1899-12-31 | 16 | 0 | 55.1097 | 0
1 | 1899-12-31 | 17 | 0 | 43.1132 | 0
1 | 1899-12-31 | 18 | 0 | 41.6424 | 0
1 | 1899-12-31 | 19 | 0 | 51.4645 | 0
1 | 1899-12-31 | 20 | 0 | 23.9224 | 0
1 | 1899-12-31 | 21 | 0 | 27.3412 | 0
1 | 1899-12-31 | 22 | 0 | 35.8974 | 0
1 | 1899-12-31 | 23 | 0 | 22.2632 | 0
1 | 1899-12-31 | 24 | 0 | 31.9763 | 0
2 | 1900-01-01 | 25 | 0 | 24.3883 | 0
2 | 1900-01-01 | 26 | 0 | 32.4641 | 0
2 | 1900-01-01 | 27 | 0 | 24.5208 | 0
2 | 1900-01-01 | 28 | 0 | 25.5111 | 0
2 | 1900-01-01 | 29 | 0 | 33.3961 | 0
2 | 1900-01-01 | 30 | 0 | 24.9132 | 0
2 | 1900-01-01 | 31 | 0 | 29.3418 | 0
2 | 1900-01-01 | 32 | 0 | 39.5093 | 0
2 | 1900-01-01 | 33 | 0 | 47.9677 | 0
2 | 1900-01-01 | 34 | 0 | 248.5421 | 0
2 | 1900-01-01 | 35 | 0 | 45.9085 | 0
2 | 1900-01-01 | 36 | 0 | 48.5094 | 0
2 | 1900-01-01 | 37 | 0 | 42.1889 | 0
2 | 1900-01-01 | 38 | 0 | 48.4479 | 0
2 | 1900-01-01 | 39 | 0 | 54.0008 | 0
2 | 1900-01-01 | 40 | 0 | 43.9271 | 0
2 | 1900-01-01 | 41 | 0 | 46.6585 | 0
2 | 1900-01-01 | 42 | 0 | 43.5524 | 0
2 | 1900-01-01 | 43 | 0 | 43.9588 | 0
2 | 1900-01-01 | 44 | 0 | 31.2894 | 0
2 | 1900-01-01 | 45 | 0 | 30.5482 | 0
2 | 1900-01-01 | 46 | 0 | 30.2655 | 0
2 | 1900-01-01 | 47 | 0 | 24.8339 | 0
2 | 1900-01-01 | 48 | 0 | 28.2249 | 0
3 | 1900-01-02 | 49 | 0 | 23.9772 | 0
3 | 1900-01-02 | 50 | 0 | 27.9619 | 0
3 | 1900-01-02 | 51 | 0 | 25.8889 | 0
3 | 1900-01-02 | 52 | 0 | 23.8979 | 0
3 | 1900-01-02 | 53 | 0 | 28.6893 | 0
3 | 1900-01-02 | 54 | 0 | 30.9944 | 0
3 | 1900-01-02 | 55 | 0 | 36.1961 | 0
3 | 1900-01-02 | 56 | 0 | 42.1813 | 0
3 | 1900-01-02 | 57 | 0 | 43.9248 | 0
3 | 1900-01-02 | 58 | 0 | 49.6227 | 0
3 | 1900-01-02 | 59 | 0 | 37.8531 | 0
3 | 1900-01-02 | 60 | 0 | 231.6315 | 0
3 | 1900-01-02 | 61 | 0 | 41.9285 | 0
3 | 1900-01-02 | 62 | 0 | 28.5706 | 0
3 | 1900-01-02 | 63 | 0 | 57.7758 | 0
3 | 1900-01-02 | 64 | 0 | 25.2863 | 0
3 | 1900-01-02 | 65 | 0 | 46.8403 | 0
3 | 1900-01-02 | 66 | 0 | 48.7685 | 0
3 | 1900-01-02 | 67 | 0 | 44.783 | 0
3 | 1900-01-02 | 68 | 0 | 29.8794 | 0
3 | 1900-01-02 | 69 | 0 | 30.9745 | 0
3 | 1900-01-02 | 70 | 0 | 29.0631 | 0
3 | 1900-01-02 | 71 | 0 | 22.0088 | 0
3 | 1900-01-02 | 72 | 0 | 28.3787 | 0
4 | 1900-01-03 | 73 | 0 | 35.2363 | 0
4 | 1900-01-03 | 74 | 0 | 22.4102 | 0
4 | 1900-01-03 | 75 | 0 | 31.9103 | 0
4 | 1900-01-03 | 76 | 0 | 24.9303 | 0
4 | 1900-01-03 | 77 | 0 | 35.8227 | 0
4 | 1900-01-03 | 78 | 0 | 235.6684 | 0
4 | 1900-01-03 | 79 | 0 | 25.5531 | 0
4 | 1900-01-03 | 80 | 0 | 33.4271 | 0
4 | 1900-01-03 | 81 | 0 | 28.2756 | 0
4 | 1900-01-03 | 82 | 0 | 33.6969 | 0
4 | 1900-01-03 | 83 | 0 | 45.5294 | 0
4 | 1900-01-03 | 84 | 0 | 34.4547 | 0
4 | 1900-01-03 | 85 | 0 | 33.6957 | 0
4 | 1900-01-03 | 86 | 0 | 52.75 | 0
4 | 1900-01-03 | 87 | 0 | 36.0955 | 0
4 | 1900-01-03 | 88 | 0 | 37.5425 | 0
4 | 1900-01-03 | 89 | 0 | 33.8665 | 0
4 | 1900-01-03 | 90 | 0 | 47.4211 | 0
4 | 1900-01-03 | 91 | 0 | 53.5283 | 0
4 | 1900-01-03 | 92 | 0 | 25.7104 | 0
4 | 1900-01-03 | 93 | 0 | 35.1875 | 0
4 | 1900-01-03 | 94 | 0 | 23.4989 | 0
4 | 1900-01-03 | 95 | 0 | 29.8849 | 0
4 | 1900-01-03 | 96 | 0 | 27.9688 | 0
5 | 1900-01-04 | 97 | 0 | 31.2013 | 0
5 | 1900-01-04 | 98 | 0 | 22.9091 | 0
5 | 1900-01-04 | 99 | 0 | 32.0143 | 0
5 | 1900-01-04 | 100 | 0 | 22.1166 | 0
5 | 1900-01-04 | 101 | 0 | 35.5603 | 0
5 | 1900-01-04 | 102 | 0 | 22.1261 | 0
5 | 1900-01-04 | 103 | 0 | 23.3406 | 0
5 | 1900-01-04 | 104 | 0 | 37.2854 | 0
5 | 1900-01-04 | 105 | 0 | 40.7334 | 0
5 | 1900-01-04 | 106 | 0 | 32.8957 | 0
5 | 1900-01-04 | 107 | 0 | 45.4595 | 0
5 | 1900-01-04 | 108 | 0 | 37.5915 | 0
5 | 1900-01-04 | 109 | 0 | 41.8928 | 0
5 | 1900-01-04 | 110 | 0 | 48.7033 | 0
5 | 1900-01-04 | 111 | 0 | 49.7054 | 0
5 | 1900-01-04 | 112 | 0 | 33.6307 | 0
5 | 1900-01-04 | 113 | 0 | 32.8219 | 0
5 | 1900-01-04 | 114 | 0 | 43.4129 | 0
5 | 1900-01-04 | 115 | 0 | 36.8413 | 0
5 | 1900-01-04 | 116 | 0 | 32.8393 | 0
5 | 1900-01-04 | 117 | 0 | 24.7761 | 0
5 | 1900-01-04 | 118 | 0 | 23.1862 | 0
5 | 1900-01-04 | 119 | 0 | 31.7762 | 0
5 | 1900-01-04 | 120 | 0 | 431.6943 | 0
6 | 1900-01-05 | 121 | 0 | 33.0922 | 0
6 | 1900-01-05 | 122 | 0 | 18.9229 | 0
6 | 1900-01-05 | 123 | 0 | 28.2923 | 0
6 | 1900-01-05 | 124 | 0 | 27.6968 | 0
6 | 1900-01-05 | 125 | 0 | 29.9238 | 0
6 | 1900-01-05 | 126 | 0 | 26.377 | 0
6 | 1900-01-05 | 127 | 0 | 37.3332 | 0
6 | 1900-01-05 | 128 | 0 | 43.1001 | 0
6 | 1900-01-05 | 129 | 0 | 52.5587 | 0
6 | 1900-01-05 | 130 | 0 | 42.8053 | 0
6 | 1900-01-05 | 131 | 0 | 45.2001 | 0
6 | 1900-01-05 | 132 | 0 | 48.3255 | 0
6 | 1900-01-05 | 133 | 0 | 32.9895 | 0
6 | 1900-01-05 | 134 | 0 | 38.7787 | 0
6 | 1900-01-05 | 135 | 0 | 44.7976 | 0
6 | 1900-01-05 | 136 | 0 | 40.2855 | 0
6 | 1900-01-05 | 137 | 0 | 53.5259 | 0
6 | 1900-01-05 | 138 | 0 | 40.4084 | 0
6 | 1900-01-05 | 139 | 0 | 42.761 | 0
6 | 1900-01-05 | 140 | 0 | 30.1487 | 0
6 | 1900-01-05 | 141 | 0 | 36.1485 | 0
6 | 1900-01-05 | 142 | 0 | 31.3935 | 0
6 | 1900-01-05 | 143 | 0 | 23.0256 | 0
6 | 1900-01-05 | 144 | 0 | 30.977 | 0
7 | 1900-01-06 | 145 | 0 | 30.4247 | 0
7 | 1900-01-06 | 146 | 0 | 28.4062 | 0
7 | 1900-01-06 | 147 | 0 | 24.3526 | 0
7 | 1900-01-06 | 148 | 0 | 31.3259 | 0
7 | 1900-01-06 | 149 | 0 | 22.6671 | 0
7 | 1900-01-06 | 150 | 0 | 22.858 | 0
7 | 1900-01-06 | 151 | 0 | 226.0971 | 0
7 | 1900-01-06 | 152 | 0 | 39.7564 | 0
7 | 1900-01-06 | 153 | 0 | 44.0862 | 0
7 | 1900-01-06 | 154 | 0 | 38.9313 | 0
7 | 1900-01-06 | 155 | 0 | 46.1114 | 0
7 | 1900-01-06 | 156 | 0 | 54.1144 | 0
7 | 1900-01-06 | 157 | 0 | 34.1323 | 0
7 | 1900-01-06 | 158 | 0 | 41.958 | 0
7 | 1900-01-06 | 159 | 0 | 40.7691 | 0
7 | 1900-01-06 | 160 | 0 | 46.6282 | 0
7 | 1900-01-06 | 161 | 0 | 42.7553 | 0
7 | 1900-01-06 | 162 | 0 | 41.2473 | 0
7 | 1900-01-06 | 163 | 0 | 51.7915 | 0
7 | 1900-01-06 | 164 | 0 | 31.3043 | 0
7 | 1900-01-06 | 165 | 0 | 34.7601 | 0
7 | 1900-01-06 | 166 | 0 | 21.5202 | 0
7 | 1900-01-06 | 167 | 0 | 23.6005 | 0
7 | 1900-01-06 | 168 | 0 | 33.523 | 0
8 | 1900-01-07 | 169 | 0 | 228.8656 | 0
8 | 1900-01-07 | 170 | 0 | 25.3045 | 0
8 | 1900-01-07 | 171 | 0 | 35.6126 | 0
8 | 1900-01-07 | 172 | 0 | 23.8576 | 0
8 | 1900-01-07 | 173 | 0 | 23.7407 | 0
8 | 1900-01-07 | 174 | 0 | 26.0575 | 0
8 | 1900-01-07 | 175 | 0 | 27.2866 | 0
8 | 1900-01-07 | 176 | 0 | 52.6294 | 0
8 | 1900-01-07 | 177 | 0 | 43.1389 | 0
8 | 1900-01-07 | 178 | 0 | 50.5542 | 0
8 | 1900-01-07 | 179 | 0 | 51.7882 | 0
8 | 1900-01-07 | 180 | 0 | 241.0379 | 0
8 | 1900-01-07 | 181 | 0 | 43.4748 | 0
8 | 1900-01-07 | 182 | 0 | 40.2777 | 0
8 | 1900-01-07 | 183 | 0 | 41.0516 | 0
8 | 1900-01-07 | 184 | 0 | 44.0272 | 0
8 | 1900-01-07 | 185 | 0 | 41.921 | 0
8 | 1900-01-07 | 186 | 0 | 42.9007 | 0
8 | 1900-01-07 | 187 | 0 | 43.9097 | 0
8 | 1900-01-07 | 188 | 0 | 25.4261 | 0
8 | 1900-01-07 | 189 | 0 | 229.0005 | 0
8 | 1900-01-07 | 190 | 0 | 34.6662 | 0
8 | 1900-01-07 | 191 | 0 | 32.2576 | 0
8 | 1900-01-07 | 192 | 0 | 32.0297 | 0
9 | 1900-01-08 | 193 | 0 | 33.0117 | 0
9 | 1900-01-08 | 194 | 0 | 24.3904 | 0
9 | 1900-01-08 | 195 | 0 | 24.2588 | 0
9 | 1900-01-08 | 196 | 0 | 30.496 | 0
9 | 1900-01-08 | 197 | 0 | 27.5075 | 0
9 | 1900-01-08 | 198 | 0 | 22.0403 | 0
9 | 1900-01-08 | 199 | 0 | 34.1844 | 0
9 | 1900-01-08 | 200 | 0 | 45.2439 | 0
9 | 1900-01-08 | 201 | 0 | 48.1079 | 0
9 | 1900-01-08 | 202 | 0 | 38.6436 | 0
9 | 1900-01-08 | 203 | 0 | 49.0646 | 0
9 | 1900-01-08 | 204 | 0 | 50.2374 | 0
9 | 1900-01-08 | 205 | 0 | 41.5301 | 0
9 | 1900-01-08 | 206 | 0 | 54.9905 | 0
9 | 1900-01-08 | 207 | 0 | 47.071 | 0
9 | 1900-01-08 | 208 | 0 | 40.3432 | 0
9 | 1900-01-08 | 209 | 0 | 25.8587 | 0
9 | 1900-01-08 | 210 | 0 | 240.5802 | 0
9 | 1900-01-08 | 211 | 0 | 51.385 | 0
9 | 1900-01-08 | 212 | 0 | 27.6282 | 0
9 | 1900-01-08 | 213 | 0 | 19.5394 | 0
9 | 1900-01-08 | 214 | 0 | 31.887 | 0
9 | 1900-01-08 | 215 | 0 | 33.5202 | 0
9 | 1900-01-08 | 216 | 0 | 36.0171 | 0
10 | 1900-01-09 | 217 | 0 | 28.021 | 0
10 | 1900-01-09 | 218 | 0 | 41.0792 | 0
10 | 1900-01-09 | 219 | 0 | 30.1636 | 0
10 | 1900-01-09 | 220 | 0 | 28.0007 | 0
10 | 1900-01-09 | 221 | 0 | 27.146 | 0
10 | 1900-01-09 | 222 | 0 | 30.2858 | 0
10 | 1900-01-09 | 223 | 0 | 30.6458 | 0
10 | 1900-01-09 | 224 | 0 | 42.6602 | 0
10 | 1900-01-09 | 225 | 0 | 52.8529 | 0
10 | 1900-01-09 | 226 | 0 | 54.5596 | 0
10 | 1900-01-09 | 227 | 0 | 34.4641 | 0
10 | 1900-01-09 | 228 | 0 | 41.5989 | 0
10 | 1900-01-09 | 229 | 0 | 43.4105 | 0
10 | 1900-01-09 | 230 | 0 | 45.9566 | 0
10 | 1900-01-09 | 231 | 0 | 34.1904 | 0
10 | 1900-01-09 | 232 | 0 | 47.7479 | 0
10 | 1900-01-09 | 233 | 0 | 55.6522 | 0
10 | 1900-01-09 | 234 | 0 | 42.5504 | 0
10 | 1900-01-09 | 235 | 0 | 46.5565 | 0
10 | 1900-01-09 | 236 | 0 | 21.2737 | 0
10 | 1900-01-09 | 237 | 0 | 29.7703 | 0
10 | 1900-01-09 | 238 | 0 | 33.3671 | 0
10 | 1900-01-09 | 239 | 0 | 24.0949 | 0
10 | 1900-01-09 | 240 | 0 | 25.7918 | 0
11 | 1900-01-10 | 241 | 0 | 29.9687 | 0
11 | 1900-01-10 | 242 | 0 | 229.5169 | 0
11 | 1900-01-10 | 243 | 0 | 29.1475 | 0
11 | 1900-01-10 | 244 | 0 | 31.0844 | 0
11 | 1900-01-10 | 245 | 0 | 229.9448 | 0
11 | 1900-01-10 | 246 | 0 | 27.6725 | 0
11 | 1900-01-10 | 247 | 0 | 33.4882 | 0
11 | 1900-01-10 | 248 | 0 | 49.3691 | 0
11 | 1900-01-10 | 249 | 0 | 30.8677 | 0
11 | 1900-01-10 | 250 | 0 | 35.6441 | 0
11 | 1900-01-10 | 251 | 0 | 54.9441 | 0
11 | 1900-01-10 | 252 | 0 | 45.4064 | 0
11 | 1900-01-10 | 253 | 0 | 28.2977 | 0
11 | 1900-01-10 | 254 | 0 | 38.5729 | 0
11 | 1900-01-10 | 255 | 0 | 35.4517 | 0
11 | 1900-01-10 | 256 | 0 | 40.0605 | 0
11 | 1900-01-10 | 257 | 0 | 34.8538 | 0
11 | 1900-01-10 | 258 | 0 | 38.0373 | 0
11 | 1900-01-10 | 259 | 0 | 42.5274 | 0
11 | 1900-01-10 | 260 | 0 | 25.3995 | 0
11 | 1900-01-10 | 261 | 0 | 28.6898 | 0
11 | 1900-01-10 | 262 | 0 | 26.68 | 0
11 | 1900-01-10 | 263 | 0 | 32.5721 | 0
11 | 1900-01-10 | 264 | 0 | 27.2078 | 0
12 | 1900-01-11 | 265 | 0 | 36.9587 | 0
12 | 1900-01-11 | 266 | 0 | 27.7303 | 0
12 | 1900-01-11 | 267 | 0 | 29.9659 | 0
12 | 1900-01-11 | 268 | 0 | 31.0686 | 0
12 | 1900-01-11 | 269 | 0 | 230.4364 | 0
12 | 1900-01-11 | 270 | 0 | 29.7964 | 0
12 | 1900-01-11 | 271 | 0 | 29.0842 | 0
12 | 1900-01-11 | 272 | 0 | 49.5716 | 0
12 | 1900-01-11 | 273 | 0 | 54.3311 | 0
12 | 1900-01-11 | 274 | 0 | 38.4665 | 0
12 | 1900-01-11 | 275 | 0 | 36.1302 | 0
12 | 1900-01-11 | 276 | 0 | 47.6277 | 0
12 | 1900-01-11 | 277 | 0 | 26.6245 | 0
12 | 1900-01-11 | 278 | 0 | 39.5272 | 0
12 | 1900-01-11 | 279 | 0 | 43.897 | 0
12 | 1900-01-11 | 280 | 0 | 47.8077 | 0
12 | 1900-01-11 | 281 | 0 | 44.7449 | 0
12 | 1900-01-11 | 282 | 0 | 46.293 | 0
12 | 1900-01-11 | 283 | 0 | 44.8239 | 0
12 | 1900-01-11 | 284 | 0 | 24.8297 | 0
12 | 1900-01-11 | 285 | 0 | 26.8345 | 0
12 | 1900-01-11 | 286 | 0 | 32.4557 | 0
12 | 1900-01-11 | 287 | 0 | 25.1488 | 0
12 | 1900-01-11 | 288 | 0 | 28.9378 | 0
13 | 1900-01-12 | 289 | 0 | 28.351 | 0
13 | 1900-01-12 | 290 | 0 | 24.858 | 0
13 | 1900-01-12 | 291 | 0 | 34.4758 | 0
13 | 1900-01-12 | 292 | 0 | 29.2364 | 0
13 | 1900-01-12 | 293 | 0 | 26.0787 | 0
13 | 1900-01-12 | 294 | 0 | 25.1098 | 0
13 | 1900-01-12 | 295 | 0 | 32.6647 | 0
13 | 1900-01-12 | 296 | 0 | 39.8042 | 0
13 | 1900-01-12 | 297 | 0 | 54.5725 | 0
13 | 1900-01-12 | 298 | 0 | 52.0711 | 0
13 | 1900-01-12 | 299 | 0 | 34.9701 | 0
13 | 1900-01-12 | 300 | 0 | 54.6123 | 0
13 | 1900-01-12 | 301 | 0 | 43.6734 | 0
13 | 1900-01-12 | 302 | 0 | 452.8076 | 0
13 | 1900-01-12 | 303 | 0 | 43.0241 | 0
13 | 1900-01-12 | 304 | 0 | 39.5461 | 0
13 | 1900-01-12 | 305 | 0 | 49.749 | 0
13 | 1900-01-12 | 306 | 0 | 32.325 | 0
13 | 1900-01-12 | 307 | 0 | 40.1412 | 0
13 | 1900-01-12 | 308 | 0 | 33.0661 | 0
13 | 1900-01-12 | 309 | 0 | 30.2421 | 0
13 | 1900-01-12 | 310 | 0 | 22.2817 | 0
13 | 1900-01-12 | 311 | 0 | 28.1395 | 0
13 | 1900-01-12 | 312 | 0 | 26.3932 | 0
14 | 1900-01-13 | 313 | 0 | 38.3196 | 0
14 | 1900-01-13 | 314 | 0 | 29.669 | 0
14 | 1900-01-13 | 315 | 0 | 27.646 | 0
14 | 1900-01-13 | 316 | 0 | 33.1385 | 0
14 | 1900-01-13 | 317 | 0 | 23.683 | 0
14 | 1900-01-13 | 318 | 0 | 25.2497 | 0
14 | 1900-01-13 | 319 | 0 | 31.1686 | 0
14 | 1900-01-13 | 320 | 0 | 43.3721 | 0
14 | 1900-01-13 | 321 | 0 | 50.3204 | 0
14 | 1900-01-13 | 322 | 0 | 45.8122 | 0
14 | 1900-01-13 | 323 | 0 | 46.7834 | 0
14 | 1900-01-13 | 324 | 0 | 42.5473 | 0
14 | 1900-01-13 | 325 | 0 | 50.8058 | 0
14 | 1900-01-13 | 326 | 0 | 50.03 | 0
14 | 1900-01-13 | 327 | 0 | 40.7372 | 0
14 | 1900-01-13 | 328 | 0 | 51.8051 | 0
14 | 1900-01-13 | 329 | 0 | 244.6048 | 0
14 | 1900-01-13 | 330 | 0 | 40.1052 | 0
14 | 1900-01-13 | 331 | 0 | 46.6648 | 0
14 | 1900-01-13 | 332 | 0 | 28.7799 | 0
14 | 1900-01-13 | 333 | 0 | 27.929 | 0
14 | 1900-01-13 | 334 | 0 | 25.9792 | 0
14 | 1900-01-13 | 335 | 0 | 25.5159 | 0
14 | 1900-01-13 | 336 | 0 | 27.8932 | 0
15 | 1900-01-14 | 337 | 0 | 26.0457 | 0
15 | 1900-01-14 | 338 | 0 | 23.4963 | 0
15 | 1900-01-14 | 339 | 0 | 23.1824 | 0
15 | 1900-01-14 | 340 | 0 | 32.0736 | 0
15 | 1900-01-14 | 341 | 0 | 24.4647 | 0
15 | 1900-01-14 | 342 | 0 | 38.4082 | 0
15 | 1900-01-14 | 343 | 0 | 30.9335 | 0
15 | 1900-01-14 | 344 | 0 | 42.7928 | 0
15 | 1900-01-14 | 345 | 0 | 54.5577 | 0
15 | 1900-01-14 | 346 | 0 | 42.2026 | 0
15 | 1900-01-14 | 347 | 0 | 41.3912 | 0
15 | 1900-01-14 | 348 | 0 | 41.7165 | 0
15 | 1900-01-14 | 349 | 0 | 47.9135 | 0
15 | 1900-01-14 | 350 | 0 | 29.2914 | 0
15 | 1900-01-14 | 351 | 0 | 46.3217 | 0
15 | 1900-01-14 | 352 | 0 | 51.2278 | 0
15 | 1900-01-14 | 353 | 0 | 28.1498 | 0
15 | 1900-01-14 | 354 | 0 | 30.7991 | 0
15 | 1900-01-14 | 355 | 0 | 37.9944 | 0
15 | 1900-01-14 | 356 | 0 | 29.6628 | 0
15 | 1900-01-14 | 357 | 0 | 26.6537 | 0
15 | 1900-01-14 | 358 | 0 | 27.4278 | 0
15 | 1900-01-14 | 359 | 0 | 29.1334 | 0
15 | 1900-01-14 | 360 | 0 | 224.1588 | 0
16 | 1900-01-15 | 361 | 0 | 28.7125 | 0
16 | 1900-01-15 | 362 | 0 | 222.6216 | 0
16 | 1900-01-15 | 363 | 0 | 20.8378 | 0
16 | 1900-01-15 | 364 | 0 | 26.5316 | 0
16 | 1900-01-15 | 365 | 0 | 28.2154 | 0
16 | 1900-01-15 | 366 | 0 | 29.3027 | 0
16 | 1900-01-15 | 367 | 0 | 32.4015 | 0
16 | 1900-01-15 | 368 | 0 | 44.9524 | 0
16 | 1900-01-15 | 369 | 0 | 38.9096 | 0
16 | 1900-01-15 | 370 | 0 | 45.1064 | 0
16 | 1900-01-15 | 371 | 0 | 38.1916 | 0
16 | 1900-01-15 | 372 | 0 | 26.4661 | 0
16 | 1900-01-15 | 373 | 0 | 60.2435 | 0
16 | 1900-01-15 | 374 | 0 | 34.0384 | 0
16 | 1900-01-15 | 375 | 0 | 36.8046 | 0
16 | 1900-01-15 | 376 | 0 | 47.3114 | 0
16 | 1900-01-15 | 377 | 0 | 44.5228 | 0
16 | 1900-01-15 | 378 | 0 | 57.7534 | 0
16 | 1900-01-15 | 379 | 0 | 41.5012 | 0
16 | 1900-01-15 | 380 | 0 | 31.717 | 0
16 | 1900-01-15 | 381 | 0 | 27.5847 | 0
16 | 1900-01-15 | 382 | 0 | 26.3845 | 0
16 | 1900-01-15 | 383 | 0 | 23.1147 | 0
16 | 1900-01-15 | 384 | 0 | 225.928 | 0
17 | 1900-01-16 | 385 | 0 | 18.0538 | 0
17 | 1900-01-16 | 386 | 0 | 28.6275 | 0
17 | 1900-01-16 | 387 | 0 | 28.882 | 0
17 | 1900-01-16 | 388 | 0 | 26.4434 | 0
17 | 1900-01-16 | 389 | 0 | 27.9837 | 0
17 | 1900-01-16 | 390 | 0 | 37.1355 | 0
17 | 1900-01-16 | 391 | 0 | 28.4755 | 0
17 | 1900-01-16 | 392 | 0 | 39.7175 | 0
17 | 1900-01-16 | 393 | 0 | 43.9915 | 0
17 | 1900-01-16 | 394 | 0 | 38.4562 | 0
17 | 1900-01-16 | 395 | 0 | 38.615 | 0
17 | 1900-01-16 | 396 | 0 | 42.8996 | 0
17 | 1900-01-16 | 397 | 0 | 27.8984 | 0
17 | 1900-01-16 | 398 | 0 | 33.8755 | 0
17 | 1900-01-16 | 399 | 0 | 45.4069 | 0
17 | 1900-01-16 | 400 | 0 | 47.8644 | 0
17 | 1900-01-16 | 401 | 0 | 30.5519 | 0
17 | 1900-01-16 | 402 | 0 | 46.3837 | 0
17 | 1900-01-16 | 403 | 0 | 40.8735 | 0
17 | 1900-01-16 | 404 | 0 | 19.4599 | 0
17 | 1900-01-16 | 405 | 0 | 25.8481 | 0
17 | 1900-01-16 | 406 | 0 | 25.161 | 0
17 | 1900-01-16 | 407 | 0 | 25.1178 | 0
17 | 1900-01-16 | 408 | 0 | 29.8766 | 0
18 | 1900-01-17 | 409 | 0 | 32.6216 | 0
18 | 1900-01-17 | 410 | 0 | 228.5986 | 0
18 | 1900-01-17 | 411 | 0 | 24.9925 | 0
18 | 1900-01-17 | 412 | 0 | 30.1636 | 0
18 | 1900-01-17 | 413 | 0 | 26.6804 | 0
18 | 1900-01-17 | 414 | 0 | 35.4311 | 0
18 | 1900-01-17 | 415 | 0 | 27.2988 | 0
18 | 1900-01-17 | 416 | 0 | 46.6907 | 0
18 | 1900-01-17 | 417 | 0 | 35.5752 | 0
18 | 1900-01-17 | 418 | 0 | 45.1896 | 0
18 | 1900-01-17 | 419 | 0 | 39.6697 | 0
18 | 1900-01-17 | 420 | 0 | 42.6932 | 0
18 | 1900-01-17 | 421 | 0 | 35.533 | 0
18 | 1900-01-17 | 422 | 0 | 243.5502 | 0
18 | 1900-01-17 | 423 | 0 | 38.6839 | 0
18 | 1900-01-17 | 424 | 0 | 35.5798 | 0
18 | 1900-01-17 | 425 | 0 | 36.0995 | 0
18 | 1900-01-17 | 426 | 0 | 54.8848 | 0
18 | 1900-01-17 | 427 | 0 | 40.5868 | 0
18 | 1900-01-17 | 428 | 0 | 28.6639 | 0
18 | 1900-01-17 | 429 | 0 | 31.2309 | 0
18 | 1900-01-17 | 430 | 0 | 21.9569 | 0
18 | 1900-01-17 | 431 | 0 | 25.6488 | 0
18 | 1900-01-17 | 432 | 0 | 27.8855 | 0
19 | 1900-01-18 | 433 | 0 | 31.0568 | 0
19 | 1900-01-18 | 434 | 0 | 223.5638 | 0
19 | 1900-01-18 | 435 | 0 | 29.576 | 0
19 | 1900-01-18 | 436 | 0 | 22.1916 | 0
19 | 1900-01-18 | 437 | 0 | 28.8184 | 0
19 | 1900-01-18 | 438 | 0 | 31.8114 | 0
19 | 1900-01-18 | 439 | 0 | 26.8685 | 0
19 | 1900-01-18 | 440 | 0 | 29.667 | 0
19 | 1900-01-18 | 441 | 0 | 52.0084 | 0
19 | 1900-01-18 | 442 | 0 | 44.1484 | 0
19 | 1900-01-18 | 443 | 0 | 37.1508 | 0
19 | 1900-01-18 | 444 | 0 | 47.7366 | 0
19 | 1900-01-18 | 445 | 0 | 44.651 | 0
19 | 1900-01-18 | 446 | 0 | 43.4521 | 0
19 | 1900-01-18 | 447 | 0 | 40.3799 | 0
19 | 1900-01-18 | 448 | 0 | 41.7261 | 0
19 | 1900-01-18 | 449 | 0 | 31.9703 | 0
19 | 1900-01-18 | 450 | 0 | 43.717 | 0
19 | 1900-01-18 | 451 | 0 | 47.2854 | 0
19 | 1900-01-18 | 452 | 0 | 33.1457 | 0
19 | 1900-01-18 | 453 | 0 | 24.3136 | 0
19 | 1900-01-18 | 454 | 0 | 34.9431 | 0
19 | 1900-01-18 | 455 | 0 | 27.0448 | 0
19 | 1900-01-18 | 456 | 0 | 32.6608 | 0
20 | 1900-01-19 | 457 | 0 | 32.6593 | 0
20 | 1900-01-19 | 458 | 0 | 22.2466 | 0
20 | 1900-01-19 | 459 | 0 | 27.7585 | 0
20 | 1900-01-19 | 460 | 0 | 219.481 | 0
20 | 1900-01-19 | 461 | 0 | 33.4539 | 0
20 | 1900-01-19 | 462 | 0 | 25.7861 | 0
20 | 1900-01-19 | 463 | 0 | 27.1068 | 0
20 | 1900-01-19 | 464 | 0 | 40.8722 | 0
20 | 1900-01-19 | 465 | 0 | 38.8998 | 0
20 | 1900-01-19 | 466 | 0 | 46.9709 | 0
20 | 1900-01-19 | 467 | 0 | 50.5895 | 0
20 | 1900-01-19 | 468 | 0 | 46.4616 | 0
20 | 1900-01-19 | 469 | 0 | 38.264 | 0
20 | 1900-01-19 | 470 | 0 | 46.9616 | 0
20 | 1900-01-19 | 471 | 0 | 45.3184 | 0
20 | 1900-01-19 | 472 | 0 | 46.5014 | 0
20 | 1900-01-19 | 473 | 0 | 43.866 | 0
20 | 1900-01-19 | 474 | 0 | 45.1152 | 0
20 | 1900-01-19 | 475 | 0 | 31.8667 | 0
20 | 1900-01-19 | 476 | 0 | 29.4772 | 0
20 | 1900-01-19 | 477 | 0 | 28.5616 | 0
20 | 1900-01-19 | 478 | 0 | 25.0183 | 0
20 | 1900-01-19 | 479 | 0 | 27.6388 | 0
20 | 1900-01-19 | 480 | 0 | 33.5992 | 0
21 | 1900-01-20 | 481 | 0 | 25.0849 | 0
21 | 1900-01-20 | 482 | 0 | 228.2249 | 0
21 | 1900-01-20 | 483 | 0 | 26.7338 | 0
21 | 1900-01-20 | 484 | 0 | 37.3053 | 0
21 | 1900-01-20 | 485 | 0 | 35.9388 | 0
21 | 1900-01-20 | 486 | 0 | 35.081 | 0
21 | 1900-01-20 | 487 | 0 | 229.5625 | 0
21 | 1900-01-20 | 488 | 0 | 58.7912 | 0
21 | 1900-01-20 | 489 | 0 | 35.6246 | 0
21 | 1900-01-20 | 490 | 0 | 47.9294 | 0
21 | 1900-01-20 | 491 | 0 | 40.9674 | 0
21 | 1900-01-20 | 492 | 0 | 48.1968 | 0
21 | 1900-01-20 | 493 | 0 | 34.4666 | 0
21 | 1900-01-20 | 494 | 0 | 51.0626 | 0
21 | 1900-01-20 | 495 | 0 | 41.8285 | 0
21 | 1900-01-20 | 496 | 0 | 49.594 | 0
21 | 1900-01-20 | 497 | 0 | 47.7888 | 0
21 | 1900-01-20 | 498 | 0 | 42.4315 | 0
21 | 1900-01-20 | 499 | 0 | 42.167 | 0
21 | 1900-01-20 | 500 | 0 | 31.6926 | 0
21 | 1900-01-20 | 501 | 0 | 32.3568 | 0
21 | 1900-01-20 | 502 | 0 | 28.9903 | 0
21 | 1900-01-20 | 503 | 0 | 35.4996 | 0
21 | 1900-01-20 | 504 | 0 | 37.1881 | 0
22 | 1900-01-21 | 505 | 0 | 32.0932 | 0
22 | 1900-01-21 | 506 | 0 | 23.4575 | 0
22 | 1900-01-21 | 507 | 0 | 34.6788 | 0
22 | 1900-01-21 | 508 | 0 | 26.4522 | 0
22 | 1900-01-21 | 509 | 0 | 27.7879 | 0
22 | 1900-01-21 | 510 | 0 | 37.4635 | 0
22 | 1900-01-21 | 511 | 0 | 28.4818 | 0
22 | 1900-01-21 | 512 | 0 | 252.56 | 0
22 | 1900-01-21 | 513 | 0 | 50.9635 | 0
22 | 1900-01-21 | 514 | 0 | 39.8017 | 0
22 | 1900-01-21 | 515 | 0 | 25.6067 | 0
22 | 1900-01-21 | 516 | 0 | 48.857 | 0
22 | 1900-01-21 | 517 | 0 | 42.8959 | 0
22 | 1900-01-21 | 518 | 0 | 50.8611 | 0
22 | 1900-01-21 | 519 | 0 | 31.5537 | 0
22 | 1900-01-21 | 520 | 0 | 45.8317 | 0
22 | 1900-01-21 | 521 | 0 | 33.9808 | 0
22 | 1900-01-21 | 522 | 0 | 51.0422 | 0
22 | 1900-01-21 | 523 | 0 | 49.0618 | 0
22 | 1900-01-21 | 524 | 0 | 28.4429 | 0
22 | 1900-01-21 | 525 | 0 | 28.7806 | 0
22 | 1900-01-21 | 526 | 0 | 35.0889 | 0
22 | 1900-01-21 | 527 | 0 | 27.3671 | 0
22 | 1900-01-21 | 528 | 0 | 38.4743 | 0
23 | 1900-01-22 | 529 | 0 | 22.8722 | 0
23 | 1900-01-22 | 530 | 0 | 26.6235 | 0
23 | 1900-01-22 | 531 | 0 | 19.6632 | 0
23 | 1900-01-22 | 532 | 0 | 29.835 | 0
23 | 1900-01-22 | 533 | 0 | 24.3884 | 0
23 | 1900-01-22 | 534 | 0 | 22.2841 | 0
23 | 1900-01-22 | 535 | 0 | 30.2185 | 0
23 | 1900-01-22 | 536 | 0 | 44.2324 | 0
23 | 1900-01-22 | 537 | 0 | 39.2411 | 0
23 | 1900-01-22 | 538 | 0 | 48.1178 | 0
23 | 1900-01-22 | 539 | 0 | 45.0172 | 0
23 | 1900-01-22 | 540 | 0 | 48.1857 | 0
23 | 1900-01-22 | 541 | 0 | 39.4235 | 0
23 | 1900-01-22 | 542 | 0 | 236.4306 | 0
23 | 1900-01-22 | 543 | 0 | 48.2079 | 0
23 | 1900-01-22 | 544 | 0 | 39.3884 | 0
23 | 1900-01-22 | 545 | 0 | 45.9874 | 0
23 | 1900-01-22 | 546 | 0 | 54.9375 | 0
23 | 1900-01-22 | 547 | 0 | 36.1348 | 0
23 | 1900-01-22 | 548 | 0 | 26.3085 | 0
23 | 1900-01-22 | 549 | 0 | 26.6251 | 0
23 | 1900-01-22 | 550 | 0 | 34.3396 | 0
23 | 1900-01-22 | 551 | 0 | 31.6426 | 0
23 | 1900-01-22 | 552 | 0 | 33.4594 | 0
24 | 1900-01-23 | 553 | 0 | 30.141 | 0
24 | 1900-01-23 | 554 | 0 | 29.2071 | 0
24 | 1900-01-23 | 555 | 0 | 31.9416 | 0
24 | 1900-01-23 | 556 | 0 | 30.5551 | 0
24 | 1900-01-23 | 557 | 0 | 29.2203 | 0
24 | 1900-01-23 | 558 | 0 | 35.2845 | 0
24 | 1900-01-23 | 559 | 0 | 30.8354 | 0
24 | 1900-01-23 | 560 | 0 | 52.2748 | 0
24 | 1900-01-23 | 561 | 0 | 34.4573 | 0
24 | 1900-01-23 | 562 | 0 | 47.8602 | 0
24 | 1900-01-23 | 563 | 0 | 255.7495 | 0
24 | 1900-01-23 | 564 | 0 | 44.5893 | 0
24 | 1900-01-23 | 565 | 0 | 39.3016 | 0
24 | 1900-01-23 | 566 | 0 | 50.6084 | 0
24 | 1900-01-23 | 567 | 0 | 60.8995 | 0
24 | 1900-01-23 | 568 | 0 | 52.3037 | 0
24 | 1900-01-23 | 569 | 0 | 36.4347 | 0
24 | 1900-01-23 | 570 | 0 | 55.9964 | 0
24 | 1900-01-23 | 571 | 0 | 46.8078 | 0
24 | 1900-01-23 | 572 | 0 | 30.2214 | 0
24 | 1900-01-23 | 573 | 0 | 30.6821 | 0
24 | 1900-01-23 | 574 | 0 | 19.7733 | 0
24 | 1900-01-23 | 575 | 0 | 29.8276 | 0
24 | 1900-01-23 | 576 | 0 | 29.3929 | 0
25 | 1900-01-24 | 577 | 0 | 27.8476 | 0
25 | 1900-01-24 | 578 | 0 | 26.4636 | 0
25 | 1900-01-24 | 579 | 0 | 23.5852 | 0
25 | 1900-01-24 | 580 | 0 | 22.7515 | 0
25 | 1900-01-24 | 581 | 0 | 29.1842 | 0
25 | 1900-01-24 | 582 | 0 | 26.3707 | 0
25 | 1900-01-24 | 583 | 0 | 25.1949 | 0
25 | 1900-01-24 | 584 | 0 | 41.5541 | 0
25 | 1900-01-24 | 585 | 0 | 46.4509 | 0
25 | 1900-01-24 | 586 | 0 | 32.7913 | 0
25 | 1900-01-24 | 587 | 0 | 34.586 | 0
25 | 1900-01-24 | 588 | 0 | 47.6387 | 0
25 | 1900-01-24 | 589 | 0 | 46.2206 | 0
25 | 1900-01-24 | 590 | 0 | 43.9036 | 0
25 | 1900-01-24 | 591 | 0 | 43.586 | 0
25 | 1900-01-24 | 592 | 0 | 50.4673 | 0
25 | 1900-01-24 | 593 | 0 | 46.9018 | 0
25 | 1900-01-24 | 594 | 0 | 31.8215 | 0
25 | 1900-01-24 | 595 | 0 | 36.0014 | 0
25 | 1900-01-24 | 596 | 0 | 32.1708 | 0
25 | 1900-01-24 | 597 | 0 | 26.9408 | 0
25 | 1900-01-24 | 598 | 0 | 23.3208 | 0
25 | 1900-01-24 | 599 | 0 | 23.849 | 0
25 | 1900-01-24 | 600 | 0 | 26.3956 | 0
26 | 1900-01-25 | 601 | 0 | 24.1461 | 0
26 | 1900-01-25 | 602 | 0 | 29.7635 | 0
26 | 1900-01-25 | 603 | 0 | 230.1806 | 0
26 | 1900-01-25 | 604 | 0 | 34.3061 | 0
26 | 1900-01-25 | 605 | 0 | 35.7783 | 0
26 | 1900-01-25 | 606 | 0 | 225.6449 | 0
26 | 1900-01-25 | 607 | 0 | 20.5303 | 0
26 | 1900-01-25 | 608 | 0 | 43.0221 | 0
26 | 1900-01-25 | 609 | 0 | 57.2012 | 0
26 | 1900-01-25 | 610 | 0 | 31.1815 | 0
26 | 1900-01-25 | 611 | 0 | 55.0157 | 0
26 | 1900-01-25 | 612 | 0 | 38.7594 | 0
26 | 1900-01-25 | 613 | 0 | 46.2114 | 0
26 | 1900-01-25 | 614 | 0 | 41.9285 | 0
26 | 1900-01-25 | 615 | 0 | 32.3537 | 0
26 | 1900-01-25 | 616 | 0 | 39.2805 | 0
26 | 1900-01-25 | 617 | 0 | 47.972 | 0
26 | 1900-01-25 | 618 | 0 | 35.0916 | 0
26 | 1900-01-25 | 619 | 0 | 51.2306 | 0
26 | 1900-01-25 | 620 | 0 | 31.4108 | 0
26 | 1900-01-25 | 621 | 0 | 30.1674 | 0
26 | 1900-01-25 | 622 | 0 | 27.2466 | 0
26 | 1900-01-25 | 623 | 0 | 31.0404 | 0
26 | 1900-01-25 | 624 | 0 | 27.1061 | 0
27 | 1900-01-26 | 625 | 0 | 25.322 | 0
27 | 1900-01-26 | 626 | 0 | 34.7981 | 0
27 | 1900-01-26 | 627 | 0 | 23.1989 | 0
27 | 1900-01-26 | 628 | 0 | 27.2568 | 0
27 | 1900-01-26 | 629 | 0 | 30.4834 | 0
27 | 1900-01-26 | 630 | 0 | 29.3472 | 0
27 | 1900-01-26 | 631 | 0 | 31.6479 | 0
27 | 1900-01-26 | 632 | 0 | 48.2197 | 0
27 | 1900-01-26 | 633 | 0 | 40.666 | 0
27 | 1900-01-26 | 634 | 0 | 30.9855 | 0
27 | 1900-01-26 | 635 | 0 | 48.4308 | 0
27 | 1900-01-26 | 636 | 0 | 32.3611 | 0
27 | 1900-01-26 | 637 | 0 | 54.931 | 0
27 | 1900-01-26 | 638 | 0 | 59.1787 | 0
27 | 1900-01-26 | 639 | 0 | 29.8432 | 0
27 | 1900-01-26 | 640 | 0 | 53.9323 | 0
27 | 1900-01-26 | 641 | 0 | 39.7132 | 0
27 | 1900-01-26 | 642 | 0 | 44.2596 | 0
27 | 1900-01-26 | 643 | 0 | 43.0407 | 0
27 | 1900-01-26 | 644 | 0 | 26.3463 | 0
27 | 1900-01-26 | 645 | 0 | 28.7287 | 0
27 | 1900-01-26 | 646 | 0 | 31.9707 | 0
27 | 1900-01-26 | 647 | 0 | 26.4573 | 0
27 | 1900-01-26 | 648 | 0 | 38.6188 | 0
28 | 1900-01-27 | 649 | 0 | 31.0334 | 0
28 | 1900-01-27 | 650 | 0 | 35.2486 | 0
28 | 1900-01-27 | 651 | 0 | 27.121 | 0
28 | 1900-01-27 | 652 | 0 | 29.3082 | 0
28 | 1900-01-27 | 653 | 0 | 28.6285 | 0
28 | 1900-01-27 | 654 | 0 | 225.7937 | 0
28 | 1900-01-27 | 655 | 0 | 24.7345 | 0
28 | 1900-01-27 | 656 | 0 | 44.1933 | 0
28 | 1900-01-27 | 657 | 0 | 38.2682 | 0
28 | 1900-01-27 | 658 | 0 | 41.3874 | 0
28 | 1900-01-27 | 659 | 0 | 41.6475 | 0
28 | 1900-01-27 | 660 | 0 | 46.7255 | 0
28 | 1900-01-27 | 661 | 0 | 37.8249 | 0
28 | 1900-01-27 | 662 | 0 | 52.261 | 0
28 | 1900-01-27 | 663 | 0 | 37.5801 | 0
28 | 1900-01-27 | 664 | 0 | 237.1252 | 0
28 | 1900-01-27 | 665 | 0 | 25.5135 | 0
28 | 1900-01-27 | 666 | 0 | 35.0769 | 0
28 | 1900-01-27 | 667 | 0 | 35.1314 | 0
28 | 1900-01-27 | 668 | 0 | 36.1082 | 0
28 | 1900-01-27 | 669 | 0 | 34.3977 | 0
28 | 1900-01-27 | 670 | 0 | 29.1056 | 0
28 | 1900-01-27 | 671 | 0 | 28.4642 | 0
28 | 1900-01-27 | 672 | 0 | 34.7335 | 0
29 | 1900-01-28 | 673 | 0 | 26.9206 | 0
29 | 1900-01-28 | 674 | 0 | 30.4782 | 0
29 | 1900-01-28 | 675 | 0 | 28.3494 | 0
29 | 1900-01-28 | 676 | 0 | 30.1916 | 0
29 | 1900-01-28 | 677 | 0 | 28.6293 | 0
29 | 1900-01-28 | 678 | 0 | 32.9765 | 0
29 | 1900-01-28 | 679 | 0 | 24.2772 | 0
29 | 1900-01-28 | 680 | 0 | 36.1468 | 0
29 | 1900-01-28 | 681 | 0 | 34.0107 | 0
29 | 1900-01-28 | 682 | 0 | 42.8377 | 0
29 | 1900-01-28 | 683 | 0 | 69.8699 | 0
29 | 1900-01-28 | 684 | 0 | 32.4136 | 0
29 | 1900-01-28 | 685 | 0 | 49.7578 | 0
29 | 1900-01-28 | 686 | 0 | 34.1743 | 0
29 | 1900-01-28 | 687 | 0 | 46.1379 | 0
29 | 1900-01-28 | 688 | 0 | 48.8282 | 0
29 | 1900-01-28 | 689 | 0 | 53.6402 | 0
29 | 1900-01-28 | 690 | 0 | 33.0301 | 0
29 | 1900-01-28 | 691 | 0 | 37.1868 | 0
29 | 1900-01-28 | 692 | 0 | 24.4988 | 0
29 | 1900-01-28 | 693 | 0 | 30.8055 | 0
29 | 1900-01-28 | 694 | 0 | 27.6854 | 0
29 | 1900-01-28 | 695 | 0 | 27.3404 | 0
29 | 1900-01-28 | 696 | 0 | 34.6376 | 0
30 | 1900-01-29 | 697 | 0 | 25.831 | 0
30 | 1900-01-29 | 698 | 0 | 26.8909 | 0
30 | 1900-01-29 | 699 | 0 | 228.3825 | 0
30 | 1900-01-29 | 700 | 0 | 33.6378 | 0
30 | 1900-01-29 | 701 | 0 | 22.4672 | 0
30 | 1900-01-29 | 702 | 0 | 35.39 | 0
30 | 1900-01-29 | 703 | 0 | 40.2739 | 0
30 | 1900-01-29 | 704 | 0 | 40.3111 | 0
30 | 1900-01-29 | 705 | 0 | 43.6914 | 0
30 | 1900-01-29 | 706 | 0 | 50.5462 | 0
30 | 1900-01-29 | 707 | 0 | 46.6464 | 0
30 | 1900-01-29 | 708 | 0 | 45.9565 | 0
30 | 1900-01-29 | 709 | 0 | 52.8245 | 0
30 | 1900-01-29 | 710 | 0 | 42.5111 | 0
30 | 1900-01-29 | 711 | 0 | 37.7791 | 0
30 | 1900-01-29 | 712 | 0 | 46.76 | 0
30 | 1900-01-29 | 713 | 0 | 39.0911 | 0
30 | 1900-01-29 | 714 | 0 | 41.9424 | 0
30 | 1900-01-29 | 715 | 0 | 51.6467 | 0
30 | 1900-01-29 | 716 | 0 | 28.7625 | 0
30 | 1900-01-29 | 717 | 0 | 27.6442 | 0
30 | 1900-01-29 | 718 | 0 | 24.1373 | 0
30 | 1900-01-29 | 719 | 0 | 23.9933 | 0
30 | 1900-01-29 | 720 | 0 | 34.2359 | 0
31 | 1900-01-30 | 721 | 0 | 25.8696 | 0
31 | 1900-01-30 | 722 | 0 | 27.0007 | 0
31 | 1900-01-30 | 723 | 0 | 29.368 | 0
31 | 1900-01-30 | 724 | 0 | 26.95 | 0
31 | 1900-01-30 | 725 | 0 | 223.8102 | 0
31 | 1900-01-30 | 726 | 0 | 23.2456 | 0
31 | 1900-01-30 | 727 | 0 | 19.5995 | 0
31 | 1900-01-30 | 728 | 0 | 43.3442 | 0
31 | 1900-01-30 | 729 | 0 | 32.5526 | 0
31 | 1900-01-30 | 730 | 0 | 236.7928 | 0
31 | 1900-01-30 | 731 | 0 | 36.9844 | 0
31 | 1900-01-30 | 732 | 0 | 46.57 | 0
31 | 1900-01-30 | 733 | 0 | 46.2068 | 0
31 | 1900-01-30 | 734 | 0 | 28.3922 | 0
31 | 1900-01-30 | 735 | 0 | 38.7682 | 0
31 | 1900-01-30 | 736 | 0 | 38.9071 | 0
31 | 1900-01-30 | 737 | 0 | 35.8076 | 0
31 | 1900-01-30 | 738 | 0 | 37.3653 | 0
31 | 1900-01-30 | 739 | 0 | 50.7992 | 0
31 | 1900-01-30 | 740 | 0 | 31.9679 | 0
31 | 1900-01-30 | 741 | 0 | 26.9057 | 0
31 | 1900-01-30 | 742 | 0 | 18.6215 | 0
31 | 1900-01-30 | 743 | 0 | 37.4248 | 0
31 | 1900-01-30 | 744 | 0 | 31.8545 | 0
32 | 1900-01-31 | 745 | 0 | 27.7504 | 0
32 | 1900-01-31 | 746 | 0 | 29.4674 | 0
32 | 1900-01-31 | 747 | 0 | 21.0133 | 0
32 | 1900-01-31 | 748 | 0 | 26.8104 | 0
32 | 1900-01-31 | 749 | 0 | 19.0031 | 0
32 | 1900-01-31 | 750 | 0 | 30.8492 | 0
32 | 1900-01-31 | 751 | 0 | 29.3011 | 0
32 | 1900-01-31 | 752 | 0 | 236.7833 | 0
32 | 1900-01-31 | 753 | 0 | 54.0525 | 0
32 | 1900-01-31 | 754 | 0 | 49.5317 | 0
32 | 1900-01-31 | 755 | 0 | 36.5187 | 0
32 | 1900-01-31 | 756 | 0 | 37.3961 | 0
32 | 1900-01-31 | 757 | 0 | 42.5789 | 0
32 | 1900-01-31 | 758 | 0 | 38.4489 | 0
32 | 1900-01-31 | 759 | 0 | 48.9233 | 0
32 | 1900-01-31 | 760 | 0 | 42.0748 | 0
32 | 1900-01-31 | 761 | 0 | 51.2819 | 0
32 | 1900-01-31 | 762 | 0 | 54.2755 | 0
32 | 1900-01-31 | 763 | 0 | 37.7718 | 0
32 | 1900-01-31 | 764 | 0 | 29.0436 | 0
32 | 1900-01-31 | 765 | 0 | 29.1626 | 0
32 | 1900-01-31 | 766 | 0 | 23.8339 | 0
32 | 1900-01-31 | 767 | 0 | 27.2169 | 0
32 | 1900-01-31 | 768 | 0 | 24.0932 | 0
33 | 1900-02-01 | 769 | 0 | 37.6227 | 0
33 | 1900-02-01 | 770 | 0 | 22.4747 | 0
33 | 1900-02-01 | 771 | 0 | 25.3056 | 0
33 | 1900-02-01 | 772 | 0 | 30.016 | 0
33 | 1900-02-01 | 773 | 0 | 25.4587 | 0
33 | 1900-02-01 | 774 | 0 | 25.1725 | 0
33 | 1900-02-01 | 775 | 0 | 20.1159 | 0
33 | 1900-02-01 | 776 | 0 | 49.0612 | 0
33 | 1900-02-01 | 777 | 0 | 39.0939 | 0
33 | 1900-02-01 | 778 | 0 | 241.0984 | 0
33 | 1900-02-01 | 779 | 0 | 38.4031 | 0
33 | 1900-02-01 | 780 | 0 | 60.9302 | 0
33 | 1900-02-01 | 781 | 0 | 36.0732 | 0
33 | 1900-02-01 | 782 | 0 | 43.6851 | 0
33 | 1900-02-01 | 783 | 0 | 25.37 | 0
33 | 1900-02-01 | 784 | 0 | 39.0545 | 0
33 | 1900-02-01 | 785 | 0 | 47.5025 | 0
33 | 1900-02-01 | 786 | 0 | 45.0717 | 0
33 | 1900-02-01 | 787 | 0 | 244.1567 | 0
33 | 1900-02-01 | 788 | 0 | 27.0043 | 0
33 | 1900-02-01 | 789 | 0 | 23.9091 | 0
33 | 1900-02-01 | 790 | 0 | 26.7609 | 0
33 | 1900-02-01 | 791 | 0 | 31.1597 | 0
33 | 1900-02-01 | 792 | 0 | 23.9608 | 0
34 | 1900-02-02 | 793 | 0 | 27.5059 | 0
34 | 1900-02-02 | 794 | 0 | 26.1358 | 0
34 | 1900-02-02 | 795 | 0 | 31.3816 | 0
34 | 1900-02-02 | 796 | 0 | 20.1976 | 0
34 | 1900-02-02 | 797 | 0 | 22.75 | 0
34 | 1900-02-02 | 798 | 0 | 28.7945 | 0
34 | 1900-02-02 | 799 | 0 | 29.0732 | 0
34 | 1900-02-02 | 800 | 0 | 41.6938 | 0
34 | 1900-02-02 | 801 | 0 | 35.5276 | 0
34 | 1900-02-02 | 802 | 0 | 43.0105 | 0
34 | 1900-02-02 | 803 | 0 | 36.8126 | 0
34 | 1900-02-02 | 804 | 0 | 47.7247 | 0
34 | 1900-02-02 | 805 | 0 | 41.086 | 0
34 | 1900-02-02 | 806 | 0 | 237.5692 | 0
34 | 1900-02-02 | 807 | 0 | 46.9677 | 0
34 | 1900-02-02 | 808 | 0 | 30.4098 | 0
34 | 1900-02-02 | 809 | 0 | 48.7209 | 0
34 | 1900-02-02 | 810 | 0 | 48.0649 | 0
34 | 1900-02-02 | 811 | 0 | 47.478 | 0
34 | 1900-02-02 | 812 | 0 | 18.8247 | 0
34 | 1900-02-02 | 813 | 0 | 23.5602 | 0
34 | 1900-02-02 | 814 | 0 | 27.4282 | 0
34 | 1900-02-02 | 815 | 0 | 30.2065 | 0
34 | 1900-02-02 | 816 | 0 | 34.2735 | 0
35 | 1900-02-03 | 817 | 0 | 21.6424 | 0
35 | 1900-02-03 | 818 | 0 | 24.5274 | 0
35 | 1900-02-03 | 819 | 0 | 27.9379 | 0
35 | 1900-02-03 | 820 | 0 | 29.208 | 0
35 | 1900-02-03 | 821 | 0 | 25.0777 | 0
35 | 1900-02-03 | 822 | 0 | 27.7651 | 0
35 | 1900-02-03 | 823 | 0 | 28.5627 | 0
35 | 1900-02-03 | 824 | 0 | 47.16 | 0
35 | 1900-02-03 | 825 | 0 | 49.7525 | 0
35 | 1900-02-03 | 826 | 0 | 40.6511 | 0
35 | 1900-02-03 | 827 | 0 | 45.8572 | 0
35 | 1900-02-03 | 828 | 0 | 44.4598 | 0
35 | 1900-02-03 | 829 | 0 | 46.4712 | 0
35 | 1900-02-03 | 830 | 0 | 244.0736 | 0
35 | 1900-02-03 | 831 | 0 | 36.6149 | 0
35 | 1900-02-03 | 832 | 0 | 46.1141 | 0
35 | 1900-02-03 | 833 | 0 | 51.9545 | 0
35 | 1900-02-03 | 834 | 0 | 51.2205 | 0
35 | 1900-02-03 | 835 | 0 | 34.7958 | 0
35 | 1900-02-03 | 836 | 0 | 31.2255 | 0
35 | 1900-02-03 | 837 | 0 | 26.4321 | 0
35 | 1900-02-03 | 838 | 0 | 23.7593 | 0
35 | 1900-02-03 | 839 | 0 | 31.5968 | 0
35 | 1900-02-03 | 840 | 0 | 30.4644 | 0
36 | 1900-02-04 | 841 | 0 | 22.7136 | 0
36 | 1900-02-04 | 842 | 0 | 31.2066 | 0
36 | 1900-02-04 | 843 | 0 | 18.8395 | 0
36 | 1900-02-04 | 844 | 0 | 30.6296 | 0
36 | 1900-02-04 | 845 | 0 | 27.7787 | 0
36 | 1900-02-04 | 846 | 0 | 27.9395 | 0
36 | 1900-02-04 | 847 | 0 | 29.4204 | 0
36 | 1900-02-04 | 848 | 0 | 37.5687 | 0
36 | 1900-02-04 | 849 | 0 | 48.1803 | 0
36 | 1900-02-04 | 850 | 0 | 454.9894 | 0
36 | 1900-02-04 | 851 | 0 | 42.5037 | 0
36 | 1900-02-04 | 852 | 0 | 32.4019 | 0
36 | 1900-02-04 | 853 | 0 | 41.071 | 0
36 | 1900-02-04 | 854 | 0 | 35.6377 | 0
36 | 1900-02-04 | 855 | 0 | 42.9479 | 0
36 | 1900-02-04 | 856 | 0 | 29.9353 | 0
36 | 1900-02-04 | 857 | 0 | 50.8124 | 0
36 | 1900-02-04 | 858 | 0 | 30.8318 | 0
36 | 1900-02-04 | 859 | 0 | 46.5226 | 0
36 | 1900-02-04 | 860 | 0 | 28.1558 | 0
36 | 1900-02-04 | 861 | 0 | 27.7353 | 0
36 | 1900-02-04 | 862 | 0 | 23.2862 | 0
36 | 1900-02-04 | 863 | 0 | 33.0772 | 0
36 | 1900-02-04 | 864 | 0 | 35.2004 | 0
37 | 1900-02-05 | 865 | 0 | 23.5877 | 0
37 | 1900-02-05 | 866 | 0 | 241.5089 | 0
37 | 1900-02-05 | 867 | 0 | 29.5932 | 0
37 | 1900-02-05 | 868 | 0 | 30.1307 | 0
37 | 1900-02-05 | 869 | 0 | 24.4375 | 0
37 | 1900-02-05 | 870 | 0 | 31.9131 | 0
37 | 1900-02-05 | 871 | 0 | 24.5555 | 0
37 | 1900-02-05 | 872 | 0 | 39.646 | 0
37 | 1900-02-05 | 873 | 0 | 47.9521 | 0
37 | 1900-02-05 | 874 | 0 | 40.9357 | 0
37 | 1900-02-05 | 875 | 0 | 27.0199 | 0
37 | 1900-02-05 | 876 | 0 | 44.072 | 0
37 | 1900-02-05 | 877 | 0 | 42.7712 | 0
37 | 1900-02-05 | 878 | 0 | 45.4015 | 0
37 | 1900-02-05 | 879 | 0 | 42.1481 | 0
37 | 1900-02-05 | 880 | 0 | 42.7899 | 0
37 | 1900-02-05 | 881 | 0 | 38.3339 | 0
37 | 1900-02-05 | 882 | 0 | 248.9582 | 0
37 | 1900-02-05 | 883 | 0 | 42.6784 | 0
37 | 1900-02-05 | 884 | 0 | 31.2446 | 0
37 | 1900-02-05 | 885 | 0 | 31.8933 | 0
37 | 1900-02-05 | 886 | 0 | 24.6425 | 0
37 | 1900-02-05 | 887 | 0 | 26.0042 | 0
37 | 1900-02-05 | 888 | 0 | 23.2878 | 0
38 | 1900-02-06 | 889 | 0 | 24.6623 | 0
38 | 1900-02-06 | 890 | 0 | 37.2879 | 0
38 | 1900-02-06 | 891 | 0 | 19.6873 | 0
38 | 1900-02-06 | 892 | 0 | 37.0377 | 0
38 | 1900-02-06 | 893 | 0 | 26.3852 | 0
38 | 1900-02-06 | 894 | 0 | 30.3763 | 0
38 | 1900-02-06 | 895 | 0 | 27.107 | 0
38 | 1900-02-06 | 896 | 0 | 248.2516 | 0
38 | 1900-02-06 | 897 | 0 | 35.2214 | 0
38 | 1900-02-06 | 898 | 0 | 34.9352 | 0
38 | 1900-02-06 | 899 | 0 | 51.2028 | 0
38 | 1900-02-06 | 900 | 0 | 41.4413 | 0
38 | 1900-02-06 | 901 | 0 | 35.068 | 0
38 | 1900-02-06 | 902 | 0 | 51.0973 | 0
38 | 1900-02-06 | 903 | 0 | 33.6938 | 0
38 | 1900-02-06 | 904 | 0 | 36.0503 | 0
38 | 1900-02-06 | 905 | 0 | 41.4148 | 0
38 | 1900-02-06 | 906 | 0 | 44.5421 | 0
38 | 1900-02-06 | 907 | 0 | 62.044 | 0
38 | 1900-02-06 | 908 | 0 | 33.2646 | 0
38 | 1900-02-06 | 909 | 0 | 31.5205 | 0
38 | 1900-02-06 | 910 | 0 | 222.9601 | 0
38 | 1900-02-06 | 911 | 0 | 35.5537 | 0
38 | 1900-02-06 | 912 | 0 | 23.3612 | 0
39 | 1900-02-07 | 913 | 0 | 229.1615 | 0
39 | 1900-02-07 | 914 | 0 | 40.0163 | 0
39 | 1900-02-07 | 915 | 0 | 26.3415 | 0
39 | 1900-02-07 | 916 | 0 | 29.5425 | 0
39 | 1900-02-07 | 917 | 0 | 17.8858 | 0
39 | 1900-02-07 | 918 | 0 | 30.3243 | 0
39 | 1900-02-07 | 919 | 0 | 19.8122 | 0
39 | 1900-02-07 | 920 | 0 | 42.4511 | 0
39 | 1900-02-07 | 921 | 0 | 54.071 | 0
39 | 1900-02-07 | 922 | 0 | 44.275 | 0
39 | 1900-02-07 | 923 | 0 | 52.8155 | 0
39 | 1900-02-07 | 924 | 0 | 35.6903 | 0
39 | 1900-02-07 | 925 | 0 | 45.01 | 0
39 | 1900-02-07 | 926 | 0 | 234.227 | 0
39 | 1900-02-07 | 927 | 0 | 39.258 | 0
39 | 1900-02-07 | 928 | 0 | 38.5521 | 0
39 | 1900-02-07 | 929 | 0 | 39.6061 | 0
39 | 1900-02-07 | 930 | 0 | 43.7313 | 0
39 | 1900-02-07 | 931 | 0 | 37.5176 | 0
39 | 1900-02-07 | 932 | 0 | 28.6655 | 0
39 | 1900-02-07 | 933 | 0 | 25.8979 | 0
39 | 1900-02-07 | 934 | 0 | 31.4318 | 0
39 | 1900-02-07 | 935 | 0 | 27.4449 | 0
39 | 1900-02-07 | 936 | 0 | 26.3503 | 0
40 | 1900-02-08 | 937 | 0 | 23.6011 | 0
40 | 1900-02-08 | 938 | 0 | 25.2462 | 0
40 | 1900-02-08 | 939 | 0 | 34.6299 | 0
40 | 1900-02-08 | 940 | 0 | 28.945 | 0
40 | 1900-02-08 | 941 | 0 | 27.2492 | 0
40 | 1900-02-08 | 942 | 0 | 23.6823 | 0
40 | 1900-02-08 | 943 | 0 | 224.6306 | 0
40 | 1900-02-08 | 944 | 0 | 49.5732 | 0
40 | 1900-02-08 | 945 | 0 | 50.3067 | 0
40 | 1900-02-08 | 946 | 0 | 50.8606 | 0
40 | 1900-02-08 | 947 | 0 | 36.3732 | 0
40 | 1900-02-08 | 948 | 0 | 31.0576 | 0
40 | 1900-02-08 | 949 | 0 | 45.1264 | 0
40 | 1900-02-08 | 950 | 0 | 46.1026 | 0
40 | 1900-02-08 | 951 | 0 | 42.3906 | 0
40 | 1900-02-08 | 952 | 0 | 47.518 | 0
40 | 1900-02-08 | 953 | 0 | 39.5822 | 0
40 | 1900-02-08 | 954 | 0 | 55.5223 | 0
40 | 1900-02-08 | 955 | 0 | 41.6583 | 0
40 | 1900-02-08 | 956 | 0 | 30.995 | 0
40 | 1900-02-08 | 957 | 0 | 29.7065 | 0
40 | 1900-02-08 | 958 | 0 | 23.928 | 0
40 | 1900-02-08 | 959 | 0 | 24.9093 | 0
40 | 1900-02-08 | 960 | 0 | 26.9518 | 0
41 | 1900-02-09 | 961 | 0 | 29.4341 | 0
41 | 1900-02-09 | 962 | 0 | 35.1751 | 0
41 | 1900-02-09 | 963 | 0 | 28.5457 | 0
41 | 1900-02-09 | 964 | 0 | 24.1631 | 0
41 | 1900-02-09 | 965 | 0 | 24.3309 | 0
41 | 1900-02-09 | 966 | 0 | 232.5897 | 0
41 | 1900-02-09 | 967 | 0 | 27.8458 | 0
41 | 1900-02-09 | 968 | 0 | 43.8683 | 0
41 | 1900-02-09 | 969 | 0 | 37.3215 | 0
41 | 1900-02-09 | 970 | 0 | 31.0052 | 0
41 | 1900-02-09 | 971 | 0 | 40.8518 | 0
41 | 1900-02-09 | 972 | 0 | 50.4274 | 0
41 | 1900-02-09 | 973 | 0 | 49.6145 | 0
41 | 1900-02-09 | 974 | 0 | 45.5072 | 0
41 | 1900-02-09 | 975 | 0 | 246.1374 | 0
41 | 1900-02-09 | 976 | 0 | 34.0574 | 0
41 | 1900-02-09 | 977 | 0 | 38.4819 | 0
41 | 1900-02-09 | 978 | 0 | 46.4548 | 0
41 | 1900-02-09 | 979 | 0 | 53.5073 | 0
41 | 1900-02-09 | 980 | 0 | 32.3672 | 0
41 | 1900-02-09 | 981 | 0 | 25.0118 | 0
41 | 1900-02-09 | 982 | 0 | 28.3948 | 0
41 | 1900-02-09 | 983 | 0 | 28.7864 | 0
41 | 1900-02-09 | 984 | 0 | 33.1314 | 0
42 | 1900-02-10 | 985 | 0 | 30.5124 | 0
42 | 1900-02-10 | 986 | 0 | 23.8835 | 0
42 | 1900-02-10 | 987 | 0 | 26.5428 | 0
42 | 1900-02-10 | 988 | 0 | 28.4619 | 0
42 | 1900-02-10 | 989 | 0 | 28.7163 | 0
42 | 1900-02-10 | 990 | 0 | 34.3446 | 0
42 | 1900-02-10 | 991 | 0 | 27.7669 | 0
42 | 1900-02-10 | 992 | 0 | 38.0501 | 0
42 | 1900-02-10 | 993 | 0 | 43.9983 | 0
42 | 1900-02-10 | 994 | 0 | 39.764 | 0
42 | 1900-02-10 | 995 | 0 | 39.4625 | 0
42 | 1900-02-10 | 996 | 0 | 39.1737 | 0
42 | 1900-02-10 | 997 | 0 | 243.3209 | 0
42 | 1900-02-10 | 998 | 0 | 45.9509 | 0
42 | 1900-02-10 | 999 | 0 | 43.7861 | 0
42 | 1900-02-10 | 1000 | 0 | 45.9544 | 0
42 | 1900-02-10 | 1001 | 0 | 27.7805 | 0
42 | 1900-02-10 | 1002 | 0 | 51.6142 | 0
42 | 1900-02-10 | 1003 | 0 | 45.2656 | 0
42 | 1900-02-10 | 1004 | 0 | 32.769 | 0
42 | 1900-02-10 | 1005 | 0 | 31.5303 | 0
42 | 1900-02-10 | 1006 | 0 | 30.6981 | 0
42 | 1900-02-10 | 1007 | 0 | 33.9295 | 0
42 | 1900-02-10 | 1008 | 0 | 29.3875 | 0
43 | 1900-02-11 | 1009 | 0 | 23.8371 | 0
43 | 1900-02-11 | 1010 | 0 | 24.6604 | 0
43 | 1900-02-11 | 1011 | 0 | 28.5887 | 0
43 | 1900-02-11 | 1012 | 0 | 28.3262 | 0
43 | 1900-02-11 | 1013 | 0 | 27.6011 | 0
43 | 1900-02-11 | 1014 | 0 | 24.82 | 0
43 | 1900-02-11 | 1015 | 0 | 28.984 | 0
43 | 1900-02-11 | 1016 | 0 | 32.7683 | 0
43 | 1900-02-11 | 1017 | 0 | 32.9742 | 0
43 | 1900-02-11 | 1018 | 0 | 227.1155 | 0
43 | 1900-02-11 | 1019 | 0 | 48.7079 | 0
43 | 1900-02-11 | 1020 | 0 | 50.4051 | 0
43 | 1900-02-11 | 1021 | 0 | 41.9084 | 0
43 | 1900-02-11 | 1022 | 0 | 34.4938 | 0
43 | 1900-02-11 | 1023 | 0 | 35.4983 | 0
43 | 1900-02-11 | 1024 | 0 | 42.7753 | 0
43 | 1900-02-11 | 1025 | 0 | 42.8639 | 0
43 | 1900-02-11 | 1026 | 0 | 41.2231 | 0
43 | 1900-02-11 | 1027 | 0 | 32.2266 | 0
43 | 1900-02-11 | 1028 | 0 | 23.4302 | 0
43 | 1900-02-11 | 1029 | 0 | 26.2641 | 0
43 | 1900-02-11 | 1030 | 0 | 32.2023 | 0
43 | 1900-02-11 | 1031 | 0 | 25.4473 | 0
43 | 1900-02-11 | 1032 | 0 | 26.6711 | 0
44 | 1900-02-12 | 1033 | 0 | 29.407 | 0
44 | 1900-02-12 | 1034 | 0 | 27.5506 | 0
44 | 1900-02-12 | 1035 | 0 | 17.0821 | 0
44 | 1900-02-12 | 1036 | 0 | 34.6764 | 0
44 | 1900-02-12 | 1037 | 0 | 231.695 | 0
44 | 1900-02-12 | 1038 | 0 | 236.3312 | 0
44 | 1900-02-12 | 1039 | 0 | 33.7219 | 0
44 | 1900-02-12 | 1040 | 0 | 49.4646 | 0
44 | 1900-02-12 | 1041 | 0 | 46.8986 | 0
44 | 1900-02-12 | 1042 | 0 | 42.0669 | 0
44 | 1900-02-12 | 1043 | 0 | 44.9306 | 0
44 | 1900-02-12 | 1044 | 0 | 36.5325 | 0
44 | 1900-02-12 | 1045 | 0 | 37.8937 | 0
44 | 1900-02-12 | 1046 | 0 | 48.6118 | 0
44 | 1900-02-12 | 1047 | 0 | 52.9352 | 0
44 | 1900-02-12 | 1048 | 0 | 41.5837 | 0
44 | 1900-02-12 | 1049 | 0 | 56.8597 | 0
44 | 1900-02-12 | 1050 | 0 | 39.355 | 0
44 | 1900-02-12 | 1051 | 0 | 49.5728 | 0
44 | 1900-02-12 | 1052 | 0 | 30.7738 | 0
44 | 1900-02-12 | 1053 | 0 | 28.5097 | 0
44 | 1900-02-12 | 1054 | 0 | 27.2214 | 0
44 | 1900-02-12 | 1055 | 0 | 25.1594 | 0
44 | 1900-02-12 | 1056 | 0 | 30.7699 | 0
45 | 1900-02-13 | 1057 | 0 | 21.3458 | 0
45 | 1900-02-13 | 1058 | 0 | 225.6436 | 0
45 | 1900-02-13 | 1059 | 0 | 24.7531 | 0
45 | 1900-02-13 | 1060 | 0 | 22.8626 | 0
45 | 1900-02-13 | 1061 | 0 | 34.7696 | 0
45 | 1900-02-13 | 1062 | 0 | 20.9508 | 0
45 | 1900-02-13 | 1063 | 0 | 31.1328 | 0
45 | 1900-02-13 | 1064 | 0 | 45.0834 | 0
45 | 1900-02-13 | 1065 | 0 | 43.5904 | 0
45 | 1900-02-13 | 1066 | 0 | 43.8907 | 0
45 | 1900-02-13 | 1067 | 0 | 22.3231 | 0
45 | 1900-02-13 | 1068 | 0 | 47.3425 | 0
45 | 1900-02-13 | 1069 | 0 | 45.5004 | 0
45 | 1900-02-13 | 1070 | 0 | 37.169 | 0
45 | 1900-02-13 | 1071 | 0 | 45.7035 | 0
45 | 1900-02-13 | 1072 | 0 | 54.903 | 0
45 | 1900-02-13 | 1073 | 0 | 41.5162 | 0
45 | 1900-02-13 | 1074 | 0 | 38.3835 | 0
45 | 1900-02-13 | 1075 | 0 | 48.16 | 0
45 | 1900-02-13 | 1076 | 0 | 34.4913 | 0
45 | 1900-02-13 | 1077 | 0 | 26.8361 | 0
45 | 1900-02-13 | 1078 | 0 | 26.6508 | 0
45 | 1900-02-13 | 1079 | 0 | 29.3156 | 0
45 | 1900-02-13 | 1080 | 0 | 24.7294 | 0
46 | 1900-02-14 | 1081 | 0 | 232.5214 | 0
46 | 1900-02-14 | 1082 | 0 | 32.6275 | 0
46 | 1900-02-14 | 1083 | 0 | 29.7883 | 0
46 | 1900-02-14 | 1084 | 0 | 24.6405 | 0
46 | 1900-02-14 | 1085 | 0 | 28.1922 | 0
46 | 1900-02-14 | 1086 | 0 | 22.7569 | 0
46 | 1900-02-14 | 1087 | 0 | 36.4643 | 0
46 | 1900-02-14 | 1088 | 0 | 40.4196 | 0
46 | 1900-02-14 | 1089 | 0 | 37.2901 | 0
46 | 1900-02-14 | 1090 | 0 | 43.8243 | 0
46 | 1900-02-14 | 1091 | 0 | 47.7576 | 0
46 | 1900-02-14 | 1092 | 0 | 54.3189 | 0
46 | 1900-02-14 | 1093 | 0 | 38.784 | 0
46 | 1900-02-14 | 1094 | 0 | 40.0597 | 0
46 | 1900-02-14 | 1095 | 0 | 53.9211 | 0
46 | 1900-02-14 | 1096 | 0 | 47.3188 | 0
46 | 1900-02-14 | 1097 | 0 | 50.9669 | 0
46 | 1900-02-14 | 1098 | 0 | 234.3623 | 0
46 | 1900-02-14 | 1099 | 0 | 26.3929 | 0
46 | 1900-02-14 | 1100 | 0 | 27.0777 | 0
46 | 1900-02-14 | 1101 | 0 | 27.4702 | 0
46 | 1900-02-14 | 1102 | 0 | 26.8576 | 0
46 | 1900-02-14 | 1103 | 0 | 22.0869 | 0
46 | 1900-02-14 | 1104 | 0 | 226.2586 | 0
47 | 1900-02-15 | 1105 | 0 | 36.4563 | 0
47 | 1900-02-15 | 1106 | 0 | 25.5304 | 0
47 | 1900-02-15 | 1107 | 0 | 32.9379 | 0
47 | 1900-02-15 | 1108 | 0 | 26.9056 | 0
47 | 1900-02-15 | 1109 | 0 | 24.1278 | 0
47 | 1900-02-15 | 1110 | 0 | 31.6212 | 0
47 | 1900-02-15 | 1111 | 0 | 32.2698 | 0
47 | 1900-02-15 | 1112 | 0 | 39.131 | 0
47 | 1900-02-15 | 1113 | 0 | 49.2088 | 0
47 | 1900-02-15 | 1114 | 0 | 35.4681 | 0
47 | 1900-02-15 | 1115 | 0 | 67.5506 | 0
47 | 1900-02-15 | 1116 | 0 | 47.064 | 0
47 | 1900-02-15 | 1117 | 0 | 32.9211 | 0
47 | 1900-02-15 | 1118 | 0 | 43.4233 | 0
47 | 1900-02-15 | 1119 | 0 | 34.3999 | 0
47 | 1900-02-15 | 1120 | 0 | 43.5748 | 0
47 | 1900-02-15 | 1121 | 0 | 43.6336 | 0
47 | 1900-02-15 | 1122 | 0 | 49.7645 | 0
47 | 1900-02-15 | 1123 | 0 | 39.933 | 0
47 | 1900-02-15 | 1124 | 0 | 225.2738 | 0
47 | 1900-02-15 | 1125 | 0 | 27.0908 | 0
47 | 1900-02-15 | 1126 | 0 | 32.1955 | 0
47 | 1900-02-15 | 1127 | 0 | 22.8427 | 0
47 | 1900-02-15 | 1128 | 0 | 26.425 | 0
48 | 1900-02-16 | 1129 | 0 | 29.4357 | 0
48 | 1900-02-16 | 1130 | 0 | 23.2053 | 0
48 | 1900-02-16 | 1131 | 0 | 31.0175 | 0
48 | 1900-02-16 | 1132 | 0 | 27.141 | 0
48 | 1900-02-16 | 1133 | 0 | 26.1936 | 0
48 | 1900-02-16 | 1134 | 0 | 28.4477 | 0
48 | 1900-02-16 | 1135 | 0 | 21.9522 | 0
48 | 1900-02-16 | 1136 | 0 | 44.1421 | 0
48 | 1900-02-16 | 1137 | 0 | 37.7402 | 0
48 | 1900-02-16 | 1138 | 0 | 44.1891 | 0
48 | 1900-02-16 | 1139 | 0 | 31.5079 | 0
48 | 1900-02-16 | 1140 | 0 | 57.305 | 0
48 | 1900-02-16 | 1141 | 0 | 38.8158 | 0
48 | 1900-02-16 | 1142 | 0 | 47.2483 | 0
48 | 1900-02-16 | 1143 | 0 | 49.2801 | 0
48 | 1900-02-16 | 1144 | 0 | 40.9252 | 0
48 | 1900-02-16 | 1145 | 0 | 230.6516 | 0
48 | 1900-02-16 | 1146 | 0 | 29.5804 | 0
48 | 1900-02-16 | 1147 | 0 | 48.6306 | 0
48 | 1900-02-16 | 1148 | 0 | 24.325 | 0
48 | 1900-02-16 | 1149 | 0 | 31.7448 | 0
48 | 1900-02-16 | 1150 | 0 | 30.443 | 0
48 | 1900-02-16 | 1151 | 0 | 36.0715 | 0
48 | 1900-02-16 | 1152 | 0 | 30.4415 | 0
49 | 1900-02-17 | 1153 | 0 | 25.9321 | 0
49 | 1900-02-17 | 1154 | 0 | 36.6097 | 0
49 | 1900-02-17 | 1155 | 0 | 21.7514 | 0
49 | 1900-02-17 | 1156 | 0 | 30.231 | 0
49 | 1900-02-17 | 1157 | 0 | 27.5763 | 0
49 | 1900-02-17 | 1158 | 0 | 34.6538 | 0
49 | 1900-02-17 | 1159 | 0 | 32.5374 | 0
49 | 1900-02-17 | 1160 | 0 | 240.2765 | 0
49 | 1900-02-17 | 1161 | 0 | 26.2217 | 0
49 | 1900-02-17 | 1162 | 0 | 37.5956 | 0
49 | 1900-02-17 | 1163 | 0 | 51.9836 | 0
49 | 1900-02-17 | 1164 | 0 | 46.4926 | 0
49 | 1900-02-17 | 1165 | 0 | 36.62 | 0
49 | 1900-02-17 | 1166 | 0 | 51.4722 | 0
49 | 1900-02-17 | 1167 | 0 | 32.7394 | 0
49 | 1900-02-17 | 1168 | 0 | 246.4878 | 0
49 | 1900-02-17 | 1169 | 0 | 35.7134 | 0
49 | 1900-02-17 | 1170 | 0 | 34.4785 | 0
49 | 1900-02-17 | 1171 | 0 | 36.8884 | 0
49 | 1900-02-17 | 1172 | 0 | 32.293 | 0
49 | 1900-02-17 | 1173 | 0 | 32.4077 | 0
49 | 1900-02-17 | 1174 | 0 | 28.7458 | 0
49 | 1900-02-17 | 1175 | 0 | 34.4025 | 0
49 | 1900-02-17 | 1176 | 0 | 25.8467 | 0
50 | 1900-02-18 | 1177 | 0 | 27.3773 | 0
50 | 1900-02-18 | 1178 | 0 | 32.2122 | 0
50 | 1900-02-18 | 1179 | 0 | 23.1628 | 0
50 | 1900-02-18 | 1180 | 0 | 19.3406 | 0
50 | 1900-02-18 | 1181 | 0 | 27.5506 | 0
50 | 1900-02-18 | 1182 | 0 | 62.2706 | 0
50 | 1900-02-18 | 1183 | 0 | 102.6407 | 0
50 | 1900-02-18 | 1184 | 0 | 60.577 | 0
50 | 1900-02-18 | 1185 | 0 | 58.7983 | 0
50 | 1900-02-18 | 1186 | 0 | 51.2601 | 0
50 | 1900-02-18 | 1187 | 0 | 48.852 | 0
50 | 1900-02-18 | 1188 | 0 | 17.4057 | 0
50 | 1900-02-18 | 1189 | 0 | 245.9554 | 0
50 | 1900-02-18 | 1190 | 0 | 31.2054 | 0
50 | 1900-02-18 | 1191 | 0 | 49.9978 | 0
50 | 1900-02-18 | 1192 | 0 | 52.2237 | 0
50 | 1900-02-18 | 1193 | 0 | 39.6635 | 0
50 | 1900-02-18 | 1194 | 0 | 34.3569 | 0
50 | 1900-02-18 | 1195 | 0 | 44.8131 | 0
50 | 1900-02-18 | 1196 | 0 | 27.5067 | 0
50 | 1900-02-18 | 1197 | 0 | 22.2128 | 0
50 | 1900-02-18 | 1198 | 0 | 32.6506 | 0
50 | 1900-02-18 | 1199 | 0 | 28.0464 | 0
50 | 1900-02-18 | 1200 | 0 | 28.0002 | 0
51 | 1900-02-19 | 1201 | 0 | 31.9262 | 0
51 | 1900-02-19 | 1202 | 0 | 27.9796 | 0
51 | 1900-02-19 | 1203 | 0 | 36.7374 | 0
51 | 1900-02-19 | 1204 | 0 | 32.8994 | 0
51 | 1900-02-19 | 1205 | 0 | 224.9573 | 0
51 | 1900-02-19 | 1206 | 0 | 61.9691 | 0
51 | 1900-02-19 | 1207 | 0 | 107.3517 | 0
51 | 1900-02-19 | 1208 | 0 | 106.5449 | 0
51 | 1900-02-19 | 1209 | 0 | 99.5544 | 0
51 | 1900-02-19 | 1210 | 0 | 65.5031 | 0
51 | 1900-02-19 | 1211 | 0 | 100.3389 | 0
51 | 1900-02-19 | 1212 | 0 | 53.3184 | 0
51 | 1900-02-19 | 1213 | 0 | 54.2194 | 0
51 | 1900-02-19 | 1214 | 0 | 48.978 | 0
51 | 1900-02-19 | 1215 | 0 | 49.7731 | 0
51 | 1900-02-19 | 1216 | 0 | 36.5299 | 0
51 | 1900-02-19 | 1217 | 0 | 53.0981 | 0
51 | 1900-02-19 | 1218 | 0 | 45.0473 | 0
51 | 1900-02-19 | 1219 | 0 | 58.6069 | 0
51 | 1900-02-19 | 1220 | 0 | 68.4782 | 0
51 | 1900-02-19 | 1221 | 0 | 70.5068 | 0
51 | 1900-02-19 | 1222 | 0 | 281.2849 | 0
51 | 1900-02-19 | 1223 | 0 | 41.7079 | 0
51 | 1900-02-19 | 1224 | 0 | 259.3546 | 0
52 | 1900-02-20 | 1225 | 0 | 57.0601 | 0
52 | 1900-02-20 | 1226 | 0 | 27.8851 | 0
52 | 1900-02-20 | 1227 | 0 | 23.0899 | 0
52 | 1900-02-20 | 1228 | 0 | 31.7035 | 0
52 | 1900-02-20 | 1229 | 0 | 25.3711 | 0
52 | 1900-02-20 | 1230 | 0 | 35.1376 | 0
52 | 1900-02-20 | 1231 | 0 | 41.8434 | 0
52 | 1900-02-20 | 1232 | 0 | 101.2642 | 0
52 | 1900-02-20 | 1233 | 0 | 119.0344 | 0
52 | 1900-02-20 | 1234 | 0 | 52.7971 | 0
52 | 1900-02-20 | 1235 | 0 | 54.3644 | 0
52 | 1900-02-20 | 1236 | 0 | 113.3193 | 0
52 | 1900-02-20 | 1237 | 0 | 84.1738 | 0
52 | 1900-02-20 | 1238 | 0 | 105.0904 | 0
52 | 1900-02-20 | 1239 | 0 | 110.3602 | 0
52 | 1900-02-20 | 1240 | 0 | 86.2064 | 0
52 | 1900-02-20 | 1241 | 0 | 237.1138 | 0
52 | 1900-02-20 | 1242 | 0 | 45.916 | 0
52 | 1900-02-20 | 1243 | 0 | 41.7146 | 0
52 | 1900-02-20 | 1244 | 0 | 31.1198 | 0
52 | 1900-02-20 | 1245 | 0 | 33.4178 | 0
52 | 1900-02-20 | 1246 | 0 | 29.2893 | 0
52 | 1900-02-20 | 1247 | 0 | 25.94 | 0
52 | 1900-02-20 | 1248 | 0 | 26.4008 | 0
53 | 1900-02-21 | 1249 | 0 | 25.5502 | 0
53 | 1900-02-21 | 1250 | 0 | 25.5442 | 0
53 | 1900-02-21 | 1251 | 0 | 31.083 | 0
53 | 1900-02-21 | 1252 | 0 | 31.1269 | 0
53 | 1900-02-21 | 1253 | 0 | 24.4974 | 0
53 | 1900-02-21 | 1254 | 0 | 22.6206 | 0
53 | 1900-02-21 | 1255 | 0 | 33.8785 | 0
53 | 1900-02-21 | 1256 | 0 | 41.3453 | 0
53 | 1900-02-21 | 1257 | 0 | 66.6415 | 0
53 | 1900-02-21 | 1258 | 0 | 326.9558 | 0
53 | 1900-02-21 | 1259 | 0 | 113.7466 | 0
53 | 1900-02-21 | 1260 | 0 | 106.235 | 0
53 | 1900-02-21 | 1261 | 0 | 133.121 | 0
53 | 1900-02-21 | 1262 | 0 | 121.1665 | 0
53 | 1900-02-21 | 1263 | 0 | 58.4722 | 0
53 | 1900-02-21 | 1264 | 0 | 46.5037 | 0
53 | 1900-02-21 | 1265 | 0 | 45.5327 | 0
53 | 1900-02-21 | 1266 | 0 | 43.2745 | 0
53 | 1900-02-21 | 1267 | 0 | 41.3517 | 0
53 | 1900-02-21 | 1268 | 0 | 15.3494 | 0
53 | 1900-02-21 | 1269 | 0 | 34.1867 | 0
53 | 1900-02-21 | 1270 | 0 | 25.8198 | 0
53 | 1900-02-21 | 1271 | 0 | 34.4782 | 0
53 | 1900-02-21 | 1272 | 0 | 21.5272 | 0
54 | 1900-02-22 | 1273 | 0 | 29.3284 | 0
54 | 1900-02-22 | 1274 | 0 | 28.63 | 0
54 | 1900-02-22 | 1275 | 0 | 226.2449 | 0
54 | 1900-02-22 | 1276 | 0 | 34.7195 | 0
54 | 1900-02-22 | 1277 | 0 | 22.126 | 0
54 | 1900-02-22 | 1278 | 0 | 29.3256 | 0
54 | 1900-02-22 | 1279 | 0 | 34.9674 | 0
54 | 1900-02-22 | 1280 | 0 | 48.1763 | 0
54 | 1900-02-22 | 1281 | 0 | 33.5846 | 0
54 | 1900-02-22 | 1282 | 0 | 52.4977 | 0
54 | 1900-02-22 | 1283 | 0 | 39.3677 | 0
54 | 1900-02-22 | 1284 | 0 | 238.3449 | 0
54 | 1900-02-22 | 1285 | 0 | 30.4606 | 0
54 | 1900-02-22 | 1286 | 0 | 48.0361 | 0
54 | 1900-02-22 | 1287 | 0 | 42.3136 | 0
54 | 1900-02-22 | 1288 | 0 | 41.2712 | 0
54 | 1900-02-22 | 1289 | 0 | 31.2217 | 0
54 | 1900-02-22 | 1290 | 0 | 50.7787 | 0
54 | 1900-02-22 | 1291 | 0 | 37.9285 | 0
54 | 1900-02-22 | 1292 | 0 | 28.901 | 0
54 | 1900-02-22 | 1293 | 0 | 230.8973 | 0
54 | 1900-02-22 | 1294 | 0 | 24.3479 | 0
54 | 1900-02-22 | 1295 | 0 | 27.179 | 0
54 | 1900-02-22 | 1296 | 0 | 29.7341 | 0
55 | 1900-02-23 | 1297 | 0 | 25.7631 | 0
55 | 1900-02-23 | 1298 | 0 | 36.7342 | 0
55 | 1900-02-23 | 1299 | 0 | 26.1432 | 0
55 | 1900-02-23 | 1300 | 0 | 31.5286 | 0
55 | 1900-02-23 | 1301 | 0 | 22.7249 | 0
55 | 1900-02-23 | 1302 | 0 | 28.5585 | 0
55 | 1900-02-23 | 1303 | 0 | 18.6602 | 0
55 | 1900-02-23 | 1304 | 0 | 30.6706 | 0
55 | 1900-02-23 | 1305 | 0 | 37.9893 | 0
55 | 1900-02-23 | 1306 | 0 | 43.9613 | 0
55 | 1900-02-23 | 1307 | 0 | 44.933 | 0
55 | 1900-02-23 | 1308 | 0 | 48.2779 | 0
55 | 1900-02-23 | 1309 | 0 | 39.9926 | 0
55 | 1900-02-23 | 1310 | 0 | 46.5387 | 0
55 | 1900-02-23 | 1311 | 0 | 41.4245 | 0
55 | 1900-02-23 | 1312 | 0 | 33.9934 | 0
55 | 1900-02-23 | 1313 | 0 | 254.8892 | 0
55 | 1900-02-23 | 1314 | 0 | 54.3854 | 0
55 | 1900-02-23 | 1315 | 0 | 38.2547 | 0
55 | 1900-02-23 | 1316 | 0 | 33.2418 | 0
55 | 1900-02-23 | 1317 | 0 | 27.6025 | 0
55 | 1900-02-23 | 1318 | 0 | 26.8306 | 0
55 | 1900-02-23 | 1319 | 0 | 29.9744 | 0
55 | 1900-02-23 | 1320 | 0 | 25.6796 | 0
56 | 1900-02-24 | 1321 | 0 | 25.1535 | 0
56 | 1900-02-24 | 1322 | 0 | 28.1988 | 0
56 | 1900-02-24 | 1323 | 0 | 23.7947 | 0
56 | 1900-02-24 | 1324 | 0 | 20.2424 | 0
56 | 1900-02-24 | 1325 | 0 | 32.6515 | 0
56 | 1900-02-24 | 1326 | 0 | 25.8483 | 0
56 | 1900-02-24 | 1327 | 0 | 27.2882 | 0
56 | 1900-02-24 | 1328 | 0 | 42.7214 | 0
56 | 1900-02-24 | 1329 | 0 | 46.1006 | 0
56 | 1900-02-24 | 1330 | 0 | 53.4257 | 0
56 | 1900-02-24 | 1331 | 0 | 23.2805 | 0
56 | 1900-02-24 | 1332 | 0 | 234.3032 | 0
56 | 1900-02-24 | 1333 | 0 | 45.7535 | 0
56 | 1900-02-24 | 1334 | 0 | 31.8517 | 0
56 | 1900-02-24 | 1335 | 0 | 46.2365 | 0
56 | 1900-02-24 | 1336 | 0 | 41.7134 | 0
56 | 1900-02-24 | 1337 | 0 | 32.8088 | 0
56 | 1900-02-24 | 1338 | 0 | 42.2842 | 0
56 | 1900-02-24 | 1339 | 0 | 48.1761 | 0
56 | 1900-02-24 | 1340 | 0 | 28.9345 | 0
56 | 1900-02-24 | 1341 | 0 | 25.6343 | 0
56 | 1900-02-24 | 1342 | 0 | 31.3575 | 0
56 | 1900-02-24 | 1343 | 0 | 24.5776 | 0
56 | 1900-02-24 | 1344 | 0 | 26.0664 | 0
57 | 1900-02-25 | 1345 | 0 | 32.2527 | 0
57 | 1900-02-25 | 1346 | 0 | 229.5003 | 0
57 | 1900-02-25 | 1347 | 0 | 238.28 | 0
57 | 1900-02-25 | 1348 | 0 | 26.1604 | 0
57 | 1900-02-25 | 1349 | 0 | 27.8738 | 0
57 | 1900-02-25 | 1350 | 0 | 23.5772 | 0
57 | 1900-02-25 | 1351 | 0 | 33.1877 | 0
57 | 1900-02-25 | 1352 | 0 | 31.868 | 0
57 | 1900-02-25 | 1353 | 0 | 24.141 | 0
57 | 1900-02-25 | 1354 | 0 | 43.3 | 0
57 | 1900-02-25 | 1355 | 0 | 31.8794 | 0
57 | 1900-02-25 | 1356 | 0 | 37.0738 | 0
57 | 1900-02-25 | 1357 | 0 | 43.9036 | 0
57 | 1900-02-25 | 1358 | 0 | 31.9359 | 0
57 | 1900-02-25 | 1359 | 0 | 47.3822 | 0
57 | 1900-02-25 | 1360 | 0 | 37.6085 | 0
57 | 1900-02-25 | 1361 | 0 | 255.094 | 0
57 | 1900-02-25 | 1362 | 0 | 40.461 | 0
57 | 1900-02-25 | 1363 | 0 | 39.1968 | 0
57 | 1900-02-25 | 1364 | 0 | 23.6679 | 0
57 | 1900-02-25 | 1365 | 0 | 29.8453 | 0
57 | 1900-02-25 | 1366 | 0 | 32.0434 | 0
57 | 1900-02-25 | 1367 | 0 | 23.1248 | 0
57 | 1900-02-25 | 1368 | 0 | 28.0898 | 0
58 | 1900-02-26 | 1369 | 0 | 31.9329 | 0
58 | 1900-02-26 | 1370 | 0 | 31.8125 | 0
58 | 1900-02-26 | 1371 | 0 | 28.4381 | 0
58 | 1900-02-26 | 1372 | 0 | 26.8738 | 0
58 | 1900-02-26 | 1373 | 0 | 30.6236 | 0
58 | 1900-02-26 | 1374 | 0 | 27.1077 | 0
58 | 1900-02-26 | 1375 | 0 | 219.9795 | 0
58 | 1900-02-26 | 1376 | 0 | 38.4709 | 0
58 | 1900-02-26 | 1377 | 0 | 36.623 | 0
58 | 1900-02-26 | 1378 | 0 | 47.2718 | 0
58 | 1900-02-26 | 1379 | 0 | 45.644 | 0
58 | 1900-02-26 | 1380 | 0 | 51.2707 | 0
58 | 1900-02-26 | 1381 | 0 | 42.8951 | 0
58 | 1900-02-26 | 1382 | 0 | 39.8213 | 0
58 | 1900-02-26 | 1383 | 0 | 36.9745 | 0
58 | 1900-02-26 | 1384 | 0 | 54.2859 | 0
58 | 1900-02-26 | 1385 | 0 | 36.0543 | 0
58 | 1900-02-26 | 1386 | 0 | 44.398 | 0
58 | 1900-02-26 | 1387 | 0 | 32.9151 | 0
58 | 1900-02-26 | 1388 | 0 | 230.2701 | 0
58 | 1900-02-26 | 1389 | 0 | 22.7522 | 0
58 | 1900-02-26 | 1390 | 0 | 29.6175 | 0
58 | 1900-02-26 | 1391 | 0 | 20.0647 | 0
58 | 1900-02-26 | 1392 | 0 | 33.8752 | 0
59 | 1900-02-27 | 1393 | 0 | 28.7071 | 0
59 | 1900-02-27 | 1394 | 0 | 30.796 | 0
59 | 1900-02-27 | 1395 | 0 | 35.1562 | 0
59 | 1900-02-27 | 1396 | 0 | 28.5349 | 0
59 | 1900-02-27 | 1397 | 0 | 33.4113 | 0
59 | 1900-02-27 | 1398 | 0 | 29.1302 | 0
59 | 1900-02-27 | 1399 | 0 | 25.2602 | 0
59 | 1900-02-27 | 1400 | 0 | 243.733 | 0
59 | 1900-02-27 | 1401 | 0 | 44.7512 | 0
59 | 1900-02-27 | 1402 | 0 | 62.7315 | 0
59 | 1900-02-27 | 1403 | 0 | 41.9151 | 0
59 | 1900-02-27 | 1404 | 0 | 45.1593 | 0
59 | 1900-02-27 | 1405 | 0 | 51.8574 | 0
59 | 1900-02-27 | 1406 | 0 | 41.1282 | 0
59 | 1900-02-27 | 1407 | 0 | 35.5145 | 0
59 | 1900-02-27 | 1408 | 0 | 246.8711 | 0
59 | 1900-02-27 | 1409 | 0 | 40.8765 | 0
59 | 1900-02-27 | 1410 | 0 | 38.8053 | 0
59 | 1900-02-27 | 1411 | 0 | 35.9454 | 0
59 | 1900-02-27 | 1412 | 0 | 225.9732 | 0
59 | 1900-02-27 | 1413 | 0 | 27.7613 | 0
59 | 1900-02-27 | 1414 | 0 | 30.7411 | 0
59 | 1900-02-27 | 1415 | 0 | 32.5301 | 0
59 | 1900-02-27 | 1416 | 0 | 30.4671 | 0
60 | 1900-03-01 | 1417 | 0 | 28.6062 | 0
60 | 1900-03-01 | 1418 | 0 | 39.244 | 0
60 | 1900-03-01 | 1419 | 0 | 33.092 | 0
60 | 1900-03-01 | 1420 | 0 | 27.2554 | 0
60 | 1900-03-01 | 1421 | 0 | 31.9511 | 0
60 | 1900-03-01 | 1422 | 0 | 30.7816 | 0
60 | 1900-03-01 | 1423 | 0 | 23.793 | 0
60 | 1900-03-01 | 1424 | 0 | 229.6018 | 0
60 | 1900-03-01 | 1425 | 0 | 43.2744 | 0
60 | 1900-03-01 | 1426 | 0 | 51.0547 | 0
60 | 1900-03-01 | 1427 | 0 | 40.3414 | 0
60 | 1900-03-01 | 1428 | 0 | 48.4341 | 0
60 | 1900-03-01 | 1429 | 0 | 52.3009 | 0
60 | 1900-03-01 | 1430 | 0 | 48.2735 | 0
60 | 1900-03-01 | 1431 | 0 | 50.6356 | 0
60 | 1900-03-01 | 1432 | 0 | 46.4818 | 0
60 | 1900-03-01 | 1433 | 0 | 54.5943 | 0
60 | 1900-03-01 | 1434 | 0 | 32.1278 | 0
60 | 1900-03-01 | 1435 | 0 | 39.5041 | 0
60 | 1900-03-01 | 1436 | 0 | 23.1742 | 0
60 | 1900-03-01 | 1437 | 0 | 31.8165 | 0
60 | 1900-03-01 | 1438 | 0 | 232.3626 | 0
60 | 1900-03-01 | 1439 | 0 | 37.1524 | 0
60 | 1900-03-01 | 1440 | 0 | 24.8183 | 0
61 | 1900-03-02 | 1441 | 0 | 26.907 | 0
61 | 1900-03-02 | 1442 | 0 | 30.2771 | 0
61 | 1900-03-02 | 1443 | 0 | 32.0587 | 0
61 | 1900-03-02 | 1444 | 0 | 35.3944 | 0
61 | 1900-03-02 | 1445 | 0 | 30.6516 | 0
61 | 1900-03-02 | 1446 | 0 | 36.7951 | 0
61 | 1900-03-02 | 1447 | 0 | 35.8599 | 0
61 | 1900-03-02 | 1448 | 0 | 38.138 | 0
61 | 1900-03-02 | 1449 | 0 | 33.5468 | 0
61 | 1900-03-02 | 1450 | 0 | 47.6502 | 0
61 | 1900-03-02 | 1451 | 0 | 255.8809 | 0
61 | 1900-03-02 | 1452 | 0 | 39.2557 | 0
61 | 1900-03-02 | 1453 | 0 | 46.0372 | 0
61 | 1900-03-02 | 1454 | 0 | 58.6992 | 0
61 | 1900-03-02 | 1455 | 0 | 52.6907 | 0
61 | 1900-03-02 | 1456 | 0 | 46.9533 | 0
61 | 1900-03-02 | 1457 | 0 | 32.1282 | 0
61 | 1900-03-02 | 1458 | 0 | 37.0082 | 0
61 | 1900-03-02 | 1459 | 0 | 33.2466 | 0
61 | 1900-03-02 | 1460 | 0 | 34.0591 | 0
61 | 1900-03-02 | 1461 | 0 | 31.9849 | 0
61 | 1900-03-02 | 1462 | 0 | 34.2913 | 0
61 | 1900-03-02 | 1463 | 0 | 29.0835 | 0
61 | 1900-03-02 | 1464 | 0 | 35.0135 | 0
62 | 1900-03-03 | 1465 | 0 | 31.5357 | 0
62 | 1900-03-03 | 1466 | 0 | 230.642 | 0
62 | 1900-03-03 | 1467 | 0 | 33.6174 | 0
62 | 1900-03-03 | 1468 | 0 | 26.5491 | 0
62 | 1900-03-03 | 1469 | 0 | 36.3983 | 0
62 | 1900-03-03 | 1470 | 0 | 25.333 | 0
62 | 1900-03-03 | 1471 | 0 | 33.1298 | 0
62 | 1900-03-03 | 1472 | 0 | 49.5516 | 0
62 | 1900-03-03 | 1473 | 0 | 37.7809 | 0
62 | 1900-03-03 | 1474 | 0 | 39.7608 | 0
62 | 1900-03-03 | 1475 | 0 | 243.649 | 0
62 | 1900-03-03 | 1476 | 0 | 51.1117 | 0
62 | 1900-03-03 | 1477 | 0 | 47.9744 | 0
62 | 1900-03-03 | 1478 | 0 | 47.129 | 0
62 | 1900-03-03 | 1479 | 0 | 44.534 | 0
62 | 1900-03-03 | 1480 | 0 | 29.2902 | 0
62 | 1900-03-03 | 1481 | 0 | 45.1879 | 0
62 | 1900-03-03 | 1482 | 0 | 53.6667 | 0
62 | 1900-03-03 | 1483 | 0 | 247.7969 | 0
62 | 1900-03-03 | 1484 | 0 | 22.5984 | 0
62 | 1900-03-03 | 1485 | 0 | 36.8827 | 0
62 | 1900-03-03 | 1486 | 0 | 33.4707 | 0
62 | 1900-03-03 | 1487 | 0 | 31.5959 | 0
62 | 1900-03-03 | 1488 | 0 | 35.662 | 0
63 | 1900-03-04 | 1489 | 0 | 36.4641 | 0
63 | 1900-03-04 | 1490 | 0 | 23.5752 | 0
63 | 1900-03-04 | 1491 | 0 | 30.2902 | 0
63 | 1900-03-04 | 1492 | 0 | 35.8145 | 0
63 | 1900-03-04 | 1493 | 0 | 37.0185 | 0
63 | 1900-03-04 | 1494 | 0 | 30.2612 | 0
63 | 1900-03-04 | 1495 | 0 | 29.1414 | 0
63 | 1900-03-04 | 1496 | 0 | 47.6429 | 0
63 | 1900-03-04 | 1497 | 0 | 46.3601 | 0
63 | 1900-03-04 | 1498 | 0 | 39.3985 | 0
63 | 1900-03-04 | 1499 | 0 | 43.5696 | 0
63 | 1900-03-04 | 1500 | 0 | 43.6353 | 0
63 | 1900-03-04 | 1501 | 0 | 45.2178 | 0
63 | 1900-03-04 | 1502 | 0 | 54.3604 | 0
63 | 1900-03-04 | 1503 | 0 | 37.8748 | 0
63 | 1900-03-04 | 1504 | 0 | 43.0465 | 0
63 | 1900-03-04 | 1505 | 0 | 44.581 | 0
63 | 1900-03-04 | 1506 | 0 | 51.2811 | 0
63 | 1900-03-04 | 1507 | 0 | 44.8298 | 0
63 | 1900-03-04 | 1508 | 0 | 25.469 | 0
63 | 1900-03-04 | 1509 | 0 | 34.1754 | 0
63 | 1900-03-04 | 1510 | 0 | 37.3744 | 0
63 | 1900-03-04 | 1511 | 0 | 29.762 | 0
63 | 1900-03-04 | 1512 | 0 | 32.5639 | 0
64 | 1900-03-05 | 1513 | 0 | 22.2649 | 0
64 | 1900-03-05 | 1514 | 0 | 235.1355 | 0
64 | 1900-03-05 | 1515 | 0 | 35.6054 | 0
64 | 1900-03-05 | 1516 | 0 | 27.0673 | 0
64 | 1900-03-05 | 1517 | 0 | 34.4067 | 0
64 | 1900-03-05 | 1518 | 0 | 27.0999 | 0
64 | 1900-03-05 | 1519 | 0 | 30.0618 | 0
64 | 1900-03-05 | 1520 | 0 | 56.9653 | 0
64 | 1900-03-05 | 1521 | 0 | 47.9629 | 0
64 | 1900-03-05 | 1522 | 0 | 44.9127 | 0
64 | 1900-03-05 | 1523 | 0 | 33.9334 | 0
64 | 1900-03-05 | 1524 | 0 | 52.1703 | 0
64 | 1900-03-05 | 1525 | 0 | 32.3641 | 0
64 | 1900-03-05 | 1526 | 0 | 53.3295 | 0
64 | 1900-03-05 | 1527 | 0 | 46.4153 | 0
64 | 1900-03-05 | 1528 | 0 | 45.0649 | 0
64 | 1900-03-05 | 1529 | 0 | 47.6501 | 0
64 | 1900-03-05 | 1530 | 0 | 37.4655 | 0
64 | 1900-03-05 | 1531 | 0 | 45.3056 | 0
64 | 1900-03-05 | 1532 | 0 | 32.4877 | 0
64 | 1900-03-05 | 1533 | 0 | 27.2338 | 0
64 | 1900-03-05 | 1534 | 0 | 31.8474 | 0
64 | 1900-03-05 | 1535 | 0 | 26.6374 | 0
64 | 1900-03-05 | 1536 | 0 | 39.1157 | 0
65 | 1900-03-06 | 1537 | 0 | 36.2639 | 0
65 | 1900-03-06 | 1538 | 0 | 30.9167 | 0
65 | 1900-03-06 | 1539 | 0 | 26.7791 | 0
65 | 1900-03-06 | 1540 | 0 | 31.4124 | 0
65 | 1900-03-06 | 1541 | 0 | 23.3627 | 0
65 | 1900-03-06 | 1542 | 0 | 229.5452 | 0
65 | 1900-03-06 | 1543 | 0 | 228.413 | 0
65 | 1900-03-06 | 1544 | 0 | 56.0616 | 0
65 | 1900-03-06 | 1545 | 0 | 63.4485 | 0
65 | 1900-03-06 | 1546 | 0 | 78.7215 | 0
65 | 1900-03-06 | 1547 | 0 | 56.0951 | 0
65 | 1900-03-06 | 1548 | 0 | 51.0268 | 0
65 | 1900-03-06 | 1549 | 0 | 44.2024 | 0
65 | 1900-03-06 | 1550 | 0 | 49.1345 | 0
65 | 1900-03-06 | 1551 | 0 | 35.1411 | 0
65 | 1900-03-06 | 1552 | 0 | 47.685 | 0
65 | 1900-03-06 | 1553 | 0 | 38.8063 | 0
65 | 1900-03-06 | 1554 | 0 | 27.5434 | 0
65 | 1900-03-06 | 1555 | 0 | 50.9555 | 0
65 | 1900-03-06 | 1556 | 0 | 27.4479 | 0
65 | 1900-03-06 | 1557 | 0 | 29.5776 | 0
65 | 1900-03-06 | 1558 | 0 | 30.2139 | 0
65 | 1900-03-06 | 1559 | 0 | 29.9906 | 0
65 | 1900-03-06 | 1560 | 0 | 27.7837 | 0
66 | 1900-03-07 | 1561 | 0 | 37.0385 | 0
66 | 1900-03-07 | 1562 | 0 | 31.7854 | 0
66 | 1900-03-07 | 1563 | 0 | 32.7945 | 0
66 | 1900-03-07 | 1564 | 0 | 28.146 | 0
66 | 1900-03-07 | 1565 | 0 | 28.7611 | 0
66 | 1900-03-07 | 1566 | 0 | 29.2497 | 0
66 | 1900-03-07 | 1567 | 0 | 22.5559 | 0
66 | 1900-03-07 | 1568 | 0 | 48.2746 | 0
66 | 1900-03-07 | 1569 | 0 | 45.3621 | 0
66 | 1900-03-07 | 1570 | 0 | 247.1829 | 0
66 | 1900-03-07 | 1571 | 0 | 39.6731 | 0
66 | 1900-03-07 | 1572 | 0 | 49.1693 | 0
66 | 1900-03-07 | 1573 | 0 | 42.246 | 0
66 | 1900-03-07 | 1574 | 0 | 51.8545 | 0
66 | 1900-03-07 | 1575 | 0 | 40.4271 | 0
66 | 1900-03-07 | 1576 | 0 | 46.4218 | 0
66 | 1900-03-07 | 1577 | 0 | 36.7641 | 0
66 | 1900-03-07 | 1578 | 0 | 35.9406 | 0
66 | 1900-03-07 | 1579 | 0 | 49.8903 | 0
66 | 1900-03-07 | 1580 | 0 | 26.8571 | 0
66 | 1900-03-07 | 1581 | 0 | 24.5774 | 0
66 | 1900-03-07 | 1582 | 0 | 33.095 | 0
66 | 1900-03-07 | 1583 | 0 | 24.9176 | 0
66 | 1900-03-07 | 1584 | 0 | 33.6072 | 0
67 | 1900-03-08 | 1585 | 0 | 33.1101 | 0
67 | 1900-03-08 | 1586 | 0 | 35.8479 | 0
67 | 1900-03-08 | 1587 | 0 | 36.0878 | 0
67 | 1900-03-08 | 1588 | 0 | 30.9532 | 0
67 | 1900-03-08 | 1589 | 0 | 34.6234 | 0
67 | 1900-03-08 | 1590 | 0 | 29.7346 | 0
67 | 1900-03-08 | 1591 | 0 | 24.7515 | 0
67 | 1900-03-08 | 1592 | 0 | 40.5854 | 0
67 | 1900-03-08 | 1593 | 0 | 41.1165 | 0
67 | 1900-03-08 | 1594 | 0 | 51.0804 | 0
67 | 1900-03-08 | 1595 | 0 | 49.9506 | 0
67 | 1900-03-08 | 1596 | 0 | 51.363 | 0
67 | 1900-03-08 | 1597 | 0 | 30.4656 | 0
67 | 1900-03-08 | 1598 | 0 | 40.9262 | 0
67 | 1900-03-08 | 1599 | 0 | 41.0126 | 0
67 | 1900-03-08 | 1600 | 0 | 47.2654 | 0
67 | 1900-03-08 | 1601 | 0 | 35.2574 | 0
67 | 1900-03-08 | 1602 | 0 | 245.605 | 0
67 | 1900-03-08 | 1603 | 0 | 39.9277 | 0
67 | 1900-03-08 | 1604 | 0 | 26.4766 | 0
67 | 1900-03-08 | 1605 | 0 | 35.5327 | 0
67 | 1900-03-08 | 1606 | 0 | 31.4867 | 0
67 | 1900-03-08 | 1607 | 0 | 32.1143 | 0
67 | 1900-03-08 | 1608 | 0 | 21.2597 | 0
68 | 1900-03-09 | 1609 | 0 | 28.4663 | 0
68 | 1900-03-09 | 1610 | 0 | 34.9075 | 0
68 | 1900-03-09 | 1611 | 0 | 228.4701 | 0
68 | 1900-03-09 | 1612 | 0 | 40.7128 | 0
68 | 1900-03-09 | 1613 | 0 | 30.0395 | 0
68 | 1900-03-09 | 1614 | 0 | 30.7758 | 0
68 | 1900-03-09 | 1615 | 0 | 36.511 | 0
68 | 1900-03-09 | 1616 | 0 | 46.9455 | 0
68 | 1900-03-09 | 1617 | 0 | 51.2527 | 0
68 | 1900-03-09 | 1618 | 0 | 50.2248 | 0
68 | 1900-03-09 | 1619 | 0 | 31.1369 | 0
68 | 1900-03-09 | 1620 | 0 | 40.5859 | 0
68 | 1900-03-09 | 1621 | 0 | 39.7755 | 0
68 | 1900-03-09 | 1622 | 0 | 39.2139 | 0
68 | 1900-03-09 | 1623 | 0 | 48.9566 | 0
68 | 1900-03-09 | 1624 | 0 | 33.8662 | 0
68 | 1900-03-09 | 1625 | 0 | 28.7317 | 0
68 | 1900-03-09 | 1626 | 0 | 39.1039 | 0
68 | 1900-03-09 | 1627 | 0 | 41.9399 | 0
68 | 1900-03-09 | 1628 | 0 | 27.7553 | 0
68 | 1900-03-09 | 1629 | 0 | 35.3577 | 0
68 | 1900-03-09 | 1630 | 0 | 29.7552 | 0
68 | 1900-03-09 | 1631 | 0 | 26.9766 | 0
68 | 1900-03-09 | 1632 | 0 | 36.4314 | 0
69 | 1900-03-10 | 1633 | 0 | 27.2436 | 0
69 | 1900-03-10 | 1634 | 0 | 32.0459 | 0
69 | 1900-03-10 | 1635 | 0 | 27.9961 | 0
69 | 1900-03-10 | 1636 | 0 | 40.4501 | 0
69 | 1900-03-10 | 1637 | 0 | 35.8916 | 0
69 | 1900-03-10 | 1638 | 0 | 29.9987 | 0
69 | 1900-03-10 | 1639 | 0 | 30.6296 | 0
69 | 1900-03-10 | 1640 | 0 | 41.4976 | 0
69 | 1900-03-10 | 1641 | 0 | 49.8529 | 0
69 | 1900-03-10 | 1642 | 0 | 45.0688 | 0
69 | 1900-03-10 | 1643 | 0 | 49.7324 | 0
69 | 1900-03-10 | 1644 | 0 | 49.6807 | 0
69 | 1900-03-10 | 1645 | 0 | 37.1697 | 0
69 | 1900-03-10 | 1646 | 0 | 33.8197 | 0
69 | 1900-03-10 | 1647 | 0 | 44.2521 | 0
69 | 1900-03-10 | 1648 | 0 | 49.9008 | 0
69 | 1900-03-10 | 1649 | 0 | 50.9619 | 0
69 | 1900-03-10 | 1650 | 0 | 41.3734 | 0
69 | 1900-03-10 | 1651 | 0 | 32.7823 | 0
69 | 1900-03-10 | 1652 | 0 | 34.174 | 0
69 | 1900-03-10 | 1653 | 0 | 236.8405 | 0
69 | 1900-03-10 | 1654 | 0 | 29.2427 | 0
69 | 1900-03-10 | 1655 | 0 | 21.9321 | 0
69 | 1900-03-10 | 1656 | 0 | 39.499 | 0
70 | 1900-03-11 | 1657 | 0 | 34.751 | 0
70 | 1900-03-11 | 1658 | 0 | 32.4425 | 0
70 | 1900-03-11 | 1659 | 0 | 28.4048 | 0
70 | 1900-03-11 | 1660 | 0 | 26.5259 | 0
70 | 1900-03-11 | 1661 | 0 | 35.7827 | 0
70 | 1900-03-11 | 1662 | 0 | 41.9766 | 0
70 | 1900-03-11 | 1663 | 0 | 27.6151 | 0
70 | 1900-03-11 | 1664 | 0 | 36.6502 | 0
70 | 1900-03-11 | 1665 | 0 | 35.3225 | 0
70 | 1900-03-11 | 1666 | 0 | 47.4126 | 0
70 | 1900-03-11 | 1667 | 0 | 25.4146 | 0
70 | 1900-03-11 | 1668 | 0 | 35.024 | 0
70 | 1900-03-11 | 1669 | 0 | 42.9188 | 0
70 | 1900-03-11 | 1670 | 0 | 41.1662 | 0
70 | 1900-03-11 | 1671 | 0 | 36.5219 | 0
70 | 1900-03-11 | 1672 | 0 | 44.3664 | 0
70 | 1900-03-11 | 1673 | 0 | 53.8893 | 0
70 | 1900-03-11 | 1674 | 0 | 39.1573 | 0
70 | 1900-03-11 | 1675 | 0 | 54.2402 | 0
70 | 1900-03-11 | 1676 | 0 | 33.0628 | 0
70 | 1900-03-11 | 1677 | 0 | 27.0138 | 0
70 | 1900-03-11 | 1678 | 0 | 38.4173 | 0
70 | 1900-03-11 | 1679 | 0 | 230.9903 | 0
70 | 1900-03-11 | 1680 | 0 | 34.4672 | 0
71 | 1900-03-12 | 1681 | 0 | 37.8145 | 0
71 | 1900-03-12 | 1682 | 0 | 29.8473 | 0
71 | 1900-03-12 | 1683 | 0 | 28.2225 | 0
71 | 1900-03-12 | 1684 | 0 | 30.3241 | 0
71 | 1900-03-12 | 1685 | 0 | 36.6134 | 0
71 | 1900-03-12 | 1686 | 0 | 23.2582 | 0
71 | 1900-03-12 | 1687 | 0 | 31.2376 | 0
71 | 1900-03-12 | 1688 | 0 | 48.2551 | 0
71 | 1900-03-12 | 1689 | 0 | 42.4688 | 0
71 | 1900-03-12 | 1690 | 0 | 50.5803 | 0
71 | 1900-03-12 | 1691 | 0 | 42.4784 | 0
71 | 1900-03-12 | 1692 | 0 | 40.4167 | 0
71 | 1900-03-12 | 1693 | 0 | 52.1221 | 0
71 | 1900-03-12 | 1694 | 0 | 49.6931 | 0
71 | 1900-03-12 | 1695 | 0 | 41.3322 | 0
71 | 1900-03-12 | 1696 | 0 | 47.027 | 0
71 | 1900-03-12 | 1697 | 0 | 32.322 | 0
71 | 1900-03-12 | 1698 | 0 | 57.9718 | 0
71 | 1900-03-12 | 1699 | 0 | 44.5247 | 0
71 | 1900-03-12 | 1700 | 0 | 28.7272 | 0
71 | 1900-03-12 | 1701 | 0 | 34.0732 | 0
71 | 1900-03-12 | 1702 | 0 | 35.8907 | 0
71 | 1900-03-12 | 1703 | 0 | 45.1241 | 0
71 | 1900-03-12 | 1704 | 0 | 31.2926 | 0
72 | 1900-03-13 | 1705 | 0 | 27.6197 | 0
72 | 1900-03-13 | 1706 | 0 | 26.0867 | 0
72 | 1900-03-13 | 1707 | 0 | 27.1478 | 0
72 | 1900-03-13 | 1708 | 0 | 30.1167 | 0
72 | 1900-03-13 | 1709 | 0 | 31.1995 | 0
72 | 1900-03-13 | 1710 | 0 | 33.4659 | 0
72 | 1900-03-13 | 1711 | 0 | 30.7657 | 0
72 | 1900-03-13 | 1712 | 0 | 250.9535 | 0
72 | 1900-03-13 | 1713 | 0 | 28.0395 | 0
72 | 1900-03-13 | 1714 | 0 | 31.5817 | 0
72 | 1900-03-13 | 1715 | 0 | 36.6513 | 0
72 | 1900-03-13 | 1716 | 0 | 35.3682 | 0
72 | 1900-03-13 | 1717 | 0 | 50.0977 | 0
72 | 1900-03-13 | 1718 | 0 | 89.7848 | 0
72 | 1900-03-13 | 1719 | 0 | 58.7852 | 0
72 | 1900-03-13 | 1720 | 0 | 52.0456 | 0
72 | 1900-03-13 | 1721 | 0 | 46.3781 | 0
72 | 1900-03-13 | 1722 | 0 | 53.9843 | 0
72 | 1900-03-13 | 1723 | 0 | 40.5227 | 0
72 | 1900-03-13 | 1724 | 0 | 26.3758 | 0
72 | 1900-03-13 | 1725 | 0 | 36.3956 | 0
72 | 1900-03-13 | 1726 | 0 | 36.4512 | 0
72 | 1900-03-13 | 1727 | 0 | 27.3874 | 0
72 | 1900-03-13 | 1728 | 0 | 32.8739 | 0
73 | 1900-03-14 | 1729 | 0 | 23.7499 | 0
73 | 1900-03-14 | 1730 | 0 | 30.4381 | 0
73 | 1900-03-14 | 1731 | 0 | 31.2 | 0
73 | 1900-03-14 | 1732 | 0 | 31.4411 | 0
73 | 1900-03-14 | 1733 | 0 | 32.5156 | 0
73 | 1900-03-14 | 1734 | 0 | 51.3089 | 0
73 | 1900-03-14 | 1735 | 0 | 88.544 | 0
73 | 1900-03-14 | 1736 | 0 | 47.5974 | 0
73 | 1900-03-14 | 1737 | 0 | 47.121 | 0
73 | 1900-03-14 | 1738 | 0 | 35.514 | 0
73 | 1900-03-14 | 1739 | 0 | 72.281 | 0
73 | 1900-03-14 | 1740 | 0 | 125.6339 | 0
73 | 1900-03-14 | 1741 | 0 | 115.2543 | 0
73 | 1900-03-14 | 1742 | 0 | 311.1724 | 0
73 | 1900-03-14 | 1743 | 0 | 59.7733 | 0
73 | 1900-03-14 | 1744 | 0 | 41.536 | 0
73 | 1900-03-14 | 1745 | 0 | 46.6149 | 0
73 | 1900-03-14 | 1746 | 0 | 243.2733 | 0
73 | 1900-03-14 | 1747 | 0 | 47.0934 | 0
73 | 1900-03-14 | 1748 | 0 | 33.4122 | 0
73 | 1900-03-14 | 1749 | 0 | 34.4947 | 0
73 | 1900-03-14 | 1750 | 0 | 36.4885 | 0
73 | 1900-03-14 | 1751 | 0 | 40.6367 | 0
73 | 1900-03-14 | 1752 | 0 | 30.2776 | 0
74 | 1900-03-15 | 1753 | 0 | 28.8369 | 0
74 | 1900-03-15 | 1754 | 0 | 22.7174 | 0
74 | 1900-03-15 | 1755 | 0 | 35.0865 | 0
74 | 1900-03-15 | 1756 | 0 | 21.3687 | 0
74 | 1900-03-15 | 1757 | 0 | 27.3437 | 0
74 | 1900-03-15 | 1758 | 0 | 31.607 | 0
74 | 1900-03-15 | 1759 | 0 | 45.5664 | 0
74 | 1900-03-15 | 1760 | 0 | 118.9999 | 0
74 | 1900-03-15 | 1761 | 0 | 94.4256 | 0
74 | 1900-03-15 | 1762 | 0 | 62.6047 | 0
74 | 1900-03-15 | 1763 | 0 | 101.7567 | 0
74 | 1900-03-15 | 1764 | 0 | 121.6368 | 0
74 | 1900-03-15 | 1765 | 0 | 96.0117 | 0
74 | 1900-03-15 | 1766 | 0 | 44.2411 | 0
74 | 1900-03-15 | 1767 | 0 | 29.8314 | 0
74 | 1900-03-15 | 1768 | 0 | 50.2543 | 0
74 | 1900-03-15 | 1769 | 0 | 49.1579 | 0
74 | 1900-03-15 | 1770 | 0 | 31.3393 | 0
74 | 1900-03-15 | 1771 | 0 | 32.1315 | 0
74 | 1900-03-15 | 1772 | 0 | 30.8179 | 0
74 | 1900-03-15 | 1773 | 0 | 29.5241 | 0
74 | 1900-03-15 | 1774 | 0 | 17.2187 | 0
74 | 1900-03-15 | 1775 | 0 | 27.2581 | 0
74 | 1900-03-15 | 1776 | 0 | 232.6561 | 0
75 | 1900-03-16 | 1777 | 0 | 19.5913 | 0
75 | 1900-03-16 | 1778 | 0 | 36.3607 | 0
75 | 1900-03-16 | 1779 | 0 | 34.9225 | 0
75 | 1900-03-16 | 1780 | 0 | 33.5008 | 0
75 | 1900-03-16 | 1781 | 0 | 30.964 | 0
75 | 1900-03-16 | 1782 | 0 | 63.6136 | 0
75 | 1900-03-16 | 1783 | 0 | 139.6332 | 0
75 | 1900-03-16 | 1784 | 0 | 110.6568 | 0
75 | 1900-03-16 | 1785 | 0 | 49.3994 | 0
75 | 1900-03-16 | 1786 | 0 | 71.778 | 0
75 | 1900-03-16 | 1787 | 0 | 83.1714 | 0
75 | 1900-03-16 | 1788 | 0 | 48.9312 | 0
75 | 1900-03-16 | 1789 | 0 | 44.2842 | 0
75 | 1900-03-16 | 1790 | 0 | 42.6178 | 0
75 | 1900-03-16 | 1791 | 0 | 46.9758 | 0
75 | 1900-03-16 | 1792 | 0 | 43.2553 | 0
75 | 1900-03-16 | 1793 | 0 | 38.043 | 0
75 | 1900-03-16 | 1794 | 0 | 33.365 | 0
75 | 1900-03-16 | 1795 | 0 | 41.1476 | 0
75 | 1900-03-16 | 1796 | 0 | 218.5972 | 0
75 | 1900-03-16 | 1797 | 0 | 38.0471 | 0
75 | 1900-03-16 | 1798 | 0 | 38.8737 | 0
75 | 1900-03-16 | 1799 | 0 | 28.3128 | 0
75 | 1900-03-16 | 1800 | 0 | 23.6714 | 0
76 | 1900-03-17 | 1801 | 0 | 42.4537 | 0
76 | 1900-03-17 | 1802 | 0 | 39.9028 | 0
76 | 1900-03-17 | 1803 | 0 | 28.977 | 0
76 | 1900-03-17 | 1804 | 0 | 36.7476 | 0
76 | 1900-03-17 | 1805 | 0 | 23.6316 | 0
76 | 1900-03-17 | 1806 | 0 | 22.2919 | 0
76 | 1900-03-17 | 1807 | 0 | 24.0053 | 0
76 | 1900-03-17 | 1808 | 0 | 53.1179 | 0
76 | 1900-03-17 | 1809 | 0 | 27.4312 | 0
76 | 1900-03-17 | 1810 | 0 | 37.9729 | 0
76 | 1900-03-17 | 1811 | 0 | 32.4809 | 0
76 | 1900-03-17 | 1812 | 0 | 39.9349 | 0
76 | 1900-03-17 | 1813 | 0 | 37.8473 | 0
76 | 1900-03-17 | 1814 | 0 | 52.1944 | 0
76 | 1900-03-17 | 1815 | 0 | 447.1197 | 0
76 | 1900-03-17 | 1816 | 0 | 46.7489 | 0
76 | 1900-03-17 | 1817 | 0 | 34.511 | 0
76 | 1900-03-17 | 1818 | 0 | 54.2537 | 0
76 | 1900-03-17 | 1819 | 0 | 30.5396 | 0
76 | 1900-03-17 | 1820 | 0 | 36.8594 | 0
76 | 1900-03-17 | 1821 | 0 | 29.7895 | 0
76 | 1900-03-17 | 1822 | 0 | 31.2622 | 0
76 | 1900-03-17 | 1823 | 0 | 34.5177 | 0
76 | 1900-03-17 | 1824 | 0 | 25.2956 | 0
77 | 1900-03-18 | 1825 | 0 | 31.941 | 0
77 | 1900-03-18 | 1826 | 0 | 32.8599 | 0
77 | 1900-03-18 | 1827 | 0 | 29.2657 | 0
77 | 1900-03-18 | 1828 | 0 | 37.7729 | 0
77 | 1900-03-18 | 1829 | 0 | 39.9101 | 0
77 | 1900-03-18 | 1830 | 0 | 35.3465 | 0
77 | 1900-03-18 | 1831 | 0 | 39.1146 | 0
77 | 1900-03-18 | 1832 | 0 | 49.8763 | 0
77 | 1900-03-18 | 1833 | 0 | 33.7681 | 0
77 | 1900-03-18 | 1834 | 0 | 44.4691 | 0
77 | 1900-03-18 | 1835 | 0 | 246.305 | 0
77 | 1900-03-18 | 1836 | 0 | 59.3942 | 0
77 | 1900-03-18 | 1837 | 0 | 43.5998 | 0
77 | 1900-03-18 | 1838 | 0 | 42.0825 | 0
77 | 1900-03-18 | 1839 | 0 | 34.5899 | 0
77 | 1900-03-18 | 1840 | 0 | 50.7764 | 0
77 | 1900-03-18 | 1841 | 0 | 47.4389 | 0
77 | 1900-03-18 | 1842 | 0 | 56.2656 | 0
77 | 1900-03-18 | 1843 | 0 | 46.9691 | 0
77 | 1900-03-18 | 1844 | 0 | 35.1815 | 0
77 | 1900-03-18 | 1845 | 0 | 21.857 | 0
77 | 1900-03-18 | 1846 | 0 | 32.7919 | 0
77 | 1900-03-18 | 1847 | 0 | 32.9264 | 0
77 | 1900-03-18 | 1848 | 0 | 31.8867 | 0
78 | 1900-03-19 | 1849 | 0 | 35.2066 | 0
78 | 1900-03-19 | 1850 | 0 | 25.743 | 0
78 | 1900-03-19 | 1851 | 0 | 34.0696 | 0
78 | 1900-03-19 | 1852 | 0 | 231.7525 | 0
78 | 1900-03-19 | 1853 | 0 | 38.2959 | 0
78 | 1900-03-19 | 1854 | 0 | 21.5926 | 0
78 | 1900-03-19 | 1855 | 0 | 25.6548 | 0
78 | 1900-03-19 | 1856 | 0 | 49.2117 | 0
78 | 1900-03-19 | 1857 | 0 | 44.534 | 0
78 | 1900-03-19 | 1858 | 0 | 65.6063 | 0
78 | 1900-03-19 | 1859 | 0 | 51.6483 | 0
78 | 1900-03-19 | 1860 | 0 | 61.8134 | 0
78 | 1900-03-19 | 1861 | 0 | 47.2021 | 0
78 | 1900-03-19 | 1862 | 0 | 40.7458 | 0
78 | 1900-03-19 | 1863 | 0 | 51.9982 | 0
78 | 1900-03-19 | 1864 | 0 | 32.8289 | 0
78 | 1900-03-19 | 1865 | 0 | 43.3892 | 0
78 | 1900-03-19 | 1866 | 0 | 34.7819 | 0
78 | 1900-03-19 | 1867 | 0 | 44.9428 | 0
78 | 1900-03-19 | 1868 | 0 | 34.8618 | 0
78 | 1900-03-19 | 1869 | 0 | 21.6637 | 0
78 | 1900-03-19 | 1870 | 0 | 31.4166 | 0
78 | 1900-03-19 | 1871 | 0 | 38.5289 | 0
78 | 1900-03-19 | 1872 | 0 | 230.8286 | 0
79 | 1900-03-20 | 1873 | 0 | 27.1802 | 0
79 | 1900-03-20 | 1874 | 0 | 32.3422 | 0
79 | 1900-03-20 | 1875 | 0 | 32.4888 | 0
79 | 1900-03-20 | 1876 | 0 | 30.6076 | 0
79 | 1900-03-20 | 1877 | 0 | 33.2415 | 0
79 | 1900-03-20 | 1878 | 0 | 53.0787 | 0
79 | 1900-03-20 | 1879 | 0 | 120.6565 | 0
79 | 1900-03-20 | 1880 | 0 | 117.7526 | 0
79 | 1900-03-20 | 1881 | 0 | 123.0306 | 0
79 | 1900-03-20 | 1882 | 0 | 77.5184 | 0
79 | 1900-03-20 | 1883 | 0 | 47.8353 | 0
79 | 1900-03-20 | 1884 | 0 | 239.7158 | 0
79 | 1900-03-20 | 1885 | 0 | 49.9015 | 0
79 | 1900-03-20 | 1886 | 0 | 55.0077 | 0
79 | 1900-03-20 | 1887 | 0 | 32.6199 | 0
79 | 1900-03-20 | 1888 | 0 | 39.0837 | 0
79 | 1900-03-20 | 1889 | 0 | 39.5392 | 0
79 | 1900-03-20 | 1890 | 0 | 46.4998 | 0
79 | 1900-03-20 | 1891 | 0 | 46.7282 | 0
79 | 1900-03-20 | 1892 | 0 | 29.8667 | 0
79 | 1900-03-20 | 1893 | 0 | 22.2939 | 0
79 | 1900-03-20 | 1894 | 0 | 34.0707 | 0
79 | 1900-03-20 | 1895 | 0 | 225.7745 | 0
79 | 1900-03-20 | 1896 | 0 | 31.2788 | 0
80 | 1900-03-21 | 1897 | 0 | 23.9903 | 0
80 | 1900-03-21 | 1898 | 0 | 28.8543 | 0
80 | 1900-03-21 | 1899 | 0 | 27.5433 | 0
80 | 1900-03-21 | 1900 | 0 | 31.6933 | 0
80 | 1900-03-21 | 1901 | 0 | 29.2861 | 0
80 | 1900-03-21 | 1902 | 0 | 35.2188 | 0
80 | 1900-03-21 | 1903 | 0 | 32.6395 | 0
80 | 1900-03-21 | 1904 | 0 | 42.8204 | 0
80 | 1900-03-21 | 1905 | 0 | 38.4578 | 0
80 | 1900-03-21 | 1906 | 0 | 43.2399 | 0
80 | 1900-03-21 | 1907 | 0 | 29.9838 | 0
80 | 1900-03-21 | 1908 | 0 | 43.7262 | 0
80 | 1900-03-21 | 1909 | 0 | 38.3952 | 0
80 | 1900-03-21 | 1910 | 0 | 42.927 | 0
80 | 1900-03-21 | 1911 | 0 | 40.6619 | 0
80 | 1900-03-21 | 1912 | 0 | 47.2999 | 0
80 | 1900-03-21 | 1913 | 0 | 52.8673 | 0
80 | 1900-03-21 | 1914 | 0 | 47.7718 | 0
80 | 1900-03-21 | 1915 | 0 | 46.0152 | 0
80 | 1900-03-21 | 1916 | 0 | 25.9611 | 0
80 | 1900-03-21 | 1917 | 0 | 29.9907 | 0
80 | 1900-03-21 | 1918 | 0 | 29.4502 | 0
80 | 1900-03-21 | 1919 | 0 | 25.5132 | 0
80 | 1900-03-21 | 1920 | 0 | 28.4148 | 0
81 | 1900-03-22 | 1921 | 0 | 228.7024 | 0
81 | 1900-03-22 | 1922 | 0 | 32.5664 | 0
81 | 1900-03-22 | 1923 | 0 | 29.0187 | 0
81 | 1900-03-22 | 1924 | 0 | 30.9514 | 0
81 | 1900-03-22 | 1925 | 0 | 34.1517 | 0
81 | 1900-03-22 | 1926 | 0 | 32.7748 | 0
81 | 1900-03-22 | 1927 | 0 | 41.3413 | 0
81 | 1900-03-22 | 1928 | 0 | 98.3187 | 0
81 | 1900-03-22 | 1929 | 0 | 137.8162 | 0
81 | 1900-03-22 | 1930 | 0 | 139.6796 | 0
81 | 1900-03-22 | 1931 | 0 | 142.4212 | 0
81 | 1900-03-22 | 1932 | 0 | 109.3313 | 0
81 | 1900-03-22 | 1933 | 0 | 114.3694 | 0
81 | 1900-03-22 | 1934 | 0 | 52.4704 | 0
81 | 1900-03-22 | 1935 | 0 | 33.9329 | 0
81 | 1900-03-22 | 1936 | 0 | 55.2407 | 0
81 | 1900-03-22 | 1937 | 0 | 48.0737 | 0
81 | 1900-03-22 | 1938 | 0 | 38.0818 | 0
81 | 1900-03-22 | 1939 | 0 | 48.9171 | 0
81 | 1900-03-22 | 1940 | 0 | 33.0719 | 0
81 | 1900-03-22 | 1941 | 0 | 26.854 | 0
81 | 1900-03-22 | 1942 | 0 | 26.4825 | 0
81 | 1900-03-22 | 1943 | 0 | 29.0185 | 0
81 | 1900-03-22 | 1944 | 0 | 32.975 | 0
82 | 1900-03-23 | 1945 | 0 | 27.6152 | 0
82 | 1900-03-23 | 1946 | 0 | 25.1603 | 0
82 | 1900-03-23 | 1947 | 0 | 42.635 | 0
82 | 1900-03-23 | 1948 | 0 | 28.7569 | 0
82 | 1900-03-23 | 1949 | 0 | 32.1692 | 0
82 | 1900-03-23 | 1950 | 0 | 27.1946 | 0
82 | 1900-03-23 | 1951 | 0 | 226.8986 | 0
82 | 1900-03-23 | 1952 | 0 | 246.6106 | 0
82 | 1900-03-23 | 1953 | 0 | 30.4658 | 0
82 | 1900-03-23 | 1954 | 0 | 41.178 | 0
82 | 1900-03-23 | 1955 | 0 | 42.1579 | 0
82 | 1900-03-23 | 1956 | 0 | 48.0239 | 0
82 | 1900-03-23 | 1957 | 0 | 34.4791 | 0
82 | 1900-03-23 | 1958 | 0 | 41.2522 | 0
82 | 1900-03-23 | 1959 | 0 | 37.1101 | 0
82 | 1900-03-23 | 1960 | 0 | 43.3719 | 0
82 | 1900-03-23 | 1961 | 0 | 49.43 | 0
82 | 1900-03-23 | 1962 | 0 | 47.6573 | 0
82 | 1900-03-23 | 1963 | 0 | 56.662 | 0
82 | 1900-03-23 | 1964 | 0 | 24.4756 | 0
82 | 1900-03-23 | 1965 | 0 | 34.0936 | 0
82 | 1900-03-23 | 1966 | 0 | 31.4487 | 0
82 | 1900-03-23 | 1967 | 0 | 34.5531 | 0
82 | 1900-03-23 | 1968 | 0 | 22.5081 | 0
83 | 1900-03-24 | 1969 | 0 | 31.22 | 0
83 | 1900-03-24 | 1970 | 0 | 25.2947 | 0
83 | 1900-03-24 | 1971 | 0 | 33.8394 | 0
83 | 1900-03-24 | 1972 | 0 | 30.5588 | 0
83 | 1900-03-24 | 1973 | 0 | 28.2815 | 0
83 | 1900-03-24 | 1974 | 0 | 30.3601 | 0
83 | 1900-03-24 | 1975 | 0 | 34.7608 | 0
83 | 1900-03-24 | 1976 | 0 | 42.7847 | 0
83 | 1900-03-24 | 1977 | 0 | 52.2002 | 0
83 | 1900-03-24 | 1978 | 0 | 45.3539 | 0
83 | 1900-03-24 | 1979 | 0 | 43.3408 | 0
83 | 1900-03-24 | 1980 | 0 | 48.0608 | 0
83 | 1900-03-24 | 1981 | 0 | 34.8256 | 0
83 | 1900-03-24 | 1982 | 0 | 34.1483 | 0
83 | 1900-03-24 | 1983 | 0 | 44.6147 | 0
83 | 1900-03-24 | 1984 | 0 | 52.4606 | 0
83 | 1900-03-24 | 1985 | 0 | 48.9917 | 0
83 | 1900-03-24 | 1986 | 0 | 45.312 | 0
83 | 1900-03-24 | 1987 | 0 | 44.6673 | 0
83 | 1900-03-24 | 1988 | 0 | 25.6898 | 0
83 | 1900-03-24 | 1989 | 0 | 33.5434 | 0
83 | 1900-03-24 | 1990 | 0 | 34.2507 | 0
83 | 1900-03-24 | 1991 | 0 | 31.3138 | 0
83 | 1900-03-24 | 1992 | 0 | 38.0566 | 0
84 | 1900-03-25 | 1993 | 0 | 32.4601 | 0
84 | 1900-03-25 | 1994 | 0 | 234.781 | 0
84 | 1900-03-25 | 1995 | 0 | 30.1585 | 0
84 | 1900-03-25 | 1996 | 0 | 32.8412 | 0
84 | 1900-03-25 | 1997 | 0 | 40.1665 | 0
84 | 1900-03-25 | 1998 | 0 | 20.3379 | 0
84 | 1900-03-25 | 1999 | 0 | 27.5042 | 0
84 | 1900-03-25 | 2000 | 0 | 32.5867 | 0
84 | 1900-03-25 | 2001 | 0 | 28.3694 | 0
84 | 1900-03-25 | 2002 | 0 | 41.2693 | 0
84 | 1900-03-25 | 2003 | 0 | 55.05 | 0
84 | 1900-03-25 | 2004 | 0 | 39.8061 | 0
84 | 1900-03-25 | 2005 | 0 | 44.3968 | 0
84 | 1900-03-25 | 2006 | 0 | 44.9774 | 0
84 | 1900-03-25 | 2007 | 0 | 51.9839 | 0
84 | 1900-03-25 | 2008 | 0 | 50.5294 | 0
84 | 1900-03-25 | 2009 | 0 | 56.0319 | 0
84 | 1900-03-25 | 2010 | 0 | 49.452 | 0
84 | 1900-03-25 | 2011 | 0 | 45.5382 | 0
84 | 1900-03-25 | 2012 | 0 | 33.0368 | 0
84 | 1900-03-25 | 2013 | 0 | 32.8028 | 0
84 | 1900-03-25 | 2014 | 0 | 21.5492 | 0
84 | 1900-03-25 | 2015 | 0 | 32.8884 | 0
84 | 1900-03-25 | 2016 | 0 | 33.2787 | 0
85 | 1900-03-26 | 2017 | 0 | 31.4783 | 0
85 | 1900-03-26 | 2018 | 0 | 33.4113 | 0
85 | 1900-03-26 | 2019 | 0 | 226.1812 | 0
85 | 1900-03-26 | 2020 | 0 | 32.3386 | 0
85 | 1900-03-26 | 2021 | 0 | 30.1305 | 0
85 | 1900-03-26 | 2022 | 0 | 32.3429 | 0
85 | 1900-03-26 | 2023 | 0 | 35.7432 | 0
85 | 1900-03-26 | 2024 | 0 | 253.7034 | 0
85 | 1900-03-26 | 2025 | 0 | 44.5429 | 0
85 | 1900-03-26 | 2026 | 0 | 44.0188 | 0
85 | 1900-03-26 | 2027 | 0 | 44.865 | 0
85 | 1900-03-26 | 2028 | 0 | 53.3303 | 0
85 | 1900-03-26 | 2029 | 0 | 51.7373 | 0
85 | 1900-03-26 | 2030 | 0 | 37.0778 | 0
85 | 1900-03-26 | 2031 | 0 | 36.0817 | 0
85 | 1900-03-26 | 2032 | 0 | 39.5472 | 0
85 | 1900-03-26 | 2033 | 0 | 32.9316 | 0
85 | 1900-03-26 | 2034 | 0 | 42.5849 | 0
85 | 1900-03-26 | 2035 | 0 | 36.7782 | 0
85 | 1900-03-26 | 2036 | 0 | 27.2888 | 0
85 | 1900-03-26 | 2037 | 0 | 34.2568 | 0
85 | 1900-03-26 | 2038 | 0 | 29.0374 | 0
85 | 1900-03-26 | 2039 | 0 | 30.5627 | 0
85 | 1900-03-26 | 2040 | 0 | 30.3329 | 0
86 | 1900-03-27 | 2041 | 0 | 28.5312 | 0
86 | 1900-03-27 | 2042 | 0 | 34.3863 | 0
86 | 1900-03-27 | 2043 | 0 | 30.1765 | 0
86 | 1900-03-27 | 2044 | 0 | 28.49 | 0
86 | 1900-03-27 | 2045 | 0 | 33.2326 | 0
86 | 1900-03-27 | 2046 | 0 | 37.4154 | 0
86 | 1900-03-27 | 2047 | 0 | 34.0432 | 0
86 | 1900-03-27 | 2048 | 0 | 38.0389 | 0
86 | 1900-03-27 | 2049 | 0 | 38.2867 | 0
86 | 1900-03-27 | 2050 | 0 | 45.0647 | 0
86 | 1900-03-27 | 2051 | 0 | 43.7343 | 0
86 | 1900-03-27 | 2052 | 0 | 46.5593 | 0
86 | 1900-03-27 | 2053 | 0 | 77.4823 | 0
86 | 1900-03-27 | 2054 | 0 | 56.5547 | 0
86 | 1900-03-27 | 2055 | 0 | 101.0474 | 0
86 | 1900-03-27 | 2056 | 0 | 88.2117 | 0
86 | 1900-03-27 | 2057 | 0 | 46.505 | 0
86 | 1900-03-27 | 2058 | 0 | 48.4536 | 0
86 | 1900-03-27 | 2059 | 0 | 239.1611 | 0
86 | 1900-03-27 | 2060 | 0 | 23.4436 | 0
86 | 1900-03-27 | 2061 | 0 | 29.8544 | 0
86 | 1900-03-27 | 2062 | 0 | 28.4945 | 0
86 | 1900-03-27 | 2063 | 0 | 31.166 | 0
86 | 1900-03-27 | 2064 | 0 | 28.4689 | 0
87 | 1900-03-28 | 2065 | 0 | 28.5725 | 0
87 | 1900-03-28 | 2066 | 0 | 32.5545 | 0
87 | 1900-03-28 | 2067 | 0 | 31.2581 | 0
87 | 1900-03-28 | 2068 | 0 | 45.7117 | 0
87 | 1900-03-28 | 2069 | 0 | 91.9545 | 0
87 | 1900-03-28 | 2070 | 0 | 128.7132 | 0
87 | 1900-03-28 | 2071 | 0 | 110.4251 | 0
87 | 1900-03-28 | 2072 | 0 | 114.0528 | 0
87 | 1900-03-28 | 2073 | 0 | 132.3298 | 0
87 | 1900-03-28 | 2074 | 0 | 129.7277 | 0
87 | 1900-03-28 | 2075 | 0 | 127.7049 | 0
87 | 1900-03-28 | 2076 | 0 | 132.1164 | 0
87 | 1900-03-28 | 2077 | 0 | 109.9745 | 0
87 | 1900-03-28 | 2078 | 0 | 60.8747 | 0
87 | 1900-03-28 | 2079 | 0 | 48.5717 | 0
87 | 1900-03-28 | 2080 | 0 | 49.6871 | 0
87 | 1900-03-28 | 2081 | 0 | 45.5737 | 0
87 | 1900-03-28 | 2082 | 0 | 42.5775 | 0
87 | 1900-03-28 | 2083 | 0 | 44.1287 | 0
87 | 1900-03-28 | 2084 | 0 | 28.5645 | 0
87 | 1900-03-28 | 2085 | 0 | 36.4933 | 0
87 | 1900-03-28 | 2086 | 0 | 35.5242 | 0
87 | 1900-03-28 | 2087 | 0 | 224.2516 | 0
87 | 1900-03-28 | 2088 | 0 | 35.9158 | 0
88 | 1900-03-29 | 2089 | 0 | 28.1219 | 0
88 | 1900-03-29 | 2090 | 0 | 30.6469 | 0
88 | 1900-03-29 | 2091 | 0 | 229.9675 | 0
88 | 1900-03-29 | 2092 | 0 | 40.1253 | 0
88 | 1900-03-29 | 2093 | 0 | 104.7776 | 0
88 | 1900-03-29 | 2094 | 0 | 113.3938 | 0
88 | 1900-03-29 | 2095 | 0 | 110.0938 | 0
88 | 1900-03-29 | 2096 | 0 | 96.7082 | 0
88 | 1900-03-29 | 2097 | 0 | 103.2581 | 0
88 | 1900-03-29 | 2098 | 0 | 133.6476 | 0
88 | 1900-03-29 | 2099 | 0 | 91.6027 | 0
88 | 1900-03-29 | 2100 | 0 | 92.905 | 0
88 | 1900-03-29 | 2101 | 0 | 130.6387 | 0
88 | 1900-03-29 | 2102 | 0 | 82.2781 | 0
88 | 1900-03-29 | 2103 | 0 | 41.1339 | 0
88 | 1900-03-29 | 2104 | 0 | 48.0511 | 0
88 | 1900-03-29 | 2105 | 0 | 71.5199 | 0
88 | 1900-03-29 | 2106 | 0 | 82.6024 | 0
88 | 1900-03-29 | 2107 | 0 | 127.9896 | 0
88 | 1900-03-29 | 2108 | 0 | 121.511 | 0
88 | 1900-03-29 | 2109 | 0 | 133.1046 | 0
88 | 1900-03-29 | 2110 | 0 | 127.7264 | 0
88 | 1900-03-29 | 2111 | 0 | 108.5048 | 0
88 | 1900-03-29 | 2112 | 0 | 47.2228 | 0
89 | 1900-03-30 | 2113 | 0 | 49.1592 | 0
89 | 1900-03-30 | 2114 | 0 | 70.8274 | 0
89 | 1900-03-30 | 2115 | 0 | 77.9073 | 0
89 | 1900-03-30 | 2116 | 0 | 27.068 | 0
89 | 1900-03-30 | 2117 | 0 | 36.8691 | 0
89 | 1900-03-30 | 2118 | 0 | 32.2428 | 0
89 | 1900-03-30 | 2119 | 0 | 23.7445 | 0
89 | 1900-03-30 | 2120 | 0 | 51.8104 | 0
89 | 1900-03-30 | 2121 | 0 | 104.5738 | 0
89 | 1900-03-30 | 2122 | 0 | 131.67 | 0
89 | 1900-03-30 | 2123 | 0 | 74.2685 | 0
89 | 1900-03-30 | 2124 | 0 | 48.5033 | 0
89 | 1900-03-30 | 2125 | 0 | 43.3064 | 0
89 | 1900-03-30 | 2126 | 0 | 45.3589 | 0
89 | 1900-03-30 | 2127 | 0 | 31.1513 | 0
89 | 1900-03-30 | 2128 | 0 | 49.2308 | 0
89 | 1900-03-30 | 2129 | 0 | 42.887 | 0
89 | 1900-03-30 | 2130 | 0 | 46.8483 | 0
89 | 1900-03-30 | 2131 | 0 | 240.7608 | 0
89 | 1900-03-30 | 2132 | 0 | 29.4714 | 0
89 | 1900-03-30 | 2133 | 0 | 30.3076 | 0
89 | 1900-03-30 | 2134 | 0 | 27.1001 | 0
89 | 1900-03-30 | 2135 | 0 | 34.632 | 0
89 | 1900-03-30 | 2136 | 0 | 25.8187 | 0
90 | 1900-03-31 | 2137 | 0 | 29.3839 | 0
90 | 1900-03-31 | 2138 | 0 | 27.2693 | 0
90 | 1900-03-31 | 2139 | 0 | 23.1126 | 0
90 | 1900-03-31 | 2140 | 0 | 34.5605 | 0
90 | 1900-03-31 | 2141 | 0 | 38.4306 | 0
90 | 1900-03-31 | 2142 | 0 | 30.5288 | 0
90 | 1900-03-31 | 2143 | 0 | 23.2885 | 0
90 | 1900-03-31 | 2144 | 0 | 38.6542 | 0
90 | 1900-03-31 | 2145 | 0 | 40.0581 | 0
90 | 1900-03-31 | 2146 | 0 | 44.9755 | 0
90 | 1900-03-31 | 2147 | 0 | 46.5826 | 0
90 | 1900-03-31 | 2148 | 0 | 34.5203 | 0
90 | 1900-03-31 | 2149 | 0 | 49.3426 | 0
90 | 1900-03-31 | 2150 | 0 | 59.3306 | 0
90 | 1900-03-31 | 2151 | 0 | 40.3649 | 0
90 | 1900-03-31 | 2152 | 0 | 46.7864 | 0
90 | 1900-03-31 | 2153 | 0 | 34.6281 | 0
90 | 1900-03-31 | 2154 | 0 | 46.1327 | 0
90 | 1900-03-31 | 2155 | 0 | 241.7813 | 0
90 | 1900-03-31 | 2156 | 0 | 28.7473 | 0
90 | 1900-03-31 | 2157 | 0 | 26.5596 | 0
90 | 1900-03-31 | 2158 | 0 | 30.6268 | 0
90 | 1900-03-31 | 2159 | 0 | 38.9492 | 0
90 | 1900-03-31 | 2160 | 0 | 27.9538 | 0
91 | 1900-04-01 | 2161 | 0 | 32.2826 | 0
91 | 1900-04-01 | 2162 | 0 | 28.1898 | 0
91 | 1900-04-01 | 2163 | 0 | 24.0793 | 0
91 | 1900-04-01 | 2164 | 0 | 21.2136 | 0
91 | 1900-04-01 | 2165 | 0 | 28.362 | 0
91 | 1900-04-01 | 2166 | 0 | 23.776 | 0
91 | 1900-04-01 | 2167 | 0 | 34.0159 | 0
91 | 1900-04-01 | 2168 | 0 | 33.1535 | 0
91 | 1900-04-01 | 2169 | 0 | 52.5802 | 0
91 | 1900-04-01 | 2170 | 0 | 25.6467 | 0
91 | 1900-04-01 | 2171 | 0 | 42.7183 | 0
91 | 1900-04-01 | 2172 | 0 | 42.5212 | 0
91 | 1900-04-01 | 2173 | 0 | 38.5622 | 0
91 | 1900-04-01 | 2174 | 0 | 37.7082 | 0
91 | 1900-04-01 | 2175 | 0 | 50.7431 | 0
91 | 1900-04-01 | 2176 | 0 | 35.9436 | 0
91 | 1900-04-01 | 2177 | 0 | 53.2993 | 0
91 | 1900-04-01 | 2178 | 0 | 253.3833 | 0
91 | 1900-04-01 | 2179 | 0 | 35.6051 | 0
91 | 1900-04-01 | 2180 | 0 | 35.8393 | 0
91 | 1900-04-01 | 2181 | 0 | 29.5165 | 0
91 | 1900-04-01 | 2182 | 0 | 27.2136 | 0
91 | 1900-04-01 | 2183 | 0 | 21.835 | 0
91 | 1900-04-01 | 2184 | 0 | 30.8103 | 0
92 | 1900-04-02 | 2185 | 0 | 26.4346 | 0
92 | 1900-04-02 | 2186 | 0 | 32.9183 | 0
92 | 1900-04-02 | 2187 | 0 | 18.5639 | 0
92 | 1900-04-02 | 2188 | 0 | 30.0732 | 0
92 | 1900-04-02 | 2189 | 0 | 26.4375 | 0
92 | 1900-04-02 | 2190 | 0 | 24.7729 | 0
92 | 1900-04-02 | 2191 | 0 | 22.0975 | 0
92 | 1900-04-02 | 2192 | 0 | 35.7067 | 0
92 | 1900-04-02 | 2193 | 0 | 37.2552 | 0
92 | 1900-04-02 | 2194 | 0 | 47.3055 | 0
92 | 1900-04-02 | 2195 | 0 | 48.3753 | 0
92 | 1900-04-02 | 2196 | 0 | 35.2005 | 0
92 | 1900-04-02 | 2197 | 0 | 50.1484 | 0
92 | 1900-04-02 | 2198 | 0 | 39.1395 | 0
92 | 1900-04-02 | 2199 | 0 | 41.7908 | 0
92 | 1900-04-02 | 2200 | 0 | 40.5847 | 0
92 | 1900-04-02 | 2201 | 0 | 51.8021 | 0
92 | 1900-04-02 | 2202 | 0 | 29.2107 | 0
92 | 1900-04-02 | 2203 | 0 | 39.8188 | 0
92 | 1900-04-02 | 2204 | 0 | 27.7327 | 0
92 | 1900-04-02 | 2205 | 0 | 31.6073 | 0
92 | 1900-04-02 | 2206 | 0 | 27.6616 | 0
92 | 1900-04-02 | 2207 | 0 | 27.3696 | 0
92 | 1900-04-02 | 2208 | 0 | 33.2374 | 0
93 | 1900-04-03 | 2209 | 0 | 32.9861 | 0
93 | 1900-04-03 | 2210 | 0 | 28.9539 | 0
93 | 1900-04-03 | 2211 | 0 | 46.6139 | 0
93 | 1900-04-03 | 2212 | 0 | 95.8814 | 0
93 | 1900-04-03 | 2213 | 0 | 123.5004 | 0
93 | 1900-04-03 | 2214 | 0 | 116.6134 | 0
93 | 1900-04-03 | 2215 | 0 | 130.1734 | 0
93 | 1900-04-03 | 2216 | 0 | 116.442 | 0
93 | 1900-04-03 | 2217 | 0 | 112.679 | 0
93 | 1900-04-03 | 2218 | 0 | 126.9689 | 0
93 | 1900-04-03 | 2219 | 0 | 115.9563 | 0
93 | 1900-04-03 | 2220 | 0 | 123.7106 | 0
93 | 1900-04-03 | 2221 | 0 | 72.7491 | 0
93 | 1900-04-03 | 2222 | 0 | 30.478 | 0
93 | 1900-04-03 | 2223 | 0 | 232.8692 | 0
93 | 1900-04-03 | 2224 | 0 | 50.9246 | 0
93 | 1900-04-03 | 2225 | 0 | 37.2336 | 0
93 | 1900-04-03 | 2226 | 0 | 41.1381 | 0
93 | 1900-04-03 | 2227 | 0 | 35.4527 | 0
93 | 1900-04-03 | 2228 | 0 | 34.5234 | 0
93 | 1900-04-03 | 2229 | 0 | 32.6866 | 0
93 | 1900-04-03 | 2230 | 0 | 30.9781 | 0
93 | 1900-04-03 | 2231 | 0 | 32.3478 | 0
93 | 1900-04-03 | 2232 | 0 | 29.6562 | 0
94 | 1900-04-04 | 2233 | 0 | 36.6968 | 0
94 | 1900-04-04 | 2234 | 0 | 33.0205 | 0
94 | 1900-04-04 | 2235 | 0 | 33.309 | 0
94 | 1900-04-04 | 2236 | 0 | 20.1257 | 0
94 | 1900-04-04 | 2237 | 0 | 30.8564 | 0
94 | 1900-04-04 | 2238 | 0 | 47.7076 | 0
94 | 1900-04-04 | 2239 | 0 | 247.8476 | 0
94 | 1900-04-04 | 2240 | 0 | 55.5066 | 0
94 | 1900-04-04 | 2241 | 0 | 48.1782 | 0
94 | 1900-04-04 | 2242 | 0 | 71.2078 | 0
94 | 1900-04-04 | 2243 | 0 | 121.7947 | 0
94 | 1900-04-04 | 2244 | 0 | 93.3893 | 0
94 | 1900-04-04 | 2245 | 0 | 45.2389 | 0
94 | 1900-04-04 | 2246 | 0 | 37.9067 | 0
94 | 1900-04-04 | 2247 | 0 | 36.1322 | 0
94 | 1900-04-04 | 2248 | 0 | 42.6163 | 0
94 | 1900-04-04 | 2249 | 0 | 52.5267 | 0
94 | 1900-04-04 | 2250 | 0 | 54.3084 | 0
94 | 1900-04-04 | 2251 | 0 | 45.9725 | 0
94 | 1900-04-04 | 2252 | 0 | 29.5584 | 0
94 | 1900-04-04 | 2253 | 0 | 28.6757 | 0
94 | 1900-04-04 | 2254 | 0 | 34.0943 | 0
94 | 1900-04-04 | 2255 | 0 | 20.8262 | 0
94 | 1900-04-04 | 2256 | 0 | 28.4394 | 0
95 | 1900-04-05 | 2257 | 0 | 28.9868 | 0
95 | 1900-04-05 | 2258 | 0 | 22.4855 | 0
95 | 1900-04-05 | 2259 | 0 | 31.7433 | 0
95 | 1900-04-05 | 2260 | 0 | 36.3142 | 0
95 | 1900-04-05 | 2261 | 0 | 60.568 | 0
95 | 1900-04-05 | 2262 | 0 | 111.2129 | 0
95 | 1900-04-05 | 2263 | 0 | 57.2827 | 0
95 | 1900-04-05 | 2264 | 0 | 91.4128 | 0
95 | 1900-04-05 | 2265 | 0 | 104.3029 | 0
95 | 1900-04-05 | 2266 | 0 | 83.962 | 0
95 | 1900-04-05 | 2267 | 0 | 47.0464 | 0
95 | 1900-04-05 | 2268 | 0 | 44.8454 | 0
95 | 1900-04-05 | 2269 | 0 | 34.6798 | 0
95 | 1900-04-05 | 2270 | 0 | 42.8916 | 0
95 | 1900-04-05 | 2271 | 0 | 43.6349 | 0
95 | 1900-04-05 | 2272 | 0 | 39.8137 | 0
95 | 1900-04-05 | 2273 | 0 | 39.7734 | 0
95 | 1900-04-05 | 2274 | 0 | 40.2237 | 0
95 | 1900-04-05 | 2275 | 0 | 39.8185 | 0
95 | 1900-04-05 | 2276 | 0 | 32.7615 | 0
95 | 1900-04-05 | 2277 | 0 | 230.1012 | 0
95 | 1900-04-05 | 2278 | 0 | 23.5815 | 0
95 | 1900-04-05 | 2279 | 0 | 31.6688 | 0
95 | 1900-04-05 | 2280 | 0 | 24.7377 | 0
96 | 1900-04-06 | 2281 | 0 | 23.1437 | 0
96 | 1900-04-06 | 2282 | 0 | 24.685 | 0
96 | 1900-04-06 | 2283 | 0 | 24.9693 | 0
96 | 1900-04-06 | 2284 | 0 | 25.5009 | 0
96 | 1900-04-06 | 2285 | 0 | 43.0031 | 0
96 | 1900-04-06 | 2286 | 0 | 90.0744 | 0
96 | 1900-04-06 | 2287 | 0 | 97.5382 | 0
96 | 1900-04-06 | 2288 | 0 | 49.4252 | 0
96 | 1900-04-06 | 2289 | 0 | 49.1478 | 0
96 | 1900-04-06 | 2290 | 0 | 241.6535 | 0
96 | 1900-04-06 | 2291 | 0 | 42.2617 | 0
96 | 1900-04-06 | 2292 | 0 | 47.076 | 0
96 | 1900-04-06 | 2293 | 0 | 35.4137 | 0
96 | 1900-04-06 | 2294 | 0 | 46.5585 | 0
96 | 1900-04-06 | 2295 | 0 | 38.9944 | 0
96 | 1900-04-06 | 2296 | 0 | 48.735 | 0
96 | 1900-04-06 | 2297 | 0 | 40.7964 | 0
96 | 1900-04-06 | 2298 | 0 | 39.9117 | 0
96 | 1900-04-06 | 2299 | 0 | 43.5411 | 0
96 | 1900-04-06 | 2300 | 0 | 30.3588 | 0
96 | 1900-04-06 | 2301 | 0 | 26.706 | 0
96 | 1900-04-06 | 2302 | 0 | 54.4894 | 0
96 | 1900-04-06 | 2303 | 0 | 131.0121 | 0
96 | 1900-04-06 | 2304 | 0 | 110.4621 | 0
97 | 1900-04-07 | 2305 | 0 | 83.4088 | 0
97 | 1900-04-07 | 2306 | 0 | 47.8682 | 0
97 | 1900-04-07 | 2307 | 0 | 27.0205 | 0
97 | 1900-04-07 | 2308 | 0 | 33.4085 | 0
97 | 1900-04-07 | 2309 | 0 | 27.5147 | 0
97 | 1900-04-07 | 2310 | 0 | 28.4989 | 0
97 | 1900-04-07 | 2311 | 0 | 25.4537 | 0
97 | 1900-04-07 | 2312 | 0 | 35.6411 | 0
97 | 1900-04-07 | 2313 | 0 | 72.9708 | 0
97 | 1900-04-07 | 2314 | 0 | 131.2678 | 0
97 | 1900-04-07 | 2315 | 0 | 124.5748 | 0
97 | 1900-04-07 | 2316 | 0 | 90.6592 | 0
97 | 1900-04-07 | 2317 | 0 | 108.6676 | 0
97 | 1900-04-07 | 2318 | 0 | 64.3315 | 0
97 | 1900-04-07 | 2319 | 0 | 84.1036 | 0
97 | 1900-04-07 | 2320 | 0 | 46.5807 | 0
97 | 1900-04-07 | 2321 | 0 | 45.4417 | 0
97 | 1900-04-07 | 2322 | 0 | 45.7615 | 0
97 | 1900-04-07 | 2323 | 0 | 39.3742 | 0
97 | 1900-04-07 | 2324 | 0 | 25.5003 | 0
97 | 1900-04-07 | 2325 | 0 | 29.4128 | 0
97 | 1900-04-07 | 2326 | 0 | 28.8686 | 0
97 | 1900-04-07 | 2327 | 0 | 32.1671 | 0
97 | 1900-04-07 | 2328 | 0 | 40.8928 | 0
98 | 1900-04-08 | 2329 | 0 | 24.8095 | 0
98 | 1900-04-08 | 2330 | 0 | 41.294 | 0
98 | 1900-04-08 | 2331 | 0 | 29.9235 | 0
98 | 1900-04-08 | 2332 | 0 | 30.6357 | 0
98 | 1900-04-08 | 2333 | 0 | 35.7296 | 0
98 | 1900-04-08 | 2334 | 0 | 21.7726 | 0
98 | 1900-04-08 | 2335 | 0 | 21.8193 | 0
98 | 1900-04-08 | 2336 | 0 | 50.1134 | 0
98 | 1900-04-08 | 2337 | 0 | 37.0913 | 0
98 | 1900-04-08 | 2338 | 0 | 31.3352 | 0
98 | 1900-04-08 | 2339 | 0 | 33.9102 | 0
98 | 1900-04-08 | 2340 | 0 | 36.4707 | 0
98 | 1900-04-08 | 2341 | 0 | 36.7607 | 0
98 | 1900-04-08 | 2342 | 0 | 54.8145 | 0
98 | 1900-04-08 | 2343 | 0 | 244.0418 | 0
98 | 1900-04-08 | 2344 | 0 | 52.2409 | 0
98 | 1900-04-08 | 2345 | 0 | 35.2419 | 0
98 | 1900-04-08 | 2346 | 0 | 43.3045 | 0
98 | 1900-04-08 | 2347 | 0 | 26.9121 | 0
98 | 1900-04-08 | 2348 | 0 | 20.0163 | 0
98 | 1900-04-08 | 2349 | 0 | 24.8923 | 0
98 | 1900-04-08 | 2350 | 0 | 21.5522 | 0
98 | 1900-04-08 | 2351 | 0 | 24.9351 | 0
98 | 1900-04-08 | 2352 | 0 | 30.6189 | 0
99 | 1900-04-09 | 2353 | 0 | 26.6618 | 0
99 | 1900-04-09 | 2354 | 0 | 33.368 | 0
99 | 1900-04-09 | 2355 | 0 | 30.4894 | 0
99 | 1900-04-09 | 2356 | 0 | 31.2634 | 0
99 | 1900-04-09 | 2357 | 0 | 31.2964 | 0
99 | 1900-04-09 | 2358 | 0 | 225.7896 | 0
99 | 1900-04-09 | 2359 | 0 | 32.0331 | 0
99 | 1900-04-09 | 2360 | 0 | 55.3564 | 0
99 | 1900-04-09 | 2361 | 0 | 63.7434 | 0
99 | 1900-04-09 | 2362 | 0 | 55.5224 | 0
99 | 1900-04-09 | 2363 | 0 | 37.6789 | 0
99 | 1900-04-09 | 2364 | 0 | 39.8337 | 0
99 | 1900-04-09 | 2365 | 0 | 44.431 | 0
99 | 1900-04-09 | 2366 | 0 | 44.5212 | 0
99 | 1900-04-09 | 2367 | 0 | 31.113 | 0
99 | 1900-04-09 | 2368 | 0 | 50.5501 | 0
99 | 1900-04-09 | 2369 | 0 | 52.232 | 0
99 | 1900-04-09 | 2370 | 0 | 77.9983 | 0
99 | 1900-04-09 | 2371 | 0 | 74.0535 | 0
99 | 1900-04-09 | 2372 | 0 | 70.8004 | 0
99 | 1900-04-09 | 2373 | 0 | 111.9604 | 0
99 | 1900-04-09 | 2374 | 0 | 80.8167 | 0
99 | 1900-04-09 | 2375 | 0 | 28.8989 | 0
99 | 1900-04-09 | 2376 | 0 | 36.5467 | 0
100 | 1900-04-10 | 2377 | 0 | 22.9338 | 0
100 | 1900-04-10 | 2378 | 0 | 34.6197 | 0
100 | 1900-04-10 | 2379 | 0 | 31.9934 | 0
100 | 1900-04-10 | 2380 | 0 | 33.8615 | 0
100 | 1900-04-10 | 2381 | 0 | 28.1053 | 0
100 | 1900-04-10 | 2382 | 0 | 34.4314 | 0
100 | 1900-04-10 | 2383 | 0 | 43.6092 | 0
100 | 1900-04-10 | 2384 | 0 | 82.0077 | 0
100 | 1900-04-10 | 2385 | 0 | 68.6855 | 0
100 | 1900-04-10 | 2386 | 0 | 54.6015 | 0
100 | 1900-04-10 | 2387 | 0 | 102.4862 | 0
100 | 1900-04-10 | 2388 | 0 | 61.3371 | 0
100 | 1900-04-10 | 2389 | 0 | 50.7133 | 0
100 | 1900-04-10 | 2390 | 0 | 51.7079 | 0
100 | 1900-04-10 | 2391 | 0 | 52.7399 | 0
100 | 1900-04-10 | 2392 | 0 | 46.8004 | 0
100 | 1900-04-10 | 2393 | 0 | 42.991 | 0
100 | 1900-04-10 | 2394 | 0 | 49.1318 | 0
100 | 1900-04-10 | 2395 | 0 | 47.9858 | 0
100 | 1900-04-10 | 2396 | 0 | 35.0971 | 0
100 | 1900-04-10 | 2397 | 0 | 30.3096 | 0
100 | 1900-04-10 | 2398 | 0 | 37.6852 | 0
100 | 1900-04-10 | 2399 | 0 | 29.4385 | 0
100 | 1900-04-10 | 2400 | 0 | 23.708 | 0
101 | 1900-04-11 | 2401 | 0 | 25.6287 | 0
101 | 1900-04-11 | 2402 | 0 | 23.7159 | 0
101 | 1900-04-11 | 2403 | 0 | 25.3371 | 0
101 | 1900-04-11 | 2404 | 0 | 31.0478 | 0
101 | 1900-04-11 | 2405 | 0 | 71.1884 | 0
101 | 1900-04-11 | 2406 | 0 | 87.2451 | 0
101 | 1900-04-11 | 2407 | 0 | 32.3268 | 0
101 | 1900-04-11 | 2408 | 0 | 57.8075 | 0
101 | 1900-04-11 | 2409 | 0 | 38.887 | 0
101 | 1900-04-11 | 2410 | 0 | 45.1295 | 0
101 | 1900-04-11 | 2411 | 0 | 109.8033 | 0
101 | 1900-04-11 | 2412 | 0 | 97.4037 | 0
101 | 1900-04-11 | 2413 | 0 | 54.9958 | 0
101 | 1900-04-11 | 2414 | 0 | 49.9718 | 0
101 | 1900-04-11 | 2415 | 0 | 37.466 | 0
101 | 1900-04-11 | 2416 | 0 | 38.856 | 0
101 | 1900-04-11 | 2417 | 0 | 36.2409 | 0
101 | 1900-04-11 | 2418 | 0 | 39.7466 | 0
101 | 1900-04-11 | 2419 | 0 | 43.168 | 0
101 | 1900-04-11 | 2420 | 0 | 24.0548 | 0
101 | 1900-04-11 | 2421 | 0 | 24.5732 | 0
101 | 1900-04-11 | 2422 | 0 | 30.5812 | 0
101 | 1900-04-11 | 2423 | 0 | 25.1417 | 0
101 | 1900-04-11 | 2424 | 0 | 29.0126 | 0
102 | 1900-04-12 | 2425 | 0 | 237.7834 | 0
102 | 1900-04-12 | 2426 | 0 | 30.311 | 0
102 | 1900-04-12 | 2427 | 0 | 223.4418 | 0
102 | 1900-04-12 | 2428 | 0 | 36.9463 | 0
102 | 1900-04-12 | 2429 | 0 | 46.7813 | 0
102 | 1900-04-12 | 2430 | 0 | 99.3384 | 0
102 | 1900-04-12 | 2431 | 0 | 98.0879 | 0
102 | 1900-04-12 | 2432 | 0 | 89.6524 | 0
102 | 1900-04-12 | 2433 | 0 | 37.1638 | 0
102 | 1900-04-12 | 2434 | 0 | 59.4843 | 0
102 | 1900-04-12 | 2435 | 0 | 106.9633 | 0
102 | 1900-04-12 | 2436 | 0 | 124.534 | 0
102 | 1900-04-12 | 2437 | 0 | 83.0109 | 0
102 | 1900-04-12 | 2438 | 0 | 55.6157 | 0
102 | 1900-04-12 | 2439 | 0 | 34.0527 | 0
102 | 1900-04-12 | 2440 | 0 | 43.1372 | 0
102 | 1900-04-12 | 2441 | 0 | 45.6278 | 0
102 | 1900-04-12 | 2442 | 0 | 45.6317 | 0
102 | 1900-04-12 | 2443 | 0 | 38.3372 | 0
102 | 1900-04-12 | 2444 | 0 | 31.047 | 0
102 | 1900-04-12 | 2445 | 0 | 19.8084 | 0
102 | 1900-04-12 | 2446 | 0 | 25.8036 | 0
102 | 1900-04-12 | 2447 | 0 | 28.5413 | 0
102 | 1900-04-12 | 2448 | 0 | 34.3987 | 0
103 | 1900-04-13 | 2449 | 0 | 29.4832 | 0
103 | 1900-04-13 | 2450 | 0 | 36.2673 | 0
103 | 1900-04-13 | 2451 | 0 | 23.5957 | 0
103 | 1900-04-13 | 2452 | 0 | 21.7174 | 0
103 | 1900-04-13 | 2453 | 0 | 38.6022 | 0
103 | 1900-04-13 | 2454 | 0 | 34.6248 | 0
103 | 1900-04-13 | 2455 | 0 | 82.4578 | 0
103 | 1900-04-13 | 2456 | 0 | 79.1585 | 0
103 | 1900-04-13 | 2457 | 0 | 46.8254 | 0
103 | 1900-04-13 | 2458 | 0 | 54.5313 | 0
103 | 1900-04-13 | 2459 | 0 | 49.0517 | 0
103 | 1900-04-13 | 2460 | 0 | 57.755 | 0
103 | 1900-04-13 | 2461 | 0 | 40.7614 | 0
103 | 1900-04-13 | 2462 | 0 | 53.0703 | 0
103 | 1900-04-13 | 2463 | 0 | 56.93 | 0
103 | 1900-04-13 | 2464 | 0 | 54.1174 | 0
103 | 1900-04-13 | 2465 | 0 | 44.0496 | 0
103 | 1900-04-13 | 2466 | 0 | 48.7104 | 0
103 | 1900-04-13 | 2467 | 0 | 39.3939 | 0
103 | 1900-04-13 | 2468 | 0 | 29.1357 | 0
103 | 1900-04-13 | 2469 | 0 | 31.2682 | 0
103 | 1900-04-13 | 2470 | 0 | 29.6909 | 0
103 | 1900-04-13 | 2471 | 0 | 27.4234 | 0
103 | 1900-04-13 | 2472 | 0 | 28.8353 | 0
104 | 1900-04-14 | 2473 | 0 | 29.1477 | 0
104 | 1900-04-14 | 2474 | 0 | 30.5527 | 0
104 | 1900-04-14 | 2475 | 0 | 35.0441 | 0
104 | 1900-04-14 | 2476 | 0 | 23.0923 | 0
104 | 1900-04-14 | 2477 | 0 | 32.8738 | 0
104 | 1900-04-14 | 2478 | 0 | 29.8721 | 0
104 | 1900-04-14 | 2479 | 0 | 33.2339 | 0
104 | 1900-04-14 | 2480 | 0 | 41.1658 | 0
104 | 1900-04-14 | 2481 | 0 | 50.5666 | 0
104 | 1900-04-14 | 2482 | 0 | 45.8236 | 0
104 | 1900-04-14 | 2483 | 0 | 57.7658 | 0
104 | 1900-04-14 | 2484 | 0 | 45.164 | 0
104 | 1900-04-14 | 2485 | 0 | 40.409 | 0
104 | 1900-04-14 | 2486 | 0 | 36.1296 | 0
104 | 1900-04-14 | 2487 | 0 | 48.3022 | 0
104 | 1900-04-14 | 2488 | 0 | 45.0692 | 0
104 | 1900-04-14 | 2489 | 0 | 48.3344 | 0
104 | 1900-04-14 | 2490 | 0 | 21.8228 | 0
104 | 1900-04-14 | 2491 | 0 | 37.1682 | 0
104 | 1900-04-14 | 2492 | 0 | 25.8092 | 0
104 | 1900-04-14 | 2493 | 0 | 224.5988 | 0
104 | 1900-04-14 | 2494 | 0 | 29.9883 | 0
104 | 1900-04-14 | 2495 | 0 | 23.9003 | 0
104 | 1900-04-14 | 2496 | 0 | 39.3494 | 0
105 | 1900-04-15 | 2497 | 0 | 30.1971 | 0
105 | 1900-04-15 | 2498 | 0 | 25.9938 | 0
105 | 1900-04-15 | 2499 | 0 | 30.267 | 0
105 | 1900-04-15 | 2500 | 0 | 28.3972 | 0
105 | 1900-04-15 | 2501 | 0 | 30.3701 | 0
105 | 1900-04-15 | 2502 | 0 | 38.3005 | 0
105 | 1900-04-15 | 2503 | 0 | 48.6458 | 0
105 | 1900-04-15 | 2504 | 0 | 53.3945 | 0
105 | 1900-04-15 | 2505 | 0 | 33.3378 | 0
105 | 1900-04-15 | 2506 | 0 | 48.1086 | 0
105 | 1900-04-15 | 2507 | 0 | 48.8877 | 0
105 | 1900-04-15 | 2508 | 0 | 246.6632 | 0
105 | 1900-04-15 | 2509 | 0 | 29.8429 | 0
105 | 1900-04-15 | 2510 | 0 | 54.1599 | 0
105 | 1900-04-15 | 2511 | 0 | 41.3008 | 0
105 | 1900-04-15 | 2512 | 0 | 41.9413 | 0
105 | 1900-04-15 | 2513 | 0 | 35.1935 | 0
105 | 1900-04-15 | 2514 | 0 | 39.1245 | 0
105 | 1900-04-15 | 2515 | 0 | 47.6156 | 0
105 | 1900-04-15 | 2516 | 0 | 31.5275 | 0
105 | 1900-04-15 | 2517 | 0 | 22.653 | 0
105 | 1900-04-15 | 2518 | 0 | 30.235 | 0
105 | 1900-04-15 | 2519 | 0 | 27.1721 | 0
105 | 1900-04-15 | 2520 | 0 | 34.8835 | 0
106 | 1900-04-16 | 2521 | 0 | 24.8109 | 0
106 | 1900-04-16 | 2522 | 0 | 33.2945 | 0
106 | 1900-04-16 | 2523 | 0 | 76.8946 | 0
106 | 1900-04-16 | 2524 | 0 | 116.3982 | 0
106 | 1900-04-16 | 2525 | 0 | 94.3791 | 0
106 | 1900-04-16 | 2526 | 0 | 95.381 | 0
106 | 1900-04-16 | 2527 | 0 | 96.1956 | 0
106 | 1900-04-16 | 2528 | 0 | 105.7974 | 0
106 | 1900-04-16 | 2529 | 0 | 117.395 | 0
106 | 1900-04-16 | 2530 | 0 | 94.9888 | 0
106 | 1900-04-16 | 2531 | 0 | 81.1987 | 0
106 | 1900-04-16 | 2532 | 0 | 131.3214 | 0
106 | 1900-04-16 | 2533 | 0 | 147.9199 | 0
106 | 1900-04-16 | 2534 | 0 | 107.8365 | 0
106 | 1900-04-16 | 2535 | 0 | 34.4729 | 0
106 | 1900-04-16 | 2536 | 0 | 47.5199 | 0
106 | 1900-04-16 | 2537 | 0 | 56.7185 | 0
106 | 1900-04-16 | 2538 | 0 | 37.2309 | 0
106 | 1900-04-16 | 2539 | 0 | 49.7598 | 0
106 | 1900-04-16 | 2540 | 0 | 27.588 | 0
106 | 1900-04-16 | 2541 | 0 | 28.3881 | 0
106 | 1900-04-16 | 2542 | 0 | 35.7501 | 0
106 | 1900-04-16 | 2543 | 0 | 24.4065 | 0
106 | 1900-04-16 | 2544 | 0 | 23.8449 | 0
107 | 1900-04-17 | 2545 | 0 | 30.7341 | 0
107 | 1900-04-17 | 2546 | 0 | 29.3453 | 0
107 | 1900-04-17 | 2547 | 0 | 33.1973 | 0
107 | 1900-04-17 | 2548 | 0 | 41.7012 | 0
107 | 1900-04-17 | 2549 | 0 | 73.4936 | 0
107 | 1900-04-17 | 2550 | 0 | 98.9362 | 0
107 | 1900-04-17 | 2551 | 0 | 104.2478 | 0
107 | 1900-04-17 | 2552 | 0 | 95.6681 | 0
107 | 1900-04-17 | 2553 | 0 | 92.899 | 0
107 | 1900-04-17 | 2554 | 0 | 108.2684 | 0
107 | 1900-04-17 | 2555 | 0 | 131.0829 | 0
107 | 1900-04-17 | 2556 | 0 | 134.0955 | 0
107 | 1900-04-17 | 2557 | 0 | 147.7369 | 0
107 | 1900-04-17 | 2558 | 0 | 101.6878 | 0
107 | 1900-04-17 | 2559 | 0 | 78.1193 | 0
107 | 1900-04-17 | 2560 | 0 | 46.9968 | 0
107 | 1900-04-17 | 2561 | 0 | 237.6966 | 0
107 | 1900-04-17 | 2562 | 0 | 49.8575 | 0
107 | 1900-04-17 | 2563 | 0 | 47.3336 | 0
107 | 1900-04-17 | 2564 | 0 | 24.4986 | 0
107 | 1900-04-17 | 2565 | 0 | 24.0518 | 0
107 | 1900-04-17 | 2566 | 0 | 25.7981 | 0
107 | 1900-04-17 | 2567 | 0 | 26.153 | 0
107 | 1900-04-17 | 2568 | 0 | 23.2091 | 0
108 | 1900-04-18 | 2569 | 0 | 26.5265 | 0
108 | 1900-04-18 | 2570 | 0 | 32.6301 | 0
108 | 1900-04-18 | 2571 | 0 | 41.3332 | 0
108 | 1900-04-18 | 2572 | 0 | 35.22 | 0
108 | 1900-04-18 | 2573 | 0 | 84.1796 | 0
108 | 1900-04-18 | 2574 | 0 | 73.7574 | 0
108 | 1900-04-18 | 2575 | 0 | 84.5468 | 0
108 | 1900-04-18 | 2576 | 0 | 98.5812 | 0
108 | 1900-04-18 | 2577 | 0 | 100.9695 | 0
108 | 1900-04-18 | 2578 | 0 | 91.9812 | 0
108 | 1900-04-18 | 2579 | 0 | 142.905 | 0
108 | 1900-04-18 | 2580 | 0 | 127.3182 | 0
108 | 1900-04-18 | 2581 | 0 | 133.8038 | 0
108 | 1900-04-18 | 2582 | 0 | 128.4236 | 0
108 | 1900-04-18 | 2583 | 0 | 70.0565 | 0
108 | 1900-04-18 | 2584 | 0 | 45.0743 | 0
108 | 1900-04-18 | 2585 | 0 | 44.8688 | 0
108 | 1900-04-18 | 2586 | 0 | 41.8293 | 0
108 | 1900-04-18 | 2587 | 0 | 40.3717 | 0
108 | 1900-04-18 | 2588 | 0 | 25.5982 | 0
108 | 1900-04-18 | 2589 | 0 | 227.202 | 0
108 | 1900-04-18 | 2590 | 0 | 37.888 | 0
108 | 1900-04-18 | 2591 | 0 | 25.6795 | 0
108 | 1900-04-18 | 2592 | 0 | 23.3622 | 0
109 | 1900-04-19 | 2593 | 0 | 21.3957 | 0
109 | 1900-04-19 | 2594 | 0 | 28.451 | 0
109 | 1900-04-19 | 2595 | 0 | 29.2376 | 0
109 | 1900-04-19 | 2596 | 0 | 23.5652 | 0
109 | 1900-04-19 | 2597 | 0 | 35.8353 | 0
109 | 1900-04-19 | 2598 | 0 | 62.4589 | 0
109 | 1900-04-19 | 2599 | 0 | 111.6206 | 0
109 | 1900-04-19 | 2600 | 0 | 118.0028 | 0
109 | 1900-04-19 | 2601 | 0 | 82.5103 | 0
109 | 1900-04-19 | 2602 | 0 | 30.8706 | 0
109 | 1900-04-19 | 2603 | 0 | 61.2979 | 0
109 | 1900-04-19 | 2604 | 0 | 96.6345 | 0
109 | 1900-04-19 | 2605 | 0 | 102.3534 | 0
109 | 1900-04-19 | 2606 | 0 | 126.4814 | 0
109 | 1900-04-19 | 2607 | 0 | 59.6008 | 0
109 | 1900-04-19 | 2608 | 0 | 41.5799 | 0
109 | 1900-04-19 | 2609 | 0 | 43.6729 | 0
109 | 1900-04-19 | 2610 | 0 | 48.3077 | 0
109 | 1900-04-19 | 2611 | 0 | 56.4081 | 0
109 | 1900-04-19 | 2612 | 0 | 29.9284 | 0
109 | 1900-04-19 | 2613 | 0 | 32.3459 | 0
109 | 1900-04-19 | 2614 | 0 | 32.2542 | 0
109 | 1900-04-19 | 2615 | 0 | 33.2158 | 0
109 | 1900-04-19 | 2616 | 0 | 26.4251 | 0
110 | 1900-04-20 | 2617 | 0 | 20.4741 | 0
110 | 1900-04-20 | 2618 | 0 | 21.4293 | 0
110 | 1900-04-20 | 2619 | 0 | 27.4835 | 0
110 | 1900-04-20 | 2620 | 0 | 17.8485 | 0
110 | 1900-04-20 | 2621 | 0 | 42.713 | 0
110 | 1900-04-20 | 2622 | 0 | 69.8571 | 0
110 | 1900-04-20 | 2623 | 0 | 66.8401 | 0
110 | 1900-04-20 | 2624 | 0 | 44.7823 | 0
110 | 1900-04-20 | 2625 | 0 | 39.4739 | 0
110 | 1900-04-20 | 2626 | 0 | 50.6529 | 0
110 | 1900-04-20 | 2627 | 0 | 50.2611 | 0
110 | 1900-04-20 | 2628 | 0 | 38.442 | 0
110 | 1900-04-20 | 2629 | 0 | 245.9601 | 0
110 | 1900-04-20 | 2630 | 0 | 44.0844 | 0
110 | 1900-04-20 | 2631 | 0 | 46.8459 | 0
110 | 1900-04-20 | 2632 | 0 | 40.7497 | 0
110 | 1900-04-20 | 2633 | 0 | 31.9219 | 0
110 | 1900-04-20 | 2634 | 0 | 43.9623 | 0
110 | 1900-04-20 | 2635 | 0 | 46.6616 | 0
110 | 1900-04-20 | 2636 | 0 | 24.796 | 0
110 | 1900-04-20 | 2637 | 0 | 24.5879 | 0
110 | 1900-04-20 | 2638 | 0 | 27.4403 | 0
110 | 1900-04-20 | 2639 | 0 | 32.3417 | 0
110 | 1900-04-20 | 2640 | 0 | 30.4274 | 0
111 | 1900-04-21 | 2641 | 0 | 28.5102 | 0
111 | 1900-04-21 | 2642 | 0 | 35.0055 | 0
111 | 1900-04-21 | 2643 | 0 | 59.05 | 0
111 | 1900-04-21 | 2644 | 0 | 84.1503 | 0
111 | 1900-04-21 | 2645 | 0 | 82.2169 | 0
111 | 1900-04-21 | 2646 | 0 | 100.5643 | 0
111 | 1900-04-21 | 2647 | 0 | 78.4627 | 0
111 | 1900-04-21 | 2648 | 0 | 83.5162 | 0
111 | 1900-04-21 | 2649 | 0 | 83.1833 | 0
111 | 1900-04-21 | 2650 | 0 | 89.2404 | 0
111 | 1900-04-21 | 2651 | 0 | 101.1983 | 0
111 | 1900-04-21 | 2652 | 0 | 75.0701 | 0
111 | 1900-04-21 | 2653 | 0 | 36.5895 | 0
111 | 1900-04-21 | 2654 | 0 | 58.4808 | 0
111 | 1900-04-21 | 2655 | 0 | 33.9157 | 0
111 | 1900-04-21 | 2656 | 0 | 34.1579 | 0
111 | 1900-04-21 | 2657 | 0 | 32.8172 | 0
111 | 1900-04-21 | 2658 | 0 | 62.8554 | 0
111 | 1900-04-21 | 2659 | 0 | 38.7269 | 0
111 | 1900-04-21 | 2660 | 0 | 29.4923 | 0
111 | 1900-04-21 | 2661 | 0 | 27.2716 | 0
111 | 1900-04-21 | 2662 | 0 | 27.0386 | 0
111 | 1900-04-21 | 2663 | 0 | 25.7662 | 0
111 | 1900-04-21 | 2664 | 0 | 27.2754 | 0
112 | 1900-04-22 | 2665 | 0 | 32.7591 | 0
112 | 1900-04-22 | 2666 | 0 | 24.8575 | 0
112 | 1900-04-22 | 2667 | 0 | 21.7247 | 0
112 | 1900-04-22 | 2668 | 0 | 33.118 | 0
112 | 1900-04-22 | 2669 | 0 | 28.3461 | 0
112 | 1900-04-22 | 2670 | 0 | 24.5429 | 0
112 | 1900-04-22 | 2671 | 0 | 29.8963 | 0
112 | 1900-04-22 | 2672 | 0 | 49.0575 | 0
112 | 1900-04-22 | 2673 | 0 | 39.517 | 0
112 | 1900-04-22 | 2674 | 0 | 32.0403 | 0
112 | 1900-04-22 | 2675 | 0 | 54.3799 | 0
112 | 1900-04-22 | 2676 | 0 | 49.2301 | 0
112 | 1900-04-22 | 2677 | 0 | 41.3523 | 0
112 | 1900-04-22 | 2678 | 0 | 63.5676 | 0
112 | 1900-04-22 | 2679 | 0 | 51.1049 | 0
112 | 1900-04-22 | 2680 | 0 | 53.6804 | 0
112 | 1900-04-22 | 2681 | 0 | 36.7659 | 0
112 | 1900-04-22 | 2682 | 0 | 50.2826 | 0
112 | 1900-04-22 | 2683 | 0 | 44.8628 | 0
112 | 1900-04-22 | 2684 | 0 | 25.6437 | 0
112 | 1900-04-22 | 2685 | 0 | 31.7519 | 0
112 | 1900-04-22 | 2686 | 0 | 32.5171 | 0
112 | 1900-04-22 | 2687 | 0 | 29.2977 | 0
112 | 1900-04-22 | 2688 | 0 | 230.3591 | 0
113 | 1900-04-23 | 2689 | 0 | 28.7379 | 0
113 | 1900-04-23 | 2690 | 0 | 26.5907 | 0
113 | 1900-04-23 | 2691 | 0 | 23.5654 | 0
113 | 1900-04-23 | 2692 | 0 | 65.8353 | 0
113 | 1900-04-23 | 2693 | 0 | 125.7765 | 0
113 | 1900-04-23 | 2694 | 0 | 129.7718 | 0
113 | 1900-04-23 | 2695 | 0 | 100.8098 | 0
113 | 1900-04-23 | 2696 | 0 | 127.7595 | 0
113 | 1900-04-23 | 2697 | 0 | 105.5896 | 0
113 | 1900-04-23 | 2698 | 0 | 287.0016 | 0
113 | 1900-04-23 | 2699 | 0 | 68.6595 | 0
113 | 1900-04-23 | 2700 | 0 | 38.5056 | 0
113 | 1900-04-23 | 2701 | 0 | 47.4918 | 0
113 | 1900-04-23 | 2702 | 0 | 41.5787 | 0
113 | 1900-04-23 | 2703 | 0 | 44.7666 | 0
113 | 1900-04-23 | 2704 | 0 | 53.2316 | 0
113 | 1900-04-23 | 2705 | 0 | 38.0528 | 0
113 | 1900-04-23 | 2706 | 0 | 43.0221 | 0
113 | 1900-04-23 | 2707 | 0 | 25.4277 | 0
113 | 1900-04-23 | 2708 | 0 | 27.8726 | 0
113 | 1900-04-23 | 2709 | 0 | 25.9174 | 0
113 | 1900-04-23 | 2710 | 0 | 32.1845 | 0
113 | 1900-04-23 | 2711 | 0 | 33.6507 | 0
113 | 1900-04-23 | 2712 | 0 | 27.2574 | 0
114 | 1900-04-24 | 2713 | 0 | 27.9183 | 0
114 | 1900-04-24 | 2714 | 0 | 27.4783 | 0
114 | 1900-04-24 | 2715 | 0 | 35.312 | 0
114 | 1900-04-24 | 2716 | 0 | 38.1336 | 0
114 | 1900-04-24 | 2717 | 0 | 75.9118 | 0
114 | 1900-04-24 | 2718 | 0 | 69.45 | 0
114 | 1900-04-24 | 2719 | 0 | 48.8707 | 0
114 | 1900-04-24 | 2720 | 0 | 29.3875 | 0
114 | 1900-04-24 | 2721 | 0 | 57.3433 | 0
114 | 1900-04-24 | 2722 | 0 | 94.4774 | 0
114 | 1900-04-24 | 2723 | 0 | 114.4355 | 0
114 | 1900-04-24 | 2724 | 0 | 71.3031 | 0
114 | 1900-04-24 | 2725 | 0 | 39.3689 | 0
114 | 1900-04-24 | 2726 | 0 | 54.4442 | 0
114 | 1900-04-24 | 2727 | 0 | 41.5914 | 0
114 | 1900-04-24 | 2728 | 0 | 41.0446 | 0
114 | 1900-04-24 | 2729 | 0 | 47.21 | 0
114 | 1900-04-24 | 2730 | 0 | 41.2494 | 0
114 | 1900-04-24 | 2731 | 0 | 54.135 | 0
114 | 1900-04-24 | 2732 | 0 | 27.6688 | 0
114 | 1900-04-24 | 2733 | 0 | 30.4731 | 0
114 | 1900-04-24 | 2734 | 0 | 33.34 | 0
114 | 1900-04-24 | 2735 | 0 | 20.1008 | 0
114 | 1900-04-24 | 2736 | 0 | 28.9348 | 0
115 | 1900-04-25 | 2737 | 0 | 31.876 | 0
115 | 1900-04-25 | 2738 | 0 | 29.4347 | 0
115 | 1900-04-25 | 2739 | 0 | 27.7845 | 0
115 | 1900-04-25 | 2740 | 0 | 31.7987 | 0
115 | 1900-04-25 | 2741 | 0 | 34.8994 | 0
115 | 1900-04-25 | 2742 | 0 | 38.3048 | 0
115 | 1900-04-25 | 2743 | 0 | 64.9649 | 0
115 | 1900-04-25 | 2744 | 0 | 55.137 | 0
115 | 1900-04-25 | 2745 | 0 | 53.4811 | 0
115 | 1900-04-25 | 2746 | 0 | 44.5776 | 0
115 | 1900-04-25 | 2747 | 0 | 41.9041 | 0
115 | 1900-04-25 | 2748 | 0 | 43.5129 | 0
115 | 1900-04-25 | 2749 | 0 | 37.6235 | 0
115 | 1900-04-25 | 2750 | 0 | 40.4054 | 0
115 | 1900-04-25 | 2751 | 0 | 46.8524 | 0
115 | 1900-04-25 | 2752 | 0 | 49.537 | 0
115 | 1900-04-25 | 2753 | 0 | 36.7648 | 0
115 | 1900-04-25 | 2754 | 0 | 53.3516 | 0
115 | 1900-04-25 | 2755 | 0 | 54.4131 | 0
115 | 1900-04-25 | 2756 | 0 | 27.9035 | 0
115 | 1900-04-25 | 2757 | 0 | 38.4676 | 0
115 | 1900-04-25 | 2758 | 0 | 30.9226 | 0
115 | 1900-04-25 | 2759 | 0 | 30.8572 | 0
115 | 1900-04-25 | 2760 | 0 | 28.9299 | 0
116 | 1900-04-26 | 2761 | 0 | 30.7212 | 0
116 | 1900-04-26 | 2762 | 0 | 31.8203 | 0
116 | 1900-04-26 | 2763 | 0 | 234.8485 | 0
116 | 1900-04-26 | 2764 | 0 | 32.5077 | 0
116 | 1900-04-26 | 2765 | 0 | 51.2439 | 0
116 | 1900-04-26 | 2766 | 0 | 284.8111 | 0
116 | 1900-04-26 | 2767 | 0 | 40.1033 | 0
116 | 1900-04-26 | 2768 | 0 | 50.975 | 0
116 | 1900-04-26 | 2769 | 0 | 36.4372 | 0
116 | 1900-04-26 | 2770 | 0 | 39.1344 | 0
116 | 1900-04-26 | 2771 | 0 | 45.1181 | 0
116 | 1900-04-26 | 2772 | 0 | 36.2219 | 0
116 | 1900-04-26 | 2773 | 0 | 41.8394 | 0
116 | 1900-04-26 | 2774 | 0 | 45.3301 | 0
116 | 1900-04-26 | 2775 | 0 | 50.7271 | 0
116 | 1900-04-26 | 2776 | 0 | 41.39 | 0
116 | 1900-04-26 | 2777 | 0 | 27.5622 | 0
116 | 1900-04-26 | 2778 | 0 | 49.6709 | 0
116 | 1900-04-26 | 2779 | 0 | 49.957 | 0
116 | 1900-04-26 | 2780 | 0 | 31.513 | 0
116 | 1900-04-26 | 2781 | 0 | 27.109 | 0
116 | 1900-04-26 | 2782 | 0 | 29.5314 | 0
116 | 1900-04-26 | 2783 | 0 | 28.9069 | 0
116 | 1900-04-26 | 2784 | 0 | 28.3339 | 0
117 | 1900-04-27 | 2785 | 0 | 24.8894 | 0
117 | 1900-04-27 | 2786 | 0 | 28.1113 | 0
117 | 1900-04-27 | 2787 | 0 | 26.0904 | 0
117 | 1900-04-27 | 2788 | 0 | 22.664 | 0
117 | 1900-04-27 | 2789 | 0 | 33.2894 | 0
117 | 1900-04-27 | 2790 | 0 | 20.0539 | 0
117 | 1900-04-27 | 2791 | 0 | 32.9126 | 0
117 | 1900-04-27 | 2792 | 0 | 49.0166 | 0
117 | 1900-04-27 | 2793 | 0 | 51.6873 | 0
117 | 1900-04-27 | 2794 | 0 | 56.1362 | 0
117 | 1900-04-27 | 2795 | 0 | 29.5491 | 0
117 | 1900-04-27 | 2796 | 0 | 49.7408 | 0
117 | 1900-04-27 | 2797 | 0 | 42.6723 | 0
117 | 1900-04-27 | 2798 | 0 | 42.3841 | 0
117 | 1900-04-27 | 2799 | 0 | 33.1655 | 0
117 | 1900-04-27 | 2800 | 0 | 49.2043 | 0
117 | 1900-04-27 | 2801 | 0 | 47.1686 | 0
117 | 1900-04-27 | 2802 | 0 | 43.9588 | 0
117 | 1900-04-27 | 2803 | 0 | 49.1704 | 0
117 | 1900-04-27 | 2804 | 0 | 27.8229 | 0
117 | 1900-04-27 | 2805 | 0 | 34.9627 | 0
117 | 1900-04-27 | 2806 | 0 | 35.8089 | 0
117 | 1900-04-27 | 2807 | 0 | 27.281 | 0
117 | 1900-04-27 | 2808 | 0 | 29.0352 | 0
118 | 1900-04-28 | 2809 | 0 | 31.7842 | 0
118 | 1900-04-28 | 2810 | 0 | 31.8115 | 0
118 | 1900-04-28 | 2811 | 0 | 35.617 | 0
118 | 1900-04-28 | 2812 | 0 | 28.5386 | 0
118 | 1900-04-28 | 2813 | 0 | 29.7924 | 0
118 | 1900-04-28 | 2814 | 0 | 26.8432 | 0
118 | 1900-04-28 | 2815 | 0 | 34.6043 | 0
118 | 1900-04-28 | 2816 | 0 | 62.217 | 0
118 | 1900-04-28 | 2817 | 0 | 55.4332 | 0
118 | 1900-04-28 | 2818 | 0 | 57.9908 | 0
118 | 1900-04-28 | 2819 | 0 | 51.4282 | 0
118 | 1900-04-28 | 2820 | 0 | 45.7814 | 0
118 | 1900-04-28 | 2821 | 0 | 46.0492 | 0
118 | 1900-04-28 | 2822 | 0 | 44.4036 | 0
118 | 1900-04-28 | 2823 | 0 | 49.2176 | 0
118 | 1900-04-28 | 2824 | 0 | 44.712 | 0
118 | 1900-04-28 | 2825 | 0 | 41.1546 | 0
118 | 1900-04-28 | 2826 | 0 | 36.2809 | 0
118 | 1900-04-28 | 2827 | 0 | 37.3018 | 0
118 | 1900-04-28 | 2828 | 0 | 28.4767 | 0
118 | 1900-04-28 | 2829 | 0 | 28.2576 | 0
118 | 1900-04-28 | 2830 | 0 | 23.8476 | 0
118 | 1900-04-28 | 2831 | 0 | 29.2909 | 0
118 | 1900-04-28 | 2832 | 0 | 29.1779 | 0
119 | 1900-04-29 | 2833 | 0 | 225.6725 | 0
119 | 1900-04-29 | 2834 | 0 | 38.6293 | 0
119 | 1900-04-29 | 2835 | 0 | 36.773 | 0
119 | 1900-04-29 | 2836 | 0 | 35.116 | 0
119 | 1900-04-29 | 2837 | 0 | 229.0689 | 0
119 | 1900-04-29 | 2838 | 0 | 30.8317 | 0
119 | 1900-04-29 | 2839 | 0 | 19.5387 | 0
119 | 1900-04-29 | 2840 | 0 | 42.2189 | 0
119 | 1900-04-29 | 2841 | 0 | 52.696 | 0
119 | 1900-04-29 | 2842 | 0 | 44.0884 | 0
119 | 1900-04-29 | 2843 | 0 | 47.5549 | 0
119 | 1900-04-29 | 2844 | 0 | 32.1113 | 0
119 | 1900-04-29 | 2845 | 0 | 42.7932 | 0
119 | 1900-04-29 | 2846 | 0 | 45.5208 | 0
119 | 1900-04-29 | 2847 | 0 | 33.4888 | 0
119 | 1900-04-29 | 2848 | 0 | 40.5246 | 0
119 | 1900-04-29 | 2849 | 0 | 38.1068 | 0
119 | 1900-04-29 | 2850 | 0 | 58.467 | 0
119 | 1900-04-29 | 2851 | 0 | 43.7442 | 0
119 | 1900-04-29 | 2852 | 0 | 34.8203 | 0
119 | 1900-04-29 | 2853 | 0 | 33.822 | 0
119 | 1900-04-29 | 2854 | 0 | 28.356 | 0
119 | 1900-04-29 | 2855 | 0 | 28.7617 | 0
119 | 1900-04-29 | 2856 | 0 | 24.5714 | 0
120 | 1900-04-30 | 2857 | 0 | 27.0398 | 0
120 | 1900-04-30 | 2858 | 0 | 39.3868 | 0
120 | 1900-04-30 | 2859 | 0 | 33.3134 | 0
120 | 1900-04-30 | 2860 | 0 | 31.9566 | 0
120 | 1900-04-30 | 2861 | 0 | 49.3431 | 0
120 | 1900-04-30 | 2862 | 0 | 46.9345 | 0
120 | 1900-04-30 | 2863 | 0 | 107.1494 | 0
120 | 1900-04-30 | 2864 | 0 | 84.9361 | 0
120 | 1900-04-30 | 2865 | 0 | 41.8091 | 0
120 | 1900-04-30 | 2866 | 0 | 46.0542 | 0
120 | 1900-04-30 | 2867 | 0 | 52.9502 | 0
120 | 1900-04-30 | 2868 | 0 | 68.5083 | 0
120 | 1900-04-30 | 2869 | 0 | 47.5412 | 0
120 | 1900-04-30 | 2870 | 0 | 38.3889 | 0
120 | 1900-04-30 | 2871 | 0 | 29.7089 | 0
120 | 1900-04-30 | 2872 | 0 | 34.6184 | 0
120 | 1900-04-30 | 2873 | 0 | 56.5072 | 0
120 | 1900-04-30 | 2874 | 0 | 51.6042 | 0
120 | 1900-04-30 | 2875 | 0 | 39.7925 | 0
120 | 1900-04-30 | 2876 | 0 | 30.8053 | 0
120 | 1900-04-30 | 2877 | 0 | 36.3017 | 0
120 | 1900-04-30 | 2878 | 0 | 25.1732 | 0
120 | 1900-04-30 | 2879 | 0 | 35.3307 | 0
120 | 1900-04-30 | 2880 | 0 | 28.1138 | 0
121 | 1900-05-01 | 2881 | 0 | 34.7291 | 0
121 | 1900-05-01 | 2882 | 0 | 32.3645 | 0
121 | 1900-05-01 | 2883 | 0 | 37.4725 | 0
121 | 1900-05-01 | 2884 | 0 | 35.5988 | 0
121 | 1900-05-01 | 2885 | 0 | 59.6167 | 0
121 | 1900-05-01 | 2886 | 0 | 85.0423 | 0
121 | 1900-05-01 | 2887 | 0 | 98.1944 | 0
121 | 1900-05-01 | 2888 | 0 | 50.4896 | 0
121 | 1900-05-01 | 2889 | 0 | 34.3162 | 0
121 | 1900-05-01 | 2890 | 0 | 58.5479 | 0
121 | 1900-05-01 | 2891 | 0 | 79.0817 | 0
121 | 1900-05-01 | 2892 | 0 | 57.2571 | 0
121 | 1900-05-01 | 2893 | 0 | 58.911 | 0
121 | 1900-05-01 | 2894 | 0 | 247.8403 | 0
121 | 1900-05-01 | 2895 | 0 | 39.1638 | 0
121 | 1900-05-01 | 2896 | 0 | 40.2442 | 0
121 | 1900-05-01 | 2897 | 0 | 51.5317 | 0
121 | 1900-05-01 | 2898 | 0 | 36.9729 | 0
121 | 1900-05-01 | 2899 | 0 | 58.3213 | 0
121 | 1900-05-01 | 2900 | 0 | 112.2404 | 0
121 | 1900-05-01 | 2901 | 0 | 93.3463 | 0
121 | 1900-05-01 | 2902 | 0 | 65.7723 | 0
121 | 1900-05-01 | 2903 | 0 | 66.3046 | 0
121 | 1900-05-01 | 2904 | 0 | 44.2076 | 0
122 | 1900-05-02 | 2905 | 0 | 52.7197 | 0
122 | 1900-05-02 | 2906 | 0 | 45.656 | 0
122 | 1900-05-02 | 2907 | 0 | 30.3282 | 0
122 | 1900-05-02 | 2908 | 0 | 28.0303 | 0
122 | 1900-05-02 | 2909 | 0 | 40.3334 | 0
122 | 1900-05-02 | 2910 | 0 | 59.1732 | 0
122 | 1900-05-02 | 2911 | 0 | 54.1651 | 0
122 | 1900-05-02 | 2912 | 0 | 83.4725 | 0
122 | 1900-05-02 | 2913 | 0 | 121.6567 | 0
122 | 1900-05-02 | 2914 | 0 | 109.4594 | 0
122 | 1900-05-02 | 2915 | 0 | 45.3936 | 0
122 | 1900-05-02 | 2916 | 0 | 41.4695 | 0
122 | 1900-05-02 | 2917 | 0 | 240.1729 | 0
122 | 1900-05-02 | 2918 | 0 | 31.7276 | 0
122 | 1900-05-02 | 2919 | 0 | 41.4522 | 0
122 | 1900-05-02 | 2920 | 0 | 33.9905 | 0
122 | 1900-05-02 | 2921 | 0 | 32.9452 | 0
122 | 1900-05-02 | 2922 | 0 | 47.7878 | 0
122 | 1900-05-02 | 2923 | 0 | 33.0885 | 0
122 | 1900-05-02 | 2924 | 0 | 37.4514 | 0
122 | 1900-05-02 | 2925 | 0 | 55.4938 | 0
122 | 1900-05-02 | 2926 | 0 | 94.2637 | 0
122 | 1900-05-02 | 2927 | 0 | 20.9654 | 0
122 | 1900-05-02 | 2928 | 0 | 30.0745 | 0
123 | 1900-05-03 | 2929 | 0 | 35.7548 | 0
123 | 1900-05-03 | 2930 | 0 | 57.1262 | 0
123 | 1900-05-03 | 2931 | 0 | 39.8886 | 0
123 | 1900-05-03 | 2932 | 0 | 33.9634 | 0
123 | 1900-05-03 | 2933 | 0 | 32.6672 | 0
123 | 1900-05-03 | 2934 | 0 | 32.7868 | 0
123 | 1900-05-03 | 2935 | 0 | 35.8228 | 0
123 | 1900-05-03 | 2936 | 0 | 43.992 | 0
123 | 1900-05-03 | 2937 | 0 | 59.0232 | 0
123 | 1900-05-03 | 2938 | 0 | 53.9422 | 0
123 | 1900-05-03 | 2939 | 0 | 50.5934 | 0
123 | 1900-05-03 | 2940 | 0 | 34.8632 | 0
123 | 1900-05-03 | 2941 | 0 | 35.9926 | 0
123 | 1900-05-03 | 2942 | 0 | 30.1847 | 0
123 | 1900-05-03 | 2943 | 0 | 53.6088 | 0
123 | 1900-05-03 | 2944 | 0 | 41.2553 | 0
123 | 1900-05-03 | 2945 | 0 | 57.232 | 0
123 | 1900-05-03 | 2946 | 0 | 44.7911 | 0
123 | 1900-05-03 | 2947 | 0 | 60.6375 | 0
123 | 1900-05-03 | 2948 | 0 | 100.3173 | 0
123 | 1900-05-03 | 2949 | 0 | 112.7788 | 0
123 | 1900-05-03 | 2950 | 0 | 141.8245 | 0
123 | 1900-05-03 | 2951 | 0 | 311.7593 | 0
123 | 1900-05-03 | 2952 | 0 | 33.077 | 0
124 | 1900-05-04 | 2953 | 0 | 28.869 | 0
124 | 1900-05-04 | 2954 | 0 | 23.6218 | 0
124 | 1900-05-04 | 2955 | 0 | 39.5183 | 0
124 | 1900-05-04 | 2956 | 0 | 22.3698 | 0
124 | 1900-05-04 | 2957 | 0 | 47.1762 | 0
124 | 1900-05-04 | 2958 | 0 | 90.4549 | 0
124 | 1900-05-04 | 2959 | 0 | 105.4279 | 0
124 | 1900-05-04 | 2960 | 0 | 91.2107 | 0
124 | 1900-05-04 | 2961 | 0 | 94.7733 | 0
124 | 1900-05-04 | 2962 | 0 | 75.1217 | 0
124 | 1900-05-04 | 2963 | 0 | 97.8113 | 0
124 | 1900-05-04 | 2964 | 0 | 39.9538 | 0
124 | 1900-05-04 | 2965 | 0 | 42.2441 | 0
124 | 1900-05-04 | 2966 | 0 | 58.7056 | 0
124 | 1900-05-04 | 2967 | 0 | 54.5197 | 0
124 | 1900-05-04 | 2968 | 0 | 44.4811 | 0
124 | 1900-05-04 | 2969 | 0 | 50.9393 | 0
124 | 1900-05-04 | 2970 | 0 | 52.5841 | 0
124 | 1900-05-04 | 2971 | 0 | 43.8718 | 0
124 | 1900-05-04 | 2972 | 0 | 31.1653 | 0
124 | 1900-05-04 | 2973 | 0 | 23.1699 | 0
124 | 1900-05-04 | 2974 | 0 | 30.0371 | 0
124 | 1900-05-04 | 2975 | 0 | 29.6256 | 0
124 | 1900-05-04 | 2976 | 0 | 30.519 | 0
125 | 1900-05-05 | 2977 | 0 | 34.9608 | 0
125 | 1900-05-05 | 2978 | 0 | 31.6446 | 0
125 | 1900-05-05 | 2979 | 0 | 23.73 | 0
125 | 1900-05-05 | 2980 | 0 | 27.9507 | 0
125 | 1900-05-05 | 2981 | 0 | 36.7125 | 0
125 | 1900-05-05 | 2982 | 0 | 31.1482 | 0
125 | 1900-05-05 | 2983 | 0 | 27.025 | 0
125 | 1900-05-05 | 2984 | 0 | 46.2218 | 0
125 | 1900-05-05 | 2985 | 0 | 41.0139 | 0
125 | 1900-05-05 | 2986 | 0 | 37.2341 | 0
125 | 1900-05-05 | 2987 | 0 | 35.7948 | 0
125 | 1900-05-05 | 2988 | 0 | 44.8377 | 0
125 | 1900-05-05 | 2989 | 0 | 43.231 | 0
125 | 1900-05-05 | 2990 | 0 | 43.005 | 0
125 | 1900-05-05 | 2991 | 0 | 37.8524 | 0
125 | 1900-05-05 | 2992 | 0 | 43.1661 | 0
125 | 1900-05-05 | 2993 | 0 | 38.3186 | 0
125 | 1900-05-05 | 2994 | 0 | 44.3074 | 0
125 | 1900-05-05 | 2995 | 0 | 45.9198 | 0
125 | 1900-05-05 | 2996 | 0 | 29.2695 | 0
125 | 1900-05-05 | 2997 | 0 | 34.2272 | 0
125 | 1900-05-05 | 2998 | 0 | 49.2563 | 0
125 | 1900-05-05 | 2999 | 0 | 72.5819 | 0
125 | 1900-05-05 | 3000 | 0 | 69.2488 | 0
126 | 1900-05-06 | 3001 | 0 | 23.9899 | 0
126 | 1900-05-06 | 3002 | 0 | 34.5008 | 0
126 | 1900-05-06 | 3003 | 0 | 34.3204 | 0
126 | 1900-05-06 | 3004 | 0 | 38.3073 | 0
126 | 1900-05-06 | 3005 | 0 | 29.348 | 0
126 | 1900-05-06 | 3006 | 0 | 27.1474 | 0
126 | 1900-05-06 | 3007 | 0 | 29.4211 | 0
126 | 1900-05-06 | 3008 | 0 | 40.9652 | 0
126 | 1900-05-06 | 3009 | 0 | 51.2949 | 0
126 | 1900-05-06 | 3010 | 0 | 42.3024 | 0
126 | 1900-05-06 | 3011 | 0 | 32.2865 | 0
126 | 1900-05-06 | 3012 | 0 | 51.0258 | 0
126 | 1900-05-06 | 3013 | 0 | 40.0968 | 0
126 | 1900-05-06 | 3014 | 0 | 55.0581 | 0
126 | 1900-05-06 | 3015 | 0 | 43.7795 | 0
126 | 1900-05-06 | 3016 | 0 | 43.505 | 0
126 | 1900-05-06 | 3017 | 0 | 45.1122 | 0
126 | 1900-05-06 | 3018 | 0 | 43.561 | 0
126 | 1900-05-06 | 3019 | 0 | 42.5532 | 0
126 | 1900-05-06 | 3020 | 0 | 20.6664 | 0
126 | 1900-05-06 | 3021 | 0 | 32.2939 | 0
126 | 1900-05-06 | 3022 | 0 | 35.2163 | 0
126 | 1900-05-06 | 3023 | 0 | 28.7523 | 0
126 | 1900-05-06 | 3024 | 0 | 22.7348 | 0
127 | 1900-05-07 | 3025 | 0 | 33.8677 | 0
127 | 1900-05-07 | 3026 | 0 | 28.8998 | 0
127 | 1900-05-07 | 3027 | 0 | 28.916 | 0
127 | 1900-05-07 | 3028 | 0 | 39.4906 | 0
127 | 1900-05-07 | 3029 | 0 | 105.6811 | 0
127 | 1900-05-07 | 3030 | 0 | 91.9264 | 0
127 | 1900-05-07 | 3031 | 0 | 239.8236 | 0
127 | 1900-05-07 | 3032 | 0 | 42.8161 | 0
127 | 1900-05-07 | 3033 | 0 | 38.3199 | 0
127 | 1900-05-07 | 3034 | 0 | 62.9478 | 0
127 | 1900-05-07 | 3035 | 0 | 117.7546 | 0
127 | 1900-05-07 | 3036 | 0 | 101.4157 | 0
127 | 1900-05-07 | 3037 | 0 | 49.0927 | 0
127 | 1900-05-07 | 3038 | 0 | 45.1959 | 0
127 | 1900-05-07 | 3039 | 0 | 37.0808 | 0
127 | 1900-05-07 | 3040 | 0 | 37.1706 | 0
127 | 1900-05-07 | 3041 | 0 | 28.15 | 0
127 | 1900-05-07 | 3042 | 0 | 48.9978 | 0
127 | 1900-05-07 | 3043 | 0 | 40.7898 | 0
127 | 1900-05-07 | 3044 | 0 | 25.1473 | 0
127 | 1900-05-07 | 3045 | 0 | 26.441 | 0
127 | 1900-05-07 | 3046 | 0 | 40.0005 | 0
127 | 1900-05-07 | 3047 | 0 | 229.6874 | 0
127 | 1900-05-07 | 3048 | 0 | 26.2838 | 0
128 | 1900-05-08 | 3049 | 0 | 33.5557 | 0
128 | 1900-05-08 | 3050 | 0 | 33.1054 | 0
128 | 1900-05-08 | 3051 | 0 | 28.838 | 0
128 | 1900-05-08 | 3052 | 0 | 33.983 | 0
128 | 1900-05-08 | 3053 | 0 | 60.3636 | 0
128 | 1900-05-08 | 3054 | 0 | 84.5471 | 0
128 | 1900-05-08 | 3055 | 0 | 55.2681 | 0
128 | 1900-05-08 | 3056 | 0 | 101.5939 | 0
128 | 1900-05-08 | 3057 | 0 | 116.5149 | 0
128 | 1900-05-08 | 3058 | 0 | 112.8441 | 0
128 | 1900-05-08 | 3059 | 0 | 107.6088 | 0
128 | 1900-05-08 | 3060 | 0 | 109.4463 | 0
128 | 1900-05-08 | 3061 | 0 | 101.5161 | 0
128 | 1900-05-08 | 3062 | 0 | 45.4511 | 0
128 | 1900-05-08 | 3063 | 0 | 47.8587 | 0
128 | 1900-05-08 | 3064 | 0 | 46.1266 | 0
128 | 1900-05-08 | 3065 | 0 | 44.3667 | 0
128 | 1900-05-08 | 3066 | 0 | 42.1928 | 0
128 | 1900-05-08 | 3067 | 0 | 56.5058 | 0
128 | 1900-05-08 | 3068 | 0 | 31.1073 | 0
128 | 1900-05-08 | 3069 | 0 | 38.5394 | 0
128 | 1900-05-08 | 3070 | 0 | 23.0926 | 0
128 | 1900-05-08 | 3071 | 0 | 27.8588 | 0
128 | 1900-05-08 | 3072 | 0 | 27.4101 | 0
129 | 1900-05-09 | 3073 | 0 | 34.387 | 0
129 | 1900-05-09 | 3074 | 0 | 35.4315 | 0
129 | 1900-05-09 | 3075 | 0 | 29.9941 | 0
129 | 1900-05-09 | 3076 | 0 | 37.8367 | 0
129 | 1900-05-09 | 3077 | 0 | 41.951 | 0
129 | 1900-05-09 | 3078 | 0 | 64.0388 | 0
129 | 1900-05-09 | 3079 | 0 | 28.7638 | 0
129 | 1900-05-09 | 3080 | 0 | 54.4324 | 0
129 | 1900-05-09 | 3081 | 0 | 47.4684 | 0
129 | 1900-05-09 | 3082 | 0 | 41.7464 | 0
129 | 1900-05-09 | 3083 | 0 | 57.2135 | 0
129 | 1900-05-09 | 3084 | 0 | 51.9434 | 0
129 | 1900-05-09 | 3085 | 0 | 48.8094 | 0
129 | 1900-05-09 | 3086 | 0 | 50.4418 | 0
129 | 1900-05-09 | 3087 | 0 | 29.1015 | 0
129 | 1900-05-09 | 3088 | 0 | 42.334 | 0
129 | 1900-05-09 | 3089 | 0 | 40.5246 | 0
129 | 1900-05-09 | 3090 | 0 | 36.3756 | 0
129 | 1900-05-09 | 3091 | 0 | 46.2132 | 0
129 | 1900-05-09 | 3092 | 0 | 23.6266 | 0
129 | 1900-05-09 | 3093 | 0 | 26.3198 | 0
129 | 1900-05-09 | 3094 | 0 | 34.5423 | 0
129 | 1900-05-09 | 3095 | 0 | 35.2714 | 0
129 | 1900-05-09 | 3096 | 0 | 30.3634 | 0
130 | 1900-05-10 | 3097 | 0 | 31.254 | 0
130 | 1900-05-10 | 3098 | 0 | 22.678 | 0
130 | 1900-05-10 | 3099 | 0 | 29.542 | 0
130 | 1900-05-10 | 3100 | 0 | 25.5182 | 0
130 | 1900-05-10 | 3101 | 0 | 32.19 | 0
130 | 1900-05-10 | 3102 | 0 | 28.6023 | 0
130 | 1900-05-10 | 3103 | 0 | 35.8033 | 0
130 | 1900-05-10 | 3104 | 0 | 37.8764 | 0
130 | 1900-05-10 | 3105 | 0 | 45.0943 | 0
130 | 1900-05-10 | 3106 | 0 | 45.3448 | 0
130 | 1900-05-10 | 3107 | 0 | 59.5533 | 0
130 | 1900-05-10 | 3108 | 0 | 48.3723 | 0
130 | 1900-05-10 | 3109 | 0 | 55.8668 | 0
130 | 1900-05-10 | 3110 | 0 | 37.9081 | 0
130 | 1900-05-10 | 3111 | 0 | 48.4091 | 0
130 | 1900-05-10 | 3112 | 0 | 46.1277 | 0
130 | 1900-05-10 | 3113 | 0 | 44.38 | 0
130 | 1900-05-10 | 3114 | 0 | 63.9841 | 0
130 | 1900-05-10 | 3115 | 0 | 49.5699 | 0
130 | 1900-05-10 | 3116 | 0 | 33.7142 | 0
130 | 1900-05-10 | 3117 | 0 | 29.1689 | 0
130 | 1900-05-10 | 3118 | 0 | 37.6114 | 0
130 | 1900-05-10 | 3119 | 0 | 22.2857 | 0
130 | 1900-05-10 | 3120 | 0 | 30.2751 | 0
131 | 1900-05-11 | 3121 | 0 | 32.299 | 0
131 | 1900-05-11 | 3122 | 0 | 24.7165 | 0
131 | 1900-05-11 | 3123 | 0 | 28.9627 | 0
131 | 1900-05-11 | 3124 | 0 | 27.4901 | 0
131 | 1900-05-11 | 3125 | 0 | 28.6333 | 0
131 | 1900-05-11 | 3126 | 0 | 24.4047 | 0
131 | 1900-05-11 | 3127 | 0 | 33.8486 | 0
131 | 1900-05-11 | 3128 | 0 | 45.6095 | 0
131 | 1900-05-11 | 3129 | 0 | 48.4276 | 0
131 | 1900-05-11 | 3130 | 0 | 34.6197 | 0
131 | 1900-05-11 | 3131 | 0 | 52.5037 | 0
131 | 1900-05-11 | 3132 | 0 | 50.4524 | 0
131 | 1900-05-11 | 3133 | 0 | 41.4997 | 0
131 | 1900-05-11 | 3134 | 0 | 37.5756 | 0
131 | 1900-05-11 | 3135 | 0 | 247.1778 | 0
131 | 1900-05-11 | 3136 | 0 | 45.0508 | 0
131 | 1900-05-11 | 3137 | 0 | 42.7086 | 0
131 | 1900-05-11 | 3138 | 0 | 41.9515 | 0
131 | 1900-05-11 | 3139 | 0 | 40.2993 | 0
131 | 1900-05-11 | 3140 | 0 | 36.0371 | 0
131 | 1900-05-11 | 3141 | 0 | 28.4702 | 0
131 | 1900-05-11 | 3142 | 0 | 19.6979 | 0
131 | 1900-05-11 | 3143 | 0 | 35.1541 | 0
131 | 1900-05-11 | 3144 | 0 | 34.0425 | 0
132 | 1900-05-12 | 3145 | 0 | 29.2721 | 0
132 | 1900-05-12 | 3146 | 0 | 236.1635 | 0
132 | 1900-05-12 | 3147 | 0 | 34.8963 | 0
132 | 1900-05-12 | 3148 | 0 | 34.6622 | 0
132 | 1900-05-12 | 3149 | 0 | 41.4656 | 0
132 | 1900-05-12 | 3150 | 0 | 31.7986 | 0
132 | 1900-05-12 | 3151 | 0 | 26.4196 | 0
132 | 1900-05-12 | 3152 | 0 | 49.7204 | 0
132 | 1900-05-12 | 3153 | 0 | 43.6806 | 0
132 | 1900-05-12 | 3154 | 0 | 41.8515 | 0
132 | 1900-05-12 | 3155 | 0 | 54.0813 | 0
132 | 1900-05-12 | 3156 | 0 | 48.1586 | 0
132 | 1900-05-12 | 3157 | 0 | 47.9748 | 0
132 | 1900-05-12 | 3158 | 0 | 28.1194 | 0
132 | 1900-05-12 | 3159 | 0 | 42.5324 | 0
132 | 1900-05-12 | 3160 | 0 | 66.9833 | 0
132 | 1900-05-12 | 3161 | 0 | 39.6152 | 0
132 | 1900-05-12 | 3162 | 0 | 33.444 | 0
132 | 1900-05-12 | 3163 | 0 | 45.6159 | 0
132 | 1900-05-12 | 3164 | 0 | 18.8309 | 0
132 | 1900-05-12 | 3165 | 0 | 31.8212 | 0
132 | 1900-05-12 | 3166 | 0 | 37.8884 | 0
132 | 1900-05-12 | 3167 | 0 | 26.9283 | 0
132 | 1900-05-12 | 3168 | 0 | 31.9539 | 0
133 | 1900-05-13 | 3169 | 0 | 26.09 | 0
133 | 1900-05-13 | 3170 | 0 | 33.0964 | 0
133 | 1900-05-13 | 3171 | 0 | 32.3257 | 0
133 | 1900-05-13 | 3172 | 0 | 26.3403 | 0
133 | 1900-05-13 | 3173 | 0 | 23.4858 | 0
133 | 1900-05-13 | 3174 | 0 | 26.3001 | 0
133 | 1900-05-13 | 3175 | 0 | 19.1906 | 0
133 | 1900-05-13 | 3176 | 0 | 49.1833 | 0
133 | 1900-05-13 | 3177 | 0 | 52.3162 | 0
133 | 1900-05-13 | 3178 | 0 | 44.7166 | 0
133 | 1900-05-13 | 3179 | 0 | 44.9177 | 0
133 | 1900-05-13 | 3180 | 0 | 44.961 | 0
133 | 1900-05-13 | 3181 | 0 | 36.818 | 0
133 | 1900-05-13 | 3182 | 0 | 47.0736 | 0
133 | 1900-05-13 | 3183 | 0 | 37.4478 | 0
133 | 1900-05-13 | 3184 | 0 | 34.2474 | 0
133 | 1900-05-13 | 3185 | 0 | 45.5989 | 0
133 | 1900-05-13 | 3186 | 0 | 40.4498 | 0
133 | 1900-05-13 | 3187 | 0 | 41.0042 | 0
133 | 1900-05-13 | 3188 | 0 | 37.5856 | 0
133 | 1900-05-13 | 3189 | 0 | 29.9874 | 0
133 | 1900-05-13 | 3190 | 0 | 39.0391 | 0
133 | 1900-05-13 | 3191 | 0 | 29.3784 | 0
133 | 1900-05-13 | 3192 | 0 | 28.5255 | 0
134 | 1900-05-14 | 3193 | 0 | 28.1665 | 0
134 | 1900-05-14 | 3194 | 0 | 36.3729 | 0
134 | 1900-05-14 | 3195 | 0 | 32.7378 | 0
134 | 1900-05-14 | 3196 | 0 | 59.9177 | 0
134 | 1900-05-14 | 3197 | 0 | 128.6758 | 0
134 | 1900-05-14 | 3198 | 0 | 140.7127 | 0
134 | 1900-05-14 | 3199 | 0 | 117.5569 | 0
134 | 1900-05-14 | 3200 | 0 | 146.6242 | 0
134 | 1900-05-14 | 3201 | 0 | 150.224 | 0
134 | 1900-05-14 | 3202 | 0 | 131.974 | 0
134 | 1900-05-14 | 3203 | 0 | 136.7568 | 0
134 | 1900-05-14 | 3204 | 0 | 106.3568 | 0
134 | 1900-05-14 | 3205 | 0 | 33.9278 | 0
134 | 1900-05-14 | 3206 | 0 | 46.6286 | 0
134 | 1900-05-14 | 3207 | 0 | 44.7529 | 0
134 | 1900-05-14 | 3208 | 0 | 53.5317 | 0
134 | 1900-05-14 | 3209 | 0 | 47.5055 | 0
134 | 1900-05-14 | 3210 | 0 | 48.2181 | 0
134 | 1900-05-14 | 3211 | 0 | 43.964 | 0
134 | 1900-05-14 | 3212 | 0 | 28.3414 | 0
134 | 1900-05-14 | 3213 | 0 | 29.3919 | 0
134 | 1900-05-14 | 3214 | 0 | 39.1619 | 0
134 | 1900-05-14 | 3215 | 0 | 31.5045 | 0
134 | 1900-05-14 | 3216 | 0 | 32.6561 | 0
135 | 1900-05-15 | 3217 | 0 | 31.8005 | 0
135 | 1900-05-15 | 3218 | 0 | 29.3276 | 0
135 | 1900-05-15 | 3219 | 0 | 36.5272 | 0
135 | 1900-05-15 | 3220 | 0 | 45.4041 | 0
135 | 1900-05-15 | 3221 | 0 | 62.6768 | 0
135 | 1900-05-15 | 3222 | 0 | 57.4704 | 0
135 | 1900-05-15 | 3223 | 0 | 29.6982 | 0
135 | 1900-05-15 | 3224 | 0 | 46.9642 | 0
135 | 1900-05-15 | 3225 | 0 | 55.0486 | 0
135 | 1900-05-15 | 3226 | 0 | 37.2176 | 0
135 | 1900-05-15 | 3227 | 0 | 41.7937 | 0
135 | 1900-05-15 | 3228 | 0 | 31.8298 | 0
135 | 1900-05-15 | 3229 | 0 | 34.5191 | 0
135 | 1900-05-15 | 3230 | 0 | 45.2469 | 0
135 | 1900-05-15 | 3231 | 0 | 52.0297 | 0
135 | 1900-05-15 | 3232 | 0 | 40.8392 | 0
135 | 1900-05-15 | 3233 | 0 | 49.3277 | 0
135 | 1900-05-15 | 3234 | 0 | 44.3988 | 0
135 | 1900-05-15 | 3235 | 0 | 43.3462 | 0
135 | 1900-05-15 | 3236 | 0 | 33.8248 | 0
135 | 1900-05-15 | 3237 | 0 | 23.1677 | 0
135 | 1900-05-15 | 3238 | 0 | 29.8839 | 0
135 | 1900-05-15 | 3239 | 0 | 230.6124 | 0
135 | 1900-05-15 | 3240 | 0 | 37.8818 | 0
136 | 1900-05-16 | 3241 | 0 | 32.8581 | 0
136 | 1900-05-16 | 3242 | 0 | 26.7949 | 0
136 | 1900-05-16 | 3243 | 0 | 30.9979 | 0
136 | 1900-05-16 | 3244 | 0 | 28.6788 | 0
136 | 1900-05-16 | 3245 | 0 | 31.281 | 0
136 | 1900-05-16 | 3246 | 0 | 42.6652 | 0
136 | 1900-05-16 | 3247 | 0 | 61.8929 | 0
136 | 1900-05-16 | 3248 | 0 | 63.0743 | 0
136 | 1900-05-16 | 3249 | 0 | 60.7076 | 0
136 | 1900-05-16 | 3250 | 0 | 135.3766 | 0
136 | 1900-05-16 | 3251 | 0 | 101.2465 | 0
136 | 1900-05-16 | 3252 | 0 | 66.6185 | 0
136 | 1900-05-16 | 3253 | 0 | 44.3954 | 0
136 | 1900-05-16 | 3254 | 0 | 29.4771 | 0
136 | 1900-05-16 | 3255 | 0 | 52.1493 | 0
136 | 1900-05-16 | 3256 | 0 | 31.7932 | 0
136 | 1900-05-16 | 3257 | 0 | 37.5659 | 0
136 | 1900-05-16 | 3258 | 0 | 45.0684 | 0
136 | 1900-05-16 | 3259 | 0 | 47.0179 | 0
136 | 1900-05-16 | 3260 | 0 | 40.1616 | 0
136 | 1900-05-16 | 3261 | 0 | 229.0694 | 0
136 | 1900-05-16 | 3262 | 0 | 31.2023 | 0
136 | 1900-05-16 | 3263 | 0 | 28.3914 | 0
136 | 1900-05-16 | 3264 | 0 | 58.7772 | 0
137 | 1900-05-17 | 3265 | 0 | 118.9531 | 0
137 | 1900-05-17 | 3266 | 0 | 87.1981 | 0
137 | 1900-05-17 | 3267 | 0 | 29.003 | 0
137 | 1900-05-17 | 3268 | 0 | 36.5343 | 0
137 | 1900-05-17 | 3269 | 0 | 42.9382 | 0
137 | 1900-05-17 | 3270 | 0 | 80.6629 | 0
137 | 1900-05-17 | 3271 | 0 | 84.8779 | 0
137 | 1900-05-17 | 3272 | 0 | 87.0637 | 0
137 | 1900-05-17 | 3273 | 0 | 97.4079 | 0
137 | 1900-05-17 | 3274 | 0 | 42.8937 | 0
137 | 1900-05-17 | 3275 | 0 | 40.2407 | 0
137 | 1900-05-17 | 3276 | 0 | 46.6707 | 0
137 | 1900-05-17 | 3277 | 0 | 45.5196 | 0
137 | 1900-05-17 | 3278 | 0 | 39.8653 | 0
137 | 1900-05-17 | 3279 | 0 | 48.4605 | 0
137 | 1900-05-17 | 3280 | 0 | 49.2971 | 0
137 | 1900-05-17 | 3281 | 0 | 43.3388 | 0
137 | 1900-05-17 | 3282 | 0 | 30.9929 | 0
137 | 1900-05-17 | 3283 | 0 | 48.9254 | 0
137 | 1900-05-17 | 3284 | 0 | 32.7926 | 0
137 | 1900-05-17 | 3285 | 0 | 53.2163 | 0
137 | 1900-05-17 | 3286 | 0 | 99.1263 | 0
137 | 1900-05-17 | 3287 | 0 | 110.3036 | 0
137 | 1900-05-17 | 3288 | 0 | 101.9978 | 0
138 | 1900-05-18 | 3289 | 0 | 59.4274 | 0
138 | 1900-05-18 | 3290 | 0 | 34.9719 | 0
138 | 1900-05-18 | 3291 | 0 | 27.702 | 0
138 | 1900-05-18 | 3292 | 0 | 28.499 | 0
138 | 1900-05-18 | 3293 | 0 | 41.6417 | 0
138 | 1900-05-18 | 3294 | 0 | 108.2222 | 0
138 | 1900-05-18 | 3295 | 0 | 95.2996 | 0
138 | 1900-05-18 | 3296 | 0 | 83.8941 | 0
138 | 1900-05-18 | 3297 | 0 | 94.2167 | 0
138 | 1900-05-18 | 3298 | 0 | 92.5897 | 0
138 | 1900-05-18 | 3299 | 0 | 52.6935 | 0
138 | 1900-05-18 | 3300 | 0 | 47.7061 | 0
138 | 1900-05-18 | 3301 | 0 | 47.4102 | 0
138 | 1900-05-18 | 3302 | 0 | 45.2859 | 0
138 | 1900-05-18 | 3303 | 0 | 29.3491 | 0
138 | 1900-05-18 | 3304 | 0 | 41.282 | 0
138 | 1900-05-18 | 3305 | 0 | 41.4267 | 0
138 | 1900-05-18 | 3306 | 0 | 41.2549 | 0
138 | 1900-05-18 | 3307 | 0 | 51.5355 | 0
138 | 1900-05-18 | 3308 | 0 | 36.409 | 0
138 | 1900-05-18 | 3309 | 0 | 31.4456 | 0
138 | 1900-05-18 | 3310 | 0 | 29.7903 | 0
138 | 1900-05-18 | 3311 | 0 | 25.2184 | 0
138 | 1900-05-18 | 3312 | 0 | 29.6094 | 0
139 | 1900-05-19 | 3313 | 0 | 26.4012 | 0
139 | 1900-05-19 | 3314 | 0 | 28.4328 | 0
139 | 1900-05-19 | 3315 | 0 | 29.4942 | 0
139 | 1900-05-19 | 3316 | 0 | 33.0559 | 0
139 | 1900-05-19 | 3317 | 0 | 37.4552 | 0
139 | 1900-05-19 | 3318 | 0 | 236.0842 | 0
139 | 1900-05-19 | 3319 | 0 | 31.5798 | 0
139 | 1900-05-19 | 3320 | 0 | 32.0556 | 0
139 | 1900-05-19 | 3321 | 0 | 38.4168 | 0
139 | 1900-05-19 | 3322 | 0 | 32.7043 | 0
139 | 1900-05-19 | 3323 | 0 | 42.3379 | 0
139 | 1900-05-19 | 3324 | 0 | 47.5299 | 0
139 | 1900-05-19 | 3325 | 0 | 48.0037 | 0
139 | 1900-05-19 | 3326 | 0 | 45.1027 | 0
139 | 1900-05-19 | 3327 | 0 | 40.3975 | 0
139 | 1900-05-19 | 3328 | 0 | 44.5115 | 0
139 | 1900-05-19 | 3329 | 0 | 40.676 | 0
139 | 1900-05-19 | 3330 | 0 | 55.555 | 0
139 | 1900-05-19 | 3331 | 0 | 33.9009 | 0
139 | 1900-05-19 | 3332 | 0 | 34.7351 | 0
139 | 1900-05-19 | 3333 | 0 | 32.4057 | 0
139 | 1900-05-19 | 3334 | 0 | 29.8794 | 0
139 | 1900-05-19 | 3335 | 0 | 34.188 | 0
139 | 1900-05-19 | 3336 | 0 | 23.0481 | 0
140 | 1900-05-20 | 3337 | 0 | 30.6216 | 0
140 | 1900-05-20 | 3338 | 0 | 32.3765 | 0
140 | 1900-05-20 | 3339 | 0 | 39.7977 | 0
140 | 1900-05-20 | 3340 | 0 | 37.0851 | 0
140 | 1900-05-20 | 3341 | 0 | 29.8198 | 0
140 | 1900-05-20 | 3342 | 0 | 35.7167 | 0
140 | 1900-05-20 | 3343 | 0 | 32.5085 | 0
140 | 1900-05-20 | 3344 | 0 | 30.8435 | 0
140 | 1900-05-20 | 3345 | 0 | 40.026 | 0
140 | 1900-05-20 | 3346 | 0 | 42.6697 | 0
140 | 1900-05-20 | 3347 | 0 | 56.4883 | 0
140 | 1900-05-20 | 3348 | 0 | 62.8589 | 0
140 | 1900-05-20 | 3349 | 0 | 43.9801 | 0
140 | 1900-05-20 | 3350 | 0 | 50.7985 | 0
140 | 1900-05-20 | 3351 | 0 | 45.1892 | 0
140 | 1900-05-20 | 3352 | 0 | 25.0289 | 0
140 | 1900-05-20 | 3353 | 0 | 49.8665 | 0
140 | 1900-05-20 | 3354 | 0 | 48.8867 | 0
140 | 1900-05-20 | 3355 | 0 | 41.5016 | 0
140 | 1900-05-20 | 3356 | 0 | 36.6741 | 0
140 | 1900-05-20 | 3357 | 0 | 28.9616 | 0
140 | 1900-05-20 | 3358 | 0 | 33.7395 | 0
140 | 1900-05-20 | 3359 | 0 | 26.6979 | 0
140 | 1900-05-20 | 3360 | 0 | 26.6732 | 0
141 | 1900-05-21 | 3361 | 0 | 32.8984 | 0
141 | 1900-05-21 | 3362 | 0 | 23.7404 | 0
141 | 1900-05-21 | 3363 | 0 | 31.559 | 0
141 | 1900-05-21 | 3364 | 0 | 33.4525 | 0
141 | 1900-05-21 | 3365 | 0 | 36.0945 | 0
141 | 1900-05-21 | 3366 | 0 | 28.9339 | 0
141 | 1900-05-21 | 3367 | 0 | 24.7975 | 0
141 | 1900-05-21 | 3368 | 0 | 42.5631 | 0
141 | 1900-05-21 | 3369 | 0 | 43.4421 | 0
141 | 1900-05-21 | 3370 | 0 | 39.7577 | 0
141 | 1900-05-21 | 3371 | 0 | 52.7402 | 0
141 | 1900-05-21 | 3372 | 0 | 50.3283 | 0
141 | 1900-05-21 | 3373 | 0 | 47.6919 | 0
141 | 1900-05-21 | 3374 | 0 | 34.6744 | 0
141 | 1900-05-21 | 3375 | 0 | 251.4478 | 0
141 | 1900-05-21 | 3376 | 0 | 35.4781 | 0
141 | 1900-05-21 | 3377 | 0 | 38.4082 | 0
141 | 1900-05-21 | 3378 | 0 | 42.9915 | 0
141 | 1900-05-21 | 3379 | 0 | 35.7009 | 0
141 | 1900-05-21 | 3380 | 0 | 29.3203 | 0
141 | 1900-05-21 | 3381 | 0 | 30.6894 | 0
141 | 1900-05-21 | 3382 | 0 | 32.04 | 0
141 | 1900-05-21 | 3383 | 0 | 29.9065 | 0
141 | 1900-05-21 | 3384 | 0 | 30.9515 | 0
142 | 1900-05-22 | 3385 | 0 | 29.2278 | 0
142 | 1900-05-22 | 3386 | 0 | 30.8129 | 0
142 | 1900-05-22 | 3387 | 0 | 26.1858 | 0
142 | 1900-05-22 | 3388 | 0 | 45.444 | 0
142 | 1900-05-22 | 3389 | 0 | 60.5766 | 0
142 | 1900-05-22 | 3390 | 0 | 80.7938 | 0
142 | 1900-05-22 | 3391 | 0 | 50.1859 | 0
142 | 1900-05-22 | 3392 | 0 | 57.6724 | 0
142 | 1900-05-22 | 3393 | 0 | 51.4598 | 0
142 | 1900-05-22 | 3394 | 0 | 98.6346 | 0
142 | 1900-05-22 | 3395 | 0 | 81.8815 | 0
142 | 1900-05-22 | 3396 | 0 | 58.9091 | 0
142 | 1900-05-22 | 3397 | 0 | 47.9897 | 0
142 | 1900-05-22 | 3398 | 0 | 40.1196 | 0
142 | 1900-05-22 | 3399 | 0 | 40.3141 | 0
142 | 1900-05-22 | 3400 | 0 | 44.5415 | 0
142 | 1900-05-22 | 3401 | 0 | 63.0969 | 0
142 | 1900-05-22 | 3402 | 0 | 46.5804 | 0
142 | 1900-05-22 | 3403 | 0 | 50.336 | 0
142 | 1900-05-22 | 3404 | 0 | 26.7798 | 0
142 | 1900-05-22 | 3405 | 0 | 27.5845 | 0
142 | 1900-05-22 | 3406 | 0 | 32.4132 | 0
142 | 1900-05-22 | 3407 | 0 | 35.1967 | 0
142 | 1900-05-22 | 3408 | 0 | 29.8266 | 0
143 | 1900-05-23 | 3409 | 0 | 25.5663 | 0
143 | 1900-05-23 | 3410 | 0 | 30.5039 | 0
143 | 1900-05-23 | 3411 | 0 | 227.158 | 0
143 | 1900-05-23 | 3412 | 0 | 41.9549 | 0
143 | 1900-05-23 | 3413 | 0 | 74.8221 | 0
143 | 1900-05-23 | 3414 | 0 | 84.3253 | 0
143 | 1900-05-23 | 3415 | 0 | 40.7297 | 0
143 | 1900-05-23 | 3416 | 0 | 61.1006 | 0
143 | 1900-05-23 | 3417 | 0 | 70.0453 | 0
143 | 1900-05-23 | 3418 | 0 | 79.7031 | 0
143 | 1900-05-23 | 3419 | 0 | 57.97 | 0
143 | 1900-05-23 | 3420 | 0 | 81.6758 | 0
143 | 1900-05-23 | 3421 | 0 | 52.6056 | 0
143 | 1900-05-23 | 3422 | 0 | 38.3091 | 0
143 | 1900-05-23 | 3423 | 0 | 37.2129 | 0
143 | 1900-05-23 | 3424 | 0 | 47.2863 | 0
143 | 1900-05-23 | 3425 | 0 | 52.4271 | 0
143 | 1900-05-23 | 3426 | 0 | 51.9714 | 0
143 | 1900-05-23 | 3427 | 0 | 39.3758 | 0
143 | 1900-05-23 | 3428 | 0 | 33.1127 | 0
143 | 1900-05-23 | 3429 | 0 | 34.2423 | 0
143 | 1900-05-23 | 3430 | 0 | 22.7174 | 0
143 | 1900-05-23 | 3431 | 0 | 32.5334 | 0
143 | 1900-05-23 | 3432 | 0 | 32.7497 | 0
144 | 1900-05-24 | 3433 | 0 | 23.0275 | 0
144 | 1900-05-24 | 3434 | 0 | 33.8662 | 0
144 | 1900-05-24 | 3435 | 0 | 23.7753 | 0
144 | 1900-05-24 | 3436 | 0 | 36.5353 | 0
144 | 1900-05-24 | 3437 | 0 | 48.1827 | 0
144 | 1900-05-24 | 3438 | 0 | 86.2951 | 0
144 | 1900-05-24 | 3439 | 0 | 55.8365 | 0
144 | 1900-05-24 | 3440 | 0 | 69.2993 | 0
144 | 1900-05-24 | 3441 | 0 | 30.7046 | 0
144 | 1900-05-24 | 3442 | 0 | 52.4874 | 0
144 | 1900-05-24 | 3443 | 0 | 78.7198 | 0
144 | 1900-05-24 | 3444 | 0 | 109.1924 | 0
144 | 1900-05-24 | 3445 | 0 | 22.9209 | 0
144 | 1900-05-24 | 3446 | 0 | 38.8197 | 0
144 | 1900-05-24 | 3447 | 0 | 43.723 | 0
144 | 1900-05-24 | 3448 | 0 | 41.8988 | 0
144 | 1900-05-24 | 3449 | 0 | 28.6869 | 0
144 | 1900-05-24 | 3450 | 0 | 49.9528 | 0
144 | 1900-05-24 | 3451 | 0 | 48.6797 | 0
144 | 1900-05-24 | 3452 | 0 | 27.8005 | 0
144 | 1900-05-24 | 3453 | 0 | 34.2164 | 0
144 | 1900-05-24 | 3454 | 0 | 23.9287 | 0
144 | 1900-05-24 | 3455 | 0 | 34.513 | 0
144 | 1900-05-24 | 3456 | 0 | 31.7143 | 0
145 | 1900-05-25 | 3457 | 0 | 30.101 | 0
145 | 1900-05-25 | 3458 | 0 | 31.2331 | 0
145 | 1900-05-25 | 3459 | 0 | 32.3385 | 0
145 | 1900-05-25 | 3460 | 0 | 33.2009 | 0
145 | 1900-05-25 | 3461 | 0 | 32.7384 | 0
145 | 1900-05-25 | 3462 | 0 | 51.9141 | 0
145 | 1900-05-25 | 3463 | 0 | 25.3458 | 0
145 | 1900-05-25 | 3464 | 0 | 44.6891 | 0
145 | 1900-05-25 | 3465 | 0 | 41.3678 | 0
145 | 1900-05-25 | 3466 | 0 | 50.3746 | 0
145 | 1900-05-25 | 3467 | 0 | 50.0911 | 0
145 | 1900-05-25 | 3468 | 0 | 28.3548 | 0
145 | 1900-05-25 | 3469 | 0 | 39.0443 | 0
145 | 1900-05-25 | 3470 | 0 | 48.228 | 0
145 | 1900-05-25 | 3471 | 0 | 48.6793 | 0
145 | 1900-05-25 | 3472 | 0 | 36.9527 | 0
145 | 1900-05-25 | 3473 | 0 | 36.0815 | 0
145 | 1900-05-25 | 3474 | 0 | 38.779 | 0
145 | 1900-05-25 | 3475 | 0 | 40.3255 | 0
145 | 1900-05-25 | 3476 | 0 | 31.6481 | 0
145 | 1900-05-25 | 3477 | 0 | 26.1659 | 0
145 | 1900-05-25 | 3478 | 0 | 25.216 | 0
145 | 1900-05-25 | 3479 | 0 | 25.5734 | 0
145 | 1900-05-25 | 3480 | 0 | 25.4696 | 0
146 | 1900-05-26 | 3481 | 0 | 32.045 | 0
146 | 1900-05-26 | 3482 | 0 | 31.7061 | 0
146 | 1900-05-26 | 3483 | 0 | 38.6412 | 0
146 | 1900-05-26 | 3484 | 0 | 28.5821 | 0
146 | 1900-05-26 | 3485 | 0 | 30.9078 | 0
146 | 1900-05-26 | 3486 | 0 | 25.3358 | 0
146 | 1900-05-26 | 3487 | 0 | 24.2277 | 0
146 | 1900-05-26 | 3488 | 0 | 39.9358 | 0
146 | 1900-05-26 | 3489 | 0 | 42.3781 | 0
146 | 1900-05-26 | 3490 | 0 | 27.8804 | 0
146 | 1900-05-26 | 3491 | 0 | 241.7726 | 0
146 | 1900-05-26 | 3492 | 0 | 41.5862 | 0
146 | 1900-05-26 | 3493 | 0 | 42.3199 | 0
146 | 1900-05-26 | 3494 | 0 | 53.8096 | 0
146 | 1900-05-26 | 3495 | 0 | 46.9096 | 0
146 | 1900-05-26 | 3496 | 0 | 37.8807 | 0
146 | 1900-05-26 | 3497 | 0 | 39.4771 | 0
146 | 1900-05-26 | 3498 | 0 | 33.8975 | 0
146 | 1900-05-26 | 3499 | 0 | 50.6423 | 0
146 | 1900-05-26 | 3500 | 0 | 27.042 | 0
146 | 1900-05-26 | 3501 | 0 | 28.7612 | 0
146 | 1900-05-26 | 3502 | 0 | 29.4056 | 0
146 | 1900-05-26 | 3503 | 0 | 36.5164 | 0
146 | 1900-05-26 | 3504 | 0 | 31.7437 | 0
147 | 1900-05-27 | 3505 | 0 | 25.8722 | 0
147 | 1900-05-27 | 3506 | 0 | 19.5028 | 0
147 | 1900-05-27 | 3507 | 0 | 32.8111 | 0
147 | 1900-05-27 | 3508 | 0 | 25.2329 | 0
147 | 1900-05-27 | 3509 | 0 | 37.4751 | 0
147 | 1900-05-27 | 3510 | 0 | 31.5778 | 0
147 | 1900-05-27 | 3511 | 0 | 25.9243 | 0
147 | 1900-05-27 | 3512 | 0 | 37.595 | 0
147 | 1900-05-27 | 3513 | 0 | 33.1692 | 0
147 | 1900-05-27 | 3514 | 0 | 249.1828 | 0
147 | 1900-05-27 | 3515 | 0 | 45.1439 | 0
147 | 1900-05-27 | 3516 | 0 | 35.6953 | 0
147 | 1900-05-27 | 3517 | 0 | 40.4766 | 0
147 | 1900-05-27 | 3518 | 0 | 57.4336 | 0
147 | 1900-05-27 | 3519 | 0 | 43.5589 | 0
147 | 1900-05-27 | 3520 | 0 | 26.4795 | 0
147 | 1900-05-27 | 3521 | 0 | 43.7299 | 0
147 | 1900-05-27 | 3522 | 0 | 43.388 | 0
147 | 1900-05-27 | 3523 | 0 | 41.3555 | 0
147 | 1900-05-27 | 3524 | 0 | 19.5089 | 0
147 | 1900-05-27 | 3525 | 0 | 33.3631 | 0
147 | 1900-05-27 | 3526 | 0 | 23.3456 | 0
147 | 1900-05-27 | 3527 | 0 | 33.7885 | 0
147 | 1900-05-27 | 3528 | 0 | 31.8329 | 0
148 | 1900-05-28 | 3529 | 0 | 32.5621 | 0
148 | 1900-05-28 | 3530 | 0 | 24.4048 | 0
148 | 1900-05-28 | 3531 | 0 | 27.8719 | 0
148 | 1900-05-28 | 3532 | 0 | 43.9114 | 0
148 | 1900-05-28 | 3533 | 0 | 89.6304 | 0
148 | 1900-05-28 | 3534 | 0 | 123.0683 | 0
148 | 1900-05-28 | 3535 | 0 | 111.3279 | 0
148 | 1900-05-28 | 3536 | 0 | 65.0524 | 0
148 | 1900-05-28 | 3537 | 0 | 44.5486 | 0
148 | 1900-05-28 | 3538 | 0 | 45.9095 | 0
148 | 1900-05-28 | 3539 | 0 | 34.1668 | 0
148 | 1900-05-28 | 3540 | 0 | 34.6028 | 0
148 | 1900-05-28 | 3541 | 0 | 57.9939 | 0
148 | 1900-05-28 | 3542 | 0 | 39.8515 | 0
148 | 1900-05-28 | 3543 | 0 | 43.0627 | 0
148 | 1900-05-28 | 3544 | 0 | 43.6824 | 0
148 | 1900-05-28 | 3545 | 0 | 37.8312 | 0
148 | 1900-05-28 | 3546 | 0 | 41.3411 | 0
148 | 1900-05-28 | 3547 | 0 | 38.8975 | 0
148 | 1900-05-28 | 3548 | 0 | 29.3553 | 0
148 | 1900-05-28 | 3549 | 0 | 27.2934 | 0
148 | 1900-05-28 | 3550 | 0 | 38.7809 | 0
148 | 1900-05-28 | 3551 | 0 | 27.3134 | 0
148 | 1900-05-28 | 3552 | 0 | 28.9982 | 0
149 | 1900-05-29 | 3553 | 0 | 24.7892 | 0
149 | 1900-05-29 | 3554 | 0 | 25.8895 | 0
149 | 1900-05-29 | 3555 | 0 | 32.2775 | 0
149 | 1900-05-29 | 3556 | 0 | 43.8929 | 0
149 | 1900-05-29 | 3557 | 0 | 98.343 | 0
149 | 1900-05-29 | 3558 | 0 | 41.9294 | 0
149 | 1900-05-29 | 3559 | 0 | 35.2141 | 0
149 | 1900-05-29 | 3560 | 0 | 45.8561 | 0
149 | 1900-05-29 | 3561 | 0 | 49.3999 | 0
149 | 1900-05-29 | 3562 | 0 | 50.3631 | 0
149 | 1900-05-29 | 3563 | 0 | 54.9211 | 0
149 | 1900-05-29 | 3564 | 0 | 35.0341 | 0
149 | 1900-05-29 | 3565 | 0 | 30.2268 | 0
149 | 1900-05-29 | 3566 | 0 | 36.2832 | 0
149 | 1900-05-29 | 3567 | 0 | 45.2231 | 0
149 | 1900-05-29 | 3568 | 0 | 41.9095 | 0
149 | 1900-05-29 | 3569 | 0 | 46.1062 | 0
149 | 1900-05-29 | 3570 | 0 | 39.1654 | 0
149 | 1900-05-29 | 3571 | 0 | 43.9703 | 0
149 | 1900-05-29 | 3572 | 0 | 32.7437 | 0
149 | 1900-05-29 | 3573 | 0 | 30.24 | 0
149 | 1900-05-29 | 3574 | 0 | 27.4799 | 0
149 | 1900-05-29 | 3575 | 0 | 31.0566 | 0
149 | 1900-05-29 | 3576 | 0 | 29.1846 | 0
150 | 1900-05-30 | 3577 | 0 | 37.3406 | 0
150 | 1900-05-30 | 3578 | 0 | 27.8151 | 0
150 | 1900-05-30 | 3579 | 0 | 30.5539 | 0
150 | 1900-05-30 | 3580 | 0 | 32.7279 | 0
150 | 1900-05-30 | 3581 | 0 | 64.357 | 0
150 | 1900-05-30 | 3582 | 0 | 99.9523 | 0
150 | 1900-05-30 | 3583 | 0 | 65.75 | 0
150 | 1900-05-30 | 3584 | 0 | 66.9361 | 0
150 | 1900-05-30 | 3585 | 0 | 104.7083 | 0
150 | 1900-05-30 | 3586 | 0 | 63.3909 | 0
150 | 1900-05-30 | 3587 | 0 | 46.5957 | 0
150 | 1900-05-30 | 3588 | 0 | 49.046 | 0
150 | 1900-05-30 | 3589 | 0 | 37.183 | 0
150 | 1900-05-30 | 3590 | 0 | 40.9511 | 0
150 | 1900-05-30 | 3591 | 0 | 53.7467 | 0
150 | 1900-05-30 | 3592 | 0 | 46.1212 | 0
150 | 1900-05-30 | 3593 | 0 | 34.5376 | 0
150 | 1900-05-30 | 3594 | 0 | 37.9147 | 0
150 | 1900-05-30 | 3595 | 0 | 40.8289 | 0
150 | 1900-05-30 | 3596 | 0 | 36.1802 | 0
150 | 1900-05-30 | 3597 | 0 | 33.1545 | 0
150 | 1900-05-30 | 3598 | 0 | 32.9589 | 0
150 | 1900-05-30 | 3599 | 0 | 25.182 | 0
150 | 1900-05-30 | 3600 | 0 | 30.5857 | 0
151 | 1900-05-31 | 3601 | 0 | 32.9188 | 0
151 | 1900-05-31 | 3602 | 0 | 27.5558 | 0
151 | 1900-05-31 | 3603 | 0 | 26.3904 | 0
151 | 1900-05-31 | 3604 | 0 | 38.9956 | 0
151 | 1900-05-31 | 3605 | 0 | 62.3274 | 0
151 | 1900-05-31 | 3606 | 0 | 113.9892 | 0
151 | 1900-05-31 | 3607 | 0 | 275.3719 | 0
151 | 1900-05-31 | 3608 | 0 | 40.5689 | 0
151 | 1900-05-31 | 3609 | 0 | 46.8206 | 0
151 | 1900-05-31 | 3610 | 0 | 41.0102 | 0
151 | 1900-05-31 | 3611 | 0 | 37.7932 | 0
151 | 1900-05-31 | 3612 | 0 | 41.6839 | 0
151 | 1900-05-31 | 3613 | 0 | 47.716 | 0
151 | 1900-05-31 | 3614 | 0 | 243.4264 | 0
151 | 1900-05-31 | 3615 | 0 | 39.1566 | 0
151 | 1900-05-31 | 3616 | 0 | 36.482 | 0
151 | 1900-05-31 | 3617 | 0 | 39.3159 | 0
151 | 1900-05-31 | 3618 | 0 | 43.9321 | 0
151 | 1900-05-31 | 3619 | 0 | 52.2583 | 0
151 | 1900-05-31 | 3620 | 0 | 39.4351 | 0
151 | 1900-05-31 | 3621 | 0 | 21.0495 | 0
151 | 1900-05-31 | 3622 | 0 | 36.1539 | 0
151 | 1900-05-31 | 3623 | 0 | 33.9292 | 0
151 | 1900-05-31 | 3624 | 0 | 36.547 | 0
152 | 1900-06-01 | 3625 | 0 | 28.4102 | 0
152 | 1900-06-01 | 3626 | 0 | 30.0504 | 0
152 | 1900-06-01 | 3627 | 0 | 30.167 | 0
152 | 1900-06-01 | 3628 | 0 | 36.481 | 0
152 | 1900-06-01 | 3629 | 0 | 68.1943 | 0
152 | 1900-06-01 | 3630 | 0 | 58.4733 | 0
152 | 1900-06-01 | 3631 | 0 | 29.4824 | 0
152 | 1900-06-01 | 3632 | 0 | 44.4537 | 0
152 | 1900-06-01 | 3633 | 0 | 46.5278 | 0
152 | 1900-06-01 | 3634 | 0 | 47.4838 | 0
152 | 1900-06-01 | 3635 | 0 | 46.818 | 0
152 | 1900-06-01 | 3636 | 0 | 29.6957 | 0
152 | 1900-06-01 | 3637 | 0 | 44.1217 | 0
152 | 1900-06-01 | 3638 | 0 | 41.7695 | 0
152 | 1900-06-01 | 3639 | 0 | 49.9801 | 0
152 | 1900-06-01 | 3640 | 0 | 49.3504 | 0
152 | 1900-06-01 | 3641 | 0 | 47.4717 | 0
152 | 1900-06-01 | 3642 | 0 | 39.3771 | 0
152 | 1900-06-01 | 3643 | 0 | 37.7305 | 0
152 | 1900-06-01 | 3644 | 0 | 24.7697 | 0
152 | 1900-06-01 | 3645 | 0 | 28.356 | 0
152 | 1900-06-01 | 3646 | 0 | 23.4645 | 0
152 | 1900-06-01 | 3647 | 0 | 26.5969 | 0
152 | 1900-06-01 | 3648 | 0 | 28.734 | 0
153 | 1900-06-02 | 3649 | 0 | 34.99 | 0
153 | 1900-06-02 | 3650 | 0 | 28.1898 | 0
153 | 1900-06-02 | 3651 | 0 | 41.1431 | 0
153 | 1900-06-02 | 3652 | 0 | 19.8151 | 0
153 | 1900-06-02 | 3653 | 0 | 19.7992 | 0
153 | 1900-06-02 | 3654 | 0 | 30.8269 | 0
153 | 1900-06-02 | 3655 | 0 | 33.2924 | 0
153 | 1900-06-02 | 3656 | 0 | 55.5449 | 0
153 | 1900-06-02 | 3657 | 0 | 52.9374 | 0
153 | 1900-06-02 | 3658 | 0 | 45.9727 | 0
153 | 1900-06-02 | 3659 | 0 | 45.4531 | 0
153 | 1900-06-02 | 3660 | 0 | 47.3176 | 0
153 | 1900-06-02 | 3661 | 0 | 21.4808 | 0
153 | 1900-06-02 | 3662 | 0 | 45.5389 | 0
153 | 1900-06-02 | 3663 | 0 | 39.744 | 0
153 | 1900-06-02 | 3664 | 0 | 52.9596 | 0
153 | 1900-06-02 | 3665 | 0 | 45.5699 | 0
153 | 1900-06-02 | 3666 | 0 | 40.8027 | 0
153 | 1900-06-02 | 3667 | 0 | 47.6522 | 0
153 | 1900-06-02 | 3668 | 0 | 25.7166 | 0
153 | 1900-06-02 | 3669 | 0 | 23.747 | 0
153 | 1900-06-02 | 3670 | 0 | 23.3517 | 0
153 | 1900-06-02 | 3671 | 0 | 26.1737 | 0
153 | 1900-06-02 | 3672 | 0 | 29.798 | 0
154 | 1900-06-03 | 3673 | 0 | 27.4331 | 0
154 | 1900-06-03 | 3674 | 0 | 28.031 | 0
154 | 1900-06-03 | 3675 | 0 | 23.8687 | 0
154 | 1900-06-03 | 3676 | 0 | 23.9385 | 0
154 | 1900-06-03 | 3677 | 0 | 22.4551 | 0
154 | 1900-06-03 | 3678 | 0 | 29.192 | 0
154 | 1900-06-03 | 3679 | 0 | 26.5923 | 0
154 | 1900-06-03 | 3680 | 0 | 49.4262 | 0
154 | 1900-06-03 | 3681 | 0 | 45.791 | 0
154 | 1900-06-03 | 3682 | 0 | 40.591 | 0
154 | 1900-06-03 | 3683 | 0 | 28.6744 | 0
154 | 1900-06-03 | 3684 | 0 | 48.2117 | 0
154 | 1900-06-03 | 3685 | 0 | 44.586 | 0
154 | 1900-06-03 | 3686 | 0 | 33.551 | 0
154 | 1900-06-03 | 3687 | 0 | 39.3682 | 0
154 | 1900-06-03 | 3688 | 0 | 28.5336 | 0
154 | 1900-06-03 | 3689 | 0 | 39.2726 | 0
154 | 1900-06-03 | 3690 | 0 | 43.0496 | 0
154 | 1900-06-03 | 3691 | 0 | 228.7791 | 0
154 | 1900-06-03 | 3692 | 0 | 33.6075 | 0
154 | 1900-06-03 | 3693 | 0 | 23.2956 | 0
154 | 1900-06-03 | 3694 | 0 | 28.4988 | 0
154 | 1900-06-03 | 3695 | 0 | 24.6176 | 0
154 | 1900-06-03 | 3696 | 0 | 26.784 | 0
155 | 1900-06-04 | 3697 | 0 | 24.1695 | 0
155 | 1900-06-04 | 3698 | 0 | 39.3794 | 0
155 | 1900-06-04 | 3699 | 0 | 39.8862 | 0
155 | 1900-06-04 | 3700 | 0 | 90.0641 | 0
155 | 1900-06-04 | 3701 | 0 | 116.4556 | 0
155 | 1900-06-04 | 3702 | 0 | 117.5406 | 0
155 | 1900-06-04 | 3703 | 0 | 99.5352 | 0
155 | 1900-06-04 | 3704 | 0 | 131.508 | 0
155 | 1900-06-04 | 3705 | 0 | 134.2551 | 0
155 | 1900-06-04 | 3706 | 0 | 83.1877 | 0
155 | 1900-06-04 | 3707 | 0 | 73.903 | 0
155 | 1900-06-04 | 3708 | 0 | 99.1064 | 0
155 | 1900-06-04 | 3709 | 0 | 89.4166 | 0
155 | 1900-06-04 | 3710 | 0 | 60.8485 | 0
155 | 1900-06-04 | 3711 | 0 | 47.1219 | 0
155 | 1900-06-04 | 3712 | 0 | 54.7083 | 0
155 | 1900-06-04 | 3713 | 0 | 42.1523 | 0
155 | 1900-06-04 | 3714 | 0 | 20.2985 | 0
155 | 1900-06-04 | 3715 | 0 | 35.4261 | 0
155 | 1900-06-04 | 3716 | 0 | 37.2616 | 0
155 | 1900-06-04 | 3717 | 0 | 28.5476 | 0
155 | 1900-06-04 | 3718 | 0 | 225.4204 | 0
155 | 1900-06-04 | 3719 | 0 | 28.6618 | 0
155 | 1900-06-04 | 3720 | 0 | 22.0222 | 0
156 | 1900-06-05 | 3721 | 0 | 33.0071 | 0
156 | 1900-06-05 | 3722 | 0 | 31.3048 | 0
156 | 1900-06-05 | 3723 | 0 | 33.1471 | 0
156 | 1900-06-05 | 3724 | 0 | 24.8334 | 0
156 | 1900-06-05 | 3725 | 0 | 42.2895 | 0
156 | 1900-06-05 | 3726 | 0 | 70.0013 | 0
156 | 1900-06-05 | 3727 | 0 | 106.2198 | 0
156 | 1900-06-05 | 3728 | 0 | 140.3093 | 0
156 | 1900-06-05 | 3729 | 0 | 118.0421 | 0
156 | 1900-06-05 | 3730 | 0 | 105.5905 | 0
156 | 1900-06-05 | 3731 | 0 | 109.1866 | 0
156 | 1900-06-05 | 3732 | 0 | 107.5264 | 0
156 | 1900-06-05 | 3733 | 0 | 100.1322 | 0
156 | 1900-06-05 | 3734 | 0 | 47.4518 | 0
156 | 1900-06-05 | 3735 | 0 | 39.7541 | 0
156 | 1900-06-05 | 3736 | 0 | 51.0975 | 0
156 | 1900-06-05 | 3737 | 0 | 43.6471 | 0
156 | 1900-06-05 | 3738 | 0 | 31.57 | 0
156 | 1900-06-05 | 3739 | 0 | 35.9198 | 0
156 | 1900-06-05 | 3740 | 0 | 25.2131 | 0
156 | 1900-06-05 | 3741 | 0 | 27.1905 | 0
156 | 1900-06-05 | 3742 | 0 | 27.6369 | 0
156 | 1900-06-05 | 3743 | 0 | 23.7851 | 0
156 | 1900-06-05 | 3744 | 0 | 28.2094 | 0
157 | 1900-06-06 | 3745 | 0 | 27.3746 | 0
157 | 1900-06-06 | 3746 | 0 | 26.3373 | 0
157 | 1900-06-06 | 3747 | 0 | 29.0654 | 0
157 | 1900-06-06 | 3748 | 0 | 21.1074 | 0
157 | 1900-06-06 | 3749 | 0 | 34.8792 | 0
157 | 1900-06-06 | 3750 | 0 | 77.8871 | 0
157 | 1900-06-06 | 3751 | 0 | 100.0202 | 0
157 | 1900-06-06 | 3752 | 0 | 125.2017 | 0
157 | 1900-06-06 | 3753 | 0 | 124.1778 | 0
157 | 1900-06-06 | 3754 | 0 | 66.8391 | 0
157 | 1900-06-06 | 3755 | 0 | 46.8648 | 0
157 | 1900-06-06 | 3756 | 0 | 61.8512 | 0
157 | 1900-06-06 | 3757 | 0 | 33.8581 | 0
157 | 1900-06-06 | 3758 | 0 | 26.3421 | 0
157 | 1900-06-06 | 3759 | 0 | 27.7706 | 0
157 | 1900-06-06 | 3760 | 0 | 54.6286 | 0
157 | 1900-06-06 | 3761 | 0 | 33.0389 | 0
157 | 1900-06-06 | 3762 | 0 | 50.6022 | 0
157 | 1900-06-06 | 3763 | 0 | 51.4047 | 0
157 | 1900-06-06 | 3764 | 0 | 30.5809 | 0
157 | 1900-06-06 | 3765 | 0 | 31.9952 | 0
157 | 1900-06-06 | 3766 | 0 | 28.3854 | 0
157 | 1900-06-06 | 3767 | 0 | 30.0901 | 0
157 | 1900-06-06 | 3768 | 0 | 225.4308 | 0
158 | 1900-06-07 | 3769 | 0 | 23.2696 | 0
158 | 1900-06-07 | 3770 | 0 | 24.7776 | 0
158 | 1900-06-07 | 3771 | 0 | 31.0904 | 0
158 | 1900-06-07 | 3772 | 0 | 47.4439 | 0
158 | 1900-06-07 | 3773 | 0 | 107.2309 | 0
158 | 1900-06-07 | 3774 | 0 | 103.9127 | 0
158 | 1900-06-07 | 3775 | 0 | 112.4158 | 0
158 | 1900-06-07 | 3776 | 0 | 136.1435 | 0
158 | 1900-06-07 | 3777 | 0 | 91.2104 | 0
158 | 1900-06-07 | 3778 | 0 | 93.5102 | 0
158 | 1900-06-07 | 3779 | 0 | 122.1647 | 0
158 | 1900-06-07 | 3780 | 0 | 100.7609 | 0
158 | 1900-06-07 | 3781 | 0 | 48.5776 | 0
158 | 1900-06-07 | 3782 | 0 | 43.6955 | 0
158 | 1900-06-07 | 3783 | 0 | 42.0141 | 0
158 | 1900-06-07 | 3784 | 0 | 39.6236 | 0
158 | 1900-06-07 | 3785 | 0 | 49.0809 | 0
158 | 1900-06-07 | 3786 | 0 | 60.3114 | 0
158 | 1900-06-07 | 3787 | 0 | 34.6119 | 0
158 | 1900-06-07 | 3788 | 0 | 27.8641 | 0
158 | 1900-06-07 | 3789 | 0 | 33.0486 | 0
158 | 1900-06-07 | 3790 | 0 | 32.3529 | 0
158 | 1900-06-07 | 3791 | 0 | 26.9459 | 0
158 | 1900-06-07 | 3792 | 0 | 26.7567 | 0
159 | 1900-06-08 | 3793 | 0 | 36.3011 | 0
159 | 1900-06-08 | 3794 | 0 | 26.7721 | 0
159 | 1900-06-08 | 3795 | 0 | 33.648 | 0
159 | 1900-06-08 | 3796 | 0 | 33.0121 | 0
159 | 1900-06-08 | 3797 | 0 | 67.0364 | 0
159 | 1900-06-08 | 3798 | 0 | 59.5147 | 0
159 | 1900-06-08 | 3799 | 0 | 26.4023 | 0
159 | 1900-06-08 | 3800 | 0 | 44.0966 | 0
159 | 1900-06-08 | 3801 | 0 | 44.1806 | 0
159 | 1900-06-08 | 3802 | 0 | 51.8312 | 0
159 | 1900-06-08 | 3803 | 0 | 51.6351 | 0
159 | 1900-06-08 | 3804 | 0 | 36.6206 | 0
159 | 1900-06-08 | 3805 | 0 | 46.3276 | 0
159 | 1900-06-08 | 3806 | 0 | 46.0903 | 0
159 | 1900-06-08 | 3807 | 0 | 54.0052 | 0
159 | 1900-06-08 | 3808 | 0 | 44.0114 | 0
159 | 1900-06-08 | 3809 | 0 | 41.97 | 0
159 | 1900-06-08 | 3810 | 0 | 35.0925 | 0
159 | 1900-06-08 | 3811 | 0 | 49.5585 | 0
159 | 1900-06-08 | 3812 | 0 | 29.6558 | 0
159 | 1900-06-08 | 3813 | 0 | 31.3391 | 0
159 | 1900-06-08 | 3814 | 0 | 28.4209 | 0
159 | 1900-06-08 | 3815 | 0 | 24.9064 | 0
159 | 1900-06-08 | 3816 | 0 | 26.987 | 0
160 | 1900-06-09 | 3817 | 0 | 27.9988 | 0
160 | 1900-06-09 | 3818 | 0 | 221.0422 | 0
160 | 1900-06-09 | 3819 | 0 | 17.4639 | 0
160 | 1900-06-09 | 3820 | 0 | 26.3249 | 0
160 | 1900-06-09 | 3821 | 0 | 23.5313 | 0
160 | 1900-06-09 | 3822 | 0 | 32.0481 | 0
160 | 1900-06-09 | 3823 | 0 | 21.8429 | 0
160 | 1900-06-09 | 3824 | 0 | 50.5488 | 0
160 | 1900-06-09 | 3825 | 0 | 36.57 | 0
160 | 1900-06-09 | 3826 | 0 | 21.3533 | 0
160 | 1900-06-09 | 3827 | 0 | 40.6071 | 0
160 | 1900-06-09 | 3828 | 0 | 28.1568 | 0
160 | 1900-06-09 | 3829 | 0 | 34.4218 | 0
160 | 1900-06-09 | 3830 | 0 | 38.6581 | 0
160 | 1900-06-09 | 3831 | 0 | 38.5624 | 0
160 | 1900-06-09 | 3832 | 0 | 46.2937 | 0
160 | 1900-06-09 | 3833 | 0 | 31.1307 | 0
160 | 1900-06-09 | 3834 | 0 | 50.574 | 0
160 | 1900-06-09 | 3835 | 0 | 41.8877 | 0
160 | 1900-06-09 | 3836 | 0 | 29.5681 | 0
160 | 1900-06-09 | 3837 | 0 | 31.4787 | 0
160 | 1900-06-09 | 3838 | 0 | 27.5133 | 0
160 | 1900-06-09 | 3839 | 0 | 29.1241 | 0
160 | 1900-06-09 | 3840 | 0 | 33.6987 | 0
161 | 1900-06-10 | 3841 | 0 | 33.1043 | 0
161 | 1900-06-10 | 3842 | 0 | 26.7437 | 0
161 | 1900-06-10 | 3843 | 0 | 21.0322 | 0
161 | 1900-06-10 | 3844 | 0 | 30.4131 | 0
161 | 1900-06-10 | 3845 | 0 | 236.305 | 0
161 | 1900-06-10 | 3846 | 0 | 28.779 | 0
161 | 1900-06-10 | 3847 | 0 | 27.4862 | 0
161 | 1900-06-10 | 3848 | 0 | 38.007 | 0
161 | 1900-06-10 | 3849 | 0 | 36.3029 | 0
161 | 1900-06-10 | 3850 | 0 | 39.0213 | 0
161 | 1900-06-10 | 3851 | 0 | 57.9904 | 0
161 | 1900-06-10 | 3852 | 0 | 41.4674 | 0
161 | 1900-06-10 | 3853 | 0 | 42.1317 | 0
161 | 1900-06-10 | 3854 | 0 | 44.3375 | 0
161 | 1900-06-10 | 3855 | 0 | 49.9971 | 0
161 | 1900-06-10 | 3856 | 0 | 35.1343 | 0
161 | 1900-06-10 | 3857 | 0 | 42.0496 | 0
161 | 1900-06-10 | 3858 | 0 | 40.273 | 0
161 | 1900-06-10 | 3859 | 0 | 46.8537 | 0
161 | 1900-06-10 | 3860 | 0 | 28.7741 | 0
161 | 1900-06-10 | 3861 | 0 | 27.3437 | 0
161 | 1900-06-10 | 3862 | 0 | 24.375 | 0
161 | 1900-06-10 | 3863 | 0 | 29.9671 | 0
161 | 1900-06-10 | 3864 | 0 | 34.4735 | 0
162 | 1900-06-11 | 3865 | 0 | 33.5026 | 0
162 | 1900-06-11 | 3866 | 0 | 25.8952 | 0
162 | 1900-06-11 | 3867 | 0 | 27.5836 | 0
162 | 1900-06-11 | 3868 | 0 | 40.8063 | 0
162 | 1900-06-11 | 3869 | 0 | 79.9373 | 0
162 | 1900-06-11 | 3870 | 0 | 116.3777 | 0
162 | 1900-06-11 | 3871 | 0 | 107.3291 | 0
162 | 1900-06-11 | 3872 | 0 | 94.9107 | 0
162 | 1900-06-11 | 3873 | 0 | 52.2568 | 0
162 | 1900-06-11 | 3874 | 0 | 51.8283 | 0
162 | 1900-06-11 | 3875 | 0 | 90.4193 | 0
162 | 1900-06-11 | 3876 | 0 | 47.7366 | 0
162 | 1900-06-11 | 3877 | 0 | 68.6866 | 0
162 | 1900-06-11 | 3878 | 0 | 43.0419 | 0
162 | 1900-06-11 | 3879 | 0 | 34.7634 | 0
162 | 1900-06-11 | 3880 | 0 | 37.4477 | 0
162 | 1900-06-11 | 3881 | 0 | 58.8117 | 0
162 | 1900-06-11 | 3882 | 0 | 38.7773 | 0
162 | 1900-06-11 | 3883 | 0 | 39.0998 | 0
162 | 1900-06-11 | 3884 | 0 | 71.8801 | 0
162 | 1900-06-11 | 3885 | 0 | 94.2698 | 0
162 | 1900-06-11 | 3886 | 0 | 95.4344 | 0
162 | 1900-06-11 | 3887 | 0 | 27.8682 | 0
162 | 1900-06-11 | 3888 | 0 | 28.7208 | 0
163 | 1900-06-12 | 3889 | 0 | 23.6741 | 0
163 | 1900-06-12 | 3890 | 0 | 21.9597 | 0
163 | 1900-06-12 | 3891 | 0 | 27.9857 | 0
163 | 1900-06-12 | 3892 | 0 | 38.4724 | 0
163 | 1900-06-12 | 3893 | 0 | 52.0726 | 0
163 | 1900-06-12 | 3894 | 0 | 126.2288 | 0
163 | 1900-06-12 | 3895 | 0 | 112.4821 | 0
163 | 1900-06-12 | 3896 | 0 | 65.6407 | 0
163 | 1900-06-12 | 3897 | 0 | 92.117 | 0
163 | 1900-06-12 | 3898 | 0 | 85.5771 | 0
163 | 1900-06-12 | 3899 | 0 | 31.1031 | 0
163 | 1900-06-12 | 3900 | 0 | 35.8016 | 0
163 | 1900-06-12 | 3901 | 0 | 39.4885 | 0
163 | 1900-06-12 | 3902 | 0 | 43.9611 | 0
163 | 1900-06-12 | 3903 | 0 | 48.6892 | 0
163 | 1900-06-12 | 3904 | 0 | 44.0043 | 0
163 | 1900-06-12 | 3905 | 0 | 33.1424 | 0
163 | 1900-06-12 | 3906 | 0 | 59.8953 | 0
163 | 1900-06-12 | 3907 | 0 | 97.5381 | 0
163 | 1900-06-12 | 3908 | 0 | 86.8164 | 0
163 | 1900-06-12 | 3909 | 0 | 107.2753 | 0
163 | 1900-06-12 | 3910 | 0 | 70.5421 | 0
163 | 1900-06-12 | 3911 | 0 | 65.9281 | 0
163 | 1900-06-12 | 3912 | 0 | 60.0061 | 0
164 | 1900-06-13 | 3913 | 0 | 109.8183 | 0
164 | 1900-06-13 | 3914 | 0 | 57.3196 | 0
164 | 1900-06-13 | 3915 | 0 | 21.6144 | 0
164 | 1900-06-13 | 3916 | 0 | 27.978 | 0
164 | 1900-06-13 | 3917 | 0 | 37.6333 | 0
164 | 1900-06-13 | 3918 | 0 | 277.6479 | 0
164 | 1900-06-13 | 3919 | 0 | 85.7523 | 0
164 | 1900-06-13 | 3920 | 0 | 71.3766 | 0
164 | 1900-06-13 | 3921 | 0 | 86.4753 | 0
164 | 1900-06-13 | 3922 | 0 | 309.764 | 0
164 | 1900-06-13 | 3923 | 0 | 82.6668 | 0
164 | 1900-06-13 | 3924 | 0 | 74.695 | 0
164 | 1900-06-13 | 3925 | 0 | 93.9495 | 0
164 | 1900-06-13 | 3926 | 0 | 78.7388 | 0
164 | 1900-06-13 | 3927 | 0 | 40.1606 | 0
164 | 1900-06-13 | 3928 | 0 | 42.3149 | 0
164 | 1900-06-13 | 3929 | 0 | 46.3908 | 0
164 | 1900-06-13 | 3930 | 0 | 46.1155 | 0
164 | 1900-06-13 | 3931 | 0 | 86.6762 | 0
164 | 1900-06-13 | 3932 | 0 | 107.2009 | 0
164 | 1900-06-13 | 3933 | 0 | 90.8565 | 0
164 | 1900-06-13 | 3934 | 0 | 75.1172 | 0
164 | 1900-06-13 | 3935 | 0 | 48.2545 | 0
164 | 1900-06-13 | 3936 | 0 | 40.4504 | 0
165 | 1900-06-14 | 3937 | 0 | 88.7714 | 0
165 | 1900-06-14 | 3938 | 0 | 59.1978 | 0
165 | 1900-06-14 | 3939 | 0 | 21.0403 | 0
165 | 1900-06-14 | 3940 | 0 | 22.5944 | 0
165 | 1900-06-14 | 3941 | 0 | 30.3718 | 0
165 | 1900-06-14 | 3942 | 0 | 32.2804 | 0
165 | 1900-06-14 | 3943 | 0 | 21.5424 | 0
165 | 1900-06-14 | 3944 | 0 | 50.8983 | 0
165 | 1900-06-14 | 3945 | 0 | 33.2445 | 0
165 | 1900-06-14 | 3946 | 0 | 47.4793 | 0
165 | 1900-06-14 | 3947 | 0 | 92.1646 | 0
165 | 1900-06-14 | 3948 | 0 | 44.6058 | 0
165 | 1900-06-14 | 3949 | 0 | 40.7558 | 0
165 | 1900-06-14 | 3950 | 0 | 50.6899 | 0
165 | 1900-06-14 | 3951 | 0 | 42.9951 | 0
165 | 1900-06-14 | 3952 | 0 | 34.7204 | 0
165 | 1900-06-14 | 3953 | 0 | 45.2202 | 0
165 | 1900-06-14 | 3954 | 0 | 42.8211 | 0
165 | 1900-06-14 | 3955 | 0 | 34.9597 | 0
165 | 1900-06-14 | 3956 | 0 | 28.8081 | 0
165 | 1900-06-14 | 3957 | 0 | 31.6171 | 0
165 | 1900-06-14 | 3958 | 0 | 35.0397 | 0
165 | 1900-06-14 | 3959 | 0 | 68.4867 | 0
165 | 1900-06-14 | 3960 | 0 | 105.6587 | 0
166 | 1900-06-15 | 3961 | 0 | 94.7911 | 0
166 | 1900-06-15 | 3962 | 0 | 39.2885 | 0
166 | 1900-06-15 | 3963 | 0 | 33.6361 | 0
166 | 1900-06-15 | 3964 | 0 | 30.3014 | 0
166 | 1900-06-15 | 3965 | 0 | 36.3834 | 0
166 | 1900-06-15 | 3966 | 0 | 65.9575 | 0
166 | 1900-06-15 | 3967 | 0 | 116.2777 | 0
166 | 1900-06-15 | 3968 | 0 | 131.9595 | 0
166 | 1900-06-15 | 3969 | 0 | 114.6307 | 0
166 | 1900-06-15 | 3970 | 0 | 112.9073 | 0
166 | 1900-06-15 | 3971 | 0 | 117.7317 | 0
166 | 1900-06-15 | 3972 | 0 | 104.1663 | 0
166 | 1900-06-15 | 3973 | 0 | 136.4877 | 0
166 | 1900-06-15 | 3974 | 0 | 128.8522 | 0
166 | 1900-06-15 | 3975 | 0 | 62.4658 | 0
166 | 1900-06-15 | 3976 | 0 | 44.1302 | 0
166 | 1900-06-15 | 3977 | 0 | 37.0705 | 0
166 | 1900-06-15 | 3978 | 0 | 41.1766 | 0
166 | 1900-06-15 | 3979 | 0 | 34.5526 | 0
166 | 1900-06-15 | 3980 | 0 | 24.1526 | 0
166 | 1900-06-15 | 3981 | 0 | 22.5343 | 0
166 | 1900-06-15 | 3982 | 0 | 25.9216 | 0
166 | 1900-06-15 | 3983 | 0 | 24.3711 | 0
166 | 1900-06-15 | 3984 | 0 | 32.296 | 0
167 | 1900-06-16 | 3985 | 0 | 38.0922 | 0
167 | 1900-06-16 | 3986 | 0 | 25.4865 | 0
167 | 1900-06-16 | 3987 | 0 | 30.4873 | 0
167 | 1900-06-16 | 3988 | 0 | 35.8835 | 0
167 | 1900-06-16 | 3989 | 0 | 70.5091 | 0
167 | 1900-06-16 | 3990 | 0 | 92.9656 | 0
167 | 1900-06-16 | 3991 | 0 | 113.9884 | 0
167 | 1900-06-16 | 3992 | 0 | 117.2883 | 0
167 | 1900-06-16 | 3993 | 0 | 67.4848 | 0
167 | 1900-06-16 | 3994 | 0 | 50.4463 | 0
167 | 1900-06-16 | 3995 | 0 | 101.7162 | 0
167 | 1900-06-16 | 3996 | 0 | 138.0817 | 0
167 | 1900-06-16 | 3997 | 0 | 119.3368 | 0
167 | 1900-06-16 | 3998 | 0 | 116.9648 | 0
167 | 1900-06-16 | 3999 | 0 | 132.8766 | 0
167 | 1900-06-16 | 4000 | 0 | 268.2489 | 0
167 | 1900-06-16 | 4001 | 0 | 39.304 | 0
167 | 1900-06-16 | 4002 | 0 | 38.1644 | 0
167 | 1900-06-16 | 4003 | 0 | 42.6436 | 0
167 | 1900-06-16 | 4004 | 0 | 30.109 | 0
167 | 1900-06-16 | 4005 | 0 | 28.7538 | 0
167 | 1900-06-16 | 4006 | 0 | 29.8997 | 0
167 | 1900-06-16 | 4007 | 0 | 25.2213 | 0
167 | 1900-06-16 | 4008 | 0 | 32.2998 | 0
168 | 1900-06-17 | 4009 | 0 | 25.2521 | 0
168 | 1900-06-17 | 4010 | 0 | 24.1092 | 0
168 | 1900-06-17 | 4011 | 0 | 23.1315 | 0
168 | 1900-06-17 | 4012 | 0 | 25.3002 | 0
168 | 1900-06-17 | 4013 | 0 | 59.0478 | 0
168 | 1900-06-17 | 4014 | 0 | 112.7818 | 0
168 | 1900-06-17 | 4015 | 0 | 120.7847 | 0
168 | 1900-06-17 | 4016 | 0 | 139.6144 | 0
168 | 1900-06-17 | 4017 | 0 | 114.644 | 0
168 | 1900-06-17 | 4018 | 0 | 134.2638 | 0
168 | 1900-06-17 | 4019 | 0 | 128.6323 | 0
168 | 1900-06-17 | 4020 | 0 | 332.14 | 0
168 | 1900-06-17 | 4021 | 0 | 107.7343 | 0
168 | 1900-06-17 | 4022 | 0 | 51.9377 | 0
168 | 1900-06-17 | 4023 | 0 | 46.3695 | 0
168 | 1900-06-17 | 4024 | 0 | 51.5646 | 0
168 | 1900-06-17 | 4025 | 0 | 42.1493 | 0
168 | 1900-06-17 | 4026 | 0 | 39.8355 | 0
168 | 1900-06-17 | 4027 | 0 | 52.9958 | 0
168 | 1900-06-17 | 4028 | 0 | 27.833 | 0
168 | 1900-06-17 | 4029 | 0 | 33.6719 | 0
168 | 1900-06-17 | 4030 | 0 | 24.8912 | 0
168 | 1900-06-17 | 4031 | 0 | 35.7015 | 0
168 | 1900-06-17 | 4032 | 0 | 25.8582 | 0
169 | 1900-06-18 | 4033 | 0 | 33.2531 | 0
169 | 1900-06-18 | 4034 | 0 | 26.9946 | 0
169 | 1900-06-18 | 4035 | 0 | 31.3916 | 0
169 | 1900-06-18 | 4036 | 0 | 29.7689 | 0
169 | 1900-06-18 | 4037 | 0 | 40.9946 | 0
169 | 1900-06-18 | 4038 | 0 | 63.1008 | 0
169 | 1900-06-18 | 4039 | 0 | 37.1715 | 0
169 | 1900-06-18 | 4040 | 0 | 47.5243 | 0
169 | 1900-06-18 | 4041 | 0 | 83.1925 | 0
169 | 1900-06-18 | 4042 | 0 | 78.6708 | 0
169 | 1900-06-18 | 4043 | 0 | 47.5736 | 0
169 | 1900-06-18 | 4044 | 0 | 47.6935 | 0
169 | 1900-06-18 | 4045 | 0 | 43.0743 | 0
169 | 1900-06-18 | 4046 | 0 | 53.3861 | 0
169 | 1900-06-18 | 4047 | 0 | 37.7253 | 0
169 | 1900-06-18 | 4048 | 0 | 51.6992 | 0
169 | 1900-06-18 | 4049 | 0 | 42.1235 | 0
169 | 1900-06-18 | 4050 | 0 | 37.0333 | 0
169 | 1900-06-18 | 4051 | 0 | 50.2722 | 0
169 | 1900-06-18 | 4052 | 0 | 35.7492 | 0
169 | 1900-06-18 | 4053 | 0 | 20.3483 | 0
169 | 1900-06-18 | 4054 | 0 | 36.4541 | 0
169 | 1900-06-18 | 4055 | 0 | 29.8523 | 0
169 | 1900-06-18 | 4056 | 0 | 27.752 | 0
170 | 1900-06-19 | 4057 | 0 | 27.8167 | 0
170 | 1900-06-19 | 4058 | 0 | 17.5071 | 0
170 | 1900-06-19 | 4059 | 0 | 25.5526 | 0
170 | 1900-06-19 | 4060 | 0 | 25.7138 | 0
170 | 1900-06-19 | 4061 | 0 | 41.9737 | 0
170 | 1900-06-19 | 4062 | 0 | 67.5772 | 0
170 | 1900-06-19 | 4063 | 0 | 46.8997 | 0
170 | 1900-06-19 | 4064 | 0 | 57.0739 | 0
170 | 1900-06-19 | 4065 | 0 | 69.5525 | 0
170 | 1900-06-19 | 4066 | 0 | 98.7811 | 0
170 | 1900-06-19 | 4067 | 0 | 73.4467 | 0
170 | 1900-06-19 | 4068 | 0 | 34.4723 | 0
170 | 1900-06-19 | 4069 | 0 | 45.1536 | 0
170 | 1900-06-19 | 4070 | 0 | 26.8328 | 0
170 | 1900-06-19 | 4071 | 0 | 52.721 | 0
170 | 1900-06-19 | 4072 | 0 | 46.2463 | 0
170 | 1900-06-19 | 4073 | 0 | 44.2142 | 0
170 | 1900-06-19 | 4074 | 0 | 41.2496 | 0
170 | 1900-06-19 | 4075 | 0 | 40.9808 | 0
170 | 1900-06-19 | 4076 | 0 | 233.8047 | 0
170 | 1900-06-19 | 4077 | 0 | 31.0897 | 0
170 | 1900-06-19 | 4078 | 0 | 34.4248 | 0
170 | 1900-06-19 | 4079 | 0 | 30.5092 | 0
170 | 1900-06-19 | 4080 | 0 | 30.3457 | 0
171 | 1900-06-20 | 4081 | 0 | 28.8563 | 0
171 | 1900-06-20 | 4082 | 0 | 33.2672 | 0
171 | 1900-06-20 | 4083 | 0 | 22.6683 | 0
171 | 1900-06-20 | 4084 | 0 | 27.6075 | 0
171 | 1900-06-20 | 4085 | 0 | 51.3956 | 0
171 | 1900-06-20 | 4086 | 0 | 89.6994 | 0
171 | 1900-06-20 | 4087 | 0 | 81.674 | 0
171 | 1900-06-20 | 4088 | 0 | 63.1741 | 0
171 | 1900-06-20 | 4089 | 0 | 41.0701 | 0
171 | 1900-06-20 | 4090 | 0 | 30.452 | 0
171 | 1900-06-20 | 4091 | 0 | 46.7211 | 0
171 | 1900-06-20 | 4092 | 0 | 36.2918 | 0
171 | 1900-06-20 | 4093 | 0 | 47.2834 | 0
171 | 1900-06-20 | 4094 | 0 | 48.167 | 0
171 | 1900-06-20 | 4095 | 0 | 47.8253 | 0
171 | 1900-06-20 | 4096 | 0 | 40.1752 | 0
171 | 1900-06-20 | 4097 | 0 | 31.3156 | 0
171 | 1900-06-20 | 4098 | 0 | 42.0318 | 0
171 | 1900-06-20 | 4099 | 0 | 36.2664 | 0
171 | 1900-06-20 | 4100 | 0 | 28.3278 | 0
171 | 1900-06-20 | 4101 | 0 | 30.8401 | 0
171 | 1900-06-20 | 4102 | 0 | 37.281 | 0
171 | 1900-06-20 | 4103 | 0 | 26.1955 | 0
171 | 1900-06-20 | 4104 | 0 | 27.3786 | 0
172 | 1900-06-21 | 4105 | 0 | 29.4147 | 0
172 | 1900-06-21 | 4106 | 0 | 29.1685 | 0
172 | 1900-06-21 | 4107 | 0 | 29.5078 | 0
172 | 1900-06-21 | 4108 | 0 | 30.0764 | 0
172 | 1900-06-21 | 4109 | 0 | 35.5374 | 0
172 | 1900-06-21 | 4110 | 0 | 98.7091 | 0
172 | 1900-06-21 | 4111 | 0 | 104.0835 | 0
172 | 1900-06-21 | 4112 | 0 | 110.5417 | 0
172 | 1900-06-21 | 4113 | 0 | 120.2855 | 0
172 | 1900-06-21 | 4114 | 0 | 90.9752 | 0
172 | 1900-06-21 | 4115 | 0 | 41.9089 | 0
172 | 1900-06-21 | 4116 | 0 | 33.9907 | 0
172 | 1900-06-21 | 4117 | 0 | 42.2132 | 0
172 | 1900-06-21 | 4118 | 0 | 41.7238 | 0
172 | 1900-06-21 | 4119 | 0 | 45.5305 | 0
172 | 1900-06-21 | 4120 | 0 | 227.8324 | 0
172 | 1900-06-21 | 4121 | 0 | 48.303 | 0
172 | 1900-06-21 | 4122 | 0 | 48.1462 | 0
172 | 1900-06-21 | 4123 | 0 | 31.7489 | 0
172 | 1900-06-21 | 4124 | 0 | 26.8352 | 0
172 | 1900-06-21 | 4125 | 0 | 31.5466 | 0
172 | 1900-06-21 | 4126 | 0 | 28.4512 | 0
172 | 1900-06-21 | 4127 | 0 | 23.7331 | 0
172 | 1900-06-21 | 4128 | 0 | 24.9372 | 0
173 | 1900-06-22 | 4129 | 0 | 36.1872 | 0
173 | 1900-06-22 | 4130 | 0 | 33.0471 | 0
173 | 1900-06-22 | 4131 | 0 | 35.0225 | 0
173 | 1900-06-22 | 4132 | 0 | 33.6426 | 0
173 | 1900-06-22 | 4133 | 0 | 33.1499 | 0
173 | 1900-06-22 | 4134 | 0 | 27.4158 | 0
173 | 1900-06-22 | 4135 | 0 | 28.1296 | 0
173 | 1900-06-22 | 4136 | 0 | 43.2216 | 0
173 | 1900-06-22 | 4137 | 0 | 42.4326 | 0
173 | 1900-06-22 | 4138 | 0 | 33.8003 | 0
173 | 1900-06-22 | 4139 | 0 | 43.9807 | 0
173 | 1900-06-22 | 4140 | 0 | 36.9747 | 0
173 | 1900-06-22 | 4141 | 0 | 39.4808 | 0
173 | 1900-06-22 | 4142 | 0 | 41.7422 | 0
173 | 1900-06-22 | 4143 | 0 | 32.0483 | 0
173 | 1900-06-22 | 4144 | 0 | 33.1679 | 0
173 | 1900-06-22 | 4145 | 0 | 40.7763 | 0
173 | 1900-06-22 | 4146 | 0 | 39.4067 | 0
173 | 1900-06-22 | 4147 | 0 | 42.3963 | 0
173 | 1900-06-22 | 4148 | 0 | 30.518 | 0
173 | 1900-06-22 | 4149 | 0 | 24.3154 | 0
173 | 1900-06-22 | 4150 | 0 | 29.7448 | 0
173 | 1900-06-22 | 4151 | 0 | 31.0277 | 0
173 | 1900-06-22 | 4152 | 0 | 21.5355 | 0
174 | 1900-06-23 | 4153 | 0 | 26.3507 | 0
174 | 1900-06-23 | 4154 | 0 | 232.2044 | 0
174 | 1900-06-23 | 4155 | 0 | 22.3246 | 0
174 | 1900-06-23 | 4156 | 0 | 29.0848 | 0
174 | 1900-06-23 | 4157 | 0 | 20.9887 | 0
174 | 1900-06-23 | 4158 | 0 | 26.2524 | 0
174 | 1900-06-23 | 4159 | 0 | 27.4363 | 0
174 | 1900-06-23 | 4160 | 0 | 46.052 | 0
174 | 1900-06-23 | 4161 | 0 | 47.0349 | 0
174 | 1900-06-23 | 4162 | 0 | 36.3937 | 0
174 | 1900-06-23 | 4163 | 0 | 41.0546 | 0
174 | 1900-06-23 | 4164 | 0 | 41.8308 | 0
174 | 1900-06-23 | 4165 | 0 | 28.3624 | 0
174 | 1900-06-23 | 4166 | 0 | 49.934 | 0
174 | 1900-06-23 | 4167 | 0 | 46.0785 | 0
174 | 1900-06-23 | 4168 | 0 | 51.0649 | 0
174 | 1900-06-23 | 4169 | 0 | 41.0357 | 0
174 | 1900-06-23 | 4170 | 0 | 41.603 | 0
174 | 1900-06-23 | 4171 | 0 | 49.0047 | 0
174 | 1900-06-23 | 4172 | 0 | 29.9235 | 0
174 | 1900-06-23 | 4173 | 0 | 22.9598 | 0
174 | 1900-06-23 | 4174 | 0 | 30.5755 | 0
174 | 1900-06-23 | 4175 | 0 | 31.8417 | 0
174 | 1900-06-23 | 4176 | 0 | 27.7644 | 0
175 | 1900-06-24 | 4177 | 0 | 27.6207 | 0
175 | 1900-06-24 | 4178 | 0 | 26.2927 | 0
175 | 1900-06-24 | 4179 | 0 | 29.1545 | 0
175 | 1900-06-24 | 4180 | 0 | 23.7802 | 0
175 | 1900-06-24 | 4181 | 0 | 21.1197 | 0
175 | 1900-06-24 | 4182 | 0 | 32.815 | 0
175 | 1900-06-24 | 4183 | 0 | 26.96 | 0
175 | 1900-06-24 | 4184 | 0 | 38.4534 | 0
175 | 1900-06-24 | 4185 | 0 | 41.0558 | 0
175 | 1900-06-24 | 4186 | 0 | 48.928 | 0
175 | 1900-06-24 | 4187 | 0 | 43.5692 | 0
175 | 1900-06-24 | 4188 | 0 | 42.5622 | 0
175 | 1900-06-24 | 4189 | 0 | 44.2317 | 0
175 | 1900-06-24 | 4190 | 0 | 35.6328 | 0
175 | 1900-06-24 | 4191 | 0 | 41.58 | 0
175 | 1900-06-24 | 4192 | 0 | 45.6097 | 0
175 | 1900-06-24 | 4193 | 0 | 48.7075 | 0
175 | 1900-06-24 | 4194 | 0 | 34.9009 | 0
175 | 1900-06-24 | 4195 | 0 | 46.2036 | 0
175 | 1900-06-24 | 4196 | 0 | 23.8786 | 0
175 | 1900-06-24 | 4197 | 0 | 32.6627 | 0
175 | 1900-06-24 | 4198 | 0 | 28.7602 | 0
175 | 1900-06-24 | 4199 | 0 | 28.0302 | 0
175 | 1900-06-24 | 4200 | 0 | 23.1305 | 0
176 | 1900-06-25 | 4201 | 0 | 29.9756 | 0
176 | 1900-06-25 | 4202 | 0 | 21.7072 | 0
176 | 1900-06-25 | 4203 | 0 | 41.5941 | 0
176 | 1900-06-25 | 4204 | 0 | 64.1515 | 0
176 | 1900-06-25 | 4205 | 0 | 88.1702 | 0
176 | 1900-06-25 | 4206 | 0 | 98.2064 | 0
176 | 1900-06-25 | 4207 | 0 | 102.8108 | 0
176 | 1900-06-25 | 4208 | 0 | 93.8527 | 0
176 | 1900-06-25 | 4209 | 0 | 62.1941 | 0
176 | 1900-06-25 | 4210 | 0 | 83.4296 | 0
176 | 1900-06-25 | 4211 | 0 | 88.2768 | 0
176 | 1900-06-25 | 4212 | 0 | 105.0984 | 0
176 | 1900-06-25 | 4213 | 0 | 102.5069 | 0
176 | 1900-06-25 | 4214 | 0 | 92.3009 | 0
176 | 1900-06-25 | 4215 | 0 | 76.5036 | 0
176 | 1900-06-25 | 4216 | 0 | 42.8747 | 0
176 | 1900-06-25 | 4217 | 0 | 48.7452 | 0
176 | 1900-06-25 | 4218 | 0 | 48.8457 | 0
176 | 1900-06-25 | 4219 | 0 | 27.6409 | 0
176 | 1900-06-25 | 4220 | 0 | 30.2064 | 0
176 | 1900-06-25 | 4221 | 0 | 216.457 | 0
176 | 1900-06-25 | 4222 | 0 | 38.8241 | 0
176 | 1900-06-25 | 4223 | 0 | 27.5555 | 0
176 | 1900-06-25 | 4224 | 0 | 22.7354 | 0
177 | 1900-06-26 | 4225 | 0 | 31.3733 | 0
177 | 1900-06-26 | 4226 | 0 | 28.0252 | 0
177 | 1900-06-26 | 4227 | 0 | 30.1706 | 0
177 | 1900-06-26 | 4228 | 0 | 28.4517 | 0
177 | 1900-06-26 | 4229 | 0 | 41.7836 | 0
177 | 1900-06-26 | 4230 | 0 | 86.1067 | 0
177 | 1900-06-26 | 4231 | 0 | 112.9043 | 0
177 | 1900-06-26 | 4232 | 0 | 301.0981 | 0
177 | 1900-06-26 | 4233 | 0 | 97.4351 | 0
177 | 1900-06-26 | 4234 | 0 | 93.9789 | 0
177 | 1900-06-26 | 4235 | 0 | 102.5337 | 0
177 | 1900-06-26 | 4236 | 0 | 130.8599 | 0
177 | 1900-06-26 | 4237 | 0 | 98.3881 | 0
177 | 1900-06-26 | 4238 | 0 | 57.767 | 0
177 | 1900-06-26 | 4239 | 0 | 37.2208 | 0
177 | 1900-06-26 | 4240 | 0 | 31.8009 | 0
177 | 1900-06-26 | 4241 | 0 | 42.3427 | 0
177 | 1900-06-26 | 4242 | 0 | 52.8022 | 0
177 | 1900-06-26 | 4243 | 0 | 49.8348 | 0
177 | 1900-06-26 | 4244 | 0 | 31.7277 | 0
177 | 1900-06-26 | 4245 | 0 | 21.938 | 0
177 | 1900-06-26 | 4246 | 0 | 27.0798 | 0
177 | 1900-06-26 | 4247 | 0 | 21.179 | 0
177 | 1900-06-26 | 4248 | 0 | 29.4693 | 0
178 | 1900-06-27 | 4249 | 0 | 27.8638 | 0
178 | 1900-06-27 | 4250 | 0 | 30.6409 | 0
178 | 1900-06-27 | 4251 | 0 | 28.425 | 0
178 | 1900-06-27 | 4252 | 0 | 28.6482 | 0
178 | 1900-06-27 | 4253 | 0 | 37.5591 | 0
178 | 1900-06-27 | 4254 | 0 | 90.5135 | 0
178 | 1900-06-27 | 4255 | 0 | 96.8806 | 0
178 | 1900-06-27 | 4256 | 0 | 76.6269 | 0
178 | 1900-06-27 | 4257 | 0 | 53.8644 | 0
178 | 1900-06-27 | 4258 | 0 | 106.0034 | 0
178 | 1900-06-27 | 4259 | 0 | 107.8123 | 0
178 | 1900-06-27 | 4260 | 0 | 126.8535 | 0
178 | 1900-06-27 | 4261 | 0 | 100.2391 | 0
178 | 1900-06-27 | 4262 | 0 | 54.4449 | 0
178 | 1900-06-27 | 4263 | 0 | 52.2011 | 0
178 | 1900-06-27 | 4264 | 0 | 43.9612 | 0
178 | 1900-06-27 | 4265 | 0 | 33.1806 | 0
178 | 1900-06-27 | 4266 | 0 | 28.6709 | 0
178 | 1900-06-27 | 4267 | 0 | 45.4737 | 0
178 | 1900-06-27 | 4268 | 0 | 27.0427 | 0
178 | 1900-06-27 | 4269 | 0 | 29.4854 | 0
178 | 1900-06-27 | 4270 | 0 | 24.8768 | 0
178 | 1900-06-27 | 4271 | 0 | 30.1057 | 0
178 | 1900-06-27 | 4272 | 0 | 23.1979 | 0
179 | 1900-06-28 | 4273 | 0 | 29.5139 | 0
179 | 1900-06-28 | 4274 | 0 | 28.5794 | 0
179 | 1900-06-28 | 4275 | 0 | 30.1312 | 0
179 | 1900-06-28 | 4276 | 0 | 31.5074 | 0
179 | 1900-06-28 | 4277 | 0 | 28.5228 | 0
179 | 1900-06-28 | 4278 | 0 | 64.944 | 0
179 | 1900-06-28 | 4279 | 0 | 105.1994 | 0
179 | 1900-06-28 | 4280 | 0 | 115.2802 | 0
179 | 1900-06-28 | 4281 | 0 | 97.6949 | 0
179 | 1900-06-28 | 4282 | 0 | 100.4655 | 0
179 | 1900-06-28 | 4283 | 0 | 92.2473 | 0
179 | 1900-06-28 | 4284 | 0 | 88.5669 | 0
179 | 1900-06-28 | 4285 | 0 | 133.7601 | 0
179 | 1900-06-28 | 4286 | 0 | 126.6531 | 0
179 | 1900-06-28 | 4287 | 0 | 121.6344 | 0
179 | 1900-06-28 | 4288 | 0 | 55.8353 | 0
179 | 1900-06-28 | 4289 | 0 | 50.8307 | 0
179 | 1900-06-28 | 4290 | 0 | 40.7761 | 0
179 | 1900-06-28 | 4291 | 0 | 44.4791 | 0
179 | 1900-06-28 | 4292 | 0 | 34.5489 | 0
179 | 1900-06-28 | 4293 | 0 | 26.6921 | 0
179 | 1900-06-28 | 4294 | 0 | 22.5659 | 0
179 | 1900-06-28 | 4295 | 0 | 25.7539 | 0
179 | 1900-06-28 | 4296 | 0 | 19.5012 | 0
180 | 1900-06-29 | 4297 | 0 | 25.6042 | 0
180 | 1900-06-29 | 4298 | 0 | 36.6349 | 0
180 | 1900-06-29 | 4299 | 0 | 20.3799 | 0
180 | 1900-06-29 | 4300 | 0 | 30.9875 | 0
180 | 1900-06-29 | 4301 | 0 | 50.4711 | 0
180 | 1900-06-29 | 4302 | 0 | 78.302 | 0
180 | 1900-06-29 | 4303 | 0 | 87.4648 | 0
180 | 1900-06-29 | 4304 | 0 | 97.9765 | 0
180 | 1900-06-29 | 4305 | 0 | 113.4909 | 0
180 | 1900-06-29 | 4306 | 0 | 81.9165 | 0
180 | 1900-06-29 | 4307 | 0 | 97.0482 | 0
180 | 1900-06-29 | 4308 | 0 | 124.3594 | 0
180 | 1900-06-29 | 4309 | 0 | 92.3164 | 0
180 | 1900-06-29 | 4310 | 0 | 245.561 | 0
180 | 1900-06-29 | 4311 | 0 | 44.1775 | 0
180 | 1900-06-29 | 4312 | 0 | 46.7474 | 0
180 | 1900-06-29 | 4313 | 0 | 39.5733 | 0
180 | 1900-06-29 | 4314 | 0 | 29.9397 | 0
180 | 1900-06-29 | 4315 | 0 | 51.7757 | 0
180 | 1900-06-29 | 4316 | 0 | 22.0391 | 0
180 | 1900-06-29 | 4317 | 0 | 27.4249 | 0
180 | 1900-06-29 | 4318 | 0 | 23.1426 | 0
180 | 1900-06-29 | 4319 | 0 | 29.2458 | 0
180 | 1900-06-29 | 4320 | 0 | 31.2493 | 0
181 | 1900-06-30 | 4321 | 0 | 28.0501 | 0
181 | 1900-06-30 | 4322 | 0 | 229.3584 | 0
181 | 1900-06-30 | 4323 | 0 | 30.8697 | 0
181 | 1900-06-30 | 4324 | 0 | 26.6693 | 0
181 | 1900-06-30 | 4325 | 0 | 30.8964 | 0
181 | 1900-06-30 | 4326 | 0 | 15.7347 | 0
181 | 1900-06-30 | 4327 | 0 | 26.8911 | 0
181 | 1900-06-30 | 4328 | 0 | 49.0152 | 0
181 | 1900-06-30 | 4329 | 0 | 27.1568 | 0
181 | 1900-06-30 | 4330 | 0 | 47.7693 | 0
181 | 1900-06-30 | 4331 | 0 | 47.5215 | 0
181 | 1900-06-30 | 4332 | 0 | 46.1773 | 0
181 | 1900-06-30 | 4333 | 0 | 51.0915 | 0
181 | 1900-06-30 | 4334 | 0 | 44.0746 | 0
181 | 1900-06-30 | 4335 | 0 | 41.3908 | 0
181 | 1900-06-30 | 4336 | 0 | 31.9678 | 0
181 | 1900-06-30 | 4337 | 0 | 44.4332 | 0
181 | 1900-06-30 | 4338 | 0 | 46.576 | 0
181 | 1900-06-30 | 4339 | 0 | 38.246 | 0
181 | 1900-06-30 | 4340 | 0 | 21.8013 | 0
181 | 1900-06-30 | 4341 | 0 | 30.534 | 0
181 | 1900-06-30 | 4342 | 0 | 31.85 | 0
181 | 1900-06-30 | 4343 | 0 | 28.4316 | 0
181 | 1900-06-30 | 4344 | 0 | 33.1516 | 0
182 | 1900-07-01 | 4345 | 0 | 28.6264 | 0
182 | 1900-07-01 | 4346 | 0 | 34.8612 | 0
182 | 1900-07-01 | 4347 | 0 | 28.0311 | 0
182 | 1900-07-01 | 4348 | 0 | 27.9065 | 0
182 | 1900-07-01 | 4349 | 0 | 22.3091 | 0
182 | 1900-07-01 | 4350 | 0 | 24.0556 | 0
182 | 1900-07-01 | 4351 | 0 | 34.0983 | 0
182 | 1900-07-01 | 4352 | 0 | 50.5197 | 0
182 | 1900-07-01 | 4353 | 0 | 42.4138 | 0
182 | 1900-07-01 | 4354 | 0 | 43.7647 | 0
182 | 1900-07-01 | 4355 | 0 | 39.8692 | 0
182 | 1900-07-01 | 4356 | 0 | 54.323 | 0
182 | 1900-07-01 | 4357 | 0 | 48.5759 | 0
182 | 1900-07-01 | 4358 | 0 | 37.5717 | 0
182 | 1900-07-01 | 4359 | 0 | 52.1897 | 0
182 | 1900-07-01 | 4360 | 0 | 40.2814 | 0
182 | 1900-07-01 | 4361 | 0 | 32.0941 | 0
182 | 1900-07-01 | 4362 | 0 | 51.2519 | 0
182 | 1900-07-01 | 4363 | 0 | 50.9375 | 0
182 | 1900-07-01 | 4364 | 0 | 26.1847 | 0
182 | 1900-07-01 | 4365 | 0 | 28.8511 | 0
182 | 1900-07-01 | 4366 | 0 | 34.6715 | 0
182 | 1900-07-01 | 4367 | 0 | 32.3852 | 0
182 | 1900-07-01 | 4368 | 0 | 30.5701 | 0
183 | 1900-07-02 | 4369 | 0 | 27.6681 | 0
183 | 1900-07-02 | 4370 | 0 | 24.838 | 0
183 | 1900-07-02 | 4371 | 0 | 32.5395 | 0
183 | 1900-07-02 | 4372 | 0 | 57.5505 | 0
183 | 1900-07-02 | 4373 | 0 | 108.3715 | 0
183 | 1900-07-02 | 4374 | 0 | 90.0722 | 0
183 | 1900-07-02 | 4375 | 0 | 96.6411 | 0
183 | 1900-07-02 | 4376 | 0 | 88.0368 | 0
183 | 1900-07-02 | 4377 | 0 | 60.3506 | 0
183 | 1900-07-02 | 4378 | 0 | 44.6309 | 0
183 | 1900-07-02 | 4379 | 0 | 77.5277 | 0
183 | 1900-07-02 | 4380 | 0 | 88.7857 | 0
183 | 1900-07-02 | 4381 | 0 | 45.9036 | 0
183 | 1900-07-02 | 4382 | 0 | 41.8227 | 0
183 | 1900-07-02 | 4383 | 0 | 236.842 | 0
183 | 1900-07-02 | 4384 | 0 | 45.3096 | 0
183 | 1900-07-02 | 4385 | 0 | 45.5788 | 0
183 | 1900-07-02 | 4386 | 0 | 42.8071 | 0
183 | 1900-07-02 | 4387 | 0 | 49.4468 | 0
183 | 1900-07-02 | 4388 | 0 | 73.3867 | 0
183 | 1900-07-02 | 4389 | 0 | 98.5209 | 0
183 | 1900-07-02 | 4390 | 0 | 83.8811 | 0
183 | 1900-07-02 | 4391 | 0 | 38.8735 | 0
183 | 1900-07-02 | 4392 | 0 | 26.217 | 0
184 | 1900-07-03 | 4393 | 0 | 29.241 | 0
184 | 1900-07-03 | 4394 | 0 | 30.8636 | 0
184 | 1900-07-03 | 4395 | 0 | 28.0574 | 0
184 | 1900-07-03 | 4396 | 0 | 25.7677 | 0
184 | 1900-07-03 | 4397 | 0 | 44.5534 | 0
184 | 1900-07-03 | 4398 | 0 | 103.8668 | 0
184 | 1900-07-03 | 4399 | 0 | 108.0302 | 0
184 | 1900-07-03 | 4400 | 0 | 124.7751 | 0
184 | 1900-07-03 | 4401 | 0 | 105.0336 | 0
184 | 1900-07-03 | 4402 | 0 | 110.2817 | 0
184 | 1900-07-03 | 4403 | 0 | 135.1453 | 0
184 | 1900-07-03 | 4404 | 0 | 143.6228 | 0
184 | 1900-07-03 | 4405 | 0 | 121.9768 | 0
184 | 1900-07-03 | 4406 | 0 | 53.578 | 0
184 | 1900-07-03 | 4407 | 0 | 46.5159 | 0
184 | 1900-07-03 | 4408 | 0 | 45.2818 | 0
184 | 1900-07-03 | 4409 | 0 | 41.5143 | 0
184 | 1900-07-03 | 4410 | 0 | 38.3715 | 0
184 | 1900-07-03 | 4411 | 0 | 54.5705 | 0
184 | 1900-07-03 | 4412 | 0 | 29.8185 | 0
184 | 1900-07-03 | 4413 | 0 | 33.8698 | 0
184 | 1900-07-03 | 4414 | 0 | 74.5345 | 0
184 | 1900-07-03 | 4415 | 0 | 59.8328 | 0
184 | 1900-07-03 | 4416 | 0 | 49.3157 | 0
185 | 1900-07-04 | 4417 | 0 | 77.8758 | 0
185 | 1900-07-04 | 4418 | 0 | 43.9011 | 0
185 | 1900-07-04 | 4419 | 0 | 30.9695 | 0
185 | 1900-07-04 | 4420 | 0 | 24.9729 | 0
185 | 1900-07-04 | 4421 | 0 | 39.0053 | 0
185 | 1900-07-04 | 4422 | 0 | 301.5751 | 0
185 | 1900-07-04 | 4423 | 0 | 127.7571 | 0
185 | 1900-07-04 | 4424 | 0 | 92.643 | 0
185 | 1900-07-04 | 4425 | 0 | 109.1629 | 0
185 | 1900-07-04 | 4426 | 0 | 72.2063 | 0
185 | 1900-07-04 | 4427 | 0 | 62.6153 | 0
185 | 1900-07-04 | 4428 | 0 | 55.535 | 0
185 | 1900-07-04 | 4429 | 0 | 49.413 | 0
185 | 1900-07-04 | 4430 | 0 | 28.2711 | 0
185 | 1900-07-04 | 4431 | 0 | 36.0911 | 0
185 | 1900-07-04 | 4432 | 0 | 42.724 | 0
185 | 1900-07-04 | 4433 | 0 | 43.7434 | 0
185 | 1900-07-04 | 4434 | 0 | 40.1342 | 0
185 | 1900-07-04 | 4435 | 0 | 49.6744 | 0
185 | 1900-07-04 | 4436 | 0 | 41.7873 | 0
185 | 1900-07-04 | 4437 | 0 | 98.528 | 0
185 | 1900-07-04 | 4438 | 0 | 61.1438 | 0
185 | 1900-07-04 | 4439 | 0 | 57.0993 | 0
185 | 1900-07-04 | 4440 | 0 | 40.2474 | 0
186 | 1900-07-05 | 4441 | 0 | 37.9765 | 0
186 | 1900-07-05 | 4442 | 0 | 46.8086 | 0
186 | 1900-07-05 | 4443 | 0 | 27.8158 | 0
186 | 1900-07-05 | 4444 | 0 | 39.7767 | 0
186 | 1900-07-05 | 4445 | 0 | 82.7714 | 0
186 | 1900-07-05 | 4446 | 0 | 89.0924 | 0
186 | 1900-07-05 | 4447 | 0 | 71.4238 | 0
186 | 1900-07-05 | 4448 | 0 | 86.0258 | 0
186 | 1900-07-05 | 4449 | 0 | 35.4934 | 0
186 | 1900-07-05 | 4450 | 0 | 50.6901 | 0
186 | 1900-07-05 | 4451 | 0 | 296.5557 | 0
186 | 1900-07-05 | 4452 | 0 | 121.7626 | 0
186 | 1900-07-05 | 4453 | 0 | 98.9358 | 0
186 | 1900-07-05 | 4454 | 0 | 95.0926 | 0
186 | 1900-07-05 | 4455 | 0 | 76.307 | 0
186 | 1900-07-05 | 4456 | 0 | 61.5537 | 0
186 | 1900-07-05 | 4457 | 0 | 92.566 | 0
186 | 1900-07-05 | 4458 | 0 | 121.5319 | 0
186 | 1900-07-05 | 4459 | 0 | 72.5916 | 0
186 | 1900-07-05 | 4460 | 0 | 25.6601 | 0
186 | 1900-07-05 | 4461 | 0 | 33.5241 | 0
186 | 1900-07-05 | 4462 | 0 | 64.1792 | 0
186 | 1900-07-05 | 4463 | 0 | 83.7831 | 0
186 | 1900-07-05 | 4464 | 0 | 30.0563 | 0
187 | 1900-07-06 | 4465 | 0 | 22.2761 | 0
187 | 1900-07-06 | 4466 | 0 | 22.5288 | 0
187 | 1900-07-06 | 4467 | 0 | 29.0898 | 0
187 | 1900-07-06 | 4468 | 0 | 24.9835 | 0
187 | 1900-07-06 | 4469 | 0 | 39.8615 | 0
187 | 1900-07-06 | 4470 | 0 | 66.4162 | 0
187 | 1900-07-06 | 4471 | 0 | 34.7791 | 0
187 | 1900-07-06 | 4472 | 0 | 35.9553 | 0
187 | 1900-07-06 | 4473 | 0 | 72.5666 | 0
187 | 1900-07-06 | 4474 | 0 | 85.6924 | 0
187 | 1900-07-06 | 4475 | 0 | 34.5027 | 0
187 | 1900-07-06 | 4476 | 0 | 38.4116 | 0
187 | 1900-07-06 | 4477 | 0 | 44.8008 | 0
187 | 1900-07-06 | 4478 | 0 | 38.3931 | 0
187 | 1900-07-06 | 4479 | 0 | 49.2401 | 0
187 | 1900-07-06 | 4480 | 0 | 41.2268 | 0
187 | 1900-07-06 | 4481 | 0 | 40.8075 | 0
187 | 1900-07-06 | 4482 | 0 | 47.4584 | 0
187 | 1900-07-06 | 4483 | 0 | 36.5032 | 0
187 | 1900-07-06 | 4484 | 0 | 26.8087 | 0
187 | 1900-07-06 | 4485 | 0 | 23.5494 | 0
187 | 1900-07-06 | 4486 | 0 | 25.1584 | 0
187 | 1900-07-06 | 4487 | 0 | 26.485 | 0
187 | 1900-07-06 | 4488 | 0 | 21.456 | 0
188 | 1900-07-07 | 4489 | 0 | 27.3453 | 0
188 | 1900-07-07 | 4490 | 0 | 27.3063 | 0
188 | 1900-07-07 | 4491 | 0 | 34.8906 | 0
188 | 1900-07-07 | 4492 | 0 | 29.0103 | 0
188 | 1900-07-07 | 4493 | 0 | 24.0802 | 0
188 | 1900-07-07 | 4494 | 0 | 23.4372 | 0
188 | 1900-07-07 | 4495 | 0 | 26.2293 | 0
188 | 1900-07-07 | 4496 | 0 | 35.7518 | 0
188 | 1900-07-07 | 4497 | 0 | 41.0064 | 0
188 | 1900-07-07 | 4498 | 0 | 42.9723 | 0
188 | 1900-07-07 | 4499 | 0 | 50.2401 | 0
188 | 1900-07-07 | 4500 | 0 | 27.7456 | 0
188 | 1900-07-07 | 4501 | 0 | 40.5512 | 0
188 | 1900-07-07 | 4502 | 0 | 47.5775 | 0
188 | 1900-07-07 | 4503 | 0 | 47.2713 | 0
188 | 1900-07-07 | 4504 | 0 | 37.9473 | 0
188 | 1900-07-07 | 4505 | 0 | 20.0599 | 0
188 | 1900-07-07 | 4506 | 0 | 41.4465 | 0
188 | 1900-07-07 | 4507 | 0 | 50.1116 | 0
188 | 1900-07-07 | 4508 | 0 | 23.3173 | 0
188 | 1900-07-07 | 4509 | 0 | 27.2687 | 0
188 | 1900-07-07 | 4510 | 0 | 27.8964 | 0
188 | 1900-07-07 | 4511 | 0 | 24.101 | 0
188 | 1900-07-07 | 4512 | 0 | 20.3061 | 0
189 | 1900-07-08 | 4513 | 0 | 27.6087 | 0
189 | 1900-07-08 | 4514 | 0 | 35.117 | 0
189 | 1900-07-08 | 4515 | 0 | 31.8897 | 0
189 | 1900-07-08 | 4516 | 0 | 26.2423 | 0
189 | 1900-07-08 | 4517 | 0 | 27.5277 | 0
189 | 1900-07-08 | 4518 | 0 | 29.0599 | 0
189 | 1900-07-08 | 4519 | 0 | 224.2116 | 0
189 | 1900-07-08 | 4520 | 0 | 38.9238 | 0
189 | 1900-07-08 | 4521 | 0 | 33.115 | 0
189 | 1900-07-08 | 4522 | 0 | 39.6534 | 0
189 | 1900-07-08 | 4523 | 0 | 49.1257 | 0
189 | 1900-07-08 | 4524 | 0 | 244.6237 | 0
189 | 1900-07-08 | 4525 | 0 | 30.6465 | 0
189 | 1900-07-08 | 4526 | 0 | 39.1922 | 0
189 | 1900-07-08 | 4527 | 0 | 52.2204 | 0
189 | 1900-07-08 | 4528 | 0 | 41.6226 | 0
189 | 1900-07-08 | 4529 | 0 | 28.2898 | 0
189 | 1900-07-08 | 4530 | 0 | 28.7414 | 0
189 | 1900-07-08 | 4531 | 0 | 41.2451 | 0
189 | 1900-07-08 | 4532 | 0 | 19.4321 | 0
189 | 1900-07-08 | 4533 | 0 | 30.7558 | 0
189 | 1900-07-08 | 4534 | 0 | 29.9711 | 0
189 | 1900-07-08 | 4535 | 0 | 27.6325 | 0
189 | 1900-07-08 | 4536 | 0 | 17.7274 | 0
190 | 1900-07-09 | 4537 | 0 | 30.1682 | 0
190 | 1900-07-09 | 4538 | 0 | 29.7873 | 0
190 | 1900-07-09 | 4539 | 0 | 32.9086 | 0
190 | 1900-07-09 | 4540 | 0 | 39.3664 | 0
190 | 1900-07-09 | 4541 | 0 | 72.0686 | 0
190 | 1900-07-09 | 4542 | 0 | 107.4766 | 0
190 | 1900-07-09 | 4543 | 0 | 109.3008 | 0
190 | 1900-07-09 | 4544 | 0 | 97.6076 | 0
190 | 1900-07-09 | 4545 | 0 | 107.5758 | 0
190 | 1900-07-09 | 4546 | 0 | 52.4713 | 0
190 | 1900-07-09 | 4547 | 0 | 53.9239 | 0
190 | 1900-07-09 | 4548 | 0 | 68.7576 | 0
190 | 1900-07-09 | 4549 | 0 | 134.9745 | 0
190 | 1900-07-09 | 4550 | 0 | 108.2673 | 0
190 | 1900-07-09 | 4551 | 0 | 69.3164 | 0
190 | 1900-07-09 | 4552 | 0 | 45.4016 | 0
190 | 1900-07-09 | 4553 | 0 | 33.5779 | 0
190 | 1900-07-09 | 4554 | 0 | 37.5818 | 0
190 | 1900-07-09 | 4555 | 0 | 38.5128 | 0
190 | 1900-07-09 | 4556 | 0 | 25.3026 | 0
190 | 1900-07-09 | 4557 | 0 | 34.1072 | 0
190 | 1900-07-09 | 4558 | 0 | 30.0028 | 0
190 | 1900-07-09 | 4559 | 0 | 29.3333 | 0
190 | 1900-07-09 | 4560 | 0 | 31.6635 | 0
191 | 1900-07-10 | 4561 | 0 | 32.1413 | 0
191 | 1900-07-10 | 4562 | 0 | 26.1927 | 0
191 | 1900-07-10 | 4563 | 0 | 27.1904 | 0
191 | 1900-07-10 | 4564 | 0 | 34.5111 | 0
191 | 1900-07-10 | 4565 | 0 | 20.2027 | 0
191 | 1900-07-10 | 4566 | 0 | 35.7824 | 0
191 | 1900-07-10 | 4567 | 0 | 88.9258 | 0
191 | 1900-07-10 | 4568 | 0 | 137.6358 | 0
191 | 1900-07-10 | 4569 | 0 | 112.7913 | 0
191 | 1900-07-10 | 4570 | 0 | 117.0384 | 0
191 | 1900-07-10 | 4571 | 0 | 81.3988 | 0
191 | 1900-07-10 | 4572 | 0 | 29.9563 | 0
191 | 1900-07-10 | 4573 | 0 | 53.6394 | 0
191 | 1900-07-10 | 4574 | 0 | 101.8857 | 0
191 | 1900-07-10 | 4575 | 0 | 88.8038 | 0
191 | 1900-07-10 | 4576 | 0 | 127.9213 | 0
191 | 1900-07-10 | 4577 | 0 | 124.0835 | 0
191 | 1900-07-10 | 4578 | 0 | 99.4743 | 0
191 | 1900-07-10 | 4579 | 0 | 59.4546 | 0
191 | 1900-07-10 | 4580 | 0 | 68.0961 | 0
191 | 1900-07-10 | 4581 | 0 | 45.1754 | 0
191 | 1900-07-10 | 4582 | 0 | 23.0285 | 0
191 | 1900-07-10 | 4583 | 0 | 32.5432 | 0
191 | 1900-07-10 | 4584 | 0 | 28.8415 | 0
192 | 1900-07-11 | 4585 | 0 | 27.5319 | 0
192 | 1900-07-11 | 4586 | 0 | 56.3379 | 0
192 | 1900-07-11 | 4587 | 0 | 98.7068 | 0
192 | 1900-07-11 | 4588 | 0 | 65.7266 | 0
192 | 1900-07-11 | 4589 | 0 | 75.9412 | 0
192 | 1900-07-11 | 4590 | 0 | 298.384 | 0
192 | 1900-07-11 | 4591 | 0 | 95.9756 | 0
192 | 1900-07-11 | 4592 | 0 | 117.5047 | 0
192 | 1900-07-11 | 4593 | 0 | 139.1344 | 0
192 | 1900-07-11 | 4594 | 0 | 141.2422 | 0
192 | 1900-07-11 | 4595 | 0 | 147.6109 | 0
192 | 1900-07-11 | 4596 | 0 | 144.0632 | 0
192 | 1900-07-11 | 4597 | 0 | 155.2031 | 0
192 | 1900-07-11 | 4598 | 0 | 133.9536 | 0
192 | 1900-07-11 | 4599 | 0 | 124.8341 | 0
192 | 1900-07-11 | 4600 | 0 | 119.0809 | 0
192 | 1900-07-11 | 4601 | 0 | 88.434 | 0
192 | 1900-07-11 | 4602 | 0 | 35.2434 | 0
192 | 1900-07-11 | 4603 | 0 | 45.6301 | 0
192 | 1900-07-11 | 4604 | 0 | 36.3913 | 0
192 | 1900-07-11 | 4605 | 0 | 25.0119 | 0
192 | 1900-07-11 | 4606 | 0 | 43.5779 | 0
192 | 1900-07-11 | 4607 | 0 | 88.8531 | 0
192 | 1900-07-11 | 4608 | 0 | 112.9503 | 0
193 | 1900-07-12 | 4609 | 0 | 77.301 | 0
193 | 1900-07-12 | 4610 | 0 | 29.7836 | 0
193 | 1900-07-12 | 4611 | 0 | 26.3371 | 0
193 | 1900-07-12 | 4612 | 0 | 26.8626 | 0
193 | 1900-07-12 | 4613 | 0 | 24.9825 | 0
193 | 1900-07-12 | 4614 | 0 | 31.9997 | 0
193 | 1900-07-12 | 4615 | 0 | 40.5214 | 0
193 | 1900-07-12 | 4616 | 0 | 97.9661 | 0
193 | 1900-07-12 | 4617 | 0 | 112.7 | 0
193 | 1900-07-12 | 4618 | 0 | 137.4566 | 0
193 | 1900-07-12 | 4619 | 0 | 109.912 | 0
193 | 1900-07-12 | 4620 | 0 | 141.8461 | 0
193 | 1900-07-12 | 4621 | 0 | 98.5609 | 0
193 | 1900-07-12 | 4622 | 0 | 63.9783 | 0
193 | 1900-07-12 | 4623 | 0 | 62.8511 | 0
193 | 1900-07-12 | 4624 | 0 | 305.3764 | 0
193 | 1900-07-12 | 4625 | 0 | 108.1332 | 0
193 | 1900-07-12 | 4626 | 0 | 107.3214 | 0
193 | 1900-07-12 | 4627 | 0 | 84.8813 | 0
193 | 1900-07-12 | 4628 | 0 | 25.5788 | 0
193 | 1900-07-12 | 4629 | 0 | 17.7226 | 0
193 | 1900-07-12 | 4630 | 0 | 51.7735 | 0
193 | 1900-07-12 | 4631 | 0 | 75.4528 | 0
193 | 1900-07-12 | 4632 | 0 | 44.1592 | 0
194 | 1900-07-13 | 4633 | 0 | 34.3692 | 0
194 | 1900-07-13 | 4634 | 0 | 36.1708 | 0
194 | 1900-07-13 | 4635 | 0 | 27.7854 | 0
194 | 1900-07-13 | 4636 | 0 | 28.2 | 0
194 | 1900-07-13 | 4637 | 0 | 18.8793 | 0
194 | 1900-07-13 | 4638 | 0 | 24.5264 | 0
194 | 1900-07-13 | 4639 | 0 | 24.0674 | 0
194 | 1900-07-13 | 4640 | 0 | 44.1882 | 0
194 | 1900-07-13 | 4641 | 0 | 32.5513 | 0
194 | 1900-07-13 | 4642 | 0 | 50.7906 | 0
194 | 1900-07-13 | 4643 | 0 | 91.0388 | 0
194 | 1900-07-13 | 4644 | 0 | 94.652 | 0
194 | 1900-07-13 | 4645 | 0 | 30.0209 | 0
194 | 1900-07-13 | 4646 | 0 | 46.7304 | 0
194 | 1900-07-13 | 4647 | 0 | 38.4104 | 0
194 | 1900-07-13 | 4648 | 0 | 29.7366 | 0
194 | 1900-07-13 | 4649 | 0 | 48.1429 | 0
194 | 1900-07-13 | 4650 | 0 | 39.0719 | 0
194 | 1900-07-13 | 4651 | 0 | 35.9584 | 0
194 | 1900-07-13 | 4652 | 0 | 33.727 | 0
194 | 1900-07-13 | 4653 | 0 | 57.141 | 0
194 | 1900-07-13 | 4654 | 0 | 101.663 | 0
194 | 1900-07-13 | 4655 | 0 | 62.033 | 0
194 | 1900-07-13 | 4656 | 0 | 26.1913 | 0
195 | 1900-07-14 | 4657 | 0 | 28.524 | 0
195 | 1900-07-14 | 4658 | 0 | 18.9235 | 0
195 | 1900-07-14 | 4659 | 0 | 228.5838 | 0
195 | 1900-07-14 | 4660 | 0 | 28.1392 | 0
195 | 1900-07-14 | 4661 | 0 | 34.4218 | 0
195 | 1900-07-14 | 4662 | 0 | 70.7324 | 0
195 | 1900-07-14 | 4663 | 0 | 76.4194 | 0
195 | 1900-07-14 | 4664 | 0 | 56.0542 | 0
195 | 1900-07-14 | 4665 | 0 | 37.7691 | 0
195 | 1900-07-14 | 4666 | 0 | 46.6953 | 0
195 | 1900-07-14 | 4667 | 0 | 42.1937 | 0
195 | 1900-07-14 | 4668 | 0 | 48.6637 | 0
195 | 1900-07-14 | 4669 | 0 | 43.5085 | 0
195 | 1900-07-14 | 4670 | 0 | 45.4013 | 0
195 | 1900-07-14 | 4671 | 0 | 45.274 | 0
195 | 1900-07-14 | 4672 | 0 | 37.6363 | 0
195 | 1900-07-14 | 4673 | 0 | 35.8243 | 0
195 | 1900-07-14 | 4674 | 0 | 42.4339 | 0
195 | 1900-07-14 | 4675 | 0 | 42.8421 | 0
195 | 1900-07-14 | 4676 | 0 | 23.8915 | 0
195 | 1900-07-14 | 4677 | 0 | 25.3396 | 0
195 | 1900-07-14 | 4678 | 0 | 14.1065 | 0
195 | 1900-07-14 | 4679 | 0 | 22.1088 | 0
195 | 1900-07-14 | 4680 | 0 | 25.1893 | 0
196 | 1900-07-15 | 4681 | 0 | 22.3337 | 0
196 | 1900-07-15 | 4682 | 0 | 29.5244 | 0
196 | 1900-07-15 | 4683 | 0 | 27.1882 | 0
196 | 1900-07-15 | 4684 | 0 | 29.2559 | 0
196 | 1900-07-15 | 4685 | 0 | 23.0164 | 0
196 | 1900-07-15 | 4686 | 0 | 30.5812 | 0
196 | 1900-07-15 | 4687 | 0 | 29.0708 | 0
196 | 1900-07-15 | 4688 | 0 | 44.6428 | 0
196 | 1900-07-15 | 4689 | 0 | 37.1644 | 0
196 | 1900-07-15 | 4690 | 0 | 36.9607 | 0
196 | 1900-07-15 | 4691 | 0 | 37.7968 | 0
196 | 1900-07-15 | 4692 | 0 | 39.9941 | 0
196 | 1900-07-15 | 4693 | 0 | 42.9975 | 0
196 | 1900-07-15 | 4694 | 0 | 77.8782 | 0
196 | 1900-07-15 | 4695 | 0 | 108.7024 | 0
196 | 1900-07-15 | 4696 | 0 | 78.5453 | 0
196 | 1900-07-15 | 4697 | 0 | 53.5231 | 0
196 | 1900-07-15 | 4698 | 0 | 34.5548 | 0
196 | 1900-07-15 | 4699 | 0 | 55.8292 | 0
196 | 1900-07-15 | 4700 | 0 | 28.8598 | 0
196 | 1900-07-15 | 4701 | 0 | 26.8624 | 0
196 | 1900-07-15 | 4702 | 0 | 30.7093 | 0
196 | 1900-07-15 | 4703 | 0 | 26.0919 | 0
196 | 1900-07-15 | 4704 | 0 | 15.6266 | 0
197 | 1900-07-16 | 4705 | 0 | 22.8844 | 0
197 | 1900-07-16 | 4706 | 0 | 23.4858 | 0
197 | 1900-07-16 | 4707 | 0 | 29.9283 | 0
197 | 1900-07-16 | 4708 | 0 | 35.362 | 0
197 | 1900-07-16 | 4709 | 0 | 44.7792 | 0
197 | 1900-07-16 | 4710 | 0 | 101.2738 | 0
197 | 1900-07-16 | 4711 | 0 | 110.9519 | 0
197 | 1900-07-16 | 4712 | 0 | 106.3658 | 0
197 | 1900-07-16 | 4713 | 0 | 88.3456 | 0
197 | 1900-07-16 | 4714 | 0 | 71.8736 | 0
197 | 1900-07-16 | 4715 | 0 | 118.4989 | 0
197 | 1900-07-16 | 4716 | 0 | 117.4387 | 0
197 | 1900-07-16 | 4717 | 0 | 68.7479 | 0
197 | 1900-07-16 | 4718 | 0 | 47.6313 | 0
197 | 1900-07-16 | 4719 | 0 | 53.2358 | 0
197 | 1900-07-16 | 4720 | 0 | 43.3847 | 0
197 | 1900-07-16 | 4721 | 0 | 33.5209 | 0
197 | 1900-07-16 | 4722 | 0 | 49.4846 | 0
197 | 1900-07-16 | 4723 | 0 | 35.7671 | 0
197 | 1900-07-16 | 4724 | 0 | 30.4011 | 0
197 | 1900-07-16 | 4725 | 0 | 29.6932 | 0
197 | 1900-07-16 | 4726 | 0 | 18.8458 | 0
197 | 1900-07-16 | 4727 | 0 | 34.9186 | 0
197 | 1900-07-16 | 4728 | 0 | 428.9361 | 0
198 | 1900-07-17 | 4729 | 0 | 27.0097 | 0
198 | 1900-07-17 | 4730 | 0 | 22.648 | 0
198 | 1900-07-17 | 4731 | 0 | 28.6753 | 0
198 | 1900-07-17 | 4732 | 0 | 33.1305 | 0
198 | 1900-07-17 | 4733 | 0 | 39.8033 | 0
198 | 1900-07-17 | 4734 | 0 | 86.2308 | 0
198 | 1900-07-17 | 4735 | 0 | 78.7351 | 0
198 | 1900-07-17 | 4736 | 0 | 67.134 | 0
198 | 1900-07-17 | 4737 | 0 | 61.7501 | 0
198 | 1900-07-17 | 4738 | 0 | 72.7892 | 0
198 | 1900-07-17 | 4739 | 0 | 108.5776 | 0
198 | 1900-07-17 | 4740 | 0 | 117.4841 | 0
198 | 1900-07-17 | 4741 | 0 | 100.5406 | 0
198 | 1900-07-17 | 4742 | 0 | 28.0363 | 0
198 | 1900-07-17 | 4743 | 0 | 49.7693 | 0
198 | 1900-07-17 | 4744 | 0 | 45.1252 | 0
198 | 1900-07-17 | 4745 | 0 | 30.9808 | 0
198 | 1900-07-17 | 4746 | 0 | 44.7207 | 0
198 | 1900-07-17 | 4747 | 0 | 37.3323 | 0
198 | 1900-07-17 | 4748 | 0 | 25.6313 | 0
198 | 1900-07-17 | 4749 | 0 | 30.8721 | 0
198 | 1900-07-17 | 4750 | 0 | 27.3589 | 0
198 | 1900-07-17 | 4751 | 0 | 30.8983 | 0
198 | 1900-07-17 | 4752 | 0 | 22.3561 | 0
199 | 1900-07-18 | 4753 | 0 | 29.8457 | 0
199 | 1900-07-18 | 4754 | 0 | 30.9315 | 0
199 | 1900-07-18 | 4755 | 0 | 30.8045 | 0
199 | 1900-07-18 | 4756 | 0 | 31.144 | 0
199 | 1900-07-18 | 4757 | 0 | 85.1475 | 0
199 | 1900-07-18 | 4758 | 0 | 101.9821 | 0
199 | 1900-07-18 | 4759 | 0 | 85.4481 | 0
199 | 1900-07-18 | 4760 | 0 | 79.2032 | 0
199 | 1900-07-18 | 4761 | 0 | 96.8037 | 0
199 | 1900-07-18 | 4762 | 0 | 73.3503 | 0
199 | 1900-07-18 | 4763 | 0 | 104.3608 | 0
199 | 1900-07-18 | 4764 | 0 | 102.8932 | 0
199 | 1900-07-18 | 4765 | 0 | 98.2304 | 0
199 | 1900-07-18 | 4766 | 0 | 64.7975 | 0
199 | 1900-07-18 | 4767 | 0 | 91.6164 | 0
199 | 1900-07-18 | 4768 | 0 | 89.4052 | 0
199 | 1900-07-18 | 4769 | 0 | 102.8333 | 0
199 | 1900-07-18 | 4770 | 0 | 110.1777 | 0
199 | 1900-07-18 | 4771 | 0 | 69.541 | 0
199 | 1900-07-18 | 4772 | 0 | 53.597 | 0
199 | 1900-07-18 | 4773 | 0 | 111.3582 | 0
199 | 1900-07-18 | 4774 | 0 | 92.3942 | 0
199 | 1900-07-18 | 4775 | 0 | 27.3002 | 0
199 | 1900-07-18 | 4776 | 0 | 31.5567 | 0
200 | 1900-07-19 | 4777 | 0 | 25.0786 | 0
200 | 1900-07-19 | 4778 | 0 | 32.2415 | 0
200 | 1900-07-19 | 4779 | 0 | 31.8238 | 0
200 | 1900-07-19 | 4780 | 0 | 41.7071 | 0
200 | 1900-07-19 | 4781 | 0 | 67.3668 | 0
200 | 1900-07-19 | 4782 | 0 | 68.4197 | 0
200 | 1900-07-19 | 4783 | 0 | 74.0152 | 0
200 | 1900-07-19 | 4784 | 0 | 110.708 | 0
200 | 1900-07-19 | 4785 | 0 | 100.3959 | 0
200 | 1900-07-19 | 4786 | 0 | 95.492 | 0
200 | 1900-07-19 | 4787 | 0 | 113.5528 | 0
200 | 1900-07-19 | 4788 | 0 | 107.1982 | 0
200 | 1900-07-19 | 4789 | 0 | 106.9798 | 0
200 | 1900-07-19 | 4790 | 0 | 110.1953 | 0
200 | 1900-07-19 | 4791 | 0 | 99.7645 | 0
200 | 1900-07-19 | 4792 | 0 | 87.2373 | 0
200 | 1900-07-19 | 4793 | 0 | 63.1233 | 0
200 | 1900-07-19 | 4794 | 0 | 67.0506 | 0
200 | 1900-07-19 | 4795 | 0 | 25.3646 | 0
200 | 1900-07-19 | 4796 | 0 | 35.8571 | 0
200 | 1900-07-19 | 4797 | 0 | 224.3932 | 0
200 | 1900-07-19 | 4798 | 0 | 19.4153 | 0
200 | 1900-07-19 | 4799 | 0 | 19.3406 | 0
200 | 1900-07-19 | 4800 | 0 | 31.01 | 0
201 | 1900-07-20 | 4801 | 0 | 26.294 | 0
201 | 1900-07-20 | 4802 | 0 | 37.2776 | 0
201 | 1900-07-20 | 4803 | 0 | 57.3606 | 0
201 | 1900-07-20 | 4804 | 0 | 89.2159 | 0
201 | 1900-07-20 | 4805 | 0 | 100.1762 | 0
201 | 1900-07-20 | 4806 | 0 | 76.3464 | 0
201 | 1900-07-20 | 4807 | 0 | 81.6527 | 0
201 | 1900-07-20 | 4808 | 0 | 102.8503 | 0
201 | 1900-07-20 | 4809 | 0 | 102.998 | 0
201 | 1900-07-20 | 4810 | 0 | 115.1271 | 0
201 | 1900-07-20 | 4811 | 0 | 83.413 | 0
201 | 1900-07-20 | 4812 | 0 | 83.2631 | 0
201 | 1900-07-20 | 4813 | 0 | 81.6883 | 0
201 | 1900-07-20 | 4814 | 0 | 50.6079 | 0
201 | 1900-07-20 | 4815 | 0 | 53.5929 | 0
201 | 1900-07-20 | 4816 | 0 | 43.1865 | 0
201 | 1900-07-20 | 4817 | 0 | 35.9751 | 0
201 | 1900-07-20 | 4818 | 0 | 42.507 | 0
201 | 1900-07-20 | 4819 | 0 | 39.8861 | 0
201 | 1900-07-20 | 4820 | 0 | 28.4333 | 0
201 | 1900-07-20 | 4821 | 0 | 26.8766 | 0
201 | 1900-07-20 | 4822 | 0 | 16.9483 | 0
201 | 1900-07-20 | 4823 | 0 | 23.1711 | 0
201 | 1900-07-20 | 4824 | 0 | 28.9867 | 0
202 | 1900-07-21 | 4825 | 0 | 31.8408 | 0
202 | 1900-07-21 | 4826 | 0 | 25.8257 | 0
202 | 1900-07-21 | 4827 | 0 | 229.3561 | 0
202 | 1900-07-21 | 4828 | 0 | 62.3281 | 0
202 | 1900-07-21 | 4829 | 0 | 82.0357 | 0
202 | 1900-07-21 | 4830 | 0 | 84.8652 | 0
202 | 1900-07-21 | 4831 | 0 | 83.0369 | 0
202 | 1900-07-21 | 4832 | 0 | 92.3189 | 0
202 | 1900-07-21 | 4833 | 0 | 90.2966 | 0
202 | 1900-07-21 | 4834 | 0 | 58.0914 | 0
202 | 1900-07-21 | 4835 | 0 | 62.5398 | 0
202 | 1900-07-21 | 4836 | 0 | 82.3252 | 0
202 | 1900-07-21 | 4837 | 0 | 47.2822 | 0
202 | 1900-07-21 | 4838 | 0 | 31.3977 | 0
202 | 1900-07-21 | 4839 | 0 | 48.8165 | 0
202 | 1900-07-21 | 4840 | 0 | 44.9683 | 0
202 | 1900-07-21 | 4841 | 0 | 40.6488 | 0
202 | 1900-07-21 | 4842 | 0 | 41.1596 | 0
202 | 1900-07-21 | 4843 | 0 | 49.9598 | 0
202 | 1900-07-21 | 4844 | 0 | 23.7777 | 0
202 | 1900-07-21 | 4845 | 0 | 33.9495 | 0
202 | 1900-07-21 | 4846 | 0 | 27.8331 | 0
202 | 1900-07-21 | 4847 | 0 | 32.5373 | 0
202 | 1900-07-21 | 4848 | 0 | 23.3942 | 0
203 | 1900-07-22 | 4849 | 0 | 27.294 | 0
203 | 1900-07-22 | 4850 | 0 | 28.8432 | 0
203 | 1900-07-22 | 4851 | 0 | 19.4964 | 0
203 | 1900-07-22 | 4852 | 0 | 28.9616 | 0
203 | 1900-07-22 | 4853 | 0 | 35.5941 | 0
203 | 1900-07-22 | 4854 | 0 | 79.4122 | 0
203 | 1900-07-22 | 4855 | 0 | 83.1468 | 0
203 | 1900-07-22 | 4856 | 0 | 99.5065 | 0
203 | 1900-07-22 | 4857 | 0 | 99.4791 | 0
203 | 1900-07-22 | 4858 | 0 | 60.8565 | 0
203 | 1900-07-22 | 4859 | 0 | 45.8911 | 0
203 | 1900-07-22 | 4860 | 0 | 37.9622 | 0
203 | 1900-07-22 | 4861 | 0 | 58.0062 | 0
203 | 1900-07-22 | 4862 | 0 | 34.0994 | 0
203 | 1900-07-22 | 4863 | 0 | 46.7104 | 0
203 | 1900-07-22 | 4864 | 0 | 53.15 | 0
203 | 1900-07-22 | 4865 | 0 | 243.7475 | 0
203 | 1900-07-22 | 4866 | 0 | 41.8712 | 0
203 | 1900-07-22 | 4867 | 0 | 45.7077 | 0
203 | 1900-07-22 | 4868 | 0 | 22.6042 | 0
203 | 1900-07-22 | 4869 | 0 | 24.1959 | 0
203 | 1900-07-22 | 4870 | 0 | 21.6397 | 0
203 | 1900-07-22 | 4871 | 0 | 25.5077 | 0
203 | 1900-07-22 | 4872 | 0 | 30.4587 | 0
204 | 1900-07-23 | 4873 | 0 | 24.815 | 0
204 | 1900-07-23 | 4874 | 0 | 29.8956 | 0
204 | 1900-07-23 | 4875 | 0 | 32.7859 | 0
204 | 1900-07-23 | 4876 | 0 | 27.2061 | 0
204 | 1900-07-23 | 4877 | 0 | 54.781 | 0
204 | 1900-07-23 | 4878 | 0 | 102.6676 | 0
204 | 1900-07-23 | 4879 | 0 | 62.7749 | 0
204 | 1900-07-23 | 4880 | 0 | 114.3933 | 0
204 | 1900-07-23 | 4881 | 0 | 88.9271 | 0
204 | 1900-07-23 | 4882 | 0 | 91.0109 | 0
204 | 1900-07-23 | 4883 | 0 | 85.5736 | 0
204 | 1900-07-23 | 4884 | 0 | 119.3366 | 0
204 | 1900-07-23 | 4885 | 0 | 102.5647 | 0
204 | 1900-07-23 | 4886 | 0 | 42.696 | 0
204 | 1900-07-23 | 4887 | 0 | 42.3825 | 0
204 | 1900-07-23 | 4888 | 0 | 47.7306 | 0
204 | 1900-07-23 | 4889 | 0 | 54.6051 | 0
204 | 1900-07-23 | 4890 | 0 | 40.5992 | 0
204 | 1900-07-23 | 4891 | 0 | 43.1382 | 0
204 | 1900-07-23 | 4892 | 0 | 33.8512 | 0
204 | 1900-07-23 | 4893 | 0 | 25.8851 | 0
204 | 1900-07-23 | 4894 | 0 | 29.3082 | 0
204 | 1900-07-23 | 4895 | 0 | 26.3795 | 0
204 | 1900-07-23 | 4896 | 0 | 26.5829 | 0
205 | 1900-07-24 | 4897 | 0 | 23.013 | 0
205 | 1900-07-24 | 4898 | 0 | 17.1591 | 0
205 | 1900-07-24 | 4899 | 0 | 22.9771 | 0
205 | 1900-07-24 | 4900 | 0 | 31.4537 | 0
205 | 1900-07-24 | 4901 | 0 | 51.1985 | 0
205 | 1900-07-24 | 4902 | 0 | 89.6666 | 0
205 | 1900-07-24 | 4903 | 0 | 82.858 | 0
205 | 1900-07-24 | 4904 | 0 | 85.1761 | 0
205 | 1900-07-24 | 4905 | 0 | 85.1497 | 0
205 | 1900-07-24 | 4906 | 0 | 42.0432 | 0
205 | 1900-07-24 | 4907 | 0 | 39.8097 | 0
205 | 1900-07-24 | 4908 | 0 | 85.9825 | 0
205 | 1900-07-24 | 4909 | 0 | 93.9568 | 0
205 | 1900-07-24 | 4910 | 0 | 48.0181 | 0
205 | 1900-07-24 | 4911 | 0 | 46.7452 | 0
205 | 1900-07-24 | 4912 | 0 | 38.6987 | 0
205 | 1900-07-24 | 4913 | 0 | 44.2024 | 0
205 | 1900-07-24 | 4914 | 0 | 48.2539 | 0
205 | 1900-07-24 | 4915 | 0 | 52.8212 | 0
205 | 1900-07-24 | 4916 | 0 | 35.7832 | 0
205 | 1900-07-24 | 4917 | 0 | 28.364 | 0
205 | 1900-07-24 | 4918 | 0 | 25.3357 | 0
205 | 1900-07-24 | 4919 | 0 | 24.1539 | 0
205 | 1900-07-24 | 4920 | 0 | 30.1692 | 0
206 | 1900-07-25 | 4921 | 0 | 27.2978 | 0
206 | 1900-07-25 | 4922 | 0 | 30.4625 | 0
206 | 1900-07-25 | 4923 | 0 | 25.9078 | 0
206 | 1900-07-25 | 4924 | 0 | 42.0967 | 0
206 | 1900-07-25 | 4925 | 0 | 65.5835 | 0
206 | 1900-07-25 | 4926 | 0 | 96.8887 | 0
206 | 1900-07-25 | 4927 | 0 | 98.2961 | 0
206 | 1900-07-25 | 4928 | 0 | 116.714 | 0
206 | 1900-07-25 | 4929 | 0 | 258.8943 | 0
206 | 1900-07-25 | 4930 | 0 | 62.5735 | 0
206 | 1900-07-25 | 4931 | 0 | 58.2411 | 0
206 | 1900-07-25 | 4932 | 0 | 57.0397 | 0
206 | 1900-07-25 | 4933 | 0 | 120.7833 | 0
206 | 1900-07-25 | 4934 | 0 | 306.2177 | 0
206 | 1900-07-25 | 4935 | 0 | 71.519 | 0
206 | 1900-07-25 | 4936 | 0 | 47.9091 | 0
206 | 1900-07-25 | 4937 | 0 | 84.7438 | 0
206 | 1900-07-25 | 4938 | 0 | 101.1141 | 0
206 | 1900-07-25 | 4939 | 0 | 89.4325 | 0
206 | 1900-07-25 | 4940 | 0 | 27.721 | 0
206 | 1900-07-25 | 4941 | 0 | 24.2278 | 0
206 | 1900-07-25 | 4942 | 0 | 50.4559 | 0
206 | 1900-07-25 | 4943 | 0 | 97.6571 | 0
206 | 1900-07-25 | 4944 | 0 | 80.1164 | 0
207 | 1900-07-26 | 4945 | 0 | 24.5452 | 0
207 | 1900-07-26 | 4946 | 0 | 27.3269 | 0
207 | 1900-07-26 | 4947 | 0 | 25.7497 | 0
207 | 1900-07-26 | 4948 | 0 | 32.5963 | 0
207 | 1900-07-26 | 4949 | 0 | 70.889 | 0
207 | 1900-07-26 | 4950 | 0 | 83.4514 | 0
207 | 1900-07-26 | 4951 | 0 | 82.7846 | 0
207 | 1900-07-26 | 4952 | 0 | 91.1847 | 0
207 | 1900-07-26 | 4953 | 0 | 98.2711 | 0
207 | 1900-07-26 | 4954 | 0 | 54.8629 | 0
207 | 1900-07-26 | 4955 | 0 | 52.1418 | 0
207 | 1900-07-26 | 4956 | 0 | 63.9515 | 0
207 | 1900-07-26 | 4957 | 0 | 113.0278 | 0
207 | 1900-07-26 | 4958 | 0 | 108.9094 | 0
207 | 1900-07-26 | 4959 | 0 | 98.622 | 0
207 | 1900-07-26 | 4960 | 0 | 108.4951 | 0
207 | 1900-07-26 | 4961 | 0 | 97.3034 | 0
207 | 1900-07-26 | 4962 | 0 | 65.8857 | 0
207 | 1900-07-26 | 4963 | 0 | 74.2521 | 0
207 | 1900-07-26 | 4964 | 0 | 48.6977 | 0
207 | 1900-07-26 | 4965 | 0 | 102.7552 | 0
207 | 1900-07-26 | 4966 | 0 | 103.8718 | 0
207 | 1900-07-26 | 4967 | 0 | 75.9681 | 0
207 | 1900-07-26 | 4968 | 0 | 20.1563 | 0
208 | 1900-07-27 | 4969 | 0 | 25.9077 | 0
208 | 1900-07-27 | 4970 | 0 | 28.3661 | 0
208 | 1900-07-27 | 4971 | 0 | 26.8544 | 0
208 | 1900-07-27 | 4972 | 0 | 25.4327 | 0
208 | 1900-07-27 | 4973 | 0 | 19.4628 | 0
208 | 1900-07-27 | 4974 | 0 | 28.8052 | 0
208 | 1900-07-27 | 4975 | 0 | 27.2613 | 0
208 | 1900-07-27 | 4976 | 0 | 49.8782 | 0
208 | 1900-07-27 | 4977 | 0 | 39.0802 | 0
208 | 1900-07-27 | 4978 | 0 | 40.5015 | 0
208 | 1900-07-27 | 4979 | 0 | 48.2081 | 0
208 | 1900-07-27 | 4980 | 0 | 43.9809 | 0
208 | 1900-07-27 | 4981 | 0 | 43.5318 | 0
208 | 1900-07-27 | 4982 | 0 | 48.5174 | 0
208 | 1900-07-27 | 4983 | 0 | 38.1632 | 0
208 | 1900-07-27 | 4984 | 0 | 36.5032 | 0
208 | 1900-07-27 | 4985 | 0 | 37.2292 | 0
208 | 1900-07-27 | 4986 | 0 | 38.6898 | 0
208 | 1900-07-27 | 4987 | 0 | 33.4989 | 0
208 | 1900-07-27 | 4988 | 0 | 26.9608 | 0
208 | 1900-07-27 | 4989 | 0 | 33.1057 | 0
208 | 1900-07-27 | 4990 | 0 | 22.1474 | 0
208 | 1900-07-27 | 4991 | 0 | 23.9476 | 0
208 | 1900-07-27 | 4992 | 0 | 25.1323 | 0
209 | 1900-07-28 | 4993 | 0 | 27.2638 | 0
209 | 1900-07-28 | 4994 | 0 | 26.19 | 0
209 | 1900-07-28 | 4995 | 0 | 28.653 | 0
209 | 1900-07-28 | 4996 | 0 | 25.8555 | 0
209 | 1900-07-28 | 4997 | 0 | 25.7644 | 0
209 | 1900-07-28 | 4998 | 0 | 27.7528 | 0
209 | 1900-07-28 | 4999 | 0 | 19.2743 | 0
209 | 1900-07-28 | 5000 | 0 | 45.6649 | 0
209 | 1900-07-28 | 5001 | 0 | 35.6053 | 0
209 | 1900-07-28 | 5002 | 0 | 236.2795 | 0
209 | 1900-07-28 | 5003 | 0 | 54.5323 | 0
209 | 1900-07-28 | 5004 | 0 | 38.0388 | 0
209 | 1900-07-28 | 5005 | 0 | 39.3015 | 0
209 | 1900-07-28 | 5006 | 0 | 32.2624 | 0
209 | 1900-07-28 | 5007 | 0 | 42.8425 | 0
209 | 1900-07-28 | 5008 | 0 | 54.5239 | 0
209 | 1900-07-28 | 5009 | 0 | 42.8976 | 0
209 | 1900-07-28 | 5010 | 0 | 36.7592 | 0
209 | 1900-07-28 | 5011 | 0 | 36.7414 | 0
209 | 1900-07-28 | 5012 | 0 | 25.3542 | 0
209 | 1900-07-28 | 5013 | 0 | 28.909 | 0
209 | 1900-07-28 | 5014 | 0 | 19.7809 | 0
209 | 1900-07-28 | 5015 | 0 | 30.477 | 0
209 | 1900-07-28 | 5016 | 0 | 25.0535 | 0
210 | 1900-07-29 | 5017 | 0 | 30.3669 | 0
210 | 1900-07-29 | 5018 | 0 | 27.9131 | 0
210 | 1900-07-29 | 5019 | 0 | 22.1079 | 0
210 | 1900-07-29 | 5020 | 0 | 28.1709 | 0
210 | 1900-07-29 | 5021 | 0 | 24.4444 | 0
210 | 1900-07-29 | 5022 | 0 | 24.7995 | 0
210 | 1900-07-29 | 5023 | 0 | 20.6238 | 0
210 | 1900-07-29 | 5024 | 0 | 38.1814 | 0
210 | 1900-07-29 | 5025 | 0 | 39.2757 | 0
210 | 1900-07-29 | 5026 | 0 | 29.616 | 0
210 | 1900-07-29 | 5027 | 0 | 46.6746 | 0
210 | 1900-07-29 | 5028 | 0 | 46.0573 | 0
210 | 1900-07-29 | 5029 | 0 | 56.7193 | 0
210 | 1900-07-29 | 5030 | 0 | 42.3266 | 0
210 | 1900-07-29 | 5031 | 0 | 239.7204 | 0
210 | 1900-07-29 | 5032 | 0 | 41.3193 | 0
210 | 1900-07-29 | 5033 | 0 | 42.3041 | 0
210 | 1900-07-29 | 5034 | 0 | 44.824 | 0
210 | 1900-07-29 | 5035 | 0 | 41.195 | 0
210 | 1900-07-29 | 5036 | 0 | 29.3316 | 0
210 | 1900-07-29 | 5037 | 0 | 25.6329 | 0
210 | 1900-07-29 | 5038 | 0 | 29.5576 | 0
210 | 1900-07-29 | 5039 | 0 | 24.4122 | 0
210 | 1900-07-29 | 5040 | 0 | 26.2687 | 0
211 | 1900-07-30 | 5041 | 0 | 28.5064 | 0
211 | 1900-07-30 | 5042 | 0 | 27.763 | 0
211 | 1900-07-30 | 5043 | 0 | 27.7184 | 0
211 | 1900-07-30 | 5044 | 0 | 26.9217 | 0
211 | 1900-07-30 | 5045 | 0 | 31.0599 | 0
211 | 1900-07-30 | 5046 | 0 | 30.7109 | 0
211 | 1900-07-30 | 5047 | 0 | 24.3122 | 0
211 | 1900-07-30 | 5048 | 0 | 38.2802 | 0
211 | 1900-07-30 | 5049 | 0 | 46.2765 | 0
211 | 1900-07-30 | 5050 | 0 | 38.8107 | 0
211 | 1900-07-30 | 5051 | 0 | 47.0418 | 0
211 | 1900-07-30 | 5052 | 0 | 48.8106 | 0
211 | 1900-07-30 | 5053 | 0 | 36.1987 | 0
211 | 1900-07-30 | 5054 | 0 | 37.9538 | 0
211 | 1900-07-30 | 5055 | 0 | 44.3541 | 0
211 | 1900-07-30 | 5056 | 0 | 46.29 | 0
211 | 1900-07-30 | 5057 | 0 | 38.969 | 0
211 | 1900-07-30 | 5058 | 0 | 46.0209 | 0
211 | 1900-07-30 | 5059 | 0 | 31.4483 | 0
211 | 1900-07-30 | 5060 | 0 | 30.0142 | 0
211 | 1900-07-30 | 5061 | 0 | 33.3783 | 0
211 | 1900-07-30 | 5062 | 0 | 21.014 | 0
211 | 1900-07-30 | 5063 | 0 | 30.9178 | 0
211 | 1900-07-30 | 5064 | 0 | 26.4101 | 0
212 | 1900-07-31 | 5065 | 0 | 34.269 | 0
212 | 1900-07-31 | 5066 | 0 | 27.289 | 0
212 | 1900-07-31 | 5067 | 0 | 30.1052 | 0
212 | 1900-07-31 | 5068 | 0 | 26.6414 | 0
212 | 1900-07-31 | 5069 | 0 | 31.2288 | 0
212 | 1900-07-31 | 5070 | 0 | 26.7389 | 0
212 | 1900-07-31 | 5071 | 0 | 19.2402 | 0
212 | 1900-07-31 | 5072 | 0 | 38.0779 | 0
212 | 1900-07-31 | 5073 | 0 | 48.7011 | 0
212 | 1900-07-31 | 5074 | 0 | 233.0545 | 0
212 | 1900-07-31 | 5075 | 0 | 36.4041 | 0
212 | 1900-07-31 | 5076 | 0 | 42.3909 | 0
212 | 1900-07-31 | 5077 | 0 | 36.5327 | 0
212 | 1900-07-31 | 5078 | 0 | 38.7085 | 0
212 | 1900-07-31 | 5079 | 0 | 46.336 | 0
212 | 1900-07-31 | 5080 | 0 | 35.6809 | 0
212 | 1900-07-31 | 5081 | 0 | 29.7587 | 0
212 | 1900-07-31 | 5082 | 0 | 42.9473 | 0
212 | 1900-07-31 | 5083 | 0 | 33.9993 | 0
212 | 1900-07-31 | 5084 | 0 | 25.5542 | 0
212 | 1900-07-31 | 5085 | 0 | 21.8275 | 0
212 | 1900-07-31 | 5086 | 0 | 26.2348 | 0
212 | 1900-07-31 | 5087 | 0 | 22.8663 | 0
212 | 1900-07-31 | 5088 | 0 | 27.4933 | 0
213 | 1900-08-01 | 5089 | 0 | 3.309 | 0
213 | 1900-08-01 | 5090 | 0 | 4.407 | 0
213 | 1900-08-01 | 5091 | 0 | 4.1469 | 0
213 | 1900-08-01 | 5092 | 0 | 4.5681 | 0
213 | 1900-08-01 | 5093 | 0 | 3.5466 | 0
213 | 1900-08-01 | 5094 | 0 | 4.9782 | 0
213 | 1900-08-01 | 5095 | 0 | 4.17 | 0
213 | 1900-08-01 | 5096 | 0 | 14.3434 | 0
213 | 1900-08-01 | 5097 | 0 | 16.5934 | 0
213 | 1900-08-01 | 5098 | 0 | 18.7351 | 0
213 | 1900-08-01 | 5099 | 0 | 25.329 | 0
213 | 1900-08-01 | 5100 | 0 | 24.9714 | 0
213 | 1900-08-01 | 5101 | 0 | 19.8983 | 0
213 | 1900-08-01 | 5102 | 0 | 20.0535 | 0
213 | 1900-08-01 | 5103 | 0 | 18.3256 | 0
213 | 1900-08-01 | 5104 | 0 | 19.8183 | 0
213 | 1900-08-01 | 5105 | 0 | 21.6721 | 0
213 | 1900-08-01 | 5106 | 0 | 10.7999 | 0
213 | 1900-08-01 | 5107 | 0 | 25.9775 | 0
213 | 1900-08-01 | 5108 | 0 | 4.0538 | 0
213 | 1900-08-01 | 5109 | 0 | 3.3646 | 0
213 | 1900-08-01 | 5110 | 0 | 4.5363 | 0
213 | 1900-08-01 | 5111 | 0 | 4.7637 | 0
213 | 1900-08-01 | 5112 | 0 | 4.3999 | 0
214 | 1900-08-02 | 5113 | 0 | 5.4957 | 0
214 | 1900-08-02 | 5114 | 0 | 3.4441 | 0
214 | 1900-08-02 | 5115 | 0 | 5.6476 | 0
214 | 1900-08-02 | 5116 | 0 | 4.7705 | 0
214 | 1900-08-02 | 5117 | 0 | 4.3992 | 0
214 | 1900-08-02 | 5118 | 0 | 3.9498 | 0
214 | 1900-08-02 | 5119 | 0 | 5.4832 | 0
214 | 1900-08-02 | 5120 | 0 | 27.4499 | 0
214 | 1900-08-02 | 5121 | 0 | 18.9688 | 0
214 | 1900-08-02 | 5122 | 0 | 12.9742 | 0
214 | 1900-08-02 | 5123 | 0 | 19.8009 | 0
214 | 1900-08-02 | 5124 | 0 | 13.9426 | 0
214 | 1900-08-02 | 5125 | 0 | 15.0152 | 0
214 | 1900-08-02 | 5126 | 0 | 13.3333 | 0
214 | 1900-08-02 | 5127 | 0 | 14.8251 | 0
214 | 1900-08-02 | 5128 | 0 | 17.4553 | 0
214 | 1900-08-02 | 5129 | 0 | 25.0804 | 0
214 | 1900-08-02 | 5130 | 0 | 17.4461 | 0
214 | 1900-08-02 | 5131 | 0 | 16.2086 | 0
214 | 1900-08-02 | 5132 | 0 | 4.016 | 0
214 | 1900-08-02 | 5133 | 0 | 204.0217 | 0
214 | 1900-08-02 | 5134 | 0 | 3.7537 | 0
214 | 1900-08-02 | 5135 | 0 | 5.3119 | 0
214 | 1900-08-02 | 5136 | 0 | 4.7562 | 0
215 | 1900-08-03 | 5137 | 0 | 3.2435 | 0
215 | 1900-08-03 | 5138 | 0 | 3.3771 | 0
215 | 1900-08-03 | 5139 | 0 | 4.7375 | 0
215 | 1900-08-03 | 5140 | 0 | 3.4439 | 0
215 | 1900-08-03 | 5141 | 0 | 3.806 | 0
215 | 1900-08-03 | 5142 | 0 | 4.4213 | 0
215 | 1900-08-03 | 5143 | 0 | 4.4448 | 0
215 | 1900-08-03 | 5144 | 0 | 218.0889 | 0
215 | 1900-08-03 | 5145 | 0 | 14.5309 | 0
215 | 1900-08-03 | 5146 | 0 | 14.5786 | 0
215 | 1900-08-03 | 5147 | 0 | 6.0064 | 0
215 | 1900-08-03 | 5148 | 0 | 12.7786 | 0
215 | 1900-08-03 | 5149 | 0 | 21.191 | 0
215 | 1900-08-03 | 5150 | 0 | 17.2857 | 0
215 | 1900-08-03 | 5151 | 0 | 8.6019 | 0
215 | 1900-08-03 | 5152 | 0 | 20.3152 | 0
215 | 1900-08-03 | 5153 | 0 | 15.9747 | 0
215 | 1900-08-03 | 5154 | 0 | 29.3797 | 0
215 | 1900-08-03 | 5155 | 0 | 33.1624 | 0
215 | 1900-08-03 | 5156 | 0 | 4.442 | 0
215 | 1900-08-03 | 5157 | 0 | 4.0183 | 0
215 | 1900-08-03 | 5158 | 0 | 3.9473 | 0
215 | 1900-08-03 | 5159 | 0 | 3.8725 | 0
215 | 1900-08-03 | 5160 | 0 | 4.5483 | 0
216 | 1900-08-04 | 5161 | 0 | 3.2168 | 0
216 | 1900-08-04 | 5162 | 0 | 4.9938 | 0
216 | 1900-08-04 | 5163 | 0 | 4.2061 | 0
216 | 1900-08-04 | 5164 | 0 | 5.3555 | 0
216 | 1900-08-04 | 5165 | 0 | 4.5025 | 0
216 | 1900-08-04 | 5166 | 0 | 4.4113 | 0
216 | 1900-08-04 | 5167 | 0 | 4.2903 | 0
216 | 1900-08-04 | 5168 | 0 | 22.1918 | 0
216 | 1900-08-04 | 5169 | 0 | 19.9445 | 0
216 | 1900-08-04 | 5170 | 0 | 18.6125 | 0
216 | 1900-08-04 | 5171 | 0 | 22.4594 | 0
216 | 1900-08-04 | 5172 | 0 | 11.3081 | 0
216 | 1900-08-04 | 5173 | 0 | 16.1174 | 0
216 | 1900-08-04 | 5174 | 0 | 11.6679 | 0
216 | 1900-08-04 | 5175 | 0 | 28.4367 | 0
216 | 1900-08-04 | 5176 | 0 | 13.9482 | 0
216 | 1900-08-04 | 5177 | 0 | 25.0397 | 0
216 | 1900-08-04 | 5178 | 0 | 19.6351 | 0
216 | 1900-08-04 | 5179 | 0 | 22.1254 | 0
216 | 1900-08-04 | 5180 | 0 | 4.6044 | 0
216 | 1900-08-04 | 5181 | 0 | 4.6401 | 0
216 | 1900-08-04 | 5182 | 0 | 3.1952 | 0
216 | 1900-08-04 | 5183 | 0 | 4.9198 | 0
216 | 1900-08-04 | 5184 | 0 | 3.9217 | 0
217 | 1900-08-05 | 5185 | 0 | 4.0493 | 0
217 | 1900-08-05 | 5186 | 0 | 3.7332 | 0
217 | 1900-08-05 | 5187 | 0 | 4.5513 | 0
217 | 1900-08-05 | 5188 | 0 | 3.8037 | 0
217 | 1900-08-05 | 5189 | 0 | 3.8794 | 0
217 | 1900-08-05 | 5190 | 0 | 4.5495 | 0
217 | 1900-08-05 | 5191 | 0 | 4.8702 | 0
217 | 1900-08-05 | 5192 | 0 | 19.0176 | 0
217 | 1900-08-05 | 5193 | 0 | 21.4822 | 0
217 | 1900-08-05 | 5194 | 0 | 21.2653 | 0
217 | 1900-08-05 | 5195 | 0 | 25.7169 | 0
217 | 1900-08-05 | 5196 | 0 | 15.1652 | 0
217 | 1900-08-05 | 5197 | 0 | 16.4461 | 0
217 | 1900-08-05 | 5198 | 0 | 19.0024 | 0
217 | 1900-08-05 | 5199 | 0 | 16.1924 | 0
217 | 1900-08-05 | 5200 | 0 | 16.8477 | 0
217 | 1900-08-05 | 5201 | 0 | 13.0481 | 0
217 | 1900-08-05 | 5202 | 0 | 22.4012 | 0
217 | 1900-08-05 | 5203 | 0 | 15.5015 | 0
217 | 1900-08-05 | 5204 | 0 | 3.504 | 0
217 | 1900-08-05 | 5205 | 0 | 4.7134 | 0
217 | 1900-08-05 | 5206 | 0 | 4.6366 | 0
217 | 1900-08-05 | 5207 | 0 | 3.9079 | 0
217 | 1900-08-05 | 5208 | 0 | 3.2093 | 0
218 | 1900-08-06 | 5209 | 0 | 3.9984 | 0
218 | 1900-08-06 | 5210 | 0 | 4.3218 | 0
218 | 1900-08-06 | 5211 | 0 | 4.2901 | 0
218 | 1900-08-06 | 5212 | 0 | 3.964 | 0
218 | 1900-08-06 | 5213 | 0 | 3.7351 | 0
218 | 1900-08-06 | 5214 | 0 | 4.3585 | 0
218 | 1900-08-06 | 5215 | 0 | 203.7435 | 0
218 | 1900-08-06 | 5216 | 0 | 24.9281 | 0
218 | 1900-08-06 | 5217 | 0 | 15.514 | 0
218 | 1900-08-06 | 5218 | 0 | 32.5893 | 0
218 | 1900-08-06 | 5219 | 0 | 23.7978 | 0
218 | 1900-08-06 | 5220 | 0 | 17.8377 | 0
218 | 1900-08-06 | 5221 | 0 | 31.6828 | 0
218 | 1900-08-06 | 5222 | 0 | 44.0079 | 0
218 | 1900-08-06 | 5223 | 0 | 84.4255 | 0
218 | 1900-08-06 | 5224 | 0 | 74.0348 | 0
218 | 1900-08-06 | 5225 | 0 | 51.9969 | 0
218 | 1900-08-06 | 5226 | 0 | 16.7024 | 0
218 | 1900-08-06 | 5227 | 0 | 17.2881 | 0
218 | 1900-08-06 | 5228 | 0 | 5.2194 | 0
218 | 1900-08-06 | 5229 | 0 | 3.8651 | 0
218 | 1900-08-06 | 5230 | 0 | 4.3625 | 0
218 | 1900-08-06 | 5231 | 0 | 4.4168 | 0
218 | 1900-08-06 | 5232 | 0 | 3.8606 | 0
219 | 1900-08-07 | 5233 | 0 | 4.6657 | 0
219 | 1900-08-07 | 5234 | 0 | 205.3897 | 0
219 | 1900-08-07 | 5235 | 0 | 4.6973 | 0
219 | 1900-08-07 | 5236 | 0 | 5.4994 | 0
219 | 1900-08-07 | 5237 | 0 | 25.4455 | 0
219 | 1900-08-07 | 5238 | 0 | 82.1044 | 0
219 | 1900-08-07 | 5239 | 0 | 46.0302 | 0
219 | 1900-08-07 | 5240 | 0 | 42.772 | 0
219 | 1900-08-07 | 5241 | 0 | 44.3397 | 0
219 | 1900-08-07 | 5242 | 0 | 61.2105 | 0
219 | 1900-08-07 | 5243 | 0 | 72.8803 | 0
219 | 1900-08-07 | 5244 | 0 | 69.1216 | 0
219 | 1900-08-07 | 5245 | 0 | 73.9265 | 0
219 | 1900-08-07 | 5246 | 0 | 83.5278 | 0
219 | 1900-08-07 | 5247 | 0 | 86.0017 | 0
219 | 1900-08-07 | 5248 | 0 | 95.8563 | 0
219 | 1900-08-07 | 5249 | 0 | 97.7452 | 0
219 | 1900-08-07 | 5250 | 0 | 77.5624 | 0
219 | 1900-08-07 | 5251 | 0 | 80.4379 | 0
219 | 1900-08-07 | 5252 | 0 | 53.7259 | 0
219 | 1900-08-07 | 5253 | 0 | 39.0273 | 0
219 | 1900-08-07 | 5254 | 0 | 44.6835 | 0
219 | 1900-08-07 | 5255 | 0 | 36.9546 | 0
219 | 1900-08-07 | 5256 | 0 | 3.785 | 0
220 | 1900-08-08 | 5257 | 0 | 3.1618 | 0
220 | 1900-08-08 | 5258 | 0 | 11.6979 | 0
220 | 1900-08-08 | 5259 | 0 | 30.5781 | 0
220 | 1900-08-08 | 5260 | 0 | 23.7552 | 0
220 | 1900-08-08 | 5261 | 0 | 21.9329 | 0
220 | 1900-08-08 | 5262 | 0 | 55.9639 | 0
220 | 1900-08-08 | 5263 | 0 | 48.4496 | 0
220 | 1900-08-08 | 5264 | 0 | 57.6704 | 0
220 | 1900-08-08 | 5265 | 0 | 61.0342 | 0
220 | 1900-08-08 | 5266 | 0 | 65.789 | 0
220 | 1900-08-08 | 5267 | 0 | 38.6326 | 0
220 | 1900-08-08 | 5268 | 0 | 18.8248 | 0
220 | 1900-08-08 | 5269 | 0 | 16.5133 | 0
220 | 1900-08-08 | 5270 | 0 | 20.1378 | 0
220 | 1900-08-08 | 5271 | 0 | 19.7297 | 0
220 | 1900-08-08 | 5272 | 0 | 12.0523 | 0
220 | 1900-08-08 | 5273 | 0 | 22.5758 | 0
220 | 1900-08-08 | 5274 | 0 | 20.5507 | 0
220 | 1900-08-08 | 5275 | 0 | 26.5221 | 0
220 | 1900-08-08 | 5276 | 0 | 2.8824 | 0
220 | 1900-08-08 | 5277 | 0 | 3.5458 | 0
220 | 1900-08-08 | 5278 | 0 | 5.1589 | 0
220 | 1900-08-08 | 5279 | 0 | 3.3998 | 0
220 | 1900-08-08 | 5280 | 0 | 3.9845 | 0
221 | 1900-08-09 | 5281 | 0 | 5.3986 | 0
221 | 1900-08-09 | 5282 | 0 | 4.7574 | 0
221 | 1900-08-09 | 5283 | 0 | 4.3014 | 0
221 | 1900-08-09 | 5284 | 0 | 3.432 | 0
221 | 1900-08-09 | 5285 | 0 | 4.3552 | 0
221 | 1900-08-09 | 5286 | 0 | 204.0823 | 0
221 | 1900-08-09 | 5287 | 0 | 3.8266 | 0
221 | 1900-08-09 | 5288 | 0 | 20.2658 | 0
221 | 1900-08-09 | 5289 | 0 | 15.0616 | 0
221 | 1900-08-09 | 5290 | 0 | 31.4052 | 0
221 | 1900-08-09 | 5291 | 0 | 23.2553 | 0
221 | 1900-08-09 | 5292 | 0 | 18.9189 | 0
221 | 1900-08-09 | 5293 | 0 | 26.017 | 0
221 | 1900-08-09 | 5294 | 0 | 12.5113 | 0
221 | 1900-08-09 | 5295 | 0 | 19.3659 | 0
221 | 1900-08-09 | 5296 | 0 | 19.9207 | 0
221 | 1900-08-09 | 5297 | 0 | 12.4364 | 0
221 | 1900-08-09 | 5298 | 0 | 16.4857 | 0
221 | 1900-08-09 | 5299 | 0 | 14.9378 | 0
221 | 1900-08-09 | 5300 | 0 | 3.8404 | 0
221 | 1900-08-09 | 5301 | 0 | 4.0587 | 0
221 | 1900-08-09 | 5302 | 0 | 4.8724 | 0
221 | 1900-08-09 | 5303 | 0 | 3.1686 | 0
221 | 1900-08-09 | 5304 | 0 | 3.6423 | 0
222 | 1900-08-10 | 5305 | 0 | 4.821 | 0
222 | 1900-08-10 | 5306 | 0 | 2.8492 | 0
222 | 1900-08-10 | 5307 | 0 | 4.2589 | 0
222 | 1900-08-10 | 5308 | 0 | 3.5316 | 0
222 | 1900-08-10 | 5309 | 0 | 4.2727 | 0
222 | 1900-08-10 | 5310 | 0 | 4.6593 | 0
222 | 1900-08-10 | 5311 | 0 | 3.3748 | 0
222 | 1900-08-10 | 5312 | 0 | 11.6792 | 0
222 | 1900-08-10 | 5313 | 0 | 32.2322 | 0
222 | 1900-08-10 | 5314 | 0 | 74.2144 | 0
222 | 1900-08-10 | 5315 | 0 | 57.7523 | 0
222 | 1900-08-10 | 5316 | 0 | 90.8093 | 0
222 | 1900-08-10 | 5317 | 0 | 95.2641 | 0
222 | 1900-08-10 | 5318 | 0 | 79.8396 | 0
222 | 1900-08-10 | 5319 | 0 | 85.3797 | 0
222 | 1900-08-10 | 5320 | 0 | 73.9935 | 0
222 | 1900-08-10 | 5321 | 0 | 7.3509 | 0
222 | 1900-08-10 | 5322 | 0 | 22.697 | 0
222 | 1900-08-10 | 5323 | 0 | 10.3136 | 0
222 | 1900-08-10 | 5324 | 0 | 2.8268 | 0
222 | 1900-08-10 | 5325 | 0 | 4.8085 | 0
222 | 1900-08-10 | 5326 | 0 | 3.1215 | 0
222 | 1900-08-10 | 5327 | 0 | 2.5487 | 0
222 | 1900-08-10 | 5328 | 0 | 4.4086 | 0
223 | 1900-08-11 | 5329 | 0 | 3.6217 | 0
223 | 1900-08-11 | 5330 | 0 | 4.7704 | 0
223 | 1900-08-11 | 5331 | 0 | 2.4673 | 0
223 | 1900-08-11 | 5332 | 0 | 2.8548 | 0
223 | 1900-08-11 | 5333 | 0 | 4.932 | 0
223 | 1900-08-11 | 5334 | 0 | 204.3664 | 0
223 | 1900-08-11 | 5335 | 0 | 3.0525 | 0
223 | 1900-08-11 | 5336 | 0 | 18.4973 | 0
223 | 1900-08-11 | 5337 | 0 | 18.6457 | 0
223 | 1900-08-11 | 5338 | 0 | 14.1551 | 0
223 | 1900-08-11 | 5339 | 0 | 12.8293 | 0
223 | 1900-08-11 | 5340 | 0 | 19.9466 | 0
223 | 1900-08-11 | 5341 | 0 | 8.1928 | 0
223 | 1900-08-11 | 5342 | 0 | 23.5734 | 0
223 | 1900-08-11 | 5343 | 0 | 17.5124 | 0
223 | 1900-08-11 | 5344 | 0 | 11.3672 | 0
223 | 1900-08-11 | 5345 | 0 | 14.7971 | 0
223 | 1900-08-11 | 5346 | 0 | 13.8462 | 0
223 | 1900-08-11 | 5347 | 0 | 26.2369 | 0
223 | 1900-08-11 | 5348 | 0 | 3.7456 | 0
223 | 1900-08-11 | 5349 | 0 | 4.2206 | 0
223 | 1900-08-11 | 5350 | 0 | 4.4342 | 0
223 | 1900-08-11 | 5351 | 0 | 4.4328 | 0
223 | 1900-08-11 | 5352 | 0 | 4.0356 | 0
224 | 1900-08-12 | 5353 | 0 | 3.9051 | 0
224 | 1900-08-12 | 5354 | 0 | 4.9918 | 0
224 | 1900-08-12 | 5355 | 0 | 3.3135 | 0
224 | 1900-08-12 | 5356 | 0 | 4.0884 | 0
224 | 1900-08-12 | 5357 | 0 | 203.8123 | 0
224 | 1900-08-12 | 5358 | 0 | 3.7652 | 0
224 | 1900-08-12 | 5359 | 0 | 4.4041 | 0
224 | 1900-08-12 | 5360 | 0 | 23.6758 | 0
224 | 1900-08-12 | 5361 | 0 | 13.7865 | 0
224 | 1900-08-12 | 5362 | 0 | 16.4693 | 0
224 | 1900-08-12 | 5363 | 0 | 22.5969 | 0
224 | 1900-08-12 | 5364 | 0 | 17.0106 | 0
224 | 1900-08-12 | 5365 | 0 | 26.6865 | 0
224 | 1900-08-12 | 5366 | 0 | 11.5909 | 0
224 | 1900-08-12 | 5367 | 0 | 22.0297 | 0
224 | 1900-08-12 | 5368 | 0 | 15.8273 | 0
224 | 1900-08-12 | 5369 | 0 | 18.5062 | 0
224 | 1900-08-12 | 5370 | 0 | 28.1648 | 0
224 | 1900-08-12 | 5371 | 0 | 29.1751 | 0
224 | 1900-08-12 | 5372 | 0 | 50.3719 | 0
224 | 1900-08-12 | 5373 | 0 | 10.0968 | 0
224 | 1900-08-12 | 5374 | 0 | 18.7363 | 0
224 | 1900-08-12 | 5375 | 0 | 4.3027 | 0
224 | 1900-08-12 | 5376 | 0 | 4.3039 | 0
225 | 1900-08-13 | 5377 | 0 | 4.0016 | 0
225 | 1900-08-13 | 5378 | 0 | 4.5238 | 0
225 | 1900-08-13 | 5379 | 0 | 5.9065 | 0
225 | 1900-08-13 | 5380 | 0 | 5.1007 | 0
225 | 1900-08-13 | 5381 | 0 | 12.6731 | 0
225 | 1900-08-13 | 5382 | 0 | 24.3111 | 0
225 | 1900-08-13 | 5383 | 0 | 5.551 | 0
225 | 1900-08-13 | 5384 | 0 | 25.3198 | 0
225 | 1900-08-13 | 5385 | 0 | 13.9737 | 0
225 | 1900-08-13 | 5386 | 0 | 18.0246 | 0
225 | 1900-08-13 | 5387 | 0 | 2.0164 | 0
225 | 1900-08-13 | 5388 | 0 | 15.5037 | 0
225 | 1900-08-13 | 5389 | 0 | 17.3045 | 0
225 | 1900-08-13 | 5390 | 0 | 18.4424 | 0
225 | 1900-08-13 | 5391 | 0 | 16.2211 | 0
225 | 1900-08-13 | 5392 | 0 | 21.8364 | 0
225 | 1900-08-13 | 5393 | 0 | 15.9306 | 0
225 | 1900-08-13 | 5394 | 0 | 25.274 | 0
225 | 1900-08-13 | 5395 | 0 | 23.0517 | 0
225 | 1900-08-13 | 5396 | 0 | 4.7385 | 0
225 | 1900-08-13 | 5397 | 0 | 4.2462 | 0
225 | 1900-08-13 | 5398 | 0 | 4.2044 | 0
225 | 1900-08-13 | 5399 | 0 | 4.916 | 0
225 | 1900-08-13 | 5400 | 0 | 3.6328 | 0
226 | 1900-08-14 | 5401 | 0 | 5.0846 | 0
226 | 1900-08-14 | 5402 | 0 | 3.8708 | 0
226 | 1900-08-14 | 5403 | 0 | 3.6867 | 0
226 | 1900-08-14 | 5404 | 0 | 3.2501 | 0
226 | 1900-08-14 | 5405 | 0 | 4.1474 | 0
226 | 1900-08-14 | 5406 | 0 | 4.4283 | 0
226 | 1900-08-14 | 5407 | 0 | 3.5461 | 0
226 | 1900-08-14 | 5408 | 0 | 18.6215 | 0
226 | 1900-08-14 | 5409 | 0 | 14.828 | 0
226 | 1900-08-14 | 5410 | 0 | 10.1384 | 0
226 | 1900-08-14 | 5411 | 0 | 18.1283 | 0
226 | 1900-08-14 | 5412 | 0 | 22.093 | 0
226 | 1900-08-14 | 5413 | 0 | 17.2992 | 0
226 | 1900-08-14 | 5414 | 0 | 19.5041 | 0
226 | 1900-08-14 | 5415 | 0 | 10.1335 | 0
226 | 1900-08-14 | 5416 | 0 | 32.239 | 0
226 | 1900-08-14 | 5417 | 0 | 11.5543 | 0
226 | 1900-08-14 | 5418 | 0 | 11.8964 | 0
226 | 1900-08-14 | 5419 | 0 | 21.7053 | 0
226 | 1900-08-14 | 5420 | 0 | 3.5441 | 0
226 | 1900-08-14 | 5421 | 0 | 3.5682 | 0
226 | 1900-08-14 | 5422 | 0 | 2.9512 | 0
226 | 1900-08-14 | 5423 | 0 | 3.9332 | 0
226 | 1900-08-14 | 5424 | 0 | 4.2025 | 0
227 | 1900-08-15 | 5425 | 0 | 3.7886 | 0
227 | 1900-08-15 | 5426 | 0 | 4.6619 | 0
227 | 1900-08-15 | 5427 | 0 | 4.3457 | 0
227 | 1900-08-15 | 5428 | 0 | 12.8552 | 0
227 | 1900-08-15 | 5429 | 0 | 241.4439 | 0
227 | 1900-08-15 | 5430 | 0 | 51.4125 | 0
227 | 1900-08-15 | 5431 | 0 | 27.0007 | 0
227 | 1900-08-15 | 5432 | 0 | 18.0074 | 0
227 | 1900-08-15 | 5433 | 0 | 25.4292 | 0
227 | 1900-08-15 | 5434 | 0 | 30.9509 | 0
227 | 1900-08-15 | 5435 | 0 | 28.4526 | 0
227 | 1900-08-15 | 5436 | 0 | 225.1175 | 0
227 | 1900-08-15 | 5437 | 0 | 16.7186 | 0
227 | 1900-08-15 | 5438 | 0 | 22.6048 | 0
227 | 1900-08-15 | 5439 | 0 | 14.0231 | 0
227 | 1900-08-15 | 5440 | 0 | 8.9474 | 0
227 | 1900-08-15 | 5441 | 0 | 28.3566 | 0
227 | 1900-08-15 | 5442 | 0 | 8.7228 | 0
227 | 1900-08-15 | 5443 | 0 | 3.749 | 0
227 | 1900-08-15 | 5444 | 0 | 3.8408 | 0
227 | 1900-08-15 | 5445 | 0 | 4.1874 | 0
227 | 1900-08-15 | 5446 | 0 | 4.1317 | 0
227 | 1900-08-15 | 5447 | 0 | 3.2851 | 0
227 | 1900-08-15 | 5448 | 0 | 3.41 | 0
228 | 1900-08-16 | 5449 | 0 | 4.048 | 0
228 | 1900-08-16 | 5450 | 0 | 4.0055 | 0
228 | 1900-08-16 | 5451 | 0 | 3.4407 | 0
228 | 1900-08-16 | 5452 | 0 | 11.5756 | 0
228 | 1900-08-16 | 5453 | 0 | 29.7704 | 0
228 | 1900-08-16 | 5454 | 0 | 34.1518 | 0
228 | 1900-08-16 | 5455 | 0 | 17.4905 | 0
228 | 1900-08-16 | 5456 | 0 | 8.9663 | 0
228 | 1900-08-16 | 5457 | 0 | 15.2891 | 0
228 | 1900-08-16 | 5458 | 0 | 31.4641 | 0
228 | 1900-08-16 | 5459 | 0 | 11.2429 | 0
228 | 1900-08-16 | 5460 | 0 | 8.6055 | 0
228 | 1900-08-16 | 5461 | 0 | 18.6528 | 0
228 | 1900-08-16 | 5462 | 0 | 18.7441 | 0
228 | 1900-08-16 | 5463 | 0 | 8.5921 | 0
228 | 1900-08-16 | 5464 | 0 | 16.6611 | 0
228 | 1900-08-16 | 5465 | 0 | 18.0879 | 0
228 | 1900-08-16 | 5466 | 0 | 21.1043 | 0
228 | 1900-08-16 | 5467 | 0 | 20.3939 | 0
228 | 1900-08-16 | 5468 | 0 | 3.9894 | 0
228 | 1900-08-16 | 5469 | 0 | 3.907 | 0
228 | 1900-08-16 | 5470 | 0 | 3.0934 | 0
228 | 1900-08-16 | 5471 | 0 | 4.4748 | 0
228 | 1900-08-16 | 5472 | 0 | 3.8519 | 0
229 | 1900-08-17 | 5473 | 0 | 3.8562 | 0
229 | 1900-08-17 | 5474 | 0 | 5.0559 | 0
229 | 1900-08-17 | 5475 | 0 | 5.4341 | 0
229 | 1900-08-17 | 5476 | 0 | 4.1842 | 0
229 | 1900-08-17 | 5477 | 0 | 4.1254 | 0
229 | 1900-08-17 | 5478 | 0 | 4.0026 | 0
229 | 1900-08-17 | 5479 | 0 | 3.9947 | 0
229 | 1900-08-17 | 5480 | 0 | 13.7371 | 0
229 | 1900-08-17 | 5481 | 0 | 22.1627 | 0
229 | 1900-08-17 | 5482 | 0 | 14.2985 | 0
229 | 1900-08-17 | 5483 | 0 | 25.8827 | 0
229 | 1900-08-17 | 5484 | 0 | 14.0827 | 0
229 | 1900-08-17 | 5485 | 0 | 25.5762 | 0
229 | 1900-08-17 | 5486 | 0 | 30.9227 | 0
229 | 1900-08-17 | 5487 | 0 | 27.1833 | 0
229 | 1900-08-17 | 5488 | 0 | 11.7454 | 0
229 | 1900-08-17 | 5489 | 0 | 7.0257 | 0
229 | 1900-08-17 | 5490 | 0 | 18.9468 | 0
229 | 1900-08-17 | 5491 | 0 | 16.0184 | 0
229 | 1900-08-17 | 5492 | 0 | 4.1681 | 0
229 | 1900-08-17 | 5493 | 0 | 5.0408 | 0
229 | 1900-08-17 | 5494 | 0 | 4.9699 | 0
229 | 1900-08-17 | 5495 | 0 | 3.1474 | 0
229 | 1900-08-17 | 5496 | 0 | 4.4642 | 0
230 | 1900-08-18 | 5497 | 0 | 3.2772 | 0
230 | 1900-08-18 | 5498 | 0 | 3.4809 | 0
230 | 1900-08-18 | 5499 | 0 | 3.8764 | 0
230 | 1900-08-18 | 5500 | 0 | 204.4257 | 0
230 | 1900-08-18 | 5501 | 0 | 3.0976 | 0
230 | 1900-08-18 | 5502 | 0 | 2.9315 | 0
230 | 1900-08-18 | 5503 | 0 | 3.9784 | 0
230 | 1900-08-18 | 5504 | 0 | 18.9681 | 0
230 | 1900-08-18 | 5505 | 0 | 22.5137 | 0
230 | 1900-08-18 | 5506 | 0 | 15.5397 | 0
230 | 1900-08-18 | 5507 | 0 | 17.3896 | 0
230 | 1900-08-18 | 5508 | 0 | 21.3542 | 0
230 | 1900-08-18 | 5509 | 0 | 10.8829 | 0
230 | 1900-08-18 | 5510 | 0 | 12.0771 | 0
230 | 1900-08-18 | 5511 | 0 | 23.9516 | 0
230 | 1900-08-18 | 5512 | 0 | 15.5913 | 0
230 | 1900-08-18 | 5513 | 0 | 15.2265 | 0
230 | 1900-08-18 | 5514 | 0 | 24.1894 | 0
230 | 1900-08-18 | 5515 | 0 | 7.4355 | 0
230 | 1900-08-18 | 5516 | 0 | 3.7767 | 0
230 | 1900-08-18 | 5517 | 0 | 2.9982 | 0
230 | 1900-08-18 | 5518 | 0 | 3.9276 | 0
230 | 1900-08-18 | 5519 | 0 | 3.7609 | 0
230 | 1900-08-18 | 5520 | 0 | 3.9346 | 0
231 | 1900-08-19 | 5521 | 0 | 4.2358 | 0
231 | 1900-08-19 | 5522 | 0 | 4.1914 | 0
231 | 1900-08-19 | 5523 | 0 | 4.2477 | 0
231 | 1900-08-19 | 5524 | 0 | 3.4398 | 0
231 | 1900-08-19 | 5525 | 0 | 5.1438 | 0
231 | 1900-08-19 | 5526 | 0 | 4.1831 | 0
231 | 1900-08-19 | 5527 | 0 | 4.3158 | 0
231 | 1900-08-19 | 5528 | 0 | 9.9836 | 0
231 | 1900-08-19 | 5529 | 0 | 19.1538 | 0
231 | 1900-08-19 | 5530 | 0 | 15.017 | 0
231 | 1900-08-19 | 5531 | 0 | 25.2072 | 0
231 | 1900-08-19 | 5532 | 0 | 16.9886 | 0
231 | 1900-08-19 | 5533 | 0 | 23.5468 | 0
231 | 1900-08-19 | 5534 | 0 | 22.1101 | 0
231 | 1900-08-19 | 5535 | 0 | 19.5768 | 0
231 | 1900-08-19 | 5536 | 0 | 10.1273 | 0
231 | 1900-08-19 | 5537 | 0 | 8.082 | 0
231 | 1900-08-19 | 5538 | 0 | 18.3391 | 0
231 | 1900-08-19 | 5539 | 0 | 207.9549 | 0
231 | 1900-08-19 | 5540 | 0 | 5.2842 | 0
231 | 1900-08-19 | 5541 | 0 | 3.7637 | 0
231 | 1900-08-19 | 5542 | 0 | 4.712 | 0
231 | 1900-08-19 | 5543 | 0 | 4.6349 | 0
231 | 1900-08-19 | 5544 | 0 | 4.1212 | 0
232 | 1900-08-20 | 5545 | 0 | 3.3583 | 0
232 | 1900-08-20 | 5546 | 0 | 4.1581 | 0
232 | 1900-08-20 | 5547 | 0 | 4.5925 | 0
232 | 1900-08-20 | 5548 | 0 | 4.0695 | 0
232 | 1900-08-20 | 5549 | 0 | 3.9075 | 0
232 | 1900-08-20 | 5550 | 0 | 3.1963 | 0
232 | 1900-08-20 | 5551 | 0 | 4.9293 | 0
232 | 1900-08-20 | 5552 | 0 | 29.7173 | 0
232 | 1900-08-20 | 5553 | 0 | 19.3037 | 0
232 | 1900-08-20 | 5554 | 0 | 16.6762 | 0
232 | 1900-08-20 | 5555 | 0 | 28.2417 | 0
232 | 1900-08-20 | 5556 | 0 | 19.1156 | 0
232 | 1900-08-20 | 5557 | 0 | 9.6099 | 0
232 | 1900-08-20 | 5558 | 0 | 15.0847 | 0
232 | 1900-08-20 | 5559 | 0 | 16.3715 | 0
232 | 1900-08-20 | 5560 | 0 | 20.0907 | 0
232 | 1900-08-20 | 5561 | 0 | 14.0349 | 0
232 | 1900-08-20 | 5562 | 0 | 13.3501 | 0
232 | 1900-08-20 | 5563 | 0 | 6.61 | 0
232 | 1900-08-20 | 5564 | 0 | 4.009 | 0
232 | 1900-08-20 | 5565 | 0 | 4.1591 | 0
232 | 1900-08-20 | 5566 | 0 | 4.3408 | 0
232 | 1900-08-20 | 5567 | 0 | 2.8921 | 0
232 | 1900-08-20 | 5568 | 0 | 4.8388 | 0
233 | 1900-08-21 | 5569 | 0 | 120.2373 | 0
233 | 1900-08-21 | 5570 | 0 | 118.2414 | 0
233 | 1900-08-21 | 5571 | 0 | 100.8689 | 0
233 | 1900-08-21 | 5572 | 0 | 273.803 | 0
233 | 1900-08-21 | 5573 | 0 | 141.5506 | 0
233 | 1900-08-21 | 5574 | 0 | 178.0654 | 0
233 | 1900-08-21 | 5575 | 0 | 123.8866 | 0
233 | 1900-08-21 | 5576 | 0 | 119.2142 | 0
233 | 1900-08-21 | 5577 | 0 | 144.3667 | 0
233 | 1900-08-21 | 5578 | 0 | 152.4359 | 0
233 | 1900-08-21 | 5579 | 0 | 207.7419 | 0
233 | 1900-08-21 | 5580 | 0 | 176.3972 | 0
233 | 1900-08-21 | 5581 | 0 | 127.9979 | 0
233 | 1900-08-21 | 5582 | 0 | 123.1464 | 0
233 | 1900-08-21 | 5583 | 0 | 98.407 | 0
233 | 1900-08-21 | 5584 | 0 | 130.6831 | 0
233 | 1900-08-21 | 5585 | 0 | 93.7446 | 0
233 | 1900-08-21 | 5586 | 0 | 108.2877 | 0
233 | 1900-08-21 | 5587 | 0 | 138.7843 | 0
233 | 1900-08-21 | 5588 | 0 | 102.8114 | 0
233 | 1900-08-21 | 5589 | 0 | 108.5141 | 0
233 | 1900-08-21 | 5590 | 0 | 111.8189 | 0
233 | 1900-08-21 | 5591 | 0 | 129.8578 | 0
233 | 1900-08-21 | 5592 | 0 | 113.4462 | 0
234 | 1900-08-22 | 5593 | 0 | 110.7778 | 0
234 | 1900-08-22 | 5594 | 0 | 136.626 | 0
234 | 1900-08-22 | 5595 | 0 | 113.1534 | 0
234 | 1900-08-22 | 5596 | 0 | 121.5329 | 0
234 | 1900-08-22 | 5597 | 0 | 95.502 | 0
234 | 1900-08-22 | 5598 | 0 | 100.0825 | 0
234 | 1900-08-22 | 5599 | 0 | 125.3816 | 0
234 | 1900-08-22 | 5600 | 0 | 195.8197 | 0
234 | 1900-08-22 | 5601 | 0 | 173.1875 | 0
234 | 1900-08-22 | 5602 | 0 | 231.1776 | 0
234 | 1900-08-22 | 5603 | 0 | 183.2884 | 0
234 | 1900-08-22 | 5604 | 0 | 196.1298 | 0
234 | 1900-08-22 | 5605 | 0 | 135.9206 | 0
234 | 1900-08-22 | 5606 | 0 | 160.4296 | 0
234 | 1900-08-22 | 5607 | 0 | 136.9819 | 0
234 | 1900-08-22 | 5608 | 0 | 164.7892 | 0
234 | 1900-08-22 | 5609 | 0 | 229.4253 | 0
234 | 1900-08-22 | 5610 | 0 | 151.5779 | 0
234 | 1900-08-22 | 5611 | 0 | 178.5592 | 0
234 | 1900-08-22 | 5612 | 0 | 86.2234 | 0
234 | 1900-08-22 | 5613 | 0 | 100.3353 | 0
234 | 1900-08-22 | 5614 | 0 | 132.9506 | 0
234 | 1900-08-22 | 5615 | 0 | 117.2379 | 0
234 | 1900-08-22 | 5616 | 0 | 152.3658 | 0
235 | 1900-08-23 | 5617 | 0 | 184.135 | 0
235 | 1900-08-23 | 5618 | 0 | 201.2234 | 0
235 | 1900-08-23 | 5619 | 0 | 170.6551 | 0
235 | 1900-08-23 | 5620 | 0 | 124.5587 | 0
235 | 1900-08-23 | 5621 | 0 | 111.4723 | 0
235 | 1900-08-23 | 5622 | 0 | 104.2565 | 0
235 | 1900-08-23 | 5623 | 0 | 82.4279 | 0
235 | 1900-08-23 | 5624 | 0 | 159.1312 | 0
235 | 1900-08-23 | 5625 | 0 | 171.18 | 0
235 | 1900-08-23 | 5626 | 0 | 184.9131 | 0
235 | 1900-08-23 | 5627 | 0 | 152.3228 | 0
235 | 1900-08-23 | 5628 | 0 | 121.9183 | 0
235 | 1900-08-23 | 5629 | 0 | 122.452 | 0
235 | 1900-08-23 | 5630 | 0 | 130.5334 | 0
235 | 1900-08-23 | 5631 | 0 | 121.3806 | 0
235 | 1900-08-23 | 5632 | 0 | 130.0187 | 0
235 | 1900-08-23 | 5633 | 0 | 165.3229 | 0
235 | 1900-08-23 | 5634 | 0 | 187.0165 | 0
235 | 1900-08-23 | 5635 | 0 | 170.7228 | 0
235 | 1900-08-23 | 5636 | 0 | 91.1627 | 0
235 | 1900-08-23 | 5637 | 0 | 89.0725 | 0
235 | 1900-08-23 | 5638 | 0 | 129.6038 | 0
235 | 1900-08-23 | 5639 | 0 | 173.638 | 0
235 | 1900-08-23 | 5640 | 0 | 407.5861 | 0
236 | 1900-08-24 | 5641 | 0 | 272.5294 | 0
236 | 1900-08-24 | 5642 | 0 | 26.7862 | 0
236 | 1900-08-24 | 5643 | 0 | 28.083 | 0
236 | 1900-08-24 | 5644 | 0 | 36.9304 | 0
236 | 1900-08-24 | 5645 | 0 | 38.5015 | 0
236 | 1900-08-24 | 5646 | 0 | 69.4247 | 0
236 | 1900-08-24 | 5647 | 0 | 77.8533 | 0
236 | 1900-08-24 | 5648 | 0 | 103.0986 | 0
236 | 1900-08-24 | 5649 | 0 | 95.1843 | 0
236 | 1900-08-24 | 5650 | 0 | 104.571 | 0
236 | 1900-08-24 | 5651 | 0 | 93.929 | 0
236 | 1900-08-24 | 5652 | 0 | 99.907 | 0
236 | 1900-08-24 | 5653 | 0 | 75.2866 | 0
236 | 1900-08-24 | 5654 | 0 | 56.7146 | 0
236 | 1900-08-24 | 5655 | 0 | 63.5949 | 0
236 | 1900-08-24 | 5656 | 0 | 50.7053 | 0
236 | 1900-08-24 | 5657 | 0 | 44.6871 | 0
236 | 1900-08-24 | 5658 | 0 | 37.9704 | 0
236 | 1900-08-24 | 5659 | 0 | 49.1774 | 0
236 | 1900-08-24 | 5660 | 0 | 30.9011 | 0
236 | 1900-08-24 | 5661 | 0 | 25.2941 | 0
236 | 1900-08-24 | 5662 | 0 | 25.7738 | 0
236 | 1900-08-24 | 5663 | 0 | 33.1687 | 0
236 | 1900-08-24 | 5664 | 0 | 21.0229 | 0
237 | 1900-08-25 | 5665 | 0 | 38.6784 | 0
237 | 1900-08-25 | 5666 | 0 | 31.8176 | 0
237 | 1900-08-25 | 5667 | 0 | 23.0724 | 0
237 | 1900-08-25 | 5668 | 0 | 33.267 | 0
237 | 1900-08-25 | 5669 | 0 | 33.2362 | 0
237 | 1900-08-25 | 5670 | 0 | 29.5515 | 0
237 | 1900-08-25 | 5671 | 0 | 29.6809 | 0
237 | 1900-08-25 | 5672 | 0 | 40.9017 | 0
237 | 1900-08-25 | 5673 | 0 | 50.6598 | 0
237 | 1900-08-25 | 5674 | 0 | 50.2528 | 0
237 | 1900-08-25 | 5675 | 0 | 41.1979 | 0
237 | 1900-08-25 | 5676 | 0 | 48.6069 | 0
237 | 1900-08-25 | 5677 | 0 | 58.1659 | 0
237 | 1900-08-25 | 5678 | 0 | 49.2101 | 0
237 | 1900-08-25 | 5679 | 0 | 40.2125 | 0
237 | 1900-08-25 | 5680 | 0 | 38.5794 | 0
237 | 1900-08-25 | 5681 | 0 | 41.1354 | 0
237 | 1900-08-25 | 5682 | 0 | 23.7685 | 0
237 | 1900-08-25 | 5683 | 0 | 35.7989 | 0
237 | 1900-08-25 | 5684 | 0 | 22.7759 | 0
237 | 1900-08-25 | 5685 | 0 | 23.9717 | 0
237 | 1900-08-25 | 5686 | 0 | 27.3339 | 0
237 | 1900-08-25 | 5687 | 0 | 29.5632 | 0
237 | 1900-08-25 | 5688 | 0 | 28.3918 | 0
238 | 1900-08-26 | 5689 | 0 | 31.8252 | 0
238 | 1900-08-26 | 5690 | 0 | 21.0581 | 0
238 | 1900-08-26 | 5691 | 0 | 22.2769 | 0
238 | 1900-08-26 | 5692 | 0 | 27.24 | 0
238 | 1900-08-26 | 5693 | 0 | 32.8566 | 0
238 | 1900-08-26 | 5694 | 0 | 29.557 | 0
238 | 1900-08-26 | 5695 | 0 | 32.0684 | 0
238 | 1900-08-26 | 5696 | 0 | 43.1828 | 0
238 | 1900-08-26 | 5697 | 0 | 39.3849 | 0
238 | 1900-08-26 | 5698 | 0 | 54.4761 | 0
238 | 1900-08-26 | 5699 | 0 | 31.1111 | 0
238 | 1900-08-26 | 5700 | 0 | 54.4369 | 0
238 | 1900-08-26 | 5701 | 0 | 49.8491 | 0
238 | 1900-08-26 | 5702 | 0 | 43.3915 | 0
238 | 1900-08-26 | 5703 | 0 | 39.9871 | 0
238 | 1900-08-26 | 5704 | 0 | 43.7169 | 0
238 | 1900-08-26 | 5705 | 0 | 38.7969 | 0
238 | 1900-08-26 | 5706 | 0 | 34.8099 | 0
238 | 1900-08-26 | 5707 | 0 | 45.8633 | 0
238 | 1900-08-26 | 5708 | 0 | 25.5981 | 0
238 | 1900-08-26 | 5709 | 0 | 31.6064 | 0
238 | 1900-08-26 | 5710 | 0 | 30.4714 | 0
238 | 1900-08-26 | 5711 | 0 | 27.6507 | 0
238 | 1900-08-26 | 5712 | 0 | 229.4414 | 0
239 | 1900-08-27 | 5713 | 0 | 31.124 | 0
239 | 1900-08-27 | 5714 | 0 | 28.1178 | 0
239 | 1900-08-27 | 5715 | 0 | 66.2924 | 0
239 | 1900-08-27 | 5716 | 0 | 146.3412 | 0
239 | 1900-08-27 | 5717 | 0 | 126.5709 | 0
239 | 1900-08-27 | 5718 | 0 | 88.1216 | 0
239 | 1900-08-27 | 5719 | 0 | 97.0856 | 0
239 | 1900-08-27 | 5720 | 0 | 77.819 | 0
239 | 1900-08-27 | 5721 | 0 | 93.8614 | 0
239 | 1900-08-27 | 5722 | 0 | 98.3364 | 0
239 | 1900-08-27 | 5723 | 0 | 129.5405 | 0
239 | 1900-08-27 | 5724 | 0 | 108.4114 | 0
239 | 1900-08-27 | 5725 | 0 | 60.3352 | 0
239 | 1900-08-27 | 5726 | 0 | 53.4528 | 0
239 | 1900-08-27 | 5727 | 0 | 42.1872 | 0
239 | 1900-08-27 | 5728 | 0 | 32.2698 | 0
239 | 1900-08-27 | 5729 | 0 | 45.2748 | 0
239 | 1900-08-27 | 5730 | 0 | 36.6454 | 0
239 | 1900-08-27 | 5731 | 0 | 43.8794 | 0
239 | 1900-08-27 | 5732 | 0 | 29.1396 | 0
239 | 1900-08-27 | 5733 | 0 | 47.2518 | 0
239 | 1900-08-27 | 5734 | 0 | 91.019 | 0
239 | 1900-08-27 | 5735 | 0 | 74.7708 | 0
239 | 1900-08-27 | 5736 | 0 | 46.8058 | 0
240 | 1900-08-28 | 5737 | 0 | 95.7748 | 0
240 | 1900-08-28 | 5738 | 0 | 82.2358 | 0
240 | 1900-08-28 | 5739 | 0 | 299.4437 | 0
240 | 1900-08-28 | 5740 | 0 | 48.8643 | 0
240 | 1900-08-28 | 5741 | 0 | 42.0469 | 0
240 | 1900-08-28 | 5742 | 0 | 93.0397 | 0
240 | 1900-08-28 | 5743 | 0 | 103.8626 | 0
240 | 1900-08-28 | 5744 | 0 | 105.0613 | 0
240 | 1900-08-28 | 5745 | 0 | 102.9937 | 0
240 | 1900-08-28 | 5746 | 0 | 91.4844 | 0
240 | 1900-08-28 | 5747 | 0 | 99.922 | 0
240 | 1900-08-28 | 5748 | 0 | 112.1127 | 0
240 | 1900-08-28 | 5749 | 0 | 89.4569 | 0
240 | 1900-08-28 | 5750 | 0 | 81.3413 | 0
240 | 1900-08-28 | 5751 | 0 | 82.2173 | 0
240 | 1900-08-28 | 5752 | 0 | 52.968 | 0
240 | 1900-08-28 | 5753 | 0 | 51.9326 | 0
240 | 1900-08-28 | 5754 | 0 | 42.1056 | 0
240 | 1900-08-28 | 5755 | 0 | 43.6225 | 0
240 | 1900-08-28 | 5756 | 0 | 32.8503 | 0
240 | 1900-08-28 | 5757 | 0 | 53.1947 | 0
240 | 1900-08-28 | 5758 | 0 | 75.796 | 0
240 | 1900-08-28 | 5759 | 0 | 49.6206 | 0
240 | 1900-08-28 | 5760 | 0 | 51.9387 | 0
241 | 1900-08-29 | 5761 | 0 | 64.5643 | 0
241 | 1900-08-29 | 5762 | 0 | 55.536 | 0
241 | 1900-08-29 | 5763 | 0 | 81.6085 | 0
241 | 1900-08-29 | 5764 | 0 | 90.6486 | 0
241 | 1900-08-29 | 5765 | 0 | 80.9677 | 0
241 | 1900-08-29 | 5766 | 0 | 92.4811 | 0
241 | 1900-08-29 | 5767 | 0 | 75.6602 | 0
241 | 1900-08-29 | 5768 | 0 | 104.7083 | 0
241 | 1900-08-29 | 5769 | 0 | 104.4698 | 0
241 | 1900-08-29 | 5770 | 0 | 128.4315 | 0
241 | 1900-08-29 | 5771 | 0 | 122.2348 | 0
241 | 1900-08-29 | 5772 | 0 | 98.3746 | 0
241 | 1900-08-29 | 5773 | 0 | 109.9647 | 0
241 | 1900-08-29 | 5774 | 0 | 109.4587 | 0
241 | 1900-08-29 | 5775 | 0 | 99.2515 | 0
241 | 1900-08-29 | 5776 | 0 | 124.5331 | 0
241 | 1900-08-29 | 5777 | 0 | 93.1932 | 0
241 | 1900-08-29 | 5778 | 0 | 63.9992 | 0
241 | 1900-08-29 | 5779 | 0 | 48.198 | 0
241 | 1900-08-29 | 5780 | 0 | 59.5513 | 0
241 | 1900-08-29 | 5781 | 0 | 72.7697 | 0
241 | 1900-08-29 | 5782 | 0 | 96.0773 | 0
241 | 1900-08-29 | 5783 | 0 | 274.3865 | 0
241 | 1900-08-29 | 5784 | 0 | 33.0963 | 0
242 | 1900-08-30 | 5785 | 0 | 35.3193 | 0
242 | 1900-08-30 | 5786 | 0 | 59.1105 | 0
242 | 1900-08-30 | 5787 | 0 | 71.2272 | 0
242 | 1900-08-30 | 5788 | 0 | 37.7921 | 0
242 | 1900-08-30 | 5789 | 0 | 75.7361 | 0
242 | 1900-08-30 | 5790 | 0 | 99.3179 | 0
242 | 1900-08-30 | 5791 | 0 | 92.8291 | 0
242 | 1900-08-30 | 5792 | 0 | 98.7208 | 0
242 | 1900-08-30 | 5793 | 0 | 67.2898 | 0
242 | 1900-08-30 | 5794 | 0 | 64.292 | 0
242 | 1900-08-30 | 5795 | 0 | 86.2341 | 0
242 | 1900-08-30 | 5796 | 0 | 37.3537 | 0
242 | 1900-08-30 | 5797 | 0 | 44.906 | 0
242 | 1900-08-30 | 5798 | 0 | 53.0758 | 0
242 | 1900-08-30 | 5799 | 0 | 49.1376 | 0
242 | 1900-08-30 | 5800 | 0 | 40.1064 | 0
242 | 1900-08-30 | 5801 | 0 | 38.2267 | 0
242 | 1900-08-30 | 5802 | 0 | 31.0185 | 0
242 | 1900-08-30 | 5803 | 0 | 38.8201 | 0
242 | 1900-08-30 | 5804 | 0 | 33.7256 | 0
242 | 1900-08-30 | 5805 | 0 | 29.0581 | 0
242 | 1900-08-30 | 5806 | 0 | 27.2414 | 0
242 | 1900-08-30 | 5807 | 0 | 39.1998 | 0
242 | 1900-08-30 | 5808 | 0 | 29.1381 | 0
243 | 1900-08-31 | 5809 | 0 | 28.2341 | 0
243 | 1900-08-31 | 5810 | 0 | 27.9364 | 0
243 | 1900-08-31 | 5811 | 0 | 26.0601 | 0
243 | 1900-08-31 | 5812 | 0 | 38.1069 | 0
243 | 1900-08-31 | 5813 | 0 | 62.809 | 0
243 | 1900-08-31 | 5814 | 0 | 99.3796 | 0
243 | 1900-08-31 | 5815 | 0 | 80.3134 | 0
243 | 1900-08-31 | 5816 | 0 | 116.0804 | 0
243 | 1900-08-31 | 5817 | 0 | 91.4806 | 0
243 | 1900-08-31 | 5818 | 0 | 86.076 | 0
243 | 1900-08-31 | 5819 | 0 | 48.5222 | 0
243 | 1900-08-31 | 5820 | 0 | 33.9966 | 0
243 | 1900-08-31 | 5821 | 0 | 38.1275 | 0
243 | 1900-08-31 | 5822 | 0 | 45.997 | 0
243 | 1900-08-31 | 5823 | 0 | 37.5203 | 0
243 | 1900-08-31 | 5824 | 0 | 39.5206 | 0
243 | 1900-08-31 | 5825 | 0 | 43.6064 | 0
243 | 1900-08-31 | 5826 | 0 | 34.2676 | 0
243 | 1900-08-31 | 5827 | 0 | 35.9268 | 0
243 | 1900-08-31 | 5828 | 0 | 26.7169 | 0
243 | 1900-08-31 | 5829 | 0 | 29.2197 | 0
243 | 1900-08-31 | 5830 | 0 | 23.5334 | 0
243 | 1900-08-31 | 5831 | 0 | 32.2444 | 0
243 | 1900-08-31 | 5832 | 0 | 27.2669 | 0
244 | 1900-09-01 | 5833 | 0 | 35.6877 | 0
244 | 1900-09-01 | 5834 | 0 | 37.3207 | 0
244 | 1900-09-01 | 5835 | 0 | 233.2894 | 0
244 | 1900-09-01 | 5836 | 0 | 23.7272 | 0
244 | 1900-09-01 | 5837 | 0 | 31.1954 | 0
244 | 1900-09-01 | 5838 | 0 | 34.4809 | 0
244 | 1900-09-01 | 5839 | 0 | 35.5468 | 0
244 | 1900-09-01 | 5840 | 0 | 53.8848 | 0
244 | 1900-09-01 | 5841 | 0 | 43.6508 | 0
244 | 1900-09-01 | 5842 | 0 | 47.3409 | 0
244 | 1900-09-01 | 5843 | 0 | 44.5395 | 0
244 | 1900-09-01 | 5844 | 0 | 42.3667 | 0
244 | 1900-09-01 | 5845 | 0 | 45.6326 | 0
244 | 1900-09-01 | 5846 | 0 | 45.414 | 0
244 | 1900-09-01 | 5847 | 0 | 37.505 | 0
244 | 1900-09-01 | 5848 | 0 | 53.2934 | 0
244 | 1900-09-01 | 5849 | 0 | 48.9326 | 0
244 | 1900-09-01 | 5850 | 0 | 54.8373 | 0
244 | 1900-09-01 | 5851 | 0 | 248.2936 | 0
244 | 1900-09-01 | 5852 | 0 | 27.4699 | 0
244 | 1900-09-01 | 5853 | 0 | 28.1355 | 0
244 | 1900-09-01 | 5854 | 0 | 30.9459 | 0
244 | 1900-09-01 | 5855 | 0 | 32.237 | 0
244 | 1900-09-01 | 5856 | 0 | 23.0765 | 0
245 | 1900-09-02 | 5857 | 0 | 29.5448 | 0
245 | 1900-09-02 | 5858 | 0 | 32.7035 | 0
245 | 1900-09-02 | 5859 | 0 | 36.4747 | 0
245 | 1900-09-02 | 5860 | 0 | 28.0253 | 0
245 | 1900-09-02 | 5861 | 0 | 29.4191 | 0
245 | 1900-09-02 | 5862 | 0 | 23.5911 | 0
245 | 1900-09-02 | 5863 | 0 | 33.2374 | 0
245 | 1900-09-02 | 5864 | 0 | 47.0433 | 0
245 | 1900-09-02 | 5865 | 0 | 38.4221 | 0
245 | 1900-09-02 | 5866 | 0 | 54.1857 | 0
245 | 1900-09-02 | 5867 | 0 | 38.9454 | 0
245 | 1900-09-02 | 5868 | 0 | 39.8047 | 0
245 | 1900-09-02 | 5869 | 0 | 41.0136 | 0
245 | 1900-09-02 | 5870 | 0 | 48.2162 | 0
245 | 1900-09-02 | 5871 | 0 | 35.8829 | 0
245 | 1900-09-02 | 5872 | 0 | 32.8006 | 0
245 | 1900-09-02 | 5873 | 0 | 46.2222 | 0
245 | 1900-09-02 | 5874 | 0 | 51.9321 | 0
245 | 1900-09-02 | 5875 | 0 | 42.918 | 0
245 | 1900-09-02 | 5876 | 0 | 23.9279 | 0
245 | 1900-09-02 | 5877 | 0 | 27.0376 | 0
245 | 1900-09-02 | 5878 | 0 | 34.3735 | 0
245 | 1900-09-02 | 5879 | 0 | 27.5506 | 0
245 | 1900-09-02 | 5880 | 0 | 28.7229 | 0
246 | 1900-09-03 | 5881 | 0 | 30.4055 | 0
246 | 1900-09-03 | 5882 | 0 | 31.2793 | 0
246 | 1900-09-03 | 5883 | 0 | 28.1927 | 0
246 | 1900-09-03 | 5884 | 0 | 37.6331 | 0
246 | 1900-09-03 | 5885 | 0 | 63.2604 | 0
246 | 1900-09-03 | 5886 | 0 | 100.6489 | 0
246 | 1900-09-03 | 5887 | 0 | 105.6292 | 0
246 | 1900-09-03 | 5888 | 0 | 133.5865 | 0
246 | 1900-09-03 | 5889 | 0 | 119.6572 | 0
246 | 1900-09-03 | 5890 | 0 | 54.2 | 0
246 | 1900-09-03 | 5891 | 0 | 62.0577 | 0
246 | 1900-09-03 | 5892 | 0 | 65.3304 | 0
246 | 1900-09-03 | 5893 | 0 | 92.0306 | 0
246 | 1900-09-03 | 5894 | 0 | 43.5286 | 0
246 | 1900-09-03 | 5895 | 0 | 52.8398 | 0
246 | 1900-09-03 | 5896 | 0 | 25.4761 | 0
246 | 1900-09-03 | 5897 | 0 | 38.9545 | 0
246 | 1900-09-03 | 5898 | 0 | 40.9264 | 0
246 | 1900-09-03 | 5899 | 0 | 28.4771 | 0
246 | 1900-09-03 | 5900 | 0 | 37.1704 | 0
246 | 1900-09-03 | 5901 | 0 | 29.4107 | 0
246 | 1900-09-03 | 5902 | 0 | 26.295 | 0
246 | 1900-09-03 | 5903 | 0 | 33.9137 | 0
246 | 1900-09-03 | 5904 | 0 | 21.8439 | 0
247 | 1900-09-04 | 5905 | 0 | 32.2349 | 0
247 | 1900-09-04 | 5906 | 0 | 35.0647 | 0
247 | 1900-09-04 | 5907 | 0 | 32.8435 | 0
247 | 1900-09-04 | 5908 | 0 | 41.5665 | 0
247 | 1900-09-04 | 5909 | 0 | 31.0333 | 0
247 | 1900-09-04 | 5910 | 0 | 43.1887 | 0
247 | 1900-09-04 | 5911 | 0 | 50.707 | 0
247 | 1900-09-04 | 5912 | 0 | 33.32 | 0
247 | 1900-09-04 | 5913 | 0 | 41.6878 | 0
247 | 1900-09-04 | 5914 | 0 | 56.2701 | 0
247 | 1900-09-04 | 5915 | 0 | 113.3049 | 0
247 | 1900-09-04 | 5916 | 0 | 309.1763 | 0
247 | 1900-09-04 | 5917 | 0 | 102.0795 | 0
247 | 1900-09-04 | 5918 | 0 | 52.5302 | 0
247 | 1900-09-04 | 5919 | 0 | 36.2103 | 0
247 | 1900-09-04 | 5920 | 0 | 50.8361 | 0
247 | 1900-09-04 | 5921 | 0 | 43.5439 | 0
247 | 1900-09-04 | 5922 | 0 | 37.6651 | 0
247 | 1900-09-04 | 5923 | 0 | 46.7173 | 0
247 | 1900-09-04 | 5924 | 0 | 30.9866 | 0
247 | 1900-09-04 | 5925 | 0 | 33.2608 | 0
247 | 1900-09-04 | 5926 | 0 | 32.7342 | 0
247 | 1900-09-04 | 5927 | 0 | 22.8008 | 0
247 | 1900-09-04 | 5928 | 0 | 31.5561 | 0
248 | 1900-09-05 | 5929 | 0 | 24.1971 | 0
248 | 1900-09-05 | 5930 | 0 | 31.6068 | 0
248 | 1900-09-05 | 5931 | 0 | 35.0568 | 0
248 | 1900-09-05 | 5932 | 0 | 35.3842 | 0
248 | 1900-09-05 | 5933 | 0 | 27.9686 | 0
248 | 1900-09-05 | 5934 | 0 | 51.4621 | 0
248 | 1900-09-05 | 5935 | 0 | 96.0731 | 0
248 | 1900-09-05 | 5936 | 0 | 91.2204 | 0
248 | 1900-09-05 | 5937 | 0 | 313.6136 | 0
248 | 1900-09-05 | 5938 | 0 | 109.7762 | 0
248 | 1900-09-05 | 5939 | 0 | 121.684 | 0
248 | 1900-09-05 | 5940 | 0 | 63.1486 | 0
248 | 1900-09-05 | 5941 | 0 | 50.7432 | 0
248 | 1900-09-05 | 5942 | 0 | 41.0433 | 0
248 | 1900-09-05 | 5943 | 0 | 45.3116 | 0
248 | 1900-09-05 | 5944 | 0 | 41.7798 | 0
248 | 1900-09-05 | 5945 | 0 | 47.9255 | 0
248 | 1900-09-05 | 5946 | 0 | 81.3208 | 0
248 | 1900-09-05 | 5947 | 0 | 113.9353 | 0
248 | 1900-09-05 | 5948 | 0 | 100.618 | 0
248 | 1900-09-05 | 5949 | 0 | 78.1807 | 0
248 | 1900-09-05 | 5950 | 0 | 27.9641 | 0
248 | 1900-09-05 | 5951 | 0 | 33.3732 | 0
248 | 1900-09-05 | 5952 | 0 | 36.6569 | 0
249 | 1900-09-06 | 5953 | 0 | 27.1019 | 0
249 | 1900-09-06 | 5954 | 0 | 27.0179 | 0
249 | 1900-09-06 | 5955 | 0 | 33.8573 | 0
249 | 1900-09-06 | 5956 | 0 | 29.2999 | 0
249 | 1900-09-06 | 5957 | 0 | 37.0069 | 0
249 | 1900-09-06 | 5958 | 0 | 52.7991 | 0
249 | 1900-09-06 | 5959 | 0 | 92.0128 | 0
249 | 1900-09-06 | 5960 | 0 | 114.6468 | 0
249 | 1900-09-06 | 5961 | 0 | 94.2352 | 0
249 | 1900-09-06 | 5962 | 0 | 88.3971 | 0
249 | 1900-09-06 | 5963 | 0 | 104.6963 | 0
249 | 1900-09-06 | 5964 | 0 | 126.9483 | 0
249 | 1900-09-06 | 5965 | 0 | 81.734 | 0
249 | 1900-09-06 | 5966 | 0 | 47.794 | 0
249 | 1900-09-06 | 5967 | 0 | 46.4839 | 0
249 | 1900-09-06 | 5968 | 0 | 62.1399 | 0
249 | 1900-09-06 | 5969 | 0 | 44.6428 | 0
249 | 1900-09-06 | 5970 | 0 | 46.4111 | 0
249 | 1900-09-06 | 5971 | 0 | 48.6903 | 0
249 | 1900-09-06 | 5972 | 0 | 51.8391 | 0
249 | 1900-09-06 | 5973 | 0 | 83.3856 | 0
249 | 1900-09-06 | 5974 | 0 | 62.666 | 0
249 | 1900-09-06 | 5975 | 0 | 45.0251 | 0
249 | 1900-09-06 | 5976 | 0 | 45.671 | 0
250 | 1900-09-07 | 5977 | 0 | 103.6318 | 0
250 | 1900-09-07 | 5978 | 0 | 100.6332 | 0
250 | 1900-09-07 | 5979 | 0 | 83.3498 | 0
250 | 1900-09-07 | 5980 | 0 | 36.8978 | 0
250 | 1900-09-07 | 5981 | 0 | 222.3547 | 0
250 | 1900-09-07 | 5982 | 0 | 18.1048 | 0
250 | 1900-09-07 | 5983 | 0 | 29.6176 | 0
250 | 1900-09-07 | 5984 | 0 | 33.9757 | 0
250 | 1900-09-07 | 5985 | 0 | 46.743 | 0
250 | 1900-09-07 | 5986 | 0 | 54.5548 | 0
250 | 1900-09-07 | 5987 | 0 | 109.1256 | 0
250 | 1900-09-07 | 5988 | 0 | 94.7383 | 0
250 | 1900-09-07 | 5989 | 0 | 60.1715 | 0
250 | 1900-09-07 | 5990 | 0 | 45.9525 | 0
250 | 1900-09-07 | 5991 | 0 | 37.2679 | 0
250 | 1900-09-07 | 5992 | 0 | 44.8079 | 0
250 | 1900-09-07 | 5993 | 0 | 57.3802 | 0
250 | 1900-09-07 | 5994 | 0 | 43.5143 | 0
250 | 1900-09-07 | 5995 | 0 | 35.6359 | 0
250 | 1900-09-07 | 5996 | 0 | 30.3391 | 0
250 | 1900-09-07 | 5997 | 0 | 36.9735 | 0
250 | 1900-09-07 | 5998 | 0 | 31.836 | 0
250 | 1900-09-07 | 5999 | 0 | 30.1338 | 0
250 | 1900-09-07 | 6000 | 0 | 29.4535 | 0
251 | 1900-09-08 | 6001 | 0 | 33.0276 | 0
251 | 1900-09-08 | 6002 | 0 | 34.7718 | 0
251 | 1900-09-08 | 6003 | 0 | 33.9844 | 0
251 | 1900-09-08 | 6004 | 0 | 41.4933 | 0
251 | 1900-09-08 | 6005 | 0 | 76.9443 | 0
251 | 1900-09-08 | 6006 | 0 | 79.0901 | 0
251 | 1900-09-08 | 6007 | 0 | 26.6278 | 0
251 | 1900-09-08 | 6008 | 0 | 53.1683 | 0
251 | 1900-09-08 | 6009 | 0 | 42.3263 | 0
251 | 1900-09-08 | 6010 | 0 | 41.6441 | 0
251 | 1900-09-08 | 6011 | 0 | 40.5054 | 0
251 | 1900-09-08 | 6012 | 0 | 43.9187 | 0
251 | 1900-09-08 | 6013 | 0 | 35.161 | 0
251 | 1900-09-08 | 6014 | 0 | 32.8276 | 0
251 | 1900-09-08 | 6015 | 0 | 43.0364 | 0
251 | 1900-09-08 | 6016 | 0 | 45.0315 | 0
251 | 1900-09-08 | 6017 | 0 | 39.7472 | 0
251 | 1900-09-08 | 6018 | 0 | 48.7014 | 0
251 | 1900-09-08 | 6019 | 0 | 40.6332 | 0
251 | 1900-09-08 | 6020 | 0 | 25.4853 | 0
251 | 1900-09-08 | 6021 | 0 | 29.7855 | 0
251 | 1900-09-08 | 6022 | 0 | 28.2073 | 0
251 | 1900-09-08 | 6023 | 0 | 28.3608 | 0
251 | 1900-09-08 | 6024 | 0 | 22.2734 | 0
252 | 1900-09-09 | 6025 | 0 | 24.4389 | 0
252 | 1900-09-09 | 6026 | 0 | 31.4192 | 0
252 | 1900-09-09 | 6027 | 0 | 27.9679 | 0
252 | 1900-09-09 | 6028 | 0 | 25.9253 | 0
252 | 1900-09-09 | 6029 | 0 | 27.5069 | 0
252 | 1900-09-09 | 6030 | 0 | 27.4751 | 0
252 | 1900-09-09 | 6031 | 0 | 25.0736 | 0
252 | 1900-09-09 | 6032 | 0 | 43.0825 | 0
252 | 1900-09-09 | 6033 | 0 | 38.8319 | 0
252 | 1900-09-09 | 6034 | 0 | 48.1507 | 0
252 | 1900-09-09 | 6035 | 0 | 44.5767 | 0
252 | 1900-09-09 | 6036 | 0 | 43.3509 | 0
252 | 1900-09-09 | 6037 | 0 | 40.3698 | 0
252 | 1900-09-09 | 6038 | 0 | 36.8052 | 0
252 | 1900-09-09 | 6039 | 0 | 247.8707 | 0
252 | 1900-09-09 | 6040 | 0 | 50.7449 | 0
252 | 1900-09-09 | 6041 | 0 | 50.5474 | 0
252 | 1900-09-09 | 6042 | 0 | 41.5539 | 0
252 | 1900-09-09 | 6043 | 0 | 47.2942 | 0
252 | 1900-09-09 | 6044 | 0 | 33.8017 | 0
252 | 1900-09-09 | 6045 | 0 | 35.1031 | 0
252 | 1900-09-09 | 6046 | 0 | 18.801 | 0
252 | 1900-09-09 | 6047 | 0 | 230.0904 | 0
252 | 1900-09-09 | 6048 | 0 | 40.3639 | 0
253 | 1900-09-10 | 6049 | 0 | 27.0531 | 0
253 | 1900-09-10 | 6050 | 0 | 28.1879 | 0
253 | 1900-09-10 | 6051 | 0 | 57.2495 | 0
253 | 1900-09-10 | 6052 | 0 | 107.9366 | 0
253 | 1900-09-10 | 6053 | 0 | 104.5831 | 0
253 | 1900-09-10 | 6054 | 0 | 125.4005 | 0
253 | 1900-09-10 | 6055 | 0 | 101.8982 | 0
253 | 1900-09-10 | 6056 | 0 | 127.3644 | 0
253 | 1900-09-10 | 6057 | 0 | 126.3312 | 0
253 | 1900-09-10 | 6058 | 0 | 125.8278 | 0
253 | 1900-09-10 | 6059 | 0 | 127.5567 | 0
253 | 1900-09-10 | 6060 | 0 | 116.0779 | 0
253 | 1900-09-10 | 6061 | 0 | 129.4573 | 0
253 | 1900-09-10 | 6062 | 0 | 116.6844 | 0
253 | 1900-09-10 | 6063 | 0 | 101.9853 | 0
253 | 1900-09-10 | 6064 | 0 | 96.6619 | 0
253 | 1900-09-10 | 6065 | 0 | 66.9544 | 0
253 | 1900-09-10 | 6066 | 0 | 55.5053 | 0
253 | 1900-09-10 | 6067 | 0 | 36.5845 | 0
253 | 1900-09-10 | 6068 | 0 | 26.0848 | 0
253 | 1900-09-10 | 6069 | 0 | 39.6017 | 0
253 | 1900-09-10 | 6070 | 0 | 32.5522 | 0
253 | 1900-09-10 | 6071 | 0 | 38.093 | 0
253 | 1900-09-10 | 6072 | 0 | 28.4697 | 0
254 | 1900-09-11 | 6073 | 0 | 27.7328 | 0
254 | 1900-09-11 | 6074 | 0 | 25.3581 | 0
254 | 1900-09-11 | 6075 | 0 | 31.2932 | 0
254 | 1900-09-11 | 6076 | 0 | 37.851 | 0
254 | 1900-09-11 | 6077 | 0 | 47.0305 | 0
254 | 1900-09-11 | 6078 | 0 | 80.6661 | 0
254 | 1900-09-11 | 6079 | 0 | 112.4346 | 0
254 | 1900-09-11 | 6080 | 0 | 126.0295 | 0
254 | 1900-09-11 | 6081 | 0 | 104.9974 | 0
254 | 1900-09-11 | 6082 | 0 | 118.681 | 0
254 | 1900-09-11 | 6083 | 0 | 125.0626 | 0
254 | 1900-09-11 | 6084 | 0 | 109.5226 | 0
254 | 1900-09-11 | 6085 | 0 | 54.8509 | 0
254 | 1900-09-11 | 6086 | 0 | 103.8303 | 0
254 | 1900-09-11 | 6087 | 0 | 82.534 | 0
254 | 1900-09-11 | 6088 | 0 | 34.55 | 0
254 | 1900-09-11 | 6089 | 0 | 36.1198 | 0
254 | 1900-09-11 | 6090 | 0 | 38.8722 | 0
254 | 1900-09-11 | 6091 | 0 | 54.651 | 0
254 | 1900-09-11 | 6092 | 0 | 32.4209 | 0
254 | 1900-09-11 | 6093 | 0 | 36.9022 | 0
254 | 1900-09-11 | 6094 | 0 | 29.3108 | 0
254 | 1900-09-11 | 6095 | 0 | 26.6976 | 0
254 | 1900-09-11 | 6096 | 0 | 30.3122 | 0
255 | 1900-09-12 | 6097 | 0 | 34.2312 | 0
255 | 1900-09-12 | 6098 | 0 | 35.35 | 0
255 | 1900-09-12 | 6099 | 0 | 40.0378 | 0
255 | 1900-09-12 | 6100 | 0 | 105.7633 | 0
255 | 1900-09-12 | 6101 | 0 | 115.4765 | 0
255 | 1900-09-12 | 6102 | 0 | 99.3045 | 0
255 | 1900-09-12 | 6103 | 0 | 104.9643 | 0
255 | 1900-09-12 | 6104 | 0 | 117.8166 | 0
255 | 1900-09-12 | 6105 | 0 | 131.1827 | 0
255 | 1900-09-12 | 6106 | 0 | 113.0411 | 0
255 | 1900-09-12 | 6107 | 0 | 88.9609 | 0
255 | 1900-09-12 | 6108 | 0 | 103.4863 | 0
255 | 1900-09-12 | 6109 | 0 | 97.1477 | 0
255 | 1900-09-12 | 6110 | 0 | 99.1964 | 0
255 | 1900-09-12 | 6111 | 0 | 110.7257 | 0
255 | 1900-09-12 | 6112 | 0 | 297.461 | 0
255 | 1900-09-12 | 6113 | 0 | 54.696 | 0
255 | 1900-09-12 | 6114 | 0 | 43.6449 | 0
255 | 1900-09-12 | 6115 | 0 | 32.6153 | 0
255 | 1900-09-12 | 6116 | 0 | 27.937 | 0
255 | 1900-09-12 | 6117 | 0 | 35.3408 | 0
255 | 1900-09-12 | 6118 | 0 | 25.9154 | 0
255 | 1900-09-12 | 6119 | 0 | 22.8777 | 0
255 | 1900-09-12 | 6120 | 0 | 30.5046 | 0
256 | 1900-09-13 | 6121 | 0 | 25.1085 | 0
256 | 1900-09-13 | 6122 | 0 | 32.8404 | 0
256 | 1900-09-13 | 6123 | 0 | 33.1589 | 0
256 | 1900-09-13 | 6124 | 0 | 45.507 | 0
256 | 1900-09-13 | 6125 | 0 | 116.7942 | 0
256 | 1900-09-13 | 6126 | 0 | 97.2329 | 0
256 | 1900-09-13 | 6127 | 0 | 103.0107 | 0
256 | 1900-09-13 | 6128 | 0 | 94.9408 | 0
256 | 1900-09-13 | 6129 | 0 | 120.5621 | 0
256 | 1900-09-13 | 6130 | 0 | 133.0778 | 0
256 | 1900-09-13 | 6131 | 0 | 127.4944 | 0
256 | 1900-09-13 | 6132 | 0 | 128.262 | 0
256 | 1900-09-13 | 6133 | 0 | 117.824 | 0
256 | 1900-09-13 | 6134 | 0 | 312.4555 | 0
256 | 1900-09-13 | 6135 | 0 | 104.6045 | 0
256 | 1900-09-13 | 6136 | 0 | 50.9207 | 0
256 | 1900-09-13 | 6137 | 0 | 38.539 | 0
256 | 1900-09-13 | 6138 | 0 | 36.8726 | 0
256 | 1900-09-13 | 6139 | 0 | 49.2346 | 0
256 | 1900-09-13 | 6140 | 0 | 31.0698 | 0
256 | 1900-09-13 | 6141 | 0 | 29.9334 | 0
256 | 1900-09-13 | 6142 | 0 | 33.2091 | 0
256 | 1900-09-13 | 6143 | 0 | 26.9362 | 0
256 | 1900-09-13 | 6144 | 0 | 30.2856 | 0
257 | 1900-09-14 | 6145 | 0 | 23.1214 | 0
257 | 1900-09-14 | 6146 | 0 | 30.3581 | 0
257 | 1900-09-14 | 6147 | 0 | 30.484 | 0
257 | 1900-09-14 | 6148 | 0 | 34.4877 | 0
257 | 1900-09-14 | 6149 | 0 | 27.4982 | 0
257 | 1900-09-14 | 6150 | 0 | 52.0543 | 0
257 | 1900-09-14 | 6151 | 0 | 100.3404 | 0
257 | 1900-09-14 | 6152 | 0 | 106.8015 | 0
257 | 1900-09-14 | 6153 | 0 | 110.2962 | 0
257 | 1900-09-14 | 6154 | 0 | 90.5478 | 0
257 | 1900-09-14 | 6155 | 0 | 50.7867 | 0
257 | 1900-09-14 | 6156 | 0 | 48.9304 | 0
257 | 1900-09-14 | 6157 | 0 | 46.519 | 0
257 | 1900-09-14 | 6158 | 0 | 42.8588 | 0
257 | 1900-09-14 | 6159 | 0 | 40.0344 | 0
257 | 1900-09-14 | 6160 | 0 | 56.3426 | 0
257 | 1900-09-14 | 6161 | 0 | 39.616 | 0
257 | 1900-09-14 | 6162 | 0 | 39.3035 | 0
257 | 1900-09-14 | 6163 | 0 | 49.0514 | 0
257 | 1900-09-14 | 6164 | 0 | 40.3423 | 0
257 | 1900-09-14 | 6165 | 0 | 23.6297 | 0
257 | 1900-09-14 | 6166 | 0 | 26.8717 | 0
257 | 1900-09-14 | 6167 | 0 | 35.7584 | 0
257 | 1900-09-14 | 6168 | 0 | 29.9652 | 0
258 | 1900-09-15 | 6169 | 0 | 31.8259 | 0
258 | 1900-09-15 | 6170 | 0 | 35.8531 | 0
258 | 1900-09-15 | 6171 | 0 | 31.2971 | 0
258 | 1900-09-15 | 6172 | 0 | 30.2419 | 0
258 | 1900-09-15 | 6173 | 0 | 25.0304 | 0
258 | 1900-09-15 | 6174 | 0 | 28.2945 | 0
258 | 1900-09-15 | 6175 | 0 | 31.4236 | 0
258 | 1900-09-15 | 6176 | 0 | 244.0401 | 0
258 | 1900-09-15 | 6177 | 0 | 31.0235 | 0
258 | 1900-09-15 | 6178 | 0 | 47.6541 | 0
258 | 1900-09-15 | 6179 | 0 | 39.3486 | 0
258 | 1900-09-15 | 6180 | 0 | 54.7768 | 0
258 | 1900-09-15 | 6181 | 0 | 49.6179 | 0
258 | 1900-09-15 | 6182 | 0 | 44.0097 | 0
258 | 1900-09-15 | 6183 | 0 | 50.0206 | 0
258 | 1900-09-15 | 6184 | 0 | 49.1367 | 0
258 | 1900-09-15 | 6185 | 0 | 47.0906 | 0
258 | 1900-09-15 | 6186 | 0 | 45.6983 | 0
258 | 1900-09-15 | 6187 | 0 | 36.1629 | 0
258 | 1900-09-15 | 6188 | 0 | 38.8882 | 0
258 | 1900-09-15 | 6189 | 0 | 32.1143 | 0
258 | 1900-09-15 | 6190 | 0 | 27.5407 | 0
258 | 1900-09-15 | 6191 | 0 | 32.0408 | 0
258 | 1900-09-15 | 6192 | 0 | 28.4469 | 0
259 | 1900-09-16 | 6193 | 0 | 26.3775 | 0
259 | 1900-09-16 | 6194 | 0 | 36.9797 | 0
259 | 1900-09-16 | 6195 | 0 | 28.3755 | 0
259 | 1900-09-16 | 6196 | 0 | 36.5574 | 0
259 | 1900-09-16 | 6197 | 0 | 58.5515 | 0
259 | 1900-09-16 | 6198 | 0 | 87.7705 | 0
259 | 1900-09-16 | 6199 | 0 | 38.236 | 0
259 | 1900-09-16 | 6200 | 0 | 51.0497 | 0
259 | 1900-09-16 | 6201 | 0 | 50.9909 | 0
259 | 1900-09-16 | 6202 | 0 | 29.7155 | 0
259 | 1900-09-16 | 6203 | 0 | 42.3769 | 0
259 | 1900-09-16 | 6204 | 0 | 43.889 | 0
259 | 1900-09-16 | 6205 | 0 | 31.8235 | 0
259 | 1900-09-16 | 6206 | 0 | 47.4211 | 0
259 | 1900-09-16 | 6207 | 0 | 45.4111 | 0
259 | 1900-09-16 | 6208 | 0 | 43.0969 | 0
259 | 1900-09-16 | 6209 | 0 | 49.1346 | 0
259 | 1900-09-16 | 6210 | 0 | 42.0584 | 0
259 | 1900-09-16 | 6211 | 0 | 35.9723 | 0
259 | 1900-09-16 | 6212 | 0 | 23.0732 | 0
259 | 1900-09-16 | 6213 | 0 | 29.0544 | 0
259 | 1900-09-16 | 6214 | 0 | 30.1647 | 0
259 | 1900-09-16 | 6215 | 0 | 33.9269 | 0
259 | 1900-09-16 | 6216 | 0 | 31.0714 | 0
260 | 1900-09-17 | 6217 | 0 | 33.5038 | 0
260 | 1900-09-17 | 6218 | 0 | 31.4954 | 0
260 | 1900-09-17 | 6219 | 0 | 28.3746 | 0
260 | 1900-09-17 | 6220 | 0 | 42.8099 | 0
260 | 1900-09-17 | 6221 | 0 | 85.9851 | 0
260 | 1900-09-17 | 6222 | 0 | 109.823 | 0
260 | 1900-09-17 | 6223 | 0 | 111.7395 | 0
260 | 1900-09-17 | 6224 | 0 | 321.9842 | 0
260 | 1900-09-17 | 6225 | 0 | 98.2849 | 0
260 | 1900-09-17 | 6226 | 0 | 53.5454 | 0
260 | 1900-09-17 | 6227 | 0 | 62.1197 | 0
260 | 1900-09-17 | 6228 | 0 | 97.2959 | 0
260 | 1900-09-17 | 6229 | 0 | 109.2829 | 0
260 | 1900-09-17 | 6230 | 0 | 46.3194 | 0
260 | 1900-09-17 | 6231 | 0 | 52.8506 | 0
260 | 1900-09-17 | 6232 | 0 | 57.5246 | 0
260 | 1900-09-17 | 6233 | 0 | 35.6171 | 0
260 | 1900-09-17 | 6234 | 0 | 38.6972 | 0
260 | 1900-09-17 | 6235 | 0 | 40.2544 | 0
260 | 1900-09-17 | 6236 | 0 | 27.6779 | 0
260 | 1900-09-17 | 6237 | 0 | 24.6802 | 0
260 | 1900-09-17 | 6238 | 0 | 30.3023 | 0
260 | 1900-09-17 | 6239 | 0 | 26.5732 | 0
260 | 1900-09-17 | 6240 | 0 | 226.8489 | 0
261 | 1900-09-18 | 6241 | 0 | 32.6413 | 0
261 | 1900-09-18 | 6242 | 0 | 23.6857 | 0
261 | 1900-09-18 | 6243 | 0 | 37.8372 | 0
261 | 1900-09-18 | 6244 | 0 | 32.7116 | 0
261 | 1900-09-18 | 6245 | 0 | 45.4285 | 0
261 | 1900-09-18 | 6246 | 0 | 84.8469 | 0
261 | 1900-09-18 | 6247 | 0 | 83.4687 | 0
261 | 1900-09-18 | 6248 | 0 | 113.9427 | 0
261 | 1900-09-18 | 6249 | 0 | 90.4879 | 0
261 | 1900-09-18 | 6250 | 0 | 40.4343 | 0
261 | 1900-09-18 | 6251 | 0 | 35.4196 | 0
261 | 1900-09-18 | 6252 | 0 | 90.5628 | 0
261 | 1900-09-18 | 6253 | 0 | 109.0261 | 0
261 | 1900-09-18 | 6254 | 0 | 85.272 | 0
261 | 1900-09-18 | 6255 | 0 | 44.5005 | 0
261 | 1900-09-18 | 6256 | 0 | 41.3469 | 0
261 | 1900-09-18 | 6257 | 0 | 53.1162 | 0
261 | 1900-09-18 | 6258 | 0 | 38.2653 | 0
261 | 1900-09-18 | 6259 | 0 | 39.5774 | 0
261 | 1900-09-18 | 6260 | 0 | 36.7949 | 0
261 | 1900-09-18 | 6261 | 0 | 36.8393 | 0
261 | 1900-09-18 | 6262 | 0 | 31.119 | 0
261 | 1900-09-18 | 6263 | 0 | 32.1728 | 0
261 | 1900-09-18 | 6264 | 0 | 27.5216 | 0
262 | 1900-09-19 | 6265 | 0 | 32.2637 | 0
262 | 1900-09-19 | 6266 | 0 | 29.1257 | 0
262 | 1900-09-19 | 6267 | 0 | 25.0153 | 0
262 | 1900-09-19 | 6268 | 0 | 29.8607 | 0
262 | 1900-09-19 | 6269 | 0 | 55.6309 | 0
262 | 1900-09-19 | 6270 | 0 | 81.178 | 0
262 | 1900-09-19 | 6271 | 0 | 42.4177 | 0
262 | 1900-09-19 | 6272 | 0 | 60.1485 | 0
262 | 1900-09-19 | 6273 | 0 | 53.6021 | 0
262 | 1900-09-19 | 6274 | 0 | 61.917 | 0
262 | 1900-09-19 | 6275 | 0 | 100.2407 | 0
262 | 1900-09-19 | 6276 | 0 | 39.5349 | 0
262 | 1900-09-19 | 6277 | 0 | 41.0742 | 0
262 | 1900-09-19 | 6278 | 0 | 53.6514 | 0
262 | 1900-09-19 | 6279 | 0 | 40.1877 | 0
262 | 1900-09-19 | 6280 | 0 | 44.2169 | 0
262 | 1900-09-19 | 6281 | 0 | 43.1809 | 0
262 | 1900-09-19 | 6282 | 0 | 40.7652 | 0
262 | 1900-09-19 | 6283 | 0 | 50.8278 | 0
262 | 1900-09-19 | 6284 | 0 | 27.7718 | 0
262 | 1900-09-19 | 6285 | 0 | 25.7311 | 0
262 | 1900-09-19 | 6286 | 0 | 36.6198 | 0
262 | 1900-09-19 | 6287 | 0 | 35.0089 | 0
262 | 1900-09-19 | 6288 | 0 | 28.641 | 0
263 | 1900-09-20 | 6289 | 0 | 28.663 | 0
263 | 1900-09-20 | 6290 | 0 | 30.8788 | 0
263 | 1900-09-20 | 6291 | 0 | 30.172 | 0
263 | 1900-09-20 | 6292 | 0 | 32.5526 | 0
263 | 1900-09-20 | 6293 | 0 | 31.6815 | 0
263 | 1900-09-20 | 6294 | 0 | 29.6904 | 0
263 | 1900-09-20 | 6295 | 0 | 27.6004 | 0
263 | 1900-09-20 | 6296 | 0 | 52.6045 | 0
263 | 1900-09-20 | 6297 | 0 | 57.1266 | 0
263 | 1900-09-20 | 6298 | 0 | 42.2559 | 0
263 | 1900-09-20 | 6299 | 0 | 44.8537 | 0
263 | 1900-09-20 | 6300 | 0 | 46.2067 | 0
263 | 1900-09-20 | 6301 | 0 | 58.5944 | 0
263 | 1900-09-20 | 6302 | 0 | 94.0756 | 0
263 | 1900-09-20 | 6303 | 0 | 99.3299 | 0
263 | 1900-09-20 | 6304 | 0 | 243.407 | 0
263 | 1900-09-20 | 6305 | 0 | 32.2483 | 0
263 | 1900-09-20 | 6306 | 0 | 57.4783 | 0
263 | 1900-09-20 | 6307 | 0 | 38.5964 | 0
263 | 1900-09-20 | 6308 | 0 | 34.6348 | 0
263 | 1900-09-20 | 6309 | 0 | 31.1164 | 0
263 | 1900-09-20 | 6310 | 0 | 33.3049 | 0
263 | 1900-09-20 | 6311 | 0 | 27.3479 | 0
263 | 1900-09-20 | 6312 | 0 | 33.3103 | 0
264 | 1900-09-21 | 6313 | 0 | 29.4361 | 0
264 | 1900-09-21 | 6314 | 0 | 32.2949 | 0
264 | 1900-09-21 | 6315 | 0 | 34.5334 | 0
264 | 1900-09-21 | 6316 | 0 | 29.1793 | 0
264 | 1900-09-21 | 6317 | 0 | 75.2267 | 0
264 | 1900-09-21 | 6318 | 0 | 100.0749 | 0
264 | 1900-09-21 | 6319 | 0 | 71.762 | 0
264 | 1900-09-21 | 6320 | 0 | 98.5889 | 0
264 | 1900-09-21 | 6321 | 0 | 95.5985 | 0
264 | 1900-09-21 | 6322 | 0 | 77.8578 | 0
264 | 1900-09-21 | 6323 | 0 | 55.5247 | 0
264 | 1900-09-21 | 6324 | 0 | 293.1961 | 0
264 | 1900-09-21 | 6325 | 0 | 48.6013 | 0
264 | 1900-09-21 | 6326 | 0 | 49.452 | 0
264 | 1900-09-21 | 6327 | 0 | 54.6022 | 0
264 | 1900-09-21 | 6328 | 0 | 53.9555 | 0
264 | 1900-09-21 | 6329 | 0 | 97.5328 | 0
264 | 1900-09-21 | 6330 | 0 | 43.4066 | 0
264 | 1900-09-21 | 6331 | 0 | 42.4333 | 0
264 | 1900-09-21 | 6332 | 0 | 24.3108 | 0
264 | 1900-09-21 | 6333 | 0 | 29.5062 | 0
264 | 1900-09-21 | 6334 | 0 | 28.1853 | 0
264 | 1900-09-21 | 6335 | 0 | 31.2851 | 0
264 | 1900-09-21 | 6336 | 0 | 23.4303 | 0
265 | 1900-09-22 | 6337 | 0 | 26.4315 | 0
265 | 1900-09-22 | 6338 | 0 | 26.0217 | 0
265 | 1900-09-22 | 6339 | 0 | 26.3304 | 0
265 | 1900-09-22 | 6340 | 0 | 37.6278 | 0
265 | 1900-09-22 | 6341 | 0 | 55.3752 | 0
265 | 1900-09-22 | 6342 | 0 | 104.7936 | 0
265 | 1900-09-22 | 6343 | 0 | 94.4643 | 0
265 | 1900-09-22 | 6344 | 0 | 107.5715 | 0
265 | 1900-09-22 | 6345 | 0 | 78.6543 | 0
265 | 1900-09-22 | 6346 | 0 | 44.0778 | 0
265 | 1900-09-22 | 6347 | 0 | 41.9865 | 0
265 | 1900-09-22 | 6348 | 0 | 69.0027 | 0
265 | 1900-09-22 | 6349 | 0 | 98.3088 | 0
265 | 1900-09-22 | 6350 | 0 | 60.6545 | 0
265 | 1900-09-22 | 6351 | 0 | 46.3062 | 0
265 | 1900-09-22 | 6352 | 0 | 58.6439 | 0
265 | 1900-09-22 | 6353 | 0 | 35.7291 | 0
265 | 1900-09-22 | 6354 | 0 | 44.5818 | 0
265 | 1900-09-22 | 6355 | 0 | 38.8529 | 0
265 | 1900-09-22 | 6356 | 0 | 37.0449 | 0
265 | 1900-09-22 | 6357 | 0 | 31.3802 | 0
265 | 1900-09-22 | 6358 | 0 | 23.7302 | 0
265 | 1900-09-22 | 6359 | 0 | 25.7037 | 0
265 | 1900-09-22 | 6360 | 0 | 35.9368 | 0
266 | 1900-09-23 | 6361 | 0 | 23.4538 | 0
266 | 1900-09-23 | 6362 | 0 | 38.6866 | 0
266 | 1900-09-23 | 6363 | 0 | 25.1021 | 0
266 | 1900-09-23 | 6364 | 0 | 37.7805 | 0
266 | 1900-09-23 | 6365 | 0 | 30.9258 | 0
266 | 1900-09-23 | 6366 | 0 | 33.2887 | 0
266 | 1900-09-23 | 6367 | 0 | 31.758 | 0
266 | 1900-09-23 | 6368 | 0 | 48.3117 | 0
266 | 1900-09-23 | 6369 | 0 | 254.935 | 0
266 | 1900-09-23 | 6370 | 0 | 43.3252 | 0
266 | 1900-09-23 | 6371 | 0 | 49.1025 | 0
266 | 1900-09-23 | 6372 | 0 | 57.8031 | 0
266 | 1900-09-23 | 6373 | 0 | 37.8575 | 0
266 | 1900-09-23 | 6374 | 0 | 39.1035 | 0
266 | 1900-09-23 | 6375 | 0 | 35.1047 | 0
266 | 1900-09-23 | 6376 | 0 | 37.886 | 0
266 | 1900-09-23 | 6377 | 0 | 51.7366 | 0
266 | 1900-09-23 | 6378 | 0 | 51.7666 | 0
266 | 1900-09-23 | 6379 | 0 | 46.4157 | 0
266 | 1900-09-23 | 6380 | 0 | 33.2741 | 0
266 | 1900-09-23 | 6381 | 0 | 26.2245 | 0
266 | 1900-09-23 | 6382 | 0 | 30.821 | 0
266 | 1900-09-23 | 6383 | 0 | 22.033 | 0
266 | 1900-09-23 | 6384 | 0 | 30.603 | 0
267 | 1900-09-24 | 6385 | 0 | 35.4725 | 0
267 | 1900-09-24 | 6386 | 0 | 22.9642 | 0
267 | 1900-09-24 | 6387 | 0 | 37.0638 | 0
267 | 1900-09-24 | 6388 | 0 | 94.9574 | 0
267 | 1900-09-24 | 6389 | 0 | 116.4975 | 0
267 | 1900-09-24 | 6390 | 0 | 109.4141 | 0
267 | 1900-09-24 | 6391 | 0 | 81.3587 | 0
267 | 1900-09-24 | 6392 | 0 | 115.5017 | 0
267 | 1900-09-24 | 6393 | 0 | 133.5859 | 0
267 | 1900-09-24 | 6394 | 0 | 74.8079 | 0
267 | 1900-09-24 | 6395 | 0 | 72.5583 | 0
267 | 1900-09-24 | 6396 | 0 | 115.8082 | 0
267 | 1900-09-24 | 6397 | 0 | 70.618 | 0
267 | 1900-09-24 | 6398 | 0 | 276.6787 | 0
267 | 1900-09-24 | 6399 | 0 | 53.4738 | 0
267 | 1900-09-24 | 6400 | 0 | 35.2642 | 0
267 | 1900-09-24 | 6401 | 0 | 43.8031 | 0
267 | 1900-09-24 | 6402 | 0 | 45.6992 | 0
267 | 1900-09-24 | 6403 | 0 | 60.3221 | 0
267 | 1900-09-24 | 6404 | 0 | 112.2121 | 0
267 | 1900-09-24 | 6405 | 0 | 84.5368 | 0
267 | 1900-09-24 | 6406 | 0 | 60.7817 | 0
267 | 1900-09-24 | 6407 | 0 | 30.8027 | 0
267 | 1900-09-24 | 6408 | 0 | 24.7373 | 0
268 | 1900-09-25 | 6409 | 0 | 31.0281 | 0
268 | 1900-09-25 | 6410 | 0 | 47.9992 | 0
268 | 1900-09-25 | 6411 | 0 | 89.8174 | 0
268 | 1900-09-25 | 6412 | 0 | 75.1776 | 0
268 | 1900-09-25 | 6413 | 0 | 58.8746 | 0
268 | 1900-09-25 | 6414 | 0 | 104.681 | 0
268 | 1900-09-25 | 6415 | 0 | 112.6732 | 0
268 | 1900-09-25 | 6416 | 0 | 95.5477 | 0
268 | 1900-09-25 | 6417 | 0 | 85.4326 | 0
268 | 1900-09-25 | 6418 | 0 | 111.4153 | 0
268 | 1900-09-25 | 6419 | 0 | 111.9044 | 0
268 | 1900-09-25 | 6420 | 0 | 91.4961 | 0
268 | 1900-09-25 | 6421 | 0 | 58.1767 | 0
268 | 1900-09-25 | 6422 | 0 | 50.1496 | 0
268 | 1900-09-25 | 6423 | 0 | 43.1955 | 0
268 | 1900-09-25 | 6424 | 0 | 50.9742 | 0
268 | 1900-09-25 | 6425 | 0 | 34.7655 | 0
268 | 1900-09-25 | 6426 | 0 | 46.4688 | 0
268 | 1900-09-25 | 6427 | 0 | 63.8783 | 0
268 | 1900-09-25 | 6428 | 0 | 97.0071 | 0
268 | 1900-09-25 | 6429 | 0 | 90.0761 | 0
268 | 1900-09-25 | 6430 | 0 | 88.4434 | 0
268 | 1900-09-25 | 6431 | 0 | 52.0386 | 0
268 | 1900-09-25 | 6432 | 0 | 32.7935 | 0
269 | 1900-09-26 | 6433 | 0 | 227.0886 | 0
269 | 1900-09-26 | 6434 | 0 | 23.1164 | 0
269 | 1900-09-26 | 6435 | 0 | 43.1234 | 0
269 | 1900-09-26 | 6436 | 0 | 81.2859 | 0
269 | 1900-09-26 | 6437 | 0 | 96.8182 | 0
269 | 1900-09-26 | 6438 | 0 | 75.233 | 0
269 | 1900-09-26 | 6439 | 0 | 80.9624 | 0
269 | 1900-09-26 | 6440 | 0 | 94.4996 | 0
269 | 1900-09-26 | 6441 | 0 | 119.2344 | 0
269 | 1900-09-26 | 6442 | 0 | 115.4103 | 0
269 | 1900-09-26 | 6443 | 0 | 94.8482 | 0
269 | 1900-09-26 | 6444 | 0 | 87.9011 | 0
269 | 1900-09-26 | 6445 | 0 | 33.186 | 0
269 | 1900-09-26 | 6446 | 0 | 45.2478 | 0
269 | 1900-09-26 | 6447 | 0 | 53.3233 | 0
269 | 1900-09-26 | 6448 | 0 | 29.6684 | 0
269 | 1900-09-26 | 6449 | 0 | 52.556 | 0
269 | 1900-09-26 | 6450 | 0 | 46.0963 | 0
269 | 1900-09-26 | 6451 | 0 | 108.1739 | 0
269 | 1900-09-26 | 6452 | 0 | 91.7719 | 0
269 | 1900-09-26 | 6453 | 0 | 87.5332 | 0
269 | 1900-09-26 | 6454 | 0 | 77.261 | 0
269 | 1900-09-26 | 6455 | 0 | 64.124 | 0
269 | 1900-09-26 | 6456 | 0 | 101.7563 | 0
270 | 1900-09-27 | 6457 | 0 | 99.2365 | 0
270 | 1900-09-27 | 6458 | 0 | 120.6722 | 0
270 | 1900-09-27 | 6459 | 0 | 81.5194 | 0
270 | 1900-09-27 | 6460 | 0 | 63.622 | 0
270 | 1900-09-27 | 6461 | 0 | 48.4917 | 0
270 | 1900-09-27 | 6462 | 0 | 89.4036 | 0
270 | 1900-09-27 | 6463 | 0 | 78.964 | 0
270 | 1900-09-27 | 6464 | 0 | 282.582 | 0
270 | 1900-09-27 | 6465 | 0 | 97.6585 | 0
270 | 1900-09-27 | 6466 | 0 | 112.7371 | 0
270 | 1900-09-27 | 6467 | 0 | 88.4536 | 0
270 | 1900-09-27 | 6468 | 0 | 82.1898 | 0
270 | 1900-09-27 | 6469 | 0 | 88.867 | 0
270 | 1900-09-27 | 6470 | 0 | 75.6607 | 0
270 | 1900-09-27 | 6471 | 0 | 50.7984 | 0
270 | 1900-09-27 | 6472 | 0 | 49.8485 | 0
270 | 1900-09-27 | 6473 | 0 | 40.4151 | 0
270 | 1900-09-27 | 6474 | 0 | 56.2668 | 0
270 | 1900-09-27 | 6475 | 0 | 115.2011 | 0
270 | 1900-09-27 | 6476 | 0 | 83.1086 | 0
270 | 1900-09-27 | 6477 | 0 | 84.3691 | 0
270 | 1900-09-27 | 6478 | 0 | 77.2816 | 0
270 | 1900-09-27 | 6479 | 0 | 89.5238 | 0
270 | 1900-09-27 | 6480 | 0 | 80.1641 | 0
271 | 1900-09-28 | 6481 | 0 | 72.2703 | 0
271 | 1900-09-28 | 6482 | 0 | 80.4416 | 0
271 | 1900-09-28 | 6483 | 0 | 82.4618 | 0
271 | 1900-09-28 | 6484 | 0 | 65.8189 | 0
271 | 1900-09-28 | 6485 | 0 | 41.5869 | 0
271 | 1900-09-28 | 6486 | 0 | 68.9221 | 0
271 | 1900-09-28 | 6487 | 0 | 86.7912 | 0
271 | 1900-09-28 | 6488 | 0 | 99.4788 | 0
271 | 1900-09-28 | 6489 | 0 | 79.4291 | 0
271 | 1900-09-28 | 6490 | 0 | 77.8258 | 0
271 | 1900-09-28 | 6491 | 0 | 71.3511 | 0
271 | 1900-09-28 | 6492 | 0 | 68.5417 | 0
271 | 1900-09-28 | 6493 | 0 | 82.9979 | 0
271 | 1900-09-28 | 6494 | 0 | 47.9185 | 0
271 | 1900-09-28 | 6495 | 0 | 38.699 | 0
271 | 1900-09-28 | 6496 | 0 | 39.8558 | 0
271 | 1900-09-28 | 6497 | 0 | 52.6649 | 0
271 | 1900-09-28 | 6498 | 0 | 116.5507 | 0
271 | 1900-09-28 | 6499 | 0 | 322.6829 | 0
271 | 1900-09-28 | 6500 | 0 | 74.7436 | 0
271 | 1900-09-28 | 6501 | 0 | 26.5757 | 0
271 | 1900-09-28 | 6502 | 0 | 35.9259 | 0
271 | 1900-09-28 | 6503 | 0 | 25.0349 | 0
271 | 1900-09-28 | 6504 | 0 | 24.8055 | 0
272 | 1900-09-29 | 6505 | 0 | 35.7207 | 0
272 | 1900-09-29 | 6506 | 0 | 25.4596 | 0
272 | 1900-09-29 | 6507 | 0 | 36.3928 | 0
272 | 1900-09-29 | 6508 | 0 | 43.0038 | 0
272 | 1900-09-29 | 6509 | 0 | 102.8618 | 0
272 | 1900-09-29 | 6510 | 0 | 113.586 | 0
272 | 1900-09-29 | 6511 | 0 | 111.8689 | 0
272 | 1900-09-29 | 6512 | 0 | 113.9863 | 0
272 | 1900-09-29 | 6513 | 0 | 120.8143 | 0
272 | 1900-09-29 | 6514 | 0 | 124.151 | 0
272 | 1900-09-29 | 6515 | 0 | 121.5434 | 0
272 | 1900-09-29 | 6516 | 0 | 110.2567 | 0
272 | 1900-09-29 | 6517 | 0 | 130.8698 | 0
272 | 1900-09-29 | 6518 | 0 | 123.9095 | 0
272 | 1900-09-29 | 6519 | 0 | 110.075 | 0
272 | 1900-09-29 | 6520 | 0 | 96.8643 | 0
272 | 1900-09-29 | 6521 | 0 | 121.738 | 0
272 | 1900-09-29 | 6522 | 0 | 120.1564 | 0
272 | 1900-09-29 | 6523 | 0 | 102.5872 | 0
272 | 1900-09-29 | 6524 | 0 | 99.6466 | 0
272 | 1900-09-29 | 6525 | 0 | 119.9599 | 0
272 | 1900-09-29 | 6526 | 0 | 69.8047 | 0
272 | 1900-09-29 | 6527 | 0 | 232.6046 | 0
272 | 1900-09-29 | 6528 | 0 | 30.6583 | 0
273 | 1900-09-30 | 6529 | 0 | 22.2006 | 0
273 | 1900-09-30 | 6530 | 0 | 34.0768 | 0
273 | 1900-09-30 | 6531 | 0 | 30.5159 | 0
273 | 1900-09-30 | 6532 | 0 | 27.0941 | 0
273 | 1900-09-30 | 6533 | 0 | 43.6206 | 0
273 | 1900-09-30 | 6534 | 0 | 113.3714 | 0
273 | 1900-09-30 | 6535 | 0 | 92.4617 | 0
273 | 1900-09-30 | 6536 | 0 | 123.6332 | 0
273 | 1900-09-30 | 6537 | 0 | 113.8602 | 0
273 | 1900-09-30 | 6538 | 0 | 97.5693 | 0
273 | 1900-09-30 | 6539 | 0 | 73.6168 | 0
273 | 1900-09-30 | 6540 | 0 | 62.5685 | 0
273 | 1900-09-30 | 6541 | 0 | 84.8463 | 0
273 | 1900-09-30 | 6542 | 0 | 43.8003 | 0
273 | 1900-09-30 | 6543 | 0 | 40.278 | 0
273 | 1900-09-30 | 6544 | 0 | 41.2322 | 0
273 | 1900-09-30 | 6545 | 0 | 45.5319 | 0
273 | 1900-09-30 | 6546 | 0 | 50.718 | 0
273 | 1900-09-30 | 6547 | 0 | 39.8082 | 0
273 | 1900-09-30 | 6548 | 0 | 32.0125 | 0
273 | 1900-09-30 | 6549 | 0 | 25.6447 | 0
273 | 1900-09-30 | 6550 | 0 | 34.5652 | 0
273 | 1900-09-30 | 6551 | 0 | 31.0793 | 0
273 | 1900-09-30 | 6552 | 0 | 19.3349 | 0
274 | 1900-10-01 | 6553 | 0 | 28.0176 | 0
274 | 1900-10-01 | 6554 | 0 | 31.1271 | 0
274 | 1900-10-01 | 6555 | 0 | 36.0212 | 0
274 | 1900-10-01 | 6556 | 0 | 50.2637 | 0
274 | 1900-10-01 | 6557 | 0 | 108.1155 | 0
274 | 1900-10-01 | 6558 | 0 | 93.2683 | 0
274 | 1900-10-01 | 6559 | 0 | 86.5814 | 0
274 | 1900-10-01 | 6560 | 0 | 96.2105 | 0
274 | 1900-10-01 | 6561 | 0 | 89.4108 | 0
274 | 1900-10-01 | 6562 | 0 | 57.4371 | 0
274 | 1900-10-01 | 6563 | 0 | 257.1462 | 0
274 | 1900-10-01 | 6564 | 0 | 53.6505 | 0
274 | 1900-10-01 | 6565 | 0 | 109.2098 | 0
274 | 1900-10-01 | 6566 | 0 | 101.1846 | 0
274 | 1900-10-01 | 6567 | 0 | 77.132 | 0
274 | 1900-10-01 | 6568 | 0 | 58.6955 | 0
274 | 1900-10-01 | 6569 | 0 | 60.9274 | 0
274 | 1900-10-01 | 6570 | 0 | 46.9596 | 0
274 | 1900-10-01 | 6571 | 0 | 34.0619 | 0
274 | 1900-10-01 | 6572 | 0 | 27.6825 | 0
274 | 1900-10-01 | 6573 | 0 | 29.9527 | 0
274 | 1900-10-01 | 6574 | 0 | 23.0972 | 0
274 | 1900-10-01 | 6575 | 0 | 28.9359 | 0
274 | 1900-10-01 | 6576 | 0 | 31.3289 | 0
275 | 1900-10-02 | 6577 | 0 | 30.4567 | 0
275 | 1900-10-02 | 6578 | 0 | 21.3122 | 0
275 | 1900-10-02 | 6579 | 0 | 27.6926 | 0
275 | 1900-10-02 | 6580 | 0 | 24.7581 | 0
275 | 1900-10-02 | 6581 | 0 | 41.1436 | 0
275 | 1900-10-02 | 6582 | 0 | 88.9687 | 0
275 | 1900-10-02 | 6583 | 0 | 106.0777 | 0
275 | 1900-10-02 | 6584 | 0 | 85.7812 | 0
275 | 1900-10-02 | 6585 | 0 | 86.687 | 0
275 | 1900-10-02 | 6586 | 0 | 77.746 | 0
275 | 1900-10-02 | 6587 | 0 | 61.2557 | 0
275 | 1900-10-02 | 6588 | 0 | 47.9081 | 0
275 | 1900-10-02 | 6589 | 0 | 264.6452 | 0
275 | 1900-10-02 | 6590 | 0 | 56.1565 | 0
275 | 1900-10-02 | 6591 | 0 | 31.9385 | 0
275 | 1900-10-02 | 6592 | 0 | 47.7342 | 0
275 | 1900-10-02 | 6593 | 0 | 38.8839 | 0
275 | 1900-10-02 | 6594 | 0 | 37.6246 | 0
275 | 1900-10-02 | 6595 | 0 | 40.9393 | 0
275 | 1900-10-02 | 6596 | 0 | 25.3038 | 0
275 | 1900-10-02 | 6597 | 0 | 29.722 | 0
275 | 1900-10-02 | 6598 | 0 | 29.0632 | 0
275 | 1900-10-02 | 6599 | 0 | 26.4501 | 0
275 | 1900-10-02 | 6600 | 0 | 27.53 | 0
276 | 1900-10-03 | 6601 | 0 | 28.6478 | 0
276 | 1900-10-03 | 6602 | 0 | 24.8045 | 0
276 | 1900-10-03 | 6603 | 0 | 35.1009 | 0
276 | 1900-10-03 | 6604 | 0 | 102.3566 | 0
276 | 1900-10-03 | 6605 | 0 | 82.7916 | 0
276 | 1900-10-03 | 6606 | 0 | 82.6633 | 0
276 | 1900-10-03 | 6607 | 0 | 80.2528 | 0
276 | 1900-10-03 | 6608 | 0 | 109.9273 | 0
276 | 1900-10-03 | 6609 | 0 | 105.5288 | 0
276 | 1900-10-03 | 6610 | 0 | 102.7223 | 0
276 | 1900-10-03 | 6611 | 0 | 106.4967 | 0
276 | 1900-10-03 | 6612 | 0 | 60.0013 | 0
276 | 1900-10-03 | 6613 | 0 | 30.0683 | 0
276 | 1900-10-03 | 6614 | 0 | 57.4686 | 0
276 | 1900-10-03 | 6615 | 0 | 123.7531 | 0
276 | 1900-10-03 | 6616 | 0 | 61.2967 | 0
276 | 1900-10-03 | 6617 | 0 | 31.032 | 0
276 | 1900-10-03 | 6618 | 0 | 55.6354 | 0
276 | 1900-10-03 | 6619 | 0 | 98.6316 | 0
276 | 1900-10-03 | 6620 | 0 | 66.6331 | 0
276 | 1900-10-03 | 6621 | 0 | 46.5871 | 0
276 | 1900-10-03 | 6622 | 0 | 35.5015 | 0
276 | 1900-10-03 | 6623 | 0 | 224.579 | 0
276 | 1900-10-03 | 6624 | 0 | 27.1956 | 0
277 | 1900-10-04 | 6625 | 0 | 57.0243 | 0
277 | 1900-10-04 | 6626 | 0 | 109.4374 | 0
277 | 1900-10-04 | 6627 | 0 | 94.5727 | 0
277 | 1900-10-04 | 6628 | 0 | 60.0404 | 0
277 | 1900-10-04 | 6629 | 0 | 80.4637 | 0
277 | 1900-10-04 | 6630 | 0 | 75.5159 | 0
277 | 1900-10-04 | 6631 | 0 | 71.9523 | 0
277 | 1900-10-04 | 6632 | 0 | 68.7829 | 0
277 | 1900-10-04 | 6633 | 0 | 100.0419 | 0
277 | 1900-10-04 | 6634 | 0 | 62.1636 | 0
277 | 1900-10-04 | 6635 | 0 | 89.9436 | 0
277 | 1900-10-04 | 6636 | 0 | 97.45 | 0
277 | 1900-10-04 | 6637 | 0 | 88.4198 | 0
277 | 1900-10-04 | 6638 | 0 | 89.3445 | 0
277 | 1900-10-04 | 6639 | 0 | 66.3591 | 0
277 | 1900-10-04 | 6640 | 0 | 44.3285 | 0
277 | 1900-10-04 | 6641 | 0 | 50.7905 | 0
277 | 1900-10-04 | 6642 | 0 | 56.8575 | 0
277 | 1900-10-04 | 6643 | 0 | 82.0112 | 0
277 | 1900-10-04 | 6644 | 0 | 95.6201 | 0
277 | 1900-10-04 | 6645 | 0 | 100.017 | 0
277 | 1900-10-04 | 6646 | 0 | 87.8228 | 0
277 | 1900-10-04 | 6647 | 0 | 58.3385 | 0
277 | 1900-10-04 | 6648 | 0 | 44.2426 | 0
278 | 1900-10-05 | 6649 | 0 | 25.0061 | 0
278 | 1900-10-05 | 6650 | 0 | 47.4966 | 0
278 | 1900-10-05 | 6651 | 0 | 86.4489 | 0
278 | 1900-10-05 | 6652 | 0 | 72.1047 | 0
278 | 1900-10-05 | 6653 | 0 | 43.5821 | 0
278 | 1900-10-05 | 6654 | 0 | 99.8189 | 0
278 | 1900-10-05 | 6655 | 0 | 92.6283 | 0
278 | 1900-10-05 | 6656 | 0 | 116.0066 | 0
278 | 1900-10-05 | 6657 | 0 | 125.6863 | 0
278 | 1900-10-05 | 6658 | 0 | 126.0469 | 0
278 | 1900-10-05 | 6659 | 0 | 108.2974 | 0
278 | 1900-10-05 | 6660 | 0 | 108.0117 | 0
278 | 1900-10-05 | 6661 | 0 | 99.761 | 0
278 | 1900-10-05 | 6662 | 0 | 44.2145 | 0
278 | 1900-10-05 | 6663 | 0 | 46.2553 | 0
278 | 1900-10-05 | 6664 | 0 | 30.0573 | 0
278 | 1900-10-05 | 6665 | 0 | 33.4672 | 0
278 | 1900-10-05 | 6666 | 0 | 49.7108 | 0
278 | 1900-10-05 | 6667 | 0 | 59.5954 | 0
278 | 1900-10-05 | 6668 | 0 | 22.7898 | 0
278 | 1900-10-05 | 6669 | 0 | 23.2561 | 0
278 | 1900-10-05 | 6670 | 0 | 21.7134 | 0
278 | 1900-10-05 | 6671 | 0 | 31.6697 | 0
278 | 1900-10-05 | 6672 | 0 | 30.4948 | 0
279 | 1900-10-06 | 6673 | 0 | 31.2823 | 0
279 | 1900-10-06 | 6674 | 0 | 30.8606 | 0
279 | 1900-10-06 | 6675 | 0 | 27.7402 | 0
279 | 1900-10-06 | 6676 | 0 | 27.9693 | 0
279 | 1900-10-06 | 6677 | 0 | 31.1947 | 0
279 | 1900-10-06 | 6678 | 0 | 28.588 | 0
279 | 1900-10-06 | 6679 | 0 | 229.5781 | 0
279 | 1900-10-06 | 6680 | 0 | 55.1298 | 0
279 | 1900-10-06 | 6681 | 0 | 47.3007 | 0
279 | 1900-10-06 | 6682 | 0 | 41.0464 | 0
279 | 1900-10-06 | 6683 | 0 | 43.6842 | 0
279 | 1900-10-06 | 6684 | 0 | 237.2647 | 0
279 | 1900-10-06 | 6685 | 0 | 66.3617 | 0
279 | 1900-10-06 | 6686 | 0 | 99.39 | 0
279 | 1900-10-06 | 6687 | 0 | 107.0056 | 0
279 | 1900-10-06 | 6688 | 0 | 83.7201 | 0
279 | 1900-10-06 | 6689 | 0 | 38.7473 | 0
279 | 1900-10-06 | 6690 | 0 | 41.266 | 0
279 | 1900-10-06 | 6691 | 0 | 41.4621 | 0
279 | 1900-10-06 | 6692 | 0 | 30.5734 | 0
279 | 1900-10-06 | 6693 | 0 | 25.8713 | 0
279 | 1900-10-06 | 6694 | 0 | 28.2415 | 0
279 | 1900-10-06 | 6695 | 0 | 30.5958 | 0
279 | 1900-10-06 | 6696 | 0 | 25.812 | 0
280 | 1900-10-07 | 6697 | 0 | 35.0601 | 0
280 | 1900-10-07 | 6698 | 0 | 31.8153 | 0
280 | 1900-10-07 | 6699 | 0 | 28.196 | 0
280 | 1900-10-07 | 6700 | 0 | 30.9344 | 0
280 | 1900-10-07 | 6701 | 0 | 35.4509 | 0
280 | 1900-10-07 | 6702 | 0 | 30.9498 | 0
280 | 1900-10-07 | 6703 | 0 | 39.804 | 0
280 | 1900-10-07 | 6704 | 0 | 95.9802 | 0
280 | 1900-10-07 | 6705 | 0 | 124.1369 | 0
280 | 1900-10-07 | 6706 | 0 | 106.5384 | 0
280 | 1900-10-07 | 6707 | 0 | 57.3217 | 0
280 | 1900-10-07 | 6708 | 0 | 30.3477 | 0
280 | 1900-10-07 | 6709 | 0 | 45.1865 | 0
280 | 1900-10-07 | 6710 | 0 | 41.7967 | 0
280 | 1900-10-07 | 6711 | 0 | 40.3918 | 0
280 | 1900-10-07 | 6712 | 0 | 41.561 | 0
280 | 1900-10-07 | 6713 | 0 | 39.1861 | 0
280 | 1900-10-07 | 6714 | 0 | 44.9535 | 0
280 | 1900-10-07 | 6715 | 0 | 31.2477 | 0
280 | 1900-10-07 | 6716 | 0 | 29.2607 | 0
280 | 1900-10-07 | 6717 | 0 | 30.6979 | 0
280 | 1900-10-07 | 6718 | 0 | 18.6482 | 0
280 | 1900-10-07 | 6719 | 0 | 23.167 | 0
280 | 1900-10-07 | 6720 | 0 | 20.6548 | 0
281 | 1900-10-08 | 6721 | 0 | 32.2396 | 0
281 | 1900-10-08 | 6722 | 0 | 24.6803 | 0
281 | 1900-10-08 | 6723 | 0 | 22.5225 | 0
281 | 1900-10-08 | 6724 | 0 | 26.2137 | 0
281 | 1900-10-08 | 6725 | 0 | 45.6169 | 0
281 | 1900-10-08 | 6726 | 0 | 81.2296 | 0
281 | 1900-10-08 | 6727 | 0 | 101.9977 | 0
281 | 1900-10-08 | 6728 | 0 | 127.8031 | 0
281 | 1900-10-08 | 6729 | 0 | 97.5473 | 0
281 | 1900-10-08 | 6730 | 0 | 108.9171 | 0
281 | 1900-10-08 | 6731 | 0 | 122.5016 | 0
281 | 1900-10-08 | 6732 | 0 | 127.3455 | 0
281 | 1900-10-08 | 6733 | 0 | 132.034 | 0
281 | 1900-10-08 | 6734 | 0 | 115.0116 | 0
281 | 1900-10-08 | 6735 | 0 | 90.4393 | 0
281 | 1900-10-08 | 6736 | 0 | 31.3714 | 0
281 | 1900-10-08 | 6737 | 0 | 44.3942 | 0
281 | 1900-10-08 | 6738 | 0 | 58.1999 | 0
281 | 1900-10-08 | 6739 | 0 | 86.0189 | 0
281 | 1900-10-08 | 6740 | 0 | 74.1496 | 0
281 | 1900-10-08 | 6741 | 0 | 67.8757 | 0
281 | 1900-10-08 | 6742 | 0 | 78.2206 | 0
281 | 1900-10-08 | 6743 | 0 | 73.4571 | 0
281 | 1900-10-08 | 6744 | 0 | 275.0055 | 0
282 | 1900-10-09 | 6745 | 0 | 261.3023 | 0
282 | 1900-10-09 | 6746 | 0 | 68.8372 | 0
282 | 1900-10-09 | 6747 | 0 | 87.1692 | 0
282 | 1900-10-09 | 6748 | 0 | 91.5503 | 0
282 | 1900-10-09 | 6749 | 0 | 42.3462 | 0
282 | 1900-10-09 | 6750 | 0 | 73.0195 | 0
282 | 1900-10-09 | 6751 | 0 | 106.8312 | 0
282 | 1900-10-09 | 6752 | 0 | 109.5161 | 0
282 | 1900-10-09 | 6753 | 0 | 101.2825 | 0
282 | 1900-10-09 | 6754 | 0 | 112.3302 | 0
282 | 1900-10-09 | 6755 | 0 | 82.2131 | 0
282 | 1900-10-09 | 6756 | 0 | 97.1877 | 0
282 | 1900-10-09 | 6757 | 0 | 66.8414 | 0
282 | 1900-10-09 | 6758 | 0 | 89.2571 | 0
282 | 1900-10-09 | 6759 | 0 | 58.6654 | 0
282 | 1900-10-09 | 6760 | 0 | 29.395 | 0
282 | 1900-10-09 | 6761 | 0 | 53.166 | 0
282 | 1900-10-09 | 6762 | 0 | 65.8455 | 0
282 | 1900-10-09 | 6763 | 0 | 94.4104 | 0
282 | 1900-10-09 | 6764 | 0 | 75.2527 | 0
282 | 1900-10-09 | 6765 | 0 | 71.5954 | 0
282 | 1900-10-09 | 6766 | 0 | 85.2848 | 0
282 | 1900-10-09 | 6767 | 0 | 73.2673 | 0
282 | 1900-10-09 | 6768 | 0 | 76.5059 | 0
283 | 1900-10-10 | 6769 | 0 | 105.8105 | 0
283 | 1900-10-10 | 6770 | 0 | 95.4309 | 0
283 | 1900-10-10 | 6771 | 0 | 47.2498 | 0
283 | 1900-10-10 | 6772 | 0 | 39.8842 | 0
283 | 1900-10-10 | 6773 | 0 | 67.5035 | 0
283 | 1900-10-10 | 6774 | 0 | 102.3006 | 0
283 | 1900-10-10 | 6775 | 0 | 98.6476 | 0
283 | 1900-10-10 | 6776 | 0 | 106.452 | 0
283 | 1900-10-10 | 6777 | 0 | 76.1539 | 0
283 | 1900-10-10 | 6778 | 0 | 93.7893 | 0
283 | 1900-10-10 | 6779 | 0 | 72.7299 | 0
283 | 1900-10-10 | 6780 | 0 | 96.2185 | 0
283 | 1900-10-10 | 6781 | 0 | 116.7383 | 0
283 | 1900-10-10 | 6782 | 0 | 108.5786 | 0
283 | 1900-10-10 | 6783 | 0 | 79.5426 | 0
283 | 1900-10-10 | 6784 | 0 | 39.8207 | 0
283 | 1900-10-10 | 6785 | 0 | 49.4039 | 0
283 | 1900-10-10 | 6786 | 0 | 53.3114 | 0
283 | 1900-10-10 | 6787 | 0 | 97.2909 | 0
283 | 1900-10-10 | 6788 | 0 | 108.4403 | 0
283 | 1900-10-10 | 6789 | 0 | 112.8282 | 0
283 | 1900-10-10 | 6790 | 0 | 69.8664 | 0
283 | 1900-10-10 | 6791 | 0 | 69.6438 | 0
283 | 1900-10-10 | 6792 | 0 | 60.682 | 0
284 | 1900-10-11 | 6793 | 0 | 71.3258 | 0
284 | 1900-10-11 | 6794 | 0 | 88.2817 | 0
284 | 1900-10-11 | 6795 | 0 | 110.8697 | 0
284 | 1900-10-11 | 6796 | 0 | 91.3214 | 0
284 | 1900-10-11 | 6797 | 0 | 47.752 | 0
284 | 1900-10-11 | 6798 | 0 | 78.234 | 0
284 | 1900-10-11 | 6799 | 0 | 107.4111 | 0
284 | 1900-10-11 | 6800 | 0 | 103.0789 | 0
284 | 1900-10-11 | 6801 | 0 | 94.1647 | 0
284 | 1900-10-11 | 6802 | 0 | 92.3414 | 0
284 | 1900-10-11 | 6803 | 0 | 109.1009 | 0
284 | 1900-10-11 | 6804 | 0 | 43.5518 | 0
284 | 1900-10-11 | 6805 | 0 | 42.0698 | 0
284 | 1900-10-11 | 6806 | 0 | 256.5299 | 0
284 | 1900-10-11 | 6807 | 0 | 69.1379 | 0
284 | 1900-10-11 | 6808 | 0 | 78.8561 | 0
284 | 1900-10-11 | 6809 | 0 | 70.059 | 0
284 | 1900-10-11 | 6810 | 0 | 53.192 | 0
284 | 1900-10-11 | 6811 | 0 | 75.068 | 0
284 | 1900-10-11 | 6812 | 0 | 63.4777 | 0
284 | 1900-10-11 | 6813 | 0 | 78.0376 | 0
284 | 1900-10-11 | 6814 | 0 | 79.834 | 0
284 | 1900-10-11 | 6815 | 0 | 43.1868 | 0
284 | 1900-10-11 | 6816 | 0 | 47.7848 | 0
285 | 1900-10-12 | 6817 | 0 | 75.4514 | 0
285 | 1900-10-12 | 6818 | 0 | 78.9944 | 0
285 | 1900-10-12 | 6819 | 0 | 58.214 | 0
285 | 1900-10-12 | 6820 | 0 | 37.2265 | 0
285 | 1900-10-12 | 6821 | 0 | 39.203 | 0
285 | 1900-10-12 | 6822 | 0 | 73.5 | 0
285 | 1900-10-12 | 6823 | 0 | 89.3759 | 0
285 | 1900-10-12 | 6824 | 0 | 93.5237 | 0
285 | 1900-10-12 | 6825 | 0 | 101.2757 | 0
285 | 1900-10-12 | 6826 | 0 | 320.9139 | 0
285 | 1900-10-12 | 6827 | 0 | 97.761 | 0
285 | 1900-10-12 | 6828 | 0 | 68.0732 | 0
285 | 1900-10-12 | 6829 | 0 | 46.8534 | 0
285 | 1900-10-12 | 6830 | 0 | 56.0753 | 0
285 | 1900-10-12 | 6831 | 0 | 38.4401 | 0
285 | 1900-10-12 | 6832 | 0 | 41.7113 | 0
285 | 1900-10-12 | 6833 | 0 | 38.0008 | 0
285 | 1900-10-12 | 6834 | 0 | 47.2161 | 0
285 | 1900-10-12 | 6835 | 0 | 53.4196 | 0
285 | 1900-10-12 | 6836 | 0 | 79.3618 | 0
285 | 1900-10-12 | 6837 | 0 | 91.8809 | 0
285 | 1900-10-12 | 6838 | 0 | 83.3107 | 0
285 | 1900-10-12 | 6839 | 0 | 27.8419 | 0
285 | 1900-10-12 | 6840 | 0 | 27.6311 | 0
286 | 1900-10-13 | 6841 | 0 | 29.4128 | 0
286 | 1900-10-13 | 6842 | 0 | 37.0411 | 0
286 | 1900-10-13 | 6843 | 0 | 32.5209 | 0
286 | 1900-10-13 | 6844 | 0 | 19.528 | 0
286 | 1900-10-13 | 6845 | 0 | 25.4331 | 0
286 | 1900-10-13 | 6846 | 0 | 25.9187 | 0
286 | 1900-10-13 | 6847 | 0 | 24.9353 | 0
286 | 1900-10-13 | 6848 | 0 | 49.0059 | 0
286 | 1900-10-13 | 6849 | 0 | 36.6588 | 0
286 | 1900-10-13 | 6850 | 0 | 57.383 | 0
286 | 1900-10-13 | 6851 | 0 | 50.9432 | 0
286 | 1900-10-13 | 6852 | 0 | 31.6605 | 0
286 | 1900-10-13 | 6853 | 0 | 40.3319 | 0
286 | 1900-10-13 | 6854 | 0 | 48.6643 | 0
286 | 1900-10-13 | 6855 | 0 | 45.4995 | 0
286 | 1900-10-13 | 6856 | 0 | 47.4845 | 0
286 | 1900-10-13 | 6857 | 0 | 38.0533 | 0
286 | 1900-10-13 | 6858 | 0 | 33.2022 | 0
286 | 1900-10-13 | 6859 | 0 | 32.2221 | 0
286 | 1900-10-13 | 6860 | 0 | 27.0654 | 0
286 | 1900-10-13 | 6861 | 0 | 32.2988 | 0
286 | 1900-10-13 | 6862 | 0 | 33.5457 | 0
286 | 1900-10-13 | 6863 | 0 | 26.7175 | 0
286 | 1900-10-13 | 6864 | 0 | 22.2721 | 0
287 | 1900-10-14 | 6865 | 0 | 24.1269 | 0
287 | 1900-10-14 | 6866 | 0 | 29.1807 | 0
287 | 1900-10-14 | 6867 | 0 | 233.2477 | 0
287 | 1900-10-14 | 6868 | 0 | 29.4275 | 0
287 | 1900-10-14 | 6869 | 0 | 22.974 | 0
287 | 1900-10-14 | 6870 | 0 | 24.9233 | 0
287 | 1900-10-14 | 6871 | 0 | 27.0545 | 0
287 | 1900-10-14 | 6872 | 0 | 45.4109 | 0
287 | 1900-10-14 | 6873 | 0 | 50.7082 | 0
287 | 1900-10-14 | 6874 | 0 | 45.1979 | 0
287 | 1900-10-14 | 6875 | 0 | 50.1146 | 0
287 | 1900-10-14 | 6876 | 0 | 44.3795 | 0
287 | 1900-10-14 | 6877 | 0 | 39.979 | 0
287 | 1900-10-14 | 6878 | 0 | 44.5485 | 0
287 | 1900-10-14 | 6879 | 0 | 33.6414 | 0
287 | 1900-10-14 | 6880 | 0 | 40.3088 | 0
287 | 1900-10-14 | 6881 | 0 | 38.3995 | 0
287 | 1900-10-14 | 6882 | 0 | 51.1125 | 0
287 | 1900-10-14 | 6883 | 0 | 48.7622 | 0
287 | 1900-10-14 | 6884 | 0 | 22.0641 | 0
287 | 1900-10-14 | 6885 | 0 | 26.4867 | 0
287 | 1900-10-14 | 6886 | 0 | 28.6705 | 0
287 | 1900-10-14 | 6887 | 0 | 26.0404 | 0
287 | 1900-10-14 | 6888 | 0 | 29.8253 | 0
288 | 1900-10-15 | 6889 | 0 | 30.3024 | 0
288 | 1900-10-15 | 6890 | 0 | 36.0228 | 0
288 | 1900-10-15 | 6891 | 0 | 24.7591 | 0
288 | 1900-10-15 | 6892 | 0 | 40.7969 | 0
288 | 1900-10-15 | 6893 | 0 | 111.3337 | 0
288 | 1900-10-15 | 6894 | 0 | 69.6671 | 0
288 | 1900-10-15 | 6895 | 0 | 37.127 | 0
288 | 1900-10-15 | 6896 | 0 | 67.6624 | 0
288 | 1900-10-15 | 6897 | 0 | 40.881 | 0
288 | 1900-10-15 | 6898 | 0 | 45.3446 | 0
288 | 1900-10-15 | 6899 | 0 | 62.3046 | 0
288 | 1900-10-15 | 6900 | 0 | 104.4882 | 0
288 | 1900-10-15 | 6901 | 0 | 51.13 | 0
288 | 1900-10-15 | 6902 | 0 | 45.1363 | 0
288 | 1900-10-15 | 6903 | 0 | 47.2666 | 0
288 | 1900-10-15 | 6904 | 0 | 37.2904 | 0
288 | 1900-10-15 | 6905 | 0 | 45.044 | 0
288 | 1900-10-15 | 6906 | 0 | 82.7858 | 0
288 | 1900-10-15 | 6907 | 0 | 100.2412 | 0
288 | 1900-10-15 | 6908 | 0 | 67.248 | 0
288 | 1900-10-15 | 6909 | 0 | 90.3573 | 0
288 | 1900-10-15 | 6910 | 0 | 86.7187 | 0
288 | 1900-10-15 | 6911 | 0 | 74.6858 | 0
288 | 1900-10-15 | 6912 | 0 | 63.3195 | 0
289 | 1900-10-16 | 6913 | 0 | 107.4662 | 0
289 | 1900-10-16 | 6914 | 0 | 92.3769 | 0
289 | 1900-10-16 | 6915 | 0 | 63.0677 | 0
289 | 1900-10-16 | 6916 | 0 | 26.9963 | 0
289 | 1900-10-16 | 6917 | 0 | 33.4624 | 0
289 | 1900-10-16 | 6918 | 0 | 62.8829 | 0
289 | 1900-10-16 | 6919 | 0 | 108.0447 | 0
289 | 1900-10-16 | 6920 | 0 | 82.6931 | 0
289 | 1900-10-16 | 6921 | 0 | 37.1581 | 0
289 | 1900-10-16 | 6922 | 0 | 42.2265 | 0
289 | 1900-10-16 | 6923 | 0 | 77.7593 | 0
289 | 1900-10-16 | 6924 | 0 | 96.5712 | 0
289 | 1900-10-16 | 6925 | 0 | 43.4895 | 0
289 | 1900-10-16 | 6926 | 0 | 38.9228 | 0
289 | 1900-10-16 | 6927 | 0 | 40.964 | 0
289 | 1900-10-16 | 6928 | 0 | 236.2797 | 0
289 | 1900-10-16 | 6929 | 0 | 275.3281 | 0
289 | 1900-10-16 | 6930 | 0 | 109.9525 | 0
289 | 1900-10-16 | 6931 | 0 | 92.2558 | 0
289 | 1900-10-16 | 6932 | 0 | 90.4645 | 0
289 | 1900-10-16 | 6933 | 0 | 85.8277 | 0
289 | 1900-10-16 | 6934 | 0 | 66.5479 | 0
289 | 1900-10-16 | 6935 | 0 | 57.905 | 0
289 | 1900-10-16 | 6936 | 0 | 96.4796 | 0
290 | 1900-10-17 | 6937 | 0 | 113.5725 | 0
290 | 1900-10-17 | 6938 | 0 | 52.2683 | 0
290 | 1900-10-17 | 6939 | 0 | 37.4909 | 0
290 | 1900-10-17 | 6940 | 0 | 31.1444 | 0
290 | 1900-10-17 | 6941 | 0 | 29.3703 | 0
290 | 1900-10-17 | 6942 | 0 | 29.4322 | 0
290 | 1900-10-17 | 6943 | 0 | 71.8366 | 0
290 | 1900-10-17 | 6944 | 0 | 93.7782 | 0
290 | 1900-10-17 | 6945 | 0 | 110.9527 | 0
290 | 1900-10-17 | 6946 | 0 | 82.8986 | 0
290 | 1900-10-17 | 6947 | 0 | 41.8344 | 0
290 | 1900-10-17 | 6948 | 0 | 56.6674 | 0
290 | 1900-10-17 | 6949 | 0 | 44.9013 | 0
290 | 1900-10-17 | 6950 | 0 | 36.5082 | 0
290 | 1900-10-17 | 6951 | 0 | 43.7947 | 0
290 | 1900-10-17 | 6952 | 0 | 48.6596 | 0
290 | 1900-10-17 | 6953 | 0 | 79.0277 | 0
290 | 1900-10-17 | 6954 | 0 | 93.4729 | 0
290 | 1900-10-17 | 6955 | 0 | 127.0397 | 0
290 | 1900-10-17 | 6956 | 0 | 103.3304 | 0
290 | 1900-10-17 | 6957 | 0 | 97.3051 | 0
290 | 1900-10-17 | 6958 | 0 | 84.0085 | 0
290 | 1900-10-17 | 6959 | 0 | 84.0885 | 0
290 | 1900-10-17 | 6960 | 0 | 97.001 | 0
291 | 1900-10-18 | 6961 | 0 | 129.0499 | 0
291 | 1900-10-18 | 6962 | 0 | 104.092 | 0
291 | 1900-10-18 | 6963 | 0 | 73.1131 | 0
291 | 1900-10-18 | 6964 | 0 | 30.3901 | 0
291 | 1900-10-18 | 6965 | 0 | 36.4985 | 0
291 | 1900-10-18 | 6966 | 0 | 59.4287 | 0
291 | 1900-10-18 | 6967 | 0 | 89.893 | 0
291 | 1900-10-18 | 6968 | 0 | 96.1366 | 0
291 | 1900-10-18 | 6969 | 0 | 57.9906 | 0
291 | 1900-10-18 | 6970 | 0 | 59.4976 | 0
291 | 1900-10-18 | 6971 | 0 | 127.7656 | 0
291 | 1900-10-18 | 6972 | 0 | 110.1458 | 0
291 | 1900-10-18 | 6973 | 0 | 71.6136 | 0
291 | 1900-10-18 | 6974 | 0 | 36.8127 | 0
291 | 1900-10-18 | 6975 | 0 | 40.2571 | 0
291 | 1900-10-18 | 6976 | 0 | 41.9283 | 0
291 | 1900-10-18 | 6977 | 0 | 80.144 | 0
291 | 1900-10-18 | 6978 | 0 | 99.8417 | 0
291 | 1900-10-18 | 6979 | 0 | 118.3985 | 0
291 | 1900-10-18 | 6980 | 0 | 86.9874 | 0
291 | 1900-10-18 | 6981 | 0 | 97.7075 | 0
291 | 1900-10-18 | 6982 | 0 | 88.2325 | 0
291 | 1900-10-18 | 6983 | 0 | 92.1281 | 0
291 | 1900-10-18 | 6984 | 0 | 73.2527 | 0
292 | 1900-10-19 | 6985 | 0 | 111.8526 | 0
292 | 1900-10-19 | 6986 | 0 | 104.9194 | 0
292 | 1900-10-19 | 6987 | 0 | 77.4857 | 0
292 | 1900-10-19 | 6988 | 0 | 26.6706 | 0
292 | 1900-10-19 | 6989 | 0 | 32.9224 | 0
292 | 1900-10-19 | 6990 | 0 | 58.0467 | 0
292 | 1900-10-19 | 6991 | 0 | 256.3952 | 0
292 | 1900-10-19 | 6992 | 0 | 61.3403 | 0
292 | 1900-10-19 | 6993 | 0 | 92.2685 | 0
292 | 1900-10-19 | 6994 | 0 | 77.8759 | 0
292 | 1900-10-19 | 6995 | 0 | 43.2943 | 0
292 | 1900-10-19 | 6996 | 0 | 50.5996 | 0
292 | 1900-10-19 | 6997 | 0 | 233.5323 | 0
292 | 1900-10-19 | 6998 | 0 | 35.6299 | 0
292 | 1900-10-19 | 6999 | 0 | 41.9257 | 0
292 | 1900-10-19 | 7000 | 0 | 42.7631 | 0
292 | 1900-10-19 | 7001 | 0 | 43.9162 | 0
292 | 1900-10-19 | 7002 | 0 | 48.4675 | 0
292 | 1900-10-19 | 7003 | 0 | 48.302 | 0
292 | 1900-10-19 | 7004 | 0 | 22.3415 | 0
292 | 1900-10-19 | 7005 | 0 | 28.8539 | 0
292 | 1900-10-19 | 7006 | 0 | 26.0853 | 0
292 | 1900-10-19 | 7007 | 0 | 32.3885 | 0
292 | 1900-10-19 | 7008 | 0 | 30.9539 | 0
293 | 1900-10-20 | 7009 | 0 | 29.4739 | 0
293 | 1900-10-20 | 7010 | 0 | 24.9906 | 0
293 | 1900-10-20 | 7011 | 0 | 24.1783 | 0
293 | 1900-10-20 | 7012 | 0 | 32.9888 | 0
293 | 1900-10-20 | 7013 | 0 | 59.8491 | 0
293 | 1900-10-20 | 7014 | 0 | 78.448 | 0
293 | 1900-10-20 | 7015 | 0 | 59.1858 | 0
293 | 1900-10-20 | 7016 | 0 | 36.5546 | 0
293 | 1900-10-20 | 7017 | 0 | 42.2579 | 0
293 | 1900-10-20 | 7018 | 0 | 37.6022 | 0
293 | 1900-10-20 | 7019 | 0 | 37.8842 | 0
293 | 1900-10-20 | 7020 | 0 | 44.2301 | 0
293 | 1900-10-20 | 7021 | 0 | 37.3519 | 0
293 | 1900-10-20 | 7022 | 0 | 42.28 | 0
293 | 1900-10-20 | 7023 | 0 | 40.7745 | 0
293 | 1900-10-20 | 7024 | 0 | 38.834 | 0
293 | 1900-10-20 | 7025 | 0 | 36.2922 | 0
293 | 1900-10-20 | 7026 | 0 | 32.8364 | 0
293 | 1900-10-20 | 7027 | 0 | 50.3601 | 0
293 | 1900-10-20 | 7028 | 0 | 31.0844 | 0
293 | 1900-10-20 | 7029 | 0 | 31.0859 | 0
293 | 1900-10-20 | 7030 | 0 | 28.0035 | 0
293 | 1900-10-20 | 7031 | 0 | 24.2706 | 0
293 | 1900-10-20 | 7032 | 0 | 24.0249 | 0
294 | 1900-10-21 | 7033 | 0 | 24.115 | 0
294 | 1900-10-21 | 7034 | 0 | 26.6407 | 0
294 | 1900-10-21 | 7035 | 0 | 26.0407 | 0
294 | 1900-10-21 | 7036 | 0 | 32.6589 | 0
294 | 1900-10-21 | 7037 | 0 | 27.2326 | 0
294 | 1900-10-21 | 7038 | 0 | 26.1635 | 0
294 | 1900-10-21 | 7039 | 0 | 29.5122 | 0
294 | 1900-10-21 | 7040 | 0 | 47.5376 | 0
294 | 1900-10-21 | 7041 | 0 | 37.5792 | 0
294 | 1900-10-21 | 7042 | 0 | 41.5015 | 0
294 | 1900-10-21 | 7043 | 0 | 44.5524 | 0
294 | 1900-10-21 | 7044 | 0 | 44.2604 | 0
294 | 1900-10-21 | 7045 | 0 | 43.2611 | 0
294 | 1900-10-21 | 7046 | 0 | 49.197 | 0
294 | 1900-10-21 | 7047 | 0 | 37.2394 | 0
294 | 1900-10-21 | 7048 | 0 | 38.9525 | 0
294 | 1900-10-21 | 7049 | 0 | 35.2611 | 0
294 | 1900-10-21 | 7050 | 0 | 31.2298 | 0
294 | 1900-10-21 | 7051 | 0 | 41.8899 | 0
294 | 1900-10-21 | 7052 | 0 | 223.2946 | 0
294 | 1900-10-21 | 7053 | 0 | 26.9843 | 0
294 | 1900-10-21 | 7054 | 0 | 22.5587 | 0
294 | 1900-10-21 | 7055 | 0 | 30.7523 | 0
294 | 1900-10-21 | 7056 | 0 | 36.2401 | 0
295 | 1900-10-22 | 7057 | 0 | 34.5315 | 0
295 | 1900-10-22 | 7058 | 0 | 41.1613 | 0
295 | 1900-10-22 | 7059 | 0 | 77.0778 | 0
295 | 1900-10-22 | 7060 | 0 | 115.3156 | 0
295 | 1900-10-22 | 7061 | 0 | 120.2782 | 0
295 | 1900-10-22 | 7062 | 0 | 117.6863 | 0
295 | 1900-10-22 | 7063 | 0 | 90.3953 | 0
295 | 1900-10-22 | 7064 | 0 | 100.0508 | 0
295 | 1900-10-22 | 7065 | 0 | 275.8789 | 0
295 | 1900-10-22 | 7066 | 0 | 79.562 | 0
295 | 1900-10-22 | 7067 | 0 | 80.0349 | 0
295 | 1900-10-22 | 7068 | 0 | 56.3781 | 0
295 | 1900-10-22 | 7069 | 0 | 53.7609 | 0
295 | 1900-10-22 | 7070 | 0 | 40.3442 | 0
295 | 1900-10-22 | 7071 | 0 | 39.426 | 0
295 | 1900-10-22 | 7072 | 0 | 44.965 | 0
295 | 1900-10-22 | 7073 | 0 | 66.983 | 0
295 | 1900-10-22 | 7074 | 0 | 96.2913 | 0
295 | 1900-10-22 | 7075 | 0 | 83.3952 | 0
295 | 1900-10-22 | 7076 | 0 | 106.9137 | 0
295 | 1900-10-22 | 7077 | 0 | 104.7247 | 0
295 | 1900-10-22 | 7078 | 0 | 92.9951 | 0
295 | 1900-10-22 | 7079 | 0 | 110.4703 | 0
295 | 1900-10-22 | 7080 | 0 | 109.7133 | 0
296 | 1900-10-23 | 7081 | 0 | 100.5691 | 0
296 | 1900-10-23 | 7082 | 0 | 58.4109 | 0
296 | 1900-10-23 | 7083 | 0 | 24.2775 | 0
296 | 1900-10-23 | 7084 | 0 | 29.237 | 0
296 | 1900-10-23 | 7085 | 0 | 42.0361 | 0
296 | 1900-10-23 | 7086 | 0 | 107.4987 | 0
296 | 1900-10-23 | 7087 | 0 | 125.1582 | 0
296 | 1900-10-23 | 7088 | 0 | 126.2127 | 0
296 | 1900-10-23 | 7089 | 0 | 128.41 | 0
296 | 1900-10-23 | 7090 | 0 | 113.0826 | 0
296 | 1900-10-23 | 7091 | 0 | 113.9671 | 0
296 | 1900-10-23 | 7092 | 0 | 93.8515 | 0
296 | 1900-10-23 | 7093 | 0 | 63.9301 | 0
296 | 1900-10-23 | 7094 | 0 | 52.4764 | 0
296 | 1900-10-23 | 7095 | 0 | 33.3966 | 0
296 | 1900-10-23 | 7096 | 0 | 52.1502 | 0
296 | 1900-10-23 | 7097 | 0 | 72.5284 | 0
296 | 1900-10-23 | 7098 | 0 | 110.0269 | 0
296 | 1900-10-23 | 7099 | 0 | 112.8699 | 0
296 | 1900-10-23 | 7100 | 0 | 106.5424 | 0
296 | 1900-10-23 | 7101 | 0 | 101.1638 | 0
296 | 1900-10-23 | 7102 | 0 | 90.0524 | 0
296 | 1900-10-23 | 7103 | 0 | 91.3523 | 0
296 | 1900-10-23 | 7104 | 0 | 117.7389 | 0
297 | 1900-10-24 | 7105 | 0 | 111.8269 | 0
297 | 1900-10-24 | 7106 | 0 | 59.5244 | 0
297 | 1900-10-24 | 7107 | 0 | 23.2677 | 0
297 | 1900-10-24 | 7108 | 0 | 27.7044 | 0
297 | 1900-10-24 | 7109 | 0 | 46.1264 | 0
297 | 1900-10-24 | 7110 | 0 | 71.1711 | 0
297 | 1900-10-24 | 7111 | 0 | 97.5824 | 0
297 | 1900-10-24 | 7112 | 0 | 101.8322 | 0
297 | 1900-10-24 | 7113 | 0 | 313.8741 | 0
297 | 1900-10-24 | 7114 | 0 | 99.4261 | 0
297 | 1900-10-24 | 7115 | 0 | 103.5716 | 0
297 | 1900-10-24 | 7116 | 0 | 101.9813 | 0
297 | 1900-10-24 | 7117 | 0 | 76.7545 | 0
297 | 1900-10-24 | 7118 | 0 | 76.1049 | 0
297 | 1900-10-24 | 7119 | 0 | 52.166 | 0
297 | 1900-10-24 | 7120 | 0 | 43.1708 | 0
297 | 1900-10-24 | 7121 | 0 | 75.1744 | 0
297 | 1900-10-24 | 7122 | 0 | 114.7315 | 0
297 | 1900-10-24 | 7123 | 0 | 83.9702 | 0
297 | 1900-10-24 | 7124 | 0 | 100.0058 | 0
297 | 1900-10-24 | 7125 | 0 | 103.6693 | 0
297 | 1900-10-24 | 7126 | 0 | 105.0101 | 0
297 | 1900-10-24 | 7127 | 0 | 105.4692 | 0
297 | 1900-10-24 | 7128 | 0 | 116.8436 | 0
298 | 1900-10-25 | 7129 | 0 | 106.9096 | 0
298 | 1900-10-25 | 7130 | 0 | 63.1901 | 0
298 | 1900-10-25 | 7131 | 0 | 33.81 | 0
298 | 1900-10-25 | 7132 | 0 | 35.8182 | 0
298 | 1900-10-25 | 7133 | 0 | 40.564 | 0
298 | 1900-10-25 | 7134 | 0 | 107.2209 | 0
298 | 1900-10-25 | 7135 | 0 | 281.4391 | 0
298 | 1900-10-25 | 7136 | 0 | 79.9946 | 0
298 | 1900-10-25 | 7137 | 0 | 117.2658 | 0
298 | 1900-10-25 | 7138 | 0 | 88.4963 | 0
298 | 1900-10-25 | 7139 | 0 | 95.4759 | 0
298 | 1900-10-25 | 7140 | 0 | 45.9221 | 0
298 | 1900-10-25 | 7141 | 0 | 53.1132 | 0
298 | 1900-10-25 | 7142 | 0 | 51.7072 | 0
298 | 1900-10-25 | 7143 | 0 | 45.0031 | 0
298 | 1900-10-25 | 7144 | 0 | 42.9198 | 0
298 | 1900-10-25 | 7145 | 0 | 57.1109 | 0
298 | 1900-10-25 | 7146 | 0 | 126.3343 | 0
298 | 1900-10-25 | 7147 | 0 | 116.3737 | 0
298 | 1900-10-25 | 7148 | 0 | 96.0694 | 0
298 | 1900-10-25 | 7149 | 0 | 104.0003 | 0
298 | 1900-10-25 | 7150 | 0 | 95.6537 | 0
298 | 1900-10-25 | 7151 | 0 | 114.0766 | 0
298 | 1900-10-25 | 7152 | 0 | 96.9344 | 0
299 | 1900-10-26 | 7153 | 0 | 99.0131 | 0
299 | 1900-10-26 | 7154 | 0 | 116.5272 | 0
299 | 1900-10-26 | 7155 | 0 | 110.9908 | 0
299 | 1900-10-26 | 7156 | 0 | 54.0644 | 0
299 | 1900-10-26 | 7157 | 0 | 47.3788 | 0
299 | 1900-10-26 | 7158 | 0 | 99.3221 | 0
299 | 1900-10-26 | 7159 | 0 | 77.4945 | 0
299 | 1900-10-26 | 7160 | 0 | 95.1363 | 0
299 | 1900-10-26 | 7161 | 0 | 100.2717 | 0
299 | 1900-10-26 | 7162 | 0 | 87.9393 | 0
299 | 1900-10-26 | 7163 | 0 | 55.0155 | 0
299 | 1900-10-26 | 7164 | 0 | 38.1132 | 0
299 | 1900-10-26 | 7165 | 0 | 38.0873 | 0
299 | 1900-10-26 | 7166 | 0 | 39.402 | 0
299 | 1900-10-26 | 7167 | 0 | 35.8612 | 0
299 | 1900-10-26 | 7168 | 0 | 45.7346 | 0
299 | 1900-10-26 | 7169 | 0 | 34.6347 | 0
299 | 1900-10-26 | 7170 | 0 | 49.8154 | 0
299 | 1900-10-26 | 7171 | 0 | 42.5464 | 0
299 | 1900-10-26 | 7172 | 0 | 34.5287 | 0
299 | 1900-10-26 | 7173 | 0 | 29.3466 | 0
299 | 1900-10-26 | 7174 | 0 | 233.1363 | 0
299 | 1900-10-26 | 7175 | 0 | 28.9788 | 0
299 | 1900-10-26 | 7176 | 0 | 26.4533 | 0
300 | 1900-10-27 | 7177 | 0 | 32.4034 | 0
300 | 1900-10-27 | 7178 | 0 | 26.0941 | 0
300 | 1900-10-27 | 7179 | 0 | 29.3239 | 0
300 | 1900-10-27 | 7180 | 0 | 26.43 | 0
300 | 1900-10-27 | 7181 | 0 | 28.7398 | 0
300 | 1900-10-27 | 7182 | 0 | 22.2975 | 0
300 | 1900-10-27 | 7183 | 0 | 31.2356 | 0
300 | 1900-10-27 | 7184 | 0 | 40.6398 | 0
300 | 1900-10-27 | 7185 | 0 | 48.5771 | 0
300 | 1900-10-27 | 7186 | 0 | 42.1429 | 0
300 | 1900-10-27 | 7187 | 0 | 24.6166 | 0
300 | 1900-10-27 | 7188 | 0 | 43.3395 | 0
300 | 1900-10-27 | 7189 | 0 | 37.3828 | 0
300 | 1900-10-27 | 7190 | 0 | 52.6353 | 0
300 | 1900-10-27 | 7191 | 0 | 34.5462 | 0
300 | 1900-10-27 | 7192 | 0 | 33.8554 | 0
300 | 1900-10-27 | 7193 | 0 | 49.1857 | 0
300 | 1900-10-27 | 7194 | 0 | 247.8575 | 0
300 | 1900-10-27 | 7195 | 0 | 33.678 | 0
300 | 1900-10-27 | 7196 | 0 | 25.3151 | 0
300 | 1900-10-27 | 7197 | 0 | 23.8891 | 0
300 | 1900-10-27 | 7198 | 0 | 29.1804 | 0
300 | 1900-10-27 | 7199 | 0 | 28.3537 | 0
300 | 1900-10-27 | 7200 | 0 | 18.9772 | 0
301 | 1900-10-28 | 7201 | 0 | 25.7376 | 0
301 | 1900-10-28 | 7202 | 0 | 26.595 | 0
301 | 1900-10-28 | 7203 | 0 | 37.069 | 0
301 | 1900-10-28 | 7204 | 0 | 28.1545 | 0
301 | 1900-10-28 | 7205 | 0 | 34.6607 | 0
301 | 1900-10-28 | 7206 | 0 | 78.9795 | 0
301 | 1900-10-28 | 7207 | 0 | 124.9615 | 0
301 | 1900-10-28 | 7208 | 0 | 126.881 | 0
301 | 1900-10-28 | 7209 | 0 | 134.353 | 0
301 | 1900-10-28 | 7210 | 0 | 94.5451 | 0
301 | 1900-10-28 | 7211 | 0 | 53.5131 | 0
301 | 1900-10-28 | 7212 | 0 | 38.9138 | 0
301 | 1900-10-28 | 7213 | 0 | 66.1475 | 0
301 | 1900-10-28 | 7214 | 0 | 128.2643 | 0
301 | 1900-10-28 | 7215 | 0 | 41.3978 | 0
301 | 1900-10-28 | 7216 | 0 | 71.427 | 0
301 | 1900-10-28 | 7217 | 0 | 123.5952 | 0
301 | 1900-10-28 | 7218 | 0 | 106.2819 | 0
301 | 1900-10-28 | 7219 | 0 | 33.5464 | 0
301 | 1900-10-28 | 7220 | 0 | 28.3862 | 0
301 | 1900-10-28 | 7221 | 0 | 29.5488 | 0
301 | 1900-10-28 | 7222 | 0 | 39.9719 | 0
301 | 1900-10-28 | 7223 | 0 | 30.5866 | 0
301 | 1900-10-28 | 7224 | 0 | 219.792 | 0
302 | 1900-10-29 | 7225 | 0 | 29.838 | 0
302 | 1900-10-29 | 7226 | 0 | 27.1719 | 0
302 | 1900-10-29 | 7227 | 0 | 21.755 | 0
302 | 1900-10-29 | 7228 | 0 | 29.5593 | 0
302 | 1900-10-29 | 7229 | 0 | 31.4505 | 0
302 | 1900-10-29 | 7230 | 0 | 32.4684 | 0
302 | 1900-10-29 | 7231 | 0 | 18.938 | 0
302 | 1900-10-29 | 7232 | 0 | 41.863 | 0
302 | 1900-10-29 | 7233 | 0 | 49.5587 | 0
302 | 1900-10-29 | 7234 | 0 | 69.0118 | 0
302 | 1900-10-29 | 7235 | 0 | 56.4516 | 0
302 | 1900-10-29 | 7236 | 0 | 311.1843 | 0
302 | 1900-10-29 | 7237 | 0 | 91.4743 | 0
302 | 1900-10-29 | 7238 | 0 | 60.0321 | 0
302 | 1900-10-29 | 7239 | 0 | 50.1345 | 0
302 | 1900-10-29 | 7240 | 0 | 29.1904 | 0
302 | 1900-10-29 | 7241 | 0 | 41.4236 | 0
302 | 1900-10-29 | 7242 | 0 | 35.9983 | 0
302 | 1900-10-29 | 7243 | 0 | 38.3253 | 0
302 | 1900-10-29 | 7244 | 0 | 35.4851 | 0
302 | 1900-10-29 | 7245 | 0 | 34.1003 | 0
302 | 1900-10-29 | 7246 | 0 | 21.3491 | 0
302 | 1900-10-29 | 7247 | 0 | 26.8991 | 0
302 | 1900-10-29 | 7248 | 0 | 20.7257 | 0
303 | 1900-10-30 | 7249 | 0 | 35.9204 | 0
303 | 1900-10-30 | 7250 | 0 | 19.5208 | 0
303 | 1900-10-30 | 7251 | 0 | 18.6993 | 0
303 | 1900-10-30 | 7252 | 0 | 28.5435 | 0
303 | 1900-10-30 | 7253 | 0 | 229.0389 | 0
303 | 1900-10-30 | 7254 | 0 | 51.7201 | 0
303 | 1900-10-30 | 7255 | 0 | 119.9693 | 0
303 | 1900-10-30 | 7256 | 0 | 109.5874 | 0
303 | 1900-10-30 | 7257 | 0 | 105.1054 | 0
303 | 1900-10-30 | 7258 | 0 | 133.5301 | 0
303 | 1900-10-30 | 7259 | 0 | 123.8531 | 0
303 | 1900-10-30 | 7260 | 0 | 111.7745 | 0
303 | 1900-10-30 | 7261 | 0 | 86.2821 | 0
303 | 1900-10-30 | 7262 | 0 | 109.019 | 0
303 | 1900-10-30 | 7263 | 0 | 103.2956 | 0
303 | 1900-10-30 | 7264 | 0 | 75.9642 | 0
303 | 1900-10-30 | 7265 | 0 | 43.0179 | 0
303 | 1900-10-30 | 7266 | 0 | 42.3062 | 0
303 | 1900-10-30 | 7267 | 0 | 37.3745 | 0
303 | 1900-10-30 | 7268 | 0 | 27.3937 | 0
303 | 1900-10-30 | 7269 | 0 | 30.8161 | 0
303 | 1900-10-30 | 7270 | 0 | 33.1834 | 0
303 | 1900-10-30 | 7271 | 0 | 27.3514 | 0
303 | 1900-10-30 | 7272 | 0 | 31.4089 | 0
304 | 1900-10-31 | 7273 | 0 | 25.3325 | 0
304 | 1900-10-31 | 7274 | 0 | 25.6153 | 0
304 | 1900-10-31 | 7275 | 0 | 24.1831 | 0
304 | 1900-10-31 | 7276 | 0 | 25.0701 | 0
304 | 1900-10-31 | 7277 | 0 | 31.063 | 0
304 | 1900-10-31 | 7278 | 0 | 41.6125 | 0
304 | 1900-10-31 | 7279 | 0 | 107.4451 | 0
304 | 1900-10-31 | 7280 | 0 | 132.3404 | 0
304 | 1900-10-31 | 7281 | 0 | 90.1291 | 0
304 | 1900-10-31 | 7282 | 0 | 48.8946 | 0
304 | 1900-10-31 | 7283 | 0 | 57.7205 | 0
304 | 1900-10-31 | 7284 | 0 | 80.4198 | 0
304 | 1900-10-31 | 7285 | 0 | 105.9132 | 0
304 | 1900-10-31 | 7286 | 0 | 125.4248 | 0
304 | 1900-10-31 | 7287 | 0 | 71.7002 | 0
304 | 1900-10-31 | 7288 | 0 | 37.8236 | 0
304 | 1900-10-31 | 7289 | 0 | 44.1697 | 0
304 | 1900-10-31 | 7290 | 0 | 44.1381 | 0
304 | 1900-10-31 | 7291 | 0 | 49.9644 | 0
304 | 1900-10-31 | 7292 | 0 | 27.544 | 0
304 | 1900-10-31 | 7293 | 0 | 25.7924 | 0
304 | 1900-10-31 | 7294 | 0 | 32.8468 | 0
304 | 1900-10-31 | 7295 | 0 | 28.7697 | 0
304 | 1900-10-31 | 7296 | 0 | 235.2303 | 0
305 | 1900-11-01 | 7297 | 0 | 29.9476 | 0
305 | 1900-11-01 | 7298 | 0 | 29.5769 | 0
305 | 1900-11-01 | 7299 | 0 | 36.1266 | 0
305 | 1900-11-01 | 7300 | 0 | 230.7362 | 0
305 | 1900-11-01 | 7301 | 0 | 26.5849 | 0
305 | 1900-11-01 | 7302 | 0 | 37.2112 | 0
305 | 1900-11-01 | 7303 | 0 | 70.2345 | 0
305 | 1900-11-01 | 7304 | 0 | 118.9942 | 0
305 | 1900-11-01 | 7305 | 0 | 100.6356 | 0
305 | 1900-11-01 | 7306 | 0 | 97.6741 | 0
305 | 1900-11-01 | 7307 | 0 | 48.7099 | 0
305 | 1900-11-01 | 7308 | 0 | 50.4119 | 0
305 | 1900-11-01 | 7309 | 0 | 38.5563 | 0
305 | 1900-11-01 | 7310 | 0 | 49.4493 | 0
305 | 1900-11-01 | 7311 | 0 | 52.7903 | 0
305 | 1900-11-01 | 7312 | 0 | 39.0602 | 0
305 | 1900-11-01 | 7313 | 0 | 20.7648 | 0
305 | 1900-11-01 | 7314 | 0 | 55.943 | 0
305 | 1900-11-01 | 7315 | 0 | 59.9599 | 0
305 | 1900-11-01 | 7316 | 0 | 32.9781 | 0
305 | 1900-11-01 | 7317 | 0 | 34.1425 | 0
305 | 1900-11-01 | 7318 | 0 | 30.2502 | 0
305 | 1900-11-01 | 7319 | 0 | 32.3278 | 0
305 | 1900-11-01 | 7320 | 0 | 32.5252 | 0
306 | 1900-11-02 | 7321 | 0 | 27.5971 | 0
306 | 1900-11-02 | 7322 | 0 | 37.5691 | 0
306 | 1900-11-02 | 7323 | 0 | 25.5084 | 0
306 | 1900-11-02 | 7324 | 0 | 33.4642 | 0
306 | 1900-11-02 | 7325 | 0 | 26.7852 | 0
306 | 1900-11-02 | 7326 | 0 | 28.9048 | 0
306 | 1900-11-02 | 7327 | 0 | 24.8524 | 0
306 | 1900-11-02 | 7328 | 0 | 55.2962 | 0
306 | 1900-11-02 | 7329 | 0 | 61.4029 | 0
306 | 1900-11-02 | 7330 | 0 | 71.0691 | 0
306 | 1900-11-02 | 7331 | 0 | 44.8909 | 0
306 | 1900-11-02 | 7332 | 0 | 41.7023 | 0
306 | 1900-11-02 | 7333 | 0 | 51.443 | 0
306 | 1900-11-02 | 7334 | 0 | 44.8028 | 0
306 | 1900-11-02 | 7335 | 0 | 40.2523 | 0
306 | 1900-11-02 | 7336 | 0 | 53.8849 | 0
306 | 1900-11-02 | 7337 | 0 | 43.1972 | 0
306 | 1900-11-02 | 7338 | 0 | 36.1383 | 0
306 | 1900-11-02 | 7339 | 0 | 50.4902 | 0
306 | 1900-11-02 | 7340 | 0 | 29.4296 | 0
306 | 1900-11-02 | 7341 | 0 | 21.3992 | 0
306 | 1900-11-02 | 7342 | 0 | 33.3301 | 0
306 | 1900-11-02 | 7343 | 0 | 232.3984 | 0
306 | 1900-11-02 | 7344 | 0 | 36.7762 | 0
307 | 1900-11-03 | 7345 | 0 | 35.9334 | 0
307 | 1900-11-03 | 7346 | 0 | 35.6906 | 0
307 | 1900-11-03 | 7347 | 0 | 43.1616 | 0
307 | 1900-11-03 | 7348 | 0 | 79.9973 | 0
307 | 1900-11-03 | 7349 | 0 | 99.3603 | 0
307 | 1900-11-03 | 7350 | 0 | 115.1287 | 0
307 | 1900-11-03 | 7351 | 0 | 92.8322 | 0
307 | 1900-11-03 | 7352 | 0 | 105.9819 | 0
307 | 1900-11-03 | 7353 | 0 | 96.6991 | 0
307 | 1900-11-03 | 7354 | 0 | 111.1949 | 0
307 | 1900-11-03 | 7355 | 0 | 114.4151 | 0
307 | 1900-11-03 | 7356 | 0 | 307.8058 | 0
307 | 1900-11-03 | 7357 | 0 | 97.2875 | 0
307 | 1900-11-03 | 7358 | 0 | 69.3694 | 0
307 | 1900-11-03 | 7359 | 0 | 54.5613 | 0
307 | 1900-11-03 | 7360 | 0 | 53.6418 | 0
307 | 1900-11-03 | 7361 | 0 | 36.9867 | 0
307 | 1900-11-03 | 7362 | 0 | 42.0269 | 0
307 | 1900-11-03 | 7363 | 0 | 44.4824 | 0
307 | 1900-11-03 | 7364 | 0 | 34.6967 | 0
307 | 1900-11-03 | 7365 | 0 | 31.3369 | 0
307 | 1900-11-03 | 7366 | 0 | 27.2075 | 0
307 | 1900-11-03 | 7367 | 0 | 27.8101 | 0
307 | 1900-11-03 | 7368 | 0 | 24.8407 | 0
308 | 1900-11-04 | 7369 | 0 | 28.5969 | 0
308 | 1900-11-04 | 7370 | 0 | 39.9679 | 0
308 | 1900-11-04 | 7371 | 0 | 27.8145 | 0
308 | 1900-11-04 | 7372 | 0 | 31.063 | 0
308 | 1900-11-04 | 7373 | 0 | 23.0629 | 0
308 | 1900-11-04 | 7374 | 0 | 243.9404 | 0
308 | 1900-11-04 | 7375 | 0 | 78.0076 | 0
308 | 1900-11-04 | 7376 | 0 | 126.5806 | 0
308 | 1900-11-04 | 7377 | 0 | 113.7419 | 0
308 | 1900-11-04 | 7378 | 0 | 132.5291 | 0
308 | 1900-11-04 | 7379 | 0 | 117.7604 | 0
308 | 1900-11-04 | 7380 | 0 | 116.3513 | 0
308 | 1900-11-04 | 7381 | 0 | 110.5307 | 0
308 | 1900-11-04 | 7382 | 0 | 34.5977 | 0
308 | 1900-11-04 | 7383 | 0 | 40.6678 | 0
308 | 1900-11-04 | 7384 | 0 | 34.4673 | 0
308 | 1900-11-04 | 7385 | 0 | 40.7859 | 0
308 | 1900-11-04 | 7386 | 0 | 54.7552 | 0
308 | 1900-11-04 | 7387 | 0 | 41.2777 | 0
308 | 1900-11-04 | 7388 | 0 | 30.9184 | 0
308 | 1900-11-04 | 7389 | 0 | 31.7379 | 0
308 | 1900-11-04 | 7390 | 0 | 25.9366 | 0
308 | 1900-11-04 | 7391 | 0 | 33.9189 | 0
308 | 1900-11-04 | 7392 | 0 | 29.7543 | 0
309 | 1900-11-05 | 7393 | 0 | 32.8132 | 0
309 | 1900-11-05 | 7394 | 0 | 28.3296 | 0
309 | 1900-11-05 | 7395 | 0 | 26.132 | 0
309 | 1900-11-05 | 7396 | 0 | 40.3223 | 0
309 | 1900-11-05 | 7397 | 0 | 35.5741 | 0
309 | 1900-11-05 | 7398 | 0 | 60.2364 | 0
309 | 1900-11-05 | 7399 | 0 | 112.2448 | 0
309 | 1900-11-05 | 7400 | 0 | 137.3911 | 0
309 | 1900-11-05 | 7401 | 0 | 89.6171 | 0
309 | 1900-11-05 | 7402 | 0 | 56.2558 | 0
309 | 1900-11-05 | 7403 | 0 | 45.7266 | 0
309 | 1900-11-05 | 7404 | 0 | 78.6419 | 0
309 | 1900-11-05 | 7405 | 0 | 87.8541 | 0
309 | 1900-11-05 | 7406 | 0 | 88.9724 | 0
309 | 1900-11-05 | 7407 | 0 | 70.4713 | 0
309 | 1900-11-05 | 7408 | 0 | 56.7838 | 0
309 | 1900-11-05 | 7409 | 0 | 25.824 | 0
309 | 1900-11-05 | 7410 | 0 | 38.3654 | 0
309 | 1900-11-05 | 7411 | 0 | 40.2906 | 0
309 | 1900-11-05 | 7412 | 0 | 25.9044 | 0
309 | 1900-11-05 | 7413 | 0 | 35.9118 | 0
309 | 1900-11-05 | 7414 | 0 | 28.0375 | 0
309 | 1900-11-05 | 7415 | 0 | 237.2405 | 0
309 | 1900-11-05 | 7416 | 0 | 226.8056 | 0
310 | 1900-11-06 | 7417 | 0 | 36.1666 | 0
310 | 1900-11-06 | 7418 | 0 | 20.8905 | 0
310 | 1900-11-06 | 7419 | 0 | 33.822 | 0
310 | 1900-11-06 | 7420 | 0 | 35.9867 | 0
310 | 1900-11-06 | 7421 | 0 | 28.8914 | 0
310 | 1900-11-06 | 7422 | 0 | 45.2386 | 0
310 | 1900-11-06 | 7423 | 0 | 71.3303 | 0
310 | 1900-11-06 | 7424 | 0 | 114.8545 | 0
310 | 1900-11-06 | 7425 | 0 | 140.9758 | 0
310 | 1900-11-06 | 7426 | 0 | 92.1104 | 0
310 | 1900-11-06 | 7427 | 0 | 92.6324 | 0
310 | 1900-11-06 | 7428 | 0 | 125.1983 | 0
310 | 1900-11-06 | 7429 | 0 | 119.2577 | 0
310 | 1900-11-06 | 7430 | 0 | 87.6379 | 0
310 | 1900-11-06 | 7431 | 0 | 51.6345 | 0
310 | 1900-11-06 | 7432 | 0 | 33.2032 | 0
310 | 1900-11-06 | 7433 | 0 | 44.6317 | 0
310 | 1900-11-06 | 7434 | 0 | 51.2537 | 0
310 | 1900-11-06 | 7435 | 0 | 46.0675 | 0
310 | 1900-11-06 | 7436 | 0 | 33.7508 | 0
310 | 1900-11-06 | 7437 | 0 | 21.9828 | 0
310 | 1900-11-06 | 7438 | 0 | 29.2315 | 0
310 | 1900-11-06 | 7439 | 0 | 37.9827 | 0
310 | 1900-11-06 | 7440 | 0 | 29.7178 | 0
311 | 1900-11-07 | 7441 | 0 | 25.1595 | 0
311 | 1900-11-07 | 7442 | 0 | 19.3781 | 0
311 | 1900-11-07 | 7443 | 0 | 34.3279 | 0
311 | 1900-11-07 | 7444 | 0 | 37.2497 | 0
311 | 1900-11-07 | 7445 | 0 | 34.5213 | 0
311 | 1900-11-07 | 7446 | 0 | 64.7443 | 0
311 | 1900-11-07 | 7447 | 0 | 118.423 | 0
311 | 1900-11-07 | 7448 | 0 | 111.3641 | 0
311 | 1900-11-07 | 7449 | 0 | 118.5702 | 0
311 | 1900-11-07 | 7450 | 0 | 125.274 | 0
311 | 1900-11-07 | 7451 | 0 | 149.2696 | 0
311 | 1900-11-07 | 7452 | 0 | 89.4029 | 0
311 | 1900-11-07 | 7453 | 0 | 94.3251 | 0
311 | 1900-11-07 | 7454 | 0 | 94.7548 | 0
311 | 1900-11-07 | 7455 | 0 | 70.0352 | 0
311 | 1900-11-07 | 7456 | 0 | 54.8673 | 0
311 | 1900-11-07 | 7457 | 0 | 38.9165 | 0
311 | 1900-11-07 | 7458 | 0 | 44.0999 | 0
311 | 1900-11-07 | 7459 | 0 | 46.6819 | 0
311 | 1900-11-07 | 7460 | 0 | 37.9768 | 0
311 | 1900-11-07 | 7461 | 0 | 27.7712 | 0
311 | 1900-11-07 | 7462 | 0 | 25.4629 | 0
311 | 1900-11-07 | 7463 | 0 | 24.926 | 0
311 | 1900-11-07 | 7464 | 0 | 30.2592 | 0
312 | 1900-11-08 | 7465 | 0 | 25.7509 | 0
312 | 1900-11-08 | 7466 | 0 | 31.6884 | 0
312 | 1900-11-08 | 7467 | 0 | 26.2972 | 0
312 | 1900-11-08 | 7468 | 0 | 31.6963 | 0
312 | 1900-11-08 | 7469 | 0 | 35.2749 | 0
312 | 1900-11-08 | 7470 | 0 | 62.4036 | 0
312 | 1900-11-08 | 7471 | 0 | 40.6545 | 0
312 | 1900-11-08 | 7472 | 0 | 248.5891 | 0
312 | 1900-11-08 | 7473 | 0 | 41.9814 | 0
312 | 1900-11-08 | 7474 | 0 | 49.1528 | 0
312 | 1900-11-08 | 7475 | 0 | 70.2473 | 0
312 | 1900-11-08 | 7476 | 0 | 108.1633 | 0
312 | 1900-11-08 | 7477 | 0 | 79.0823 | 0
312 | 1900-11-08 | 7478 | 0 | 51.6903 | 0
312 | 1900-11-08 | 7479 | 0 | 70.8776 | 0
312 | 1900-11-08 | 7480 | 0 | 252.838 | 0
312 | 1900-11-08 | 7481 | 0 | 39.2255 | 0
312 | 1900-11-08 | 7482 | 0 | 37.2467 | 0
312 | 1900-11-08 | 7483 | 0 | 46.5471 | 0
312 | 1900-11-08 | 7484 | 0 | 35.6358 | 0
312 | 1900-11-08 | 7485 | 0 | 31.0768 | 0
312 | 1900-11-08 | 7486 | 0 | 27.6618 | 0
312 | 1900-11-08 | 7487 | 0 | 33.8777 | 0
312 | 1900-11-08 | 7488 | 0 | 34.4261 | 0
313 | 1900-11-09 | 7489 | 0 | 28.6679 | 0
313 | 1900-11-09 | 7490 | 0 | 39.3313 | 0
313 | 1900-11-09 | 7491 | 0 | 31.6504 | 0
313 | 1900-11-09 | 7492 | 0 | 30.6089 | 0
313 | 1900-11-09 | 7493 | 0 | 31.7271 | 0
313 | 1900-11-09 | 7494 | 0 | 43.5231 | 0
313 | 1900-11-09 | 7495 | 0 | 93.9625 | 0
313 | 1900-11-09 | 7496 | 0 | 120.2883 | 0
313 | 1900-11-09 | 7497 | 0 | 104.4503 | 0
313 | 1900-11-09 | 7498 | 0 | 115.7888 | 0
313 | 1900-11-09 | 7499 | 0 | 81.9605 | 0
313 | 1900-11-09 | 7500 | 0 | 57.4004 | 0
313 | 1900-11-09 | 7501 | 0 | 46.9771 | 0
313 | 1900-11-09 | 7502 | 0 | 52.2101 | 0
313 | 1900-11-09 | 7503 | 0 | 59.4576 | 0
313 | 1900-11-09 | 7504 | 0 | 68.8837 | 0
313 | 1900-11-09 | 7505 | 0 | 91.8739 | 0
313 | 1900-11-09 | 7506 | 0 | 45.6798 | 0
313 | 1900-11-09 | 7507 | 0 | 45.3623 | 0
313 | 1900-11-09 | 7508 | 0 | 24.8606 | 0
313 | 1900-11-09 | 7509 | 0 | 30.9704 | 0
313 | 1900-11-09 | 7510 | 0 | 29.8339 | 0
313 | 1900-11-09 | 7511 | 0 | 21.1899 | 0
313 | 1900-11-09 | 7512 | 0 | 33.0359 | 0
314 | 1900-11-10 | 7513 | 0 | 32.692 | 0
314 | 1900-11-10 | 7514 | 0 | 34.4012 | 0
314 | 1900-11-10 | 7515 | 0 | 27.8654 | 0
314 | 1900-11-10 | 7516 | 0 | 33.547 | 0
314 | 1900-11-10 | 7517 | 0 | 31.7972 | 0
314 | 1900-11-10 | 7518 | 0 | 29.4134 | 0
314 | 1900-11-10 | 7519 | 0 | 36.1598 | 0
314 | 1900-11-10 | 7520 | 0 | 60.78 | 0
314 | 1900-11-10 | 7521 | 0 | 143.5386 | 0
314 | 1900-11-10 | 7522 | 0 | 126.0388 | 0
314 | 1900-11-10 | 7523 | 0 | 53.7213 | 0
314 | 1900-11-10 | 7524 | 0 | 49.1809 | 0
314 | 1900-11-10 | 7525 | 0 | 56.9321 | 0
314 | 1900-11-10 | 7526 | 0 | 48.8614 | 0
314 | 1900-11-10 | 7527 | 0 | 45.7273 | 0
314 | 1900-11-10 | 7528 | 0 | 52.5011 | 0
314 | 1900-11-10 | 7529 | 0 | 60.6622 | 0
314 | 1900-11-10 | 7530 | 0 | 38.2643 | 0
314 | 1900-11-10 | 7531 | 0 | 60.1314 | 0
314 | 1900-11-10 | 7532 | 0 | 229.6055 | 0
314 | 1900-11-10 | 7533 | 0 | 36.5487 | 0
314 | 1900-11-10 | 7534 | 0 | 32.3256 | 0
314 | 1900-11-10 | 7535 | 0 | 24.8793 | 0
314 | 1900-11-10 | 7536 | 0 | 28.6356 | 0
315 | 1900-11-11 | 7537 | 0 | 32.4244 | 0
315 | 1900-11-11 | 7538 | 0 | 25.7623 | 0
315 | 1900-11-11 | 7539 | 0 | 28.4187 | 0
315 | 1900-11-11 | 7540 | 0 | 30.9751 | 0
315 | 1900-11-11 | 7541 | 0 | 35.4105 | 0
315 | 1900-11-11 | 7542 | 0 | 47.7419 | 0
315 | 1900-11-11 | 7543 | 0 | 98.6856 | 0
315 | 1900-11-11 | 7544 | 0 | 121.8375 | 0
315 | 1900-11-11 | 7545 | 0 | 98.4054 | 0
315 | 1900-11-11 | 7546 | 0 | 54.116 | 0
315 | 1900-11-11 | 7547 | 0 | 45.9238 | 0
315 | 1900-11-11 | 7548 | 0 | 59.0882 | 0
315 | 1900-11-11 | 7549 | 0 | 35.5762 | 0
315 | 1900-11-11 | 7550 | 0 | 46.5687 | 0
315 | 1900-11-11 | 7551 | 0 | 57.3224 | 0
315 | 1900-11-11 | 7552 | 0 | 49.5976 | 0
315 | 1900-11-11 | 7553 | 0 | 252.0698 | 0
315 | 1900-11-11 | 7554 | 0 | 52.48 | 0
315 | 1900-11-11 | 7555 | 0 | 41.4256 | 0
315 | 1900-11-11 | 7556 | 0 | 31.9894 | 0
315 | 1900-11-11 | 7557 | 0 | 24.7666 | 0
315 | 1900-11-11 | 7558 | 0 | 23.195 | 0
315 | 1900-11-11 | 7559 | 0 | 27.2583 | 0
315 | 1900-11-11 | 7560 | 0 | 30.0595 | 0
316 | 1900-11-12 | 7561 | 0 | 26.9289 | 0
316 | 1900-11-12 | 7562 | 0 | 29.8086 | 0
316 | 1900-11-12 | 7563 | 0 | 32.087 | 0
316 | 1900-11-12 | 7564 | 0 | 31.0886 | 0
316 | 1900-11-12 | 7565 | 0 | 45.1117 | 0
316 | 1900-11-12 | 7566 | 0 | 87.3167 | 0
316 | 1900-11-12 | 7567 | 0 | 86.2395 | 0
316 | 1900-11-12 | 7568 | 0 | 38.842 | 0
316 | 1900-11-12 | 7569 | 0 | 65.0956 | 0
316 | 1900-11-12 | 7570 | 0 | 103.1454 | 0
316 | 1900-11-12 | 7571 | 0 | 83.9511 | 0
316 | 1900-11-12 | 7572 | 0 | 39.3919 | 0
316 | 1900-11-12 | 7573 | 0 | 47.1515 | 0
316 | 1900-11-12 | 7574 | 0 | 56.7169 | 0
316 | 1900-11-12 | 7575 | 0 | 44.2901 | 0
316 | 1900-11-12 | 7576 | 0 | 35.7805 | 0
316 | 1900-11-12 | 7577 | 0 | 43.0155 | 0
316 | 1900-11-12 | 7578 | 0 | 50.9854 | 0
316 | 1900-11-12 | 7579 | 0 | 38.8429 | 0
316 | 1900-11-12 | 7580 | 0 | 36.5223 | 0
316 | 1900-11-12 | 7581 | 0 | 27.2675 | 0
316 | 1900-11-12 | 7582 | 0 | 29.1051 | 0
316 | 1900-11-12 | 7583 | 0 | 26.8262 | 0
316 | 1900-11-12 | 7584 | 0 | 36.6188 | 0
317 | 1900-11-13 | 7585 | 0 | 28.6884 | 0
317 | 1900-11-13 | 7586 | 0 | 32.9564 | 0
317 | 1900-11-13 | 7587 | 0 | 31.2248 | 0
317 | 1900-11-13 | 7588 | 0 | 33.7269 | 0
317 | 1900-11-13 | 7589 | 0 | 33.1125 | 0
317 | 1900-11-13 | 7590 | 0 | 26.2036 | 0
317 | 1900-11-13 | 7591 | 0 | 28.9945 | 0
317 | 1900-11-13 | 7592 | 0 | 233.3785 | 0
317 | 1900-11-13 | 7593 | 0 | 35.1557 | 0
317 | 1900-11-13 | 7594 | 0 | 57.1766 | 0
317 | 1900-11-13 | 7595 | 0 | 33.4304 | 0
317 | 1900-11-13 | 7596 | 0 | 35.7367 | 0
317 | 1900-11-13 | 7597 | 0 | 40.8494 | 0
317 | 1900-11-13 | 7598 | 0 | 49.2613 | 0
317 | 1900-11-13 | 7599 | 0 | 54.0157 | 0
317 | 1900-11-13 | 7600 | 0 | 47.6742 | 0
317 | 1900-11-13 | 7601 | 0 | 30.0754 | 0
317 | 1900-11-13 | 7602 | 0 | 53.5964 | 0
317 | 1900-11-13 | 7603 | 0 | 42.3611 | 0
317 | 1900-11-13 | 7604 | 0 | 23.5152 | 0
317 | 1900-11-13 | 7605 | 0 | 29.9571 | 0
317 | 1900-11-13 | 7606 | 0 | 35.9772 | 0
317 | 1900-11-13 | 7607 | 0 | 19.0507 | 0
317 | 1900-11-13 | 7608 | 0 | 29.209 | 0
318 | 1900-11-14 | 7609 | 0 | 32.0449 | 0
318 | 1900-11-14 | 7610 | 0 | 30.5209 | 0
318 | 1900-11-14 | 7611 | 0 | 31.2207 | 0
318 | 1900-11-14 | 7612 | 0 | 30.7258 | 0
318 | 1900-11-14 | 7613 | 0 | 41.1546 | 0
318 | 1900-11-14 | 7614 | 0 | 303.4612 | 0
318 | 1900-11-14 | 7615 | 0 | 103.0137 | 0
318 | 1900-11-14 | 7616 | 0 | 115.6031 | 0
318 | 1900-11-14 | 7617 | 0 | 90.2998 | 0
318 | 1900-11-14 | 7618 | 0 | 58.492 | 0
318 | 1900-11-14 | 7619 | 0 | 66.7731 | 0
318 | 1900-11-14 | 7620 | 0 | 37.7022 | 0
318 | 1900-11-14 | 7621 | 0 | 39.4028 | 0
318 | 1900-11-14 | 7622 | 0 | 46.1118 | 0
318 | 1900-11-14 | 7623 | 0 | 39.7949 | 0
318 | 1900-11-14 | 7624 | 0 | 41.7663 | 0
318 | 1900-11-14 | 7625 | 0 | 56.4393 | 0
318 | 1900-11-14 | 7626 | 0 | 36.7871 | 0
318 | 1900-11-14 | 7627 | 0 | 50.3662 | 0
318 | 1900-11-14 | 7628 | 0 | 39.3826 | 0
318 | 1900-11-14 | 7629 | 0 | 38.0705 | 0
318 | 1900-11-14 | 7630 | 0 | 19.2964 | 0
318 | 1900-11-14 | 7631 | 0 | 24.1137 | 0
318 | 1900-11-14 | 7632 | 0 | 32.51 | 0
319 | 1900-11-15 | 7633 | 0 | 24.575 | 0
319 | 1900-11-15 | 7634 | 0 | 28.0736 | 0
319 | 1900-11-15 | 7635 | 0 | 29.2988 | 0
319 | 1900-11-15 | 7636 | 0 | 37.505 | 0
319 | 1900-11-15 | 7637 | 0 | 36.632 | 0
319 | 1900-11-15 | 7638 | 0 | 57.8522 | 0
319 | 1900-11-15 | 7639 | 0 | 85.9333 | 0
319 | 1900-11-15 | 7640 | 0 | 55.3683 | 0
319 | 1900-11-15 | 7641 | 0 | 55.445 | 0
319 | 1900-11-15 | 7642 | 0 | 66.4433 | 0
319 | 1900-11-15 | 7643 | 0 | 123.3241 | 0
319 | 1900-11-15 | 7644 | 0 | 119.4514 | 0
319 | 1900-11-15 | 7645 | 0 | 66.7282 | 0
319 | 1900-11-15 | 7646 | 0 | 50.1831 | 0
319 | 1900-11-15 | 7647 | 0 | 254.6943 | 0
319 | 1900-11-15 | 7648 | 0 | 42.5458 | 0
319 | 1900-11-15 | 7649 | 0 | 45.8326 | 0
319 | 1900-11-15 | 7650 | 0 | 57.4727 | 0
319 | 1900-11-15 | 7651 | 0 | 258.2685 | 0
319 | 1900-11-15 | 7652 | 0 | 26.9247 | 0
319 | 1900-11-15 | 7653 | 0 | 30.7728 | 0
319 | 1900-11-15 | 7654 | 0 | 28.2423 | 0
319 | 1900-11-15 | 7655 | 0 | 30.9308 | 0
319 | 1900-11-15 | 7656 | 0 | 29.5766 | 0
320 | 1900-11-16 | 7657 | 0 | 25.9963 | 0
320 | 1900-11-16 | 7658 | 0 | 20.7816 | 0
320 | 1900-11-16 | 7659 | 0 | 33.7249 | 0
320 | 1900-11-16 | 7660 | 0 | 31.8284 | 0
320 | 1900-11-16 | 7661 | 0 | 35.2388 | 0
320 | 1900-11-16 | 7662 | 0 | 38.6 | 0
320 | 1900-11-16 | 7663 | 0 | 70.2341 | 0
320 | 1900-11-16 | 7664 | 0 | 85.4308 | 0
320 | 1900-11-16 | 7665 | 0 | 46.2153 | 0
320 | 1900-11-16 | 7666 | 0 | 50.1238 | 0
320 | 1900-11-16 | 7667 | 0 | 266.6524 | 0
320 | 1900-11-16 | 7668 | 0 | 96.1377 | 0
320 | 1900-11-16 | 7669 | 0 | 136.0064 | 0
320 | 1900-11-16 | 7670 | 0 | 76.9518 | 0
320 | 1900-11-16 | 7671 | 0 | 44.7119 | 0
320 | 1900-11-16 | 7672 | 0 | 44.453 | 0
320 | 1900-11-16 | 7673 | 0 | 44.4818 | 0
320 | 1900-11-16 | 7674 | 0 | 60.069 | 0
320 | 1900-11-16 | 7675 | 0 | 34.6083 | 0
320 | 1900-11-16 | 7676 | 0 | 24.7697 | 0
320 | 1900-11-16 | 7677 | 0 | 25.8281 | 0
320 | 1900-11-16 | 7678 | 0 | 26.386 | 0
320 | 1900-11-16 | 7679 | 0 | 33.3159 | 0
320 | 1900-11-16 | 7680 | 0 | 28.5631 | 0
321 | 1900-11-17 | 7681 | 0 | 36.0936 | 0
321 | 1900-11-17 | 7682 | 0 | 31.5521 | 0
321 | 1900-11-17 | 7683 | 0 | 27.6437 | 0
321 | 1900-11-17 | 7684 | 0 | 31.0488 | 0
321 | 1900-11-17 | 7685 | 0 | 31.8122 | 0
321 | 1900-11-17 | 7686 | 0 | 31.4294 | 0
321 | 1900-11-17 | 7687 | 0 | 31.04 | 0
321 | 1900-11-17 | 7688 | 0 | 31.4515 | 0
321 | 1900-11-17 | 7689 | 0 | 39.3074 | 0
321 | 1900-11-17 | 7690 | 0 | 45.3059 | 0
321 | 1900-11-17 | 7691 | 0 | 42.0826 | 0
321 | 1900-11-17 | 7692 | 0 | 31.4685 | 0
321 | 1900-11-17 | 7693 | 0 | 45.546 | 0
321 | 1900-11-17 | 7694 | 0 | 63.7221 | 0
321 | 1900-11-17 | 7695 | 0 | 35.2826 | 0
321 | 1900-11-17 | 7696 | 0 | 248.191 | 0
321 | 1900-11-17 | 7697 | 0 | 43.15 | 0
321 | 1900-11-17 | 7698 | 0 | 33.5766 | 0
321 | 1900-11-17 | 7699 | 0 | 47.0915 | 0
321 | 1900-11-17 | 7700 | 0 | 39.7662 | 0
321 | 1900-11-17 | 7701 | 0 | 39.8557 | 0
321 | 1900-11-17 | 7702 | 0 | 84.661 | 0
321 | 1900-11-17 | 7703 | 0 | 109.2149 | 0
321 | 1900-11-17 | 7704 | 0 | 98.1766 | 0
322 | 1900-11-18 | 7705 | 0 | 58.6321 | 0
322 | 1900-11-18 | 7706 | 0 | 35.0815 | 0
322 | 1900-11-18 | 7707 | 0 | 28.1672 | 0
322 | 1900-11-18 | 7708 | 0 | 27.4681 | 0
322 | 1900-11-18 | 7709 | 0 | 26.002 | 0
322 | 1900-11-18 | 7710 | 0 | 44.6933 | 0
322 | 1900-11-18 | 7711 | 0 | 257.5457 | 0
322 | 1900-11-18 | 7712 | 0 | 61.3251 | 0
322 | 1900-11-18 | 7713 | 0 | 48.8612 | 0
322 | 1900-11-18 | 7714 | 0 | 45.6877 | 0
322 | 1900-11-18 | 7715 | 0 | 52.1863 | 0
322 | 1900-11-18 | 7716 | 0 | 47.2096 | 0
322 | 1900-11-18 | 7717 | 0 | 48.903 | 0
322 | 1900-11-18 | 7718 | 0 | 42.6739 | 0
322 | 1900-11-18 | 7719 | 0 | 47.0891 | 0
322 | 1900-11-18 | 7720 | 0 | 49.5706 | 0
322 | 1900-11-18 | 7721 | 0 | 39.811 | 0
322 | 1900-11-18 | 7722 | 0 | 41.4073 | 0
322 | 1900-11-18 | 7723 | 0 | 243.3041 | 0
322 | 1900-11-18 | 7724 | 0 | 30.1671 | 0
322 | 1900-11-18 | 7725 | 0 | 25.1202 | 0
322 | 1900-11-18 | 7726 | 0 | 24.6219 | 0
322 | 1900-11-18 | 7727 | 0 | 28.6463 | 0
322 | 1900-11-18 | 7728 | 0 | 34.8741 | 0
323 | 1900-11-19 | 7729 | 0 | 26.0877 | 0
323 | 1900-11-19 | 7730 | 0 | 30.9787 | 0
323 | 1900-11-19 | 7731 | 0 | 31.8299 | 0
323 | 1900-11-19 | 7732 | 0 | 32.2773 | 0
323 | 1900-11-19 | 7733 | 0 | 41.4936 | 0
323 | 1900-11-19 | 7734 | 0 | 44.9198 | 0
323 | 1900-11-19 | 7735 | 0 | 70.6285 | 0
323 | 1900-11-19 | 7736 | 0 | 90.1098 | 0
323 | 1900-11-19 | 7737 | 0 | 72.4189 | 0
323 | 1900-11-19 | 7738 | 0 | 43.2534 | 0
323 | 1900-11-19 | 7739 | 0 | 43.8925 | 0
323 | 1900-11-19 | 7740 | 0 | 38.2879 | 0
323 | 1900-11-19 | 7741 | 0 | 51.0693 | 0
323 | 1900-11-19 | 7742 | 0 | 33.9756 | 0
323 | 1900-11-19 | 7743 | 0 | 52.3471 | 0
323 | 1900-11-19 | 7744 | 0 | 51.2766 | 0
323 | 1900-11-19 | 7745 | 0 | 41.4369 | 0
323 | 1900-11-19 | 7746 | 0 | 53.8859 | 0
323 | 1900-11-19 | 7747 | 0 | 49.368 | 0
323 | 1900-11-19 | 7748 | 0 | 37.9111 | 0
323 | 1900-11-19 | 7749 | 0 | 35.122 | 0
323 | 1900-11-19 | 7750 | 0 | 72.3424 | 0
323 | 1900-11-19 | 7751 | 0 | 97.9363 | 0
323 | 1900-11-19 | 7752 | 0 | 97.7321 | 0
324 | 1900-11-20 | 7753 | 0 | 307.6152 | 0
324 | 1900-11-20 | 7754 | 0 | 87.1579 | 0
324 | 1900-11-20 | 7755 | 0 | 101.5163 | 0
324 | 1900-11-20 | 7756 | 0 | 77.2517 | 0
324 | 1900-11-20 | 7757 | 0 | 37.3121 | 0
324 | 1900-11-20 | 7758 | 0 | 32.9336 | 0
324 | 1900-11-20 | 7759 | 0 | 31.2511 | 0
324 | 1900-11-20 | 7760 | 0 | 40.8721 | 0
324 | 1900-11-20 | 7761 | 0 | 44.382 | 0
324 | 1900-11-20 | 7762 | 0 | 36.5557 | 0
324 | 1900-11-20 | 7763 | 0 | 46.3674 | 0
324 | 1900-11-20 | 7764 | 0 | 35.7402 | 0
324 | 1900-11-20 | 7765 | 0 | 57.4677 | 0
324 | 1900-11-20 | 7766 | 0 | 51.8107 | 0
324 | 1900-11-20 | 7767 | 0 | 48.981 | 0
324 | 1900-11-20 | 7768 | 0 | 34.839 | 0
324 | 1900-11-20 | 7769 | 0 | 55.8336 | 0
324 | 1900-11-20 | 7770 | 0 | 45.3868 | 0
324 | 1900-11-20 | 7771 | 0 | 243.2164 | 0
324 | 1900-11-20 | 7772 | 0 | 25.9534 | 0
324 | 1900-11-20 | 7773 | 0 | 35.1038 | 0
324 | 1900-11-20 | 7774 | 0 | 77.4934 | 0
324 | 1900-11-20 | 7775 | 0 | 101.8464 | 0
324 | 1900-11-20 | 7776 | 0 | 262.9308 | 0
325 | 1900-11-21 | 7777 | 0 | 27.0296 | 0
325 | 1900-11-21 | 7778 | 0 | 40.8405 | 0
325 | 1900-11-21 | 7779 | 0 | 87.1819 | 0
325 | 1900-11-21 | 7780 | 0 | 99.4111 | 0
325 | 1900-11-21 | 7781 | 0 | 91.7714 | 0
325 | 1900-11-21 | 7782 | 0 | 54.1309 | 0
325 | 1900-11-21 | 7783 | 0 | 23.3644 | 0
325 | 1900-11-21 | 7784 | 0 | 57.1819 | 0
325 | 1900-11-21 | 7785 | 0 | 39.4637 | 0
325 | 1900-11-21 | 7786 | 0 | 65.3546 | 0
325 | 1900-11-21 | 7787 | 0 | 102.816 | 0
325 | 1900-11-21 | 7788 | 0 | 83.9074 | 0
325 | 1900-11-21 | 7789 | 0 | 46.8974 | 0
325 | 1900-11-21 | 7790 | 0 | 39.2666 | 0
325 | 1900-11-21 | 7791 | 0 | 46.5223 | 0
325 | 1900-11-21 | 7792 | 0 | 49.2335 | 0
325 | 1900-11-21 | 7793 | 0 | 48.4298 | 0
325 | 1900-11-21 | 7794 | 0 | 42.1568 | 0
325 | 1900-11-21 | 7795 | 0 | 37.523 | 0
325 | 1900-11-21 | 7796 | 0 | 45.8686 | 0
325 | 1900-11-21 | 7797 | 0 | 108.767 | 0
325 | 1900-11-21 | 7798 | 0 | 106.6305 | 0
325 | 1900-11-21 | 7799 | 0 | 268.7163 | 0
325 | 1900-11-21 | 7800 | 0 | 26.291 | 0
326 | 1900-11-22 | 7801 | 0 | 63.2486 | 0
326 | 1900-11-22 | 7802 | 0 | 89.2934 | 0
326 | 1900-11-22 | 7803 | 0 | 57.1706 | 0
326 | 1900-11-22 | 7804 | 0 | 35.8144 | 0
326 | 1900-11-22 | 7805 | 0 | 35.3185 | 0
326 | 1900-11-22 | 7806 | 0 | 27.2263 | 0
326 | 1900-11-22 | 7807 | 0 | 27.5208 | 0
326 | 1900-11-22 | 7808 | 0 | 49.7684 | 0
326 | 1900-11-22 | 7809 | 0 | 36.9307 | 0
326 | 1900-11-22 | 7810 | 0 | 52.0194 | 0
326 | 1900-11-22 | 7811 | 0 | 44.2276 | 0
326 | 1900-11-22 | 7812 | 0 | 33.2576 | 0
326 | 1900-11-22 | 7813 | 0 | 34.6031 | 0
326 | 1900-11-22 | 7814 | 0 | 50.8065 | 0
326 | 1900-11-22 | 7815 | 0 | 52.7072 | 0
326 | 1900-11-22 | 7816 | 0 | 41.294 | 0
326 | 1900-11-22 | 7817 | 0 | 34.7065 | 0
326 | 1900-11-22 | 7818 | 0 | 36.4124 | 0
326 | 1900-11-22 | 7819 | 0 | 44.0608 | 0
326 | 1900-11-22 | 7820 | 0 | 27.889 | 0
326 | 1900-11-22 | 7821 | 0 | 21.448 | 0
326 | 1900-11-22 | 7822 | 0 | 229.2915 | 0
326 | 1900-11-22 | 7823 | 0 | 27.3676 | 0
326 | 1900-11-22 | 7824 | 0 | 26.7612 | 0
327 | 1900-11-23 | 7825 | 0 | 29.8994 | 0
327 | 1900-11-23 | 7826 | 0 | 26.1769 | 0
327 | 1900-11-23 | 7827 | 0 | 34.1428 | 0
327 | 1900-11-23 | 7828 | 0 | 34.6804 | 0
327 | 1900-11-23 | 7829 | 0 | 31.6646 | 0
327 | 1900-11-23 | 7830 | 0 | 227.634 | 0
327 | 1900-11-23 | 7831 | 0 | 30.2594 | 0
327 | 1900-11-23 | 7832 | 0 | 35.6897 | 0
327 | 1900-11-23 | 7833 | 0 | 36.3388 | 0
327 | 1900-11-23 | 7834 | 0 | 39.9169 | 0
327 | 1900-11-23 | 7835 | 0 | 52.3062 | 0
327 | 1900-11-23 | 7836 | 0 | 45.7819 | 0
327 | 1900-11-23 | 7837 | 0 | 42.5619 | 0
327 | 1900-11-23 | 7838 | 0 | 53.1192 | 0
327 | 1900-11-23 | 7839 | 0 | 43.0474 | 0
327 | 1900-11-23 | 7840 | 0 | 44.8514 | 0
327 | 1900-11-23 | 7841 | 0 | 38.6824 | 0
327 | 1900-11-23 | 7842 | 0 | 35.0889 | 0
327 | 1900-11-23 | 7843 | 0 | 42.9227 | 0
327 | 1900-11-23 | 7844 | 0 | 226.8924 | 0
327 | 1900-11-23 | 7845 | 0 | 27.729 | 0
327 | 1900-11-23 | 7846 | 0 | 33.866 | 0
327 | 1900-11-23 | 7847 | 0 | 34.9543 | 0
327 | 1900-11-23 | 7848 | 0 | 22.8426 | 0
328 | 1900-11-24 | 7849 | 0 | 33.1975 | 0
328 | 1900-11-24 | 7850 | 0 | 38.8726 | 0
328 | 1900-11-24 | 7851 | 0 | 32.9414 | 0
328 | 1900-11-24 | 7852 | 0 | 36.7806 | 0
328 | 1900-11-24 | 7853 | 0 | 30.9469 | 0
328 | 1900-11-24 | 7854 | 0 | 30.6113 | 0
328 | 1900-11-24 | 7855 | 0 | 30.7641 | 0
328 | 1900-11-24 | 7856 | 0 | 49.5769 | 0
328 | 1900-11-24 | 7857 | 0 | 54.1933 | 0
328 | 1900-11-24 | 7858 | 0 | 46.7958 | 0
328 | 1900-11-24 | 7859 | 0 | 42.1222 | 0
328 | 1900-11-24 | 7860 | 0 | 45.0494 | 0
328 | 1900-11-24 | 7861 | 0 | 36.5013 | 0
328 | 1900-11-24 | 7862 | 0 | 41.0888 | 0
328 | 1900-11-24 | 7863 | 0 | 61.1831 | 0
328 | 1900-11-24 | 7864 | 0 | 33.6377 | 0
328 | 1900-11-24 | 7865 | 0 | 38.3498 | 0
328 | 1900-11-24 | 7866 | 0 | 49.6059 | 0
328 | 1900-11-24 | 7867 | 0 | 28.0957 | 0
328 | 1900-11-24 | 7868 | 0 | 38.6519 | 0
328 | 1900-11-24 | 7869 | 0 | 36.7002 | 0
328 | 1900-11-24 | 7870 | 0 | 31.31 | 0
328 | 1900-11-24 | 7871 | 0 | 29.9526 | 0
328 | 1900-11-24 | 7872 | 0 | 38.3635 | 0
329 | 1900-11-25 | 7873 | 0 | 28.0026 | 0
329 | 1900-11-25 | 7874 | 0 | 28.5372 | 0
329 | 1900-11-25 | 7875 | 0 | 238.1225 | 0
329 | 1900-11-25 | 7876 | 0 | 33.8072 | 0
329 | 1900-11-25 | 7877 | 0 | 34.899 | 0
329 | 1900-11-25 | 7878 | 0 | 28.6953 | 0
329 | 1900-11-25 | 7879 | 0 | 31.7043 | 0
329 | 1900-11-25 | 7880 | 0 | 37.7427 | 0
329 | 1900-11-25 | 7881 | 0 | 51.7849 | 0
329 | 1900-11-25 | 7882 | 0 | 42.0773 | 0
329 | 1900-11-25 | 7883 | 0 | 42.3079 | 0
329 | 1900-11-25 | 7884 | 0 | 46.4353 | 0
329 | 1900-11-25 | 7885 | 0 | 40.6664 | 0
329 | 1900-11-25 | 7886 | 0 | 45.4039 | 0
329 | 1900-11-25 | 7887 | 0 | 22.7957 | 0
329 | 1900-11-25 | 7888 | 0 | 35.4015 | 0
329 | 1900-11-25 | 7889 | 0 | 40.4563 | 0
329 | 1900-11-25 | 7890 | 0 | 233.8382 | 0
329 | 1900-11-25 | 7891 | 0 | 36.9531 | 0
329 | 1900-11-25 | 7892 | 0 | 29.643 | 0
329 | 1900-11-25 | 7893 | 0 | 31.0298 | 0
329 | 1900-11-25 | 7894 | 0 | 33.9101 | 0
329 | 1900-11-25 | 7895 | 0 | 32.9192 | 0
329 | 1900-11-25 | 7896 | 0 | 26.615 | 0
330 | 1900-11-26 | 7897 | 0 | 31.599 | 0
330 | 1900-11-26 | 7898 | 0 | 23.6654 | 0
330 | 1900-11-26 | 7899 | 0 | 35.2585 | 0
330 | 1900-11-26 | 7900 | 0 | 29.261 | 0
330 | 1900-11-26 | 7901 | 0 | 38.9636 | 0
330 | 1900-11-26 | 7902 | 0 | 80.078 | 0
330 | 1900-11-26 | 7903 | 0 | 103.7026 | 0
330 | 1900-11-26 | 7904 | 0 | 316.9899 | 0
330 | 1900-11-26 | 7905 | 0 | 110.4754 | 0
330 | 1900-11-26 | 7906 | 0 | 123.8039 | 0
330 | 1900-11-26 | 7907 | 0 | 100.84 | 0
330 | 1900-11-26 | 7908 | 0 | 103.4701 | 0
330 | 1900-11-26 | 7909 | 0 | 111.4677 | 0
330 | 1900-11-26 | 7910 | 0 | 80.4832 | 0
330 | 1900-11-26 | 7911 | 0 | 60.7471 | 0
330 | 1900-11-26 | 7912 | 0 | 39.6906 | 0
330 | 1900-11-26 | 7913 | 0 | 49.1222 | 0
330 | 1900-11-26 | 7914 | 0 | 39.8737 | 0
330 | 1900-11-26 | 7915 | 0 | 46.6794 | 0
330 | 1900-11-26 | 7916 | 0 | 25.0972 | 0
330 | 1900-11-26 | 7917 | 0 | 40.8663 | 0
330 | 1900-11-26 | 7918 | 0 | 35.8207 | 0
330 | 1900-11-26 | 7919 | 0 | 27.2684 | 0
330 | 1900-11-26 | 7920 | 0 | 25.8486 | 0
331 | 1900-11-27 | 7921 | 0 | 24.9965 | 0
331 | 1900-11-27 | 7922 | 0 | 31.1324 | 0
331 | 1900-11-27 | 7923 | 0 | 25.0338 | 0
331 | 1900-11-27 | 7924 | 0 | 31.3079 | 0
331 | 1900-11-27 | 7925 | 0 | 33.5983 | 0
331 | 1900-11-27 | 7926 | 0 | 22.4201 | 0
331 | 1900-11-27 | 7927 | 0 | 244.2084 | 0
331 | 1900-11-27 | 7928 | 0 | 110.6002 | 0
331 | 1900-11-27 | 7929 | 0 | 90.4532 | 0
331 | 1900-11-27 | 7930 | 0 | 84.7859 | 0
331 | 1900-11-27 | 7931 | 0 | 94.7171 | 0
331 | 1900-11-27 | 7932 | 0 | 62.3411 | 0
331 | 1900-11-27 | 7933 | 0 | 44.7534 | 0
331 | 1900-11-27 | 7934 | 0 | 42.2736 | 0
331 | 1900-11-27 | 7935 | 0 | 47.1691 | 0
331 | 1900-11-27 | 7936 | 0 | 43.3254 | 0
331 | 1900-11-27 | 7937 | 0 | 54.1189 | 0
331 | 1900-11-27 | 7938 | 0 | 59.6648 | 0
331 | 1900-11-27 | 7939 | 0 | 62.7277 | 0
331 | 1900-11-27 | 7940 | 0 | 27.6988 | 0
331 | 1900-11-27 | 7941 | 0 | 27.0133 | 0
331 | 1900-11-27 | 7942 | 0 | 24.853 | 0
331 | 1900-11-27 | 7943 | 0 | 32.3343 | 0
331 | 1900-11-27 | 7944 | 0 | 29.0225 | 0
332 | 1900-11-28 | 7945 | 0 | 29.0298 | 0
332 | 1900-11-28 | 7946 | 0 | 29.3035 | 0
332 | 1900-11-28 | 7947 | 0 | 27.619 | 0
332 | 1900-11-28 | 7948 | 0 | 238.7478 | 0
332 | 1900-11-28 | 7949 | 0 | 35.7435 | 0
332 | 1900-11-28 | 7950 | 0 | 229.089 | 0
332 | 1900-11-28 | 7951 | 0 | 29.8057 | 0
332 | 1900-11-28 | 7952 | 0 | 58.3936 | 0
332 | 1900-11-28 | 7953 | 0 | 40.0255 | 0
332 | 1900-11-28 | 7954 | 0 | 62.4043 | 0
332 | 1900-11-28 | 7955 | 0 | 91.4524 | 0
332 | 1900-11-28 | 7956 | 0 | 108.5687 | 0
332 | 1900-11-28 | 7957 | 0 | 81.9836 | 0
332 | 1900-11-28 | 7958 | 0 | 53.8297 | 0
332 | 1900-11-28 | 7959 | 0 | 42.6396 | 0
332 | 1900-11-28 | 7960 | 0 | 41.3381 | 0
332 | 1900-11-28 | 7961 | 0 | 35.5733 | 0
332 | 1900-11-28 | 7962 | 0 | 38.0915 | 0
332 | 1900-11-28 | 7963 | 0 | 33.079 | 0
332 | 1900-11-28 | 7964 | 0 | 32.106 | 0
332 | 1900-11-28 | 7965 | 0 | 28.0532 | 0
332 | 1900-11-28 | 7966 | 0 | 25.8465 | 0
332 | 1900-11-28 | 7967 | 0 | 30.5977 | 0
332 | 1900-11-28 | 7968 | 0 | 33.8666 | 0
333 | 1900-11-29 | 7969 | 0 | 22.6988 | 0
333 | 1900-11-29 | 7970 | 0 | 28.3818 | 0
333 | 1900-11-29 | 7971 | 0 | 26.5517 | 0
333 | 1900-11-29 | 7972 | 0 | 25.3069 | 0
333 | 1900-11-29 | 7973 | 0 | 32.1122 | 0
333 | 1900-11-29 | 7974 | 0 | 34.6043 | 0
333 | 1900-11-29 | 7975 | 0 | 36.7169 | 0
333 | 1900-11-29 | 7976 | 0 | 46.9833 | 0
333 | 1900-11-29 | 7977 | 0 | 60.0715 | 0
333 | 1900-11-29 | 7978 | 0 | 99.5774 | 0
333 | 1900-11-29 | 7979 | 0 | 72.4534 | 0
333 | 1900-11-29 | 7980 | 0 | 43.0479 | 0
333 | 1900-11-29 | 7981 | 0 | 46.2468 | 0
333 | 1900-11-29 | 7982 | 0 | 37.1769 | 0
333 | 1900-11-29 | 7983 | 0 | 46.3824 | 0
333 | 1900-11-29 | 7984 | 0 | 39.6724 | 0
333 | 1900-11-29 | 7985 | 0 | 49.4594 | 0
333 | 1900-11-29 | 7986 | 0 | 42.2761 | 0
333 | 1900-11-29 | 7987 | 0 | 45.0568 | 0
333 | 1900-11-29 | 7988 | 0 | 29.4885 | 0
333 | 1900-11-29 | 7989 | 0 | 31.2603 | 0
333 | 1900-11-29 | 7990 | 0 | 31.954 | 0
333 | 1900-11-29 | 7991 | 0 | 28.1556 | 0
333 | 1900-11-29 | 7992 | 0 | 30.5478 | 0
334 | 1900-11-30 | 7993 | 0 | 38.8641 | 0
334 | 1900-11-30 | 7994 | 0 | 35.1662 | 0
334 | 1900-11-30 | 7995 | 0 | 30.6817 | 0
334 | 1900-11-30 | 7996 | 0 | 23.762 | 0
334 | 1900-11-30 | 7997 | 0 | 34.5546 | 0
334 | 1900-11-30 | 7998 | 0 | 57.3131 | 0
334 | 1900-11-30 | 7999 | 0 | 92.921 | 0
334 | 1900-11-30 | 8000 | 0 | 294.2266 | 0
334 | 1900-11-30 | 8001 | 0 | 55.2979 | 0
334 | 1900-11-30 | 8002 | 0 | 60.6396 | 0
334 | 1900-11-30 | 8003 | 0 | 43.8652 | 0
334 | 1900-11-30 | 8004 | 0 | 36.663 | 0
334 | 1900-11-30 | 8005 | 0 | 52.0332 | 0
334 | 1900-11-30 | 8006 | 0 | 42.0041 | 0
334 | 1900-11-30 | 8007 | 0 | 41.6567 | 0
334 | 1900-11-30 | 8008 | 0 | 249.8187 | 0
334 | 1900-11-30 | 8009 | 0 | 53.3247 | 0
334 | 1900-11-30 | 8010 | 0 | 38.0254 | 0
334 | 1900-11-30 | 8011 | 0 | 47.9217 | 0
334 | 1900-11-30 | 8012 | 0 | 34.2123 | 0
334 | 1900-11-30 | 8013 | 0 | 31.2418 | 0
334 | 1900-11-30 | 8014 | 0 | 29.7912 | 0
334 | 1900-11-30 | 8015 | 0 | 30.3659 | 0
334 | 1900-11-30 | 8016 | 0 | 29.6777 | 0
335 | 1900-12-01 | 8017 | 0 | 28.2908 | 0
335 | 1900-12-01 | 8018 | 0 | 24.5351 | 0
335 | 1900-12-01 | 8019 | 0 | 33.687 | 0
335 | 1900-12-01 | 8020 | 0 | 24.7622 | 0
335 | 1900-12-01 | 8021 | 0 | 27.1313 | 0
335 | 1900-12-01 | 8022 | 0 | 28.1201 | 0
335 | 1900-12-01 | 8023 | 0 | 27.1903 | 0
335 | 1900-12-01 | 8024 | 0 | 51.2714 | 0
335 | 1900-12-01 | 8025 | 0 | 48.916 | 0
335 | 1900-12-01 | 8026 | 0 | 46.3907 | 0
335 | 1900-12-01 | 8027 | 0 | 31.4223 | 0
335 | 1900-12-01 | 8028 | 0 | 39.6988 | 0
335 | 1900-12-01 | 8029 | 0 | 42.6225 | 0
335 | 1900-12-01 | 8030 | 0 | 43.2301 | 0
335 | 1900-12-01 | 8031 | 0 | 40.0618 | 0
335 | 1900-12-01 | 8032 | 0 | 47.6455 | 0
335 | 1900-12-01 | 8033 | 0 | 56.1782 | 0
335 | 1900-12-01 | 8034 | 0 | 38.245 | 0
335 | 1900-12-01 | 8035 | 0 | 52.1455 | 0
335 | 1900-12-01 | 8036 | 0 | 30.3934 | 0
335 | 1900-12-01 | 8037 | 0 | 33.0622 | 0
335 | 1900-12-01 | 8038 | 0 | 22.7403 | 0
335 | 1900-12-01 | 8039 | 0 | 27.8354 | 0
335 | 1900-12-01 | 8040 | 0 | 31.6087 | 0
336 | 1900-12-02 | 8041 | 0 | 22.9288 | 0
336 | 1900-12-02 | 8042 | 0 | 31.6874 | 0
336 | 1900-12-02 | 8043 | 0 | 29.4703 | 0
336 | 1900-12-02 | 8044 | 0 | 28.5082 | 0
336 | 1900-12-02 | 8045 | 0 | 28.4166 | 0
336 | 1900-12-02 | 8046 | 0 | 27.2532 | 0
336 | 1900-12-02 | 8047 | 0 | 27.8336 | 0
336 | 1900-12-02 | 8048 | 0 | 41.3769 | 0
336 | 1900-12-02 | 8049 | 0 | 36.4575 | 0
336 | 1900-12-02 | 8050 | 0 | 43.6981 | 0
336 | 1900-12-02 | 8051 | 0 | 39.581 | 0
336 | 1900-12-02 | 8052 | 0 | 54.0255 | 0
336 | 1900-12-02 | 8053 | 0 | 49.4244 | 0
336 | 1900-12-02 | 8054 | 0 | 40.4802 | 0
336 | 1900-12-02 | 8055 | 0 | 41.9061 | 0
336 | 1900-12-02 | 8056 | 0 | 48.7207 | 0
336 | 1900-12-02 | 8057 | 0 | 51.9698 | 0
336 | 1900-12-02 | 8058 | 0 | 43.2024 | 0
336 | 1900-12-02 | 8059 | 0 | 45.3357 | 0
336 | 1900-12-02 | 8060 | 0 | 32.606 | 0
336 | 1900-12-02 | 8061 | 0 | 27.6226 | 0
336 | 1900-12-02 | 8062 | 0 | 27.8942 | 0
336 | 1900-12-02 | 8063 | 0 | 31.9871 | 0
336 | 1900-12-02 | 8064 | 0 | 19.9958 | 0
337 | 1900-12-03 | 8065 | 0 | 32.9392 | 0
337 | 1900-12-03 | 8066 | 0 | 31.1069 | 0
337 | 1900-12-03 | 8067 | 0 | 33.9164 | 0
337 | 1900-12-03 | 8068 | 0 | 23.4937 | 0
337 | 1900-12-03 | 8069 | 0 | 45.5594 | 0
337 | 1900-12-03 | 8070 | 0 | 101.3945 | 0
337 | 1900-12-03 | 8071 | 0 | 316.6724 | 0
337 | 1900-12-03 | 8072 | 0 | 126.1754 | 0
337 | 1900-12-03 | 8073 | 0 | 123.3389 | 0
337 | 1900-12-03 | 8074 | 0 | 86.6956 | 0
337 | 1900-12-03 | 8075 | 0 | 51.6597 | 0
337 | 1900-12-03 | 8076 | 0 | 102.8882 | 0
337 | 1900-12-03 | 8077 | 0 | 136.1415 | 0
337 | 1900-12-03 | 8078 | 0 | 111.9721 | 0
337 | 1900-12-03 | 8079 | 0 | 82.732 | 0
337 | 1900-12-03 | 8080 | 0 | 43.4655 | 0
337 | 1900-12-03 | 8081 | 0 | 31.3706 | 0
337 | 1900-12-03 | 8082 | 0 | 50.3219 | 0
337 | 1900-12-03 | 8083 | 0 | 246.5801 | 0
337 | 1900-12-03 | 8084 | 0 | 34.3077 | 0
337 | 1900-12-03 | 8085 | 0 | 36.6758 | 0
337 | 1900-12-03 | 8086 | 0 | 32.0411 | 0
337 | 1900-12-03 | 8087 | 0 | 27.3272 | 0
337 | 1900-12-03 | 8088 | 0 | 24.5054 | 0
338 | 1900-12-04 | 8089 | 0 | 30.1717 | 0
338 | 1900-12-04 | 8090 | 0 | 33.3525 | 0
338 | 1900-12-04 | 8091 | 0 | 29.8805 | 0
338 | 1900-12-04 | 8092 | 0 | 26.9201 | 0
338 | 1900-12-04 | 8093 | 0 | 33.6598 | 0
338 | 1900-12-04 | 8094 | 0 | 49.3436 | 0
338 | 1900-12-04 | 8095 | 0 | 99.2338 | 0
338 | 1900-12-04 | 8096 | 0 | 92.4654 | 0
338 | 1900-12-04 | 8097 | 0 | 66.6108 | 0
338 | 1900-12-04 | 8098 | 0 | 77.5106 | 0
338 | 1900-12-04 | 8099 | 0 | 123.8684 | 0
338 | 1900-12-04 | 8100 | 0 | 79.9666 | 0
338 | 1900-12-04 | 8101 | 0 | 41.6356 | 0
338 | 1900-12-04 | 8102 | 0 | 67.1768 | 0
338 | 1900-12-04 | 8103 | 0 | 44.7313 | 0
338 | 1900-12-04 | 8104 | 0 | 249.364 | 0
338 | 1900-12-04 | 8105 | 0 | 62.6523 | 0
338 | 1900-12-04 | 8106 | 0 | 78.4977 | 0
338 | 1900-12-04 | 8107 | 0 | 32.0589 | 0
338 | 1900-12-04 | 8108 | 0 | 33.1959 | 0
338 | 1900-12-04 | 8109 | 0 | 31.5501 | 0
338 | 1900-12-04 | 8110 | 0 | 30.6926 | 0
338 | 1900-12-04 | 8111 | 0 | 29.1855 | 0
338 | 1900-12-04 | 8112 | 0 | 32.5775 | 0
339 | 1900-12-05 | 8113 | 0 | 29.318 | 0
339 | 1900-12-05 | 8114 | 0 | 34.4811 | 0
339 | 1900-12-05 | 8115 | 0 | 31.2504 | 0
339 | 1900-12-05 | 8116 | 0 | 29.9184 | 0
339 | 1900-12-05 | 8117 | 0 | 26.1197 | 0
339 | 1900-12-05 | 8118 | 0 | 30.329 | 0
339 | 1900-12-05 | 8119 | 0 | 27.0454 | 0
339 | 1900-12-05 | 8120 | 0 | 38.3166 | 0
339 | 1900-12-05 | 8121 | 0 | 52.0312 | 0
339 | 1900-12-05 | 8122 | 0 | 53.5876 | 0
339 | 1900-12-05 | 8123 | 0 | 55.2992 | 0
339 | 1900-12-05 | 8124 | 0 | 105.9109 | 0
339 | 1900-12-05 | 8125 | 0 | 130.2401 | 0
339 | 1900-12-05 | 8126 | 0 | 122.6961 | 0
339 | 1900-12-05 | 8127 | 0 | 71.3182 | 0
339 | 1900-12-05 | 8128 | 0 | 37.3672 | 0
339 | 1900-12-05 | 8129 | 0 | 38.1744 | 0
339 | 1900-12-05 | 8130 | 0 | 47.2404 | 0
339 | 1900-12-05 | 8131 | 0 | 39.0389 | 0
339 | 1900-12-05 | 8132 | 0 | 31.5322 | 0
339 | 1900-12-05 | 8133 | 0 | 30.3893 | 0
339 | 1900-12-05 | 8134 | 0 | 33.1121 | 0
339 | 1900-12-05 | 8135 | 0 | 31.7411 | 0
339 | 1900-12-05 | 8136 | 0 | 29.3927 | 0
340 | 1900-12-06 | 8137 | 0 | 232.2018 | 0
340 | 1900-12-06 | 8138 | 0 | 23.0173 | 0
340 | 1900-12-06 | 8139 | 0 | 33.434 | 0
340 | 1900-12-06 | 8140 | 0 | 30.2474 | 0
340 | 1900-12-06 | 8141 | 0 | 34.2763 | 0
340 | 1900-12-06 | 8142 | 0 | 64.3302 | 0
340 | 1900-12-06 | 8143 | 0 | 56.9391 | 0
340 | 1900-12-06 | 8144 | 0 | 68.0157 | 0
340 | 1900-12-06 | 8145 | 0 | 110.0333 | 0
340 | 1900-12-06 | 8146 | 0 | 103.4863 | 0
340 | 1900-12-06 | 8147 | 0 | 89.6663 | 0
340 | 1900-12-06 | 8148 | 0 | 49.7329 | 0
340 | 1900-12-06 | 8149 | 0 | 73.1657 | 0
340 | 1900-12-06 | 8150 | 0 | 114.8281 | 0
340 | 1900-12-06 | 8151 | 0 | 82.3935 | 0
340 | 1900-12-06 | 8152 | 0 | 40.7098 | 0
340 | 1900-12-06 | 8153 | 0 | 36.5845 | 0
340 | 1900-12-06 | 8154 | 0 | 35.5267 | 0
340 | 1900-12-06 | 8155 | 0 | 40.5244 | 0
340 | 1900-12-06 | 8156 | 0 | 33.7389 | 0
340 | 1900-12-06 | 8157 | 0 | 29.2295 | 0
340 | 1900-12-06 | 8158 | 0 | 31.4255 | 0
340 | 1900-12-06 | 8159 | 0 | 28.8397 | 0
340 | 1900-12-06 | 8160 | 0 | 22.4818 | 0
341 | 1900-12-07 | 8161 | 0 | 228.4167 | 0
341 | 1900-12-07 | 8162 | 0 | 24.629 | 0
341 | 1900-12-07 | 8163 | 0 | 31.2314 | 0
341 | 1900-12-07 | 8164 | 0 | 28.3642 | 0
341 | 1900-12-07 | 8165 | 0 | 25.9622 | 0
341 | 1900-12-07 | 8166 | 0 | 56.1556 | 0
341 | 1900-12-07 | 8167 | 0 | 68.781 | 0
341 | 1900-12-07 | 8168 | 0 | 40.6777 | 0
341 | 1900-12-07 | 8169 | 0 | 76.9439 | 0
341 | 1900-12-07 | 8170 | 0 | 98.7766 | 0
341 | 1900-12-07 | 8171 | 0 | 73.1009 | 0
341 | 1900-12-07 | 8172 | 0 | 44.4203 | 0
341 | 1900-12-07 | 8173 | 0 | 45.9892 | 0
341 | 1900-12-07 | 8174 | 0 | 49.6195 | 0
341 | 1900-12-07 | 8175 | 0 | 47.3053 | 0
341 | 1900-12-07 | 8176 | 0 | 45.3752 | 0
341 | 1900-12-07 | 8177 | 0 | 32.2655 | 0
341 | 1900-12-07 | 8178 | 0 | 47.1129 | 0
341 | 1900-12-07 | 8179 | 0 | 45.766 | 0
341 | 1900-12-07 | 8180 | 0 | 27.1511 | 0
341 | 1900-12-07 | 8181 | 0 | 29.3748 | 0
341 | 1900-12-07 | 8182 | 0 | 29.2252 | 0
341 | 1900-12-07 | 8183 | 0 | 24.4113 | 0
341 | 1900-12-07 | 8184 | 0 | 32.989 | 0
342 | 1900-12-08 | 8185 | 0 | 33.56 | 0
342 | 1900-12-08 | 8186 | 0 | 28.4302 | 0
342 | 1900-12-08 | 8187 | 0 | 28.8917 | 0
342 | 1900-12-08 | 8188 | 0 | 28.4869 | 0
342 | 1900-12-08 | 8189 | 0 | 36.3331 | 0
342 | 1900-12-08 | 8190 | 0 | 23.9321 | 0
342 | 1900-12-08 | 8191 | 0 | 29.2262 | 0
342 | 1900-12-08 | 8192 | 0 | 51.1169 | 0
342 | 1900-12-08 | 8193 | 0 | 50.6221 | 0
342 | 1900-12-08 | 8194 | 0 | 33.1795 | 0
342 | 1900-12-08 | 8195 | 0 | 34.3774 | 0
342 | 1900-12-08 | 8196 | 0 | 46.2181 | 0
342 | 1900-12-08 | 8197 | 0 | 229.0288 | 0
342 | 1900-12-08 | 8198 | 0 | 40.9918 | 0
342 | 1900-12-08 | 8199 | 0 | 41.3867 | 0
342 | 1900-12-08 | 8200 | 0 | 46.5739 | 0
342 | 1900-12-08 | 8201 | 0 | 38.8844 | 0
342 | 1900-12-08 | 8202 | 0 | 36.9608 | 0
342 | 1900-12-08 | 8203 | 0 | 42.7004 | 0
342 | 1900-12-08 | 8204 | 0 | 21.037 | 0
342 | 1900-12-08 | 8205 | 0 | 24.9416 | 0
342 | 1900-12-08 | 8206 | 0 | 27.6453 | 0
342 | 1900-12-08 | 8207 | 0 | 24.7286 | 0
342 | 1900-12-08 | 8208 | 0 | 28.167 | 0
343 | 1900-12-09 | 8209 | 0 | 26.1845 | 0
343 | 1900-12-09 | 8210 | 0 | 23.5792 | 0
343 | 1900-12-09 | 8211 | 0 | 33.0241 | 0
343 | 1900-12-09 | 8212 | 0 | 30.2973 | 0
343 | 1900-12-09 | 8213 | 0 | 31.6869 | 0
343 | 1900-12-09 | 8214 | 0 | 31.3366 | 0
343 | 1900-12-09 | 8215 | 0 | 25.2587 | 0
343 | 1900-12-09 | 8216 | 0 | 42.1952 | 0
343 | 1900-12-09 | 8217 | 0 | 42.2931 | 0
343 | 1900-12-09 | 8218 | 0 | 44.5054 | 0
343 | 1900-12-09 | 8219 | 0 | 38.962 | 0
343 | 1900-12-09 | 8220 | 0 | 29.1008 | 0
343 | 1900-12-09 | 8221 | 0 | 51.4698 | 0
343 | 1900-12-09 | 8222 | 0 | 45.8119 | 0
343 | 1900-12-09 | 8223 | 0 | 35.4448 | 0
343 | 1900-12-09 | 8224 | 0 | 29.1325 | 0
343 | 1900-12-09 | 8225 | 0 | 35.9972 | 0
343 | 1900-12-09 | 8226 | 0 | 34.3837 | 0
343 | 1900-12-09 | 8227 | 0 | 43.9461 | 0
343 | 1900-12-09 | 8228 | 0 | 29.23 | 0
343 | 1900-12-09 | 8229 | 0 | 27.0872 | 0
343 | 1900-12-09 | 8230 | 0 | 31.7995 | 0
343 | 1900-12-09 | 8231 | 0 | 27.4459 | 0
343 | 1900-12-09 | 8232 | 0 | 27.9838 | 0
344 | 1900-12-10 | 8233 | 0 | 32.9931 | 0
344 | 1900-12-10 | 8234 | 0 | 31.492 | 0
344 | 1900-12-10 | 8235 | 0 | 24.0464 | 0
344 | 1900-12-10 | 8236 | 0 | 26.1831 | 0
344 | 1900-12-10 | 8237 | 0 | 46.7822 | 0
344 | 1900-12-10 | 8238 | 0 | 75.6236 | 0
344 | 1900-12-10 | 8239 | 0 | 123.9454 | 0
344 | 1900-12-10 | 8240 | 0 | 507.4551 | 0
344 | 1900-12-10 | 8241 | 0 | 111.8511 | 0
344 | 1900-12-10 | 8242 | 0 | 80.9954 | 0
344 | 1900-12-10 | 8243 | 0 | 128.7525 | 0
344 | 1900-12-10 | 8244 | 0 | 76.1561 | 0
344 | 1900-12-10 | 8245 | 0 | 61.2088 | 0
344 | 1900-12-10 | 8246 | 0 | 118.3478 | 0
344 | 1900-12-10 | 8247 | 0 | 83.9583 | 0
344 | 1900-12-10 | 8248 | 0 | 40.7168 | 0
344 | 1900-12-10 | 8249 | 0 | 44.1286 | 0
344 | 1900-12-10 | 8250 | 0 | 55.6957 | 0
344 | 1900-12-10 | 8251 | 0 | 34.3015 | 0
344 | 1900-12-10 | 8252 | 0 | 35.6065 | 0
344 | 1900-12-10 | 8253 | 0 | 26.5942 | 0
344 | 1900-12-10 | 8254 | 0 | 30.761 | 0
344 | 1900-12-10 | 8255 | 0 | 23.7392 | 0
344 | 1900-12-10 | 8256 | 0 | 26.0438 | 0
345 | 1900-12-11 | 8257 | 0 | 23.3794 | 0
345 | 1900-12-11 | 8258 | 0 | 27.8011 | 0
345 | 1900-12-11 | 8259 | 0 | 27.7697 | 0
345 | 1900-12-11 | 8260 | 0 | 32.0897 | 0
345 | 1900-12-11 | 8261 | 0 | 32.5094 | 0
345 | 1900-12-11 | 8262 | 0 | 35.7483 | 0
345 | 1900-12-11 | 8263 | 0 | 94.7816 | 0
345 | 1900-12-11 | 8264 | 0 | 104.2469 | 0
345 | 1900-12-11 | 8265 | 0 | 72.3961 | 0
345 | 1900-12-11 | 8266 | 0 | 68.5425 | 0
345 | 1900-12-11 | 8267 | 0 | 92.6883 | 0
345 | 1900-12-11 | 8268 | 0 | 59.5459 | 0
345 | 1900-12-11 | 8269 | 0 | 299.3321 | 0
345 | 1900-12-11 | 8270 | 0 | 47.2646 | 0
345 | 1900-12-11 | 8271 | 0 | 47.8032 | 0
345 | 1900-12-11 | 8272 | 0 | 60.1917 | 0
345 | 1900-12-11 | 8273 | 0 | 50.6268 | 0
345 | 1900-12-11 | 8274 | 0 | 44.5687 | 0
345 | 1900-12-11 | 8275 | 0 | 38.5096 | 0
345 | 1900-12-11 | 8276 | 0 | 25.3493 | 0
345 | 1900-12-11 | 8277 | 0 | 32.606 | 0
345 | 1900-12-11 | 8278 | 0 | 23.6054 | 0
345 | 1900-12-11 | 8279 | 0 | 29.3469 | 0
345 | 1900-12-11 | 8280 | 0 | 24.3486 | 0
346 | 1900-12-12 | 8281 | 0 | 22.4066 | 0
346 | 1900-12-12 | 8282 | 0 | 30.7442 | 0
346 | 1900-12-12 | 8283 | 0 | 26.9075 | 0
346 | 1900-12-12 | 8284 | 0 | 26.7397 | 0
346 | 1900-12-12 | 8285 | 0 | 25.3055 | 0
346 | 1900-12-12 | 8286 | 0 | 29.818 | 0
346 | 1900-12-12 | 8287 | 0 | 24.0943 | 0
346 | 1900-12-12 | 8288 | 0 | 39.8028 | 0
346 | 1900-12-12 | 8289 | 0 | 248.47 | 0
346 | 1900-12-12 | 8290 | 0 | 42.2085 | 0
346 | 1900-12-12 | 8291 | 0 | 34.8017 | 0
346 | 1900-12-12 | 8292 | 0 | 54.5515 | 0
346 | 1900-12-12 | 8293 | 0 | 47.7432 | 0
346 | 1900-12-12 | 8294 | 0 | 38.006 | 0
346 | 1900-12-12 | 8295 | 0 | 49.7609 | 0
346 | 1900-12-12 | 8296 | 0 | 45.9172 | 0
346 | 1900-12-12 | 8297 | 0 | 37.8507 | 0
346 | 1900-12-12 | 8298 | 0 | 56.7122 | 0
346 | 1900-12-12 | 8299 | 0 | 71.7553 | 0
346 | 1900-12-12 | 8300 | 0 | 46.9771 | 0
346 | 1900-12-12 | 8301 | 0 | 92.5952 | 0
346 | 1900-12-12 | 8302 | 0 | 67.7786 | 0
346 | 1900-12-12 | 8303 | 0 | 78.4219 | 0
346 | 1900-12-12 | 8304 | 0 | 92.6617 | 0
347 | 1900-12-13 | 8305 | 0 | 70.1312 | 0
347 | 1900-12-13 | 8306 | 0 | 41.5008 | 0
347 | 1900-12-13 | 8307 | 0 | 22.3141 | 0
347 | 1900-12-13 | 8308 | 0 | 234.6422 | 0
347 | 1900-12-13 | 8309 | 0 | 35.9158 | 0
347 | 1900-12-13 | 8310 | 0 | 56.3058 | 0
347 | 1900-12-13 | 8311 | 0 | 74.0464 | 0
347 | 1900-12-13 | 8312 | 0 | 92.1459 | 0
347 | 1900-12-13 | 8313 | 0 | 89.8072 | 0
347 | 1900-12-13 | 8314 | 0 | 47.7123 | 0
347 | 1900-12-13 | 8315 | 0 | 29.5372 | 0
347 | 1900-12-13 | 8316 | 0 | 48.6551 | 0
347 | 1900-12-13 | 8317 | 0 | 246.1481 | 0
347 | 1900-12-13 | 8318 | 0 | 38.5047 | 0
347 | 1900-12-13 | 8319 | 0 | 42.1089 | 0
347 | 1900-12-13 | 8320 | 0 | 38.0305 | 0
347 | 1900-12-13 | 8321 | 0 | 42.1431 | 0
347 | 1900-12-13 | 8322 | 0 | 33.3574 | 0
347 | 1900-12-13 | 8323 | 0 | 60.5675 | 0
347 | 1900-12-13 | 8324 | 0 | 75.353 | 0
347 | 1900-12-13 | 8325 | 0 | 45.4028 | 0
347 | 1900-12-13 | 8326 | 0 | 92.3505 | 0
347 | 1900-12-13 | 8327 | 0 | 40.9489 | 0
347 | 1900-12-13 | 8328 | 0 | 104.9472 | 0
348 | 1900-12-14 | 8329 | 0 | 76.5014 | 0
348 | 1900-12-14 | 8330 | 0 | 296.2401 | 0
348 | 1900-12-14 | 8331 | 0 | 66.5857 | 0
348 | 1900-12-14 | 8332 | 0 | 20.859 | 0
348 | 1900-12-14 | 8333 | 0 | 22.7528 | 0
348 | 1900-12-14 | 8334 | 0 | 34.4105 | 0
348 | 1900-12-14 | 8335 | 0 | 70.8516 | 0
348 | 1900-12-14 | 8336 | 0 | 45.1337 | 0
348 | 1900-12-14 | 8337 | 0 | 69.3587 | 0
348 | 1900-12-14 | 8338 | 0 | 92.436 | 0
348 | 1900-12-14 | 8339 | 0 | 59.1146 | 0
348 | 1900-12-14 | 8340 | 0 | 47.9237 | 0
348 | 1900-12-14 | 8341 | 0 | 47.8645 | 0
348 | 1900-12-14 | 8342 | 0 | 46.0715 | 0
348 | 1900-12-14 | 8343 | 0 | 49.7895 | 0
348 | 1900-12-14 | 8344 | 0 | 45.333 | 0
348 | 1900-12-14 | 8345 | 0 | 31.6848 | 0
348 | 1900-12-14 | 8346 | 0 | 51.8175 | 0
348 | 1900-12-14 | 8347 | 0 | 34.8412 | 0
348 | 1900-12-14 | 8348 | 0 | 34.0304 | 0
348 | 1900-12-14 | 8349 | 0 | 28.7348 | 0
348 | 1900-12-14 | 8350 | 0 | 221.4133 | 0
348 | 1900-12-14 | 8351 | 0 | 29.0594 | 0
348 | 1900-12-14 | 8352 | 0 | 34.0048 | 0
349 | 1900-12-15 | 8353 | 0 | 24.2617 | 0
349 | 1900-12-15 | 8354 | 0 | 27.2138 | 0
349 | 1900-12-15 | 8355 | 0 | 30.0893 | 0
349 | 1900-12-15 | 8356 | 0 | 25.1933 | 0
349 | 1900-12-15 | 8357 | 0 | 35.9141 | 0
349 | 1900-12-15 | 8358 | 0 | 24.8427 | 0
349 | 1900-12-15 | 8359 | 0 | 35.7937 | 0
349 | 1900-12-15 | 8360 | 0 | 32.3465 | 0
349 | 1900-12-15 | 8361 | 0 | 36.1303 | 0
349 | 1900-12-15 | 8362 | 0 | 44.1971 | 0
349 | 1900-12-15 | 8363 | 0 | 60.3616 | 0
349 | 1900-12-15 | 8364 | 0 | 43.367 | 0
349 | 1900-12-15 | 8365 | 0 | 33.8472 | 0
349 | 1900-12-15 | 8366 | 0 | 29.8309 | 0
349 | 1900-12-15 | 8367 | 0 | 49.0767 | 0
349 | 1900-12-15 | 8368 | 0 | 31.9156 | 0
349 | 1900-12-15 | 8369 | 0 | 48.3795 | 0
349 | 1900-12-15 | 8370 | 0 | 39.0937 | 0
349 | 1900-12-15 | 8371 | 0 | 35.8524 | 0
349 | 1900-12-15 | 8372 | 0 | 230.2328 | 0
349 | 1900-12-15 | 8373 | 0 | 36.0743 | 0
349 | 1900-12-15 | 8374 | 0 | 32.9147 | 0
349 | 1900-12-15 | 8375 | 0 | 31.3635 | 0
349 | 1900-12-15 | 8376 | 0 | 27.0581 | 0
350 | 1900-12-16 | 8377 | 0 | 23.002 | 0
350 | 1900-12-16 | 8378 | 0 | 31.3266 | 0
350 | 1900-12-16 | 8379 | 0 | 33.0835 | 0
350 | 1900-12-16 | 8380 | 0 | 39.5893 | 0
350 | 1900-12-16 | 8381 | 0 | 31.1118 | 0
350 | 1900-12-16 | 8382 | 0 | 24.6647 | 0
350 | 1900-12-16 | 8383 | 0 | 26.877 | 0
350 | 1900-12-16 | 8384 | 0 | 44.5563 | 0
350 | 1900-12-16 | 8385 | 0 | 41.9036 | 0
350 | 1900-12-16 | 8386 | 0 | 56.3217 | 0
350 | 1900-12-16 | 8387 | 0 | 47.2389 | 0
350 | 1900-12-16 | 8388 | 0 | 42.7711 | 0
350 | 1900-12-16 | 8389 | 0 | 50.0367 | 0
350 | 1900-12-16 | 8390 | 0 | 55.0605 | 0
350 | 1900-12-16 | 8391 | 0 | 30.9086 | 0
350 | 1900-12-16 | 8392 | 0 | 42.1939 | 0
350 | 1900-12-16 | 8393 | 0 | 44.5434 | 0
350 | 1900-12-16 | 8394 | 0 | 44.5631 | 0
350 | 1900-12-16 | 8395 | 0 | 249.9315 | 0
350 | 1900-12-16 | 8396 | 0 | 225.6579 | 0
350 | 1900-12-16 | 8397 | 0 | 24.3545 | 0
350 | 1900-12-16 | 8398 | 0 | 27.479 | 0
350 | 1900-12-16 | 8399 | 0 | 32.3054 | 0
350 | 1900-12-16 | 8400 | 0 | 22.1729 | 0
351 | 1900-12-17 | 8401 | 0 | 33.5682 | 0
351 | 1900-12-17 | 8402 | 0 | 31.6343 | 0
351 | 1900-12-17 | 8403 | 0 | 27.7329 | 0
351 | 1900-12-17 | 8404 | 0 | 29.0675 | 0
351 | 1900-12-17 | 8405 | 0 | 24.8192 | 0
351 | 1900-12-17 | 8406 | 0 | 18.7299 | 0
351 | 1900-12-17 | 8407 | 0 | 34.2367 | 0
351 | 1900-12-17 | 8408 | 0 | 39.7738 | 0
351 | 1900-12-17 | 8409 | 0 | 47.8207 | 0
351 | 1900-12-17 | 8410 | 0 | 46.8767 | 0
351 | 1900-12-17 | 8411 | 0 | 46.8111 | 0
351 | 1900-12-17 | 8412 | 0 | 44.9998 | 0
351 | 1900-12-17 | 8413 | 0 | 42.3736 | 0
351 | 1900-12-17 | 8414 | 0 | 36.4147 | 0
351 | 1900-12-17 | 8415 | 0 | 44.8942 | 0
351 | 1900-12-17 | 8416 | 0 | 41.7302 | 0
351 | 1900-12-17 | 8417 | 0 | 42.064 | 0
351 | 1900-12-17 | 8418 | 0 | 36.5816 | 0
351 | 1900-12-17 | 8419 | 0 | 46.6379 | 0
351 | 1900-12-17 | 8420 | 0 | 25.4059 | 0
351 | 1900-12-17 | 8421 | 0 | 28.2553 | 0
351 | 1900-12-17 | 8422 | 0 | 27.3932 | 0
351 | 1900-12-17 | 8423 | 0 | 22.0562 | 0
351 | 1900-12-17 | 8424 | 0 | 28.5045 | 0
352 | 1900-12-18 | 8425 | 0 | 30.391 | 0
352 | 1900-12-18 | 8426 | 0 | 25.2601 | 0
352 | 1900-12-18 | 8427 | 0 | 34.7213 | 0
352 | 1900-12-18 | 8428 | 0 | 229.1656 | 0
352 | 1900-12-18 | 8429 | 0 | 31.2092 | 0
352 | 1900-12-18 | 8430 | 0 | 22.4246 | 0
352 | 1900-12-18 | 8431 | 0 | 25.3983 | 0
352 | 1900-12-18 | 8432 | 0 | 42.3557 | 0
352 | 1900-12-18 | 8433 | 0 | 43.7652 | 0
352 | 1900-12-18 | 8434 | 0 | 51.1337 | 0
352 | 1900-12-18 | 8435 | 0 | 36.5882 | 0
352 | 1900-12-18 | 8436 | 0 | 41.8076 | 0
352 | 1900-12-18 | 8437 | 0 | 36.7775 | 0
352 | 1900-12-18 | 8438 | 0 | 36.3739 | 0
352 | 1900-12-18 | 8439 | 0 | 48.6655 | 0
352 | 1900-12-18 | 8440 | 0 | 39.8838 | 0
352 | 1900-12-18 | 8441 | 0 | 50.4673 | 0
352 | 1900-12-18 | 8442 | 0 | 50.7687 | 0
352 | 1900-12-18 | 8443 | 0 | 54.9389 | 0
352 | 1900-12-18 | 8444 | 0 | 28.1306 | 0
352 | 1900-12-18 | 8445 | 0 | 32.5704 | 0
352 | 1900-12-18 | 8446 | 0 | 24.8277 | 0
352 | 1900-12-18 | 8447 | 0 | 31.2916 | 0
352 | 1900-12-18 | 8448 | 0 | 22.9259 | 0
353 | 1900-12-19 | 8449 | 0 | 23.5626 | 0
353 | 1900-12-19 | 8450 | 0 | 20.4631 | 0
353 | 1900-12-19 | 8451 | 0 | 16.6457 | 0
353 | 1900-12-19 | 8452 | 0 | 28.1539 | 0
353 | 1900-12-19 | 8453 | 0 | 29.6454 | 0
353 | 1900-12-19 | 8454 | 0 | 30.6985 | 0
353 | 1900-12-19 | 8455 | 0 | 28.7949 | 0
353 | 1900-12-19 | 8456 | 0 | 50.6918 | 0
353 | 1900-12-19 | 8457 | 0 | 33.1516 | 0
353 | 1900-12-19 | 8458 | 0 | 39.9027 | 0
353 | 1900-12-19 | 8459 | 0 | 46.0946 | 0
353 | 1900-12-19 | 8460 | 0 | 42.3205 | 0
353 | 1900-12-19 | 8461 | 0 | 44.2668 | 0
353 | 1900-12-19 | 8462 | 0 | 37.0788 | 0
353 | 1900-12-19 | 8463 | 0 | 31.7223 | 0
353 | 1900-12-19 | 8464 | 0 | 36.4735 | 0
353 | 1900-12-19 | 8465 | 0 | 36.6568 | 0
353 | 1900-12-19 | 8466 | 0 | 250.1009 | 0
353 | 1900-12-19 | 8467 | 0 | 55.969 | 0
353 | 1900-12-19 | 8468 | 0 | 28.5456 | 0
353 | 1900-12-19 | 8469 | 0 | 28.9498 | 0
353 | 1900-12-19 | 8470 | 0 | 30.2361 | 0
353 | 1900-12-19 | 8471 | 0 | 24.6219 | 0
353 | 1900-12-19 | 8472 | 0 | 34.991 | 0
354 | 1900-12-20 | 8473 | 0 | 31.5389 | 0
354 | 1900-12-20 | 8474 | 0 | 220.376 | 0
354 | 1900-12-20 | 8475 | 0 | 37.4758 | 0
354 | 1900-12-20 | 8476 | 0 | 28.1803 | 0
354 | 1900-12-20 | 8477 | 0 | 29.4713 | 0
354 | 1900-12-20 | 8478 | 0 | 30.8986 | 0
354 | 1900-12-20 | 8479 | 0 | 31.3883 | 0
354 | 1900-12-20 | 8480 | 0 | 41.8055 | 0
354 | 1900-12-20 | 8481 | 0 | 45.9715 | 0
354 | 1900-12-20 | 8482 | 0 | 49.1325 | 0
354 | 1900-12-20 | 8483 | 0 | 40.9107 | 0
354 | 1900-12-20 | 8484 | 0 | 45.2558 | 0
354 | 1900-12-20 | 8485 | 0 | 40.4082 | 0
354 | 1900-12-20 | 8486 | 0 | 42.4241 | 0
354 | 1900-12-20 | 8487 | 0 | 41.3167 | 0
354 | 1900-12-20 | 8488 | 0 | 35.3661 | 0
354 | 1900-12-20 | 8489 | 0 | 38.1434 | 0
354 | 1900-12-20 | 8490 | 0 | 39.7012 | 0
354 | 1900-12-20 | 8491 | 0 | 24.2799 | 0
354 | 1900-12-20 | 8492 | 0 | 26.1027 | 0
354 | 1900-12-20 | 8493 | 0 | 35.8309 | 0
354 | 1900-12-20 | 8494 | 0 | 25.6945 | 0
354 | 1900-12-20 | 8495 | 0 | 35.7209 | 0
354 | 1900-12-20 | 8496 | 0 | 24.6707 | 0
355 | 1900-12-21 | 8497 | 0 | 35.8777 | 0
355 | 1900-12-21 | 8498 | 0 | 22.2563 | 0
355 | 1900-12-21 | 8499 | 0 | 23.4637 | 0
355 | 1900-12-21 | 8500 | 0 | 30.9654 | 0
355 | 1900-12-21 | 8501 | 0 | 29.2584 | 0
355 | 1900-12-21 | 8502 | 0 | 30.9499 | 0
355 | 1900-12-21 | 8503 | 0 | 31.3643 | 0
355 | 1900-12-21 | 8504 | 0 | 47.931 | 0
355 | 1900-12-21 | 8505 | 0 | 38.9205 | 0
355 | 1900-12-21 | 8506 | 0 | 51.9111 | 0
355 | 1900-12-21 | 8507 | 0 | 41.3684 | 0
355 | 1900-12-21 | 8508 | 0 | 45.0167 | 0
355 | 1900-12-21 | 8509 | 0 | 38.3206 | 0
355 | 1900-12-21 | 8510 | 0 | 42.7647 | 0
355 | 1900-12-21 | 8511 | 0 | 42.2361 | 0
355 | 1900-12-21 | 8512 | 0 | 34.5109 | 0
355 | 1900-12-21 | 8513 | 0 | 48.5598 | 0
355 | 1900-12-21 | 8514 | 0 | 42.5681 | 0
355 | 1900-12-21 | 8515 | 0 | 53.7892 | 0
355 | 1900-12-21 | 8516 | 0 | 227.2957 | 0
355 | 1900-12-21 | 8517 | 0 | 23.9718 | 0
355 | 1900-12-21 | 8518 | 0 | 31.336 | 0
355 | 1900-12-21 | 8519 | 0 | 33.1202 | 0
355 | 1900-12-21 | 8520 | 0 | 22.7966 | 0
356 | 1900-12-22 | 8521 | 0 | 32.804 | 0
356 | 1900-12-22 | 8522 | 0 | 34.0441 | 0
356 | 1900-12-22 | 8523 | 0 | 25.5485 | 0
356 | 1900-12-22 | 8524 | 0 | 34.7565 | 0
356 | 1900-12-22 | 8525 | 0 | 32.7634 | 0
356 | 1900-12-22 | 8526 | 0 | 31.8909 | 0
356 | 1900-12-22 | 8527 | 0 | 35.1234 | 0
356 | 1900-12-22 | 8528 | 0 | 42.681 | 0
356 | 1900-12-22 | 8529 | 0 | 54.7089 | 0
356 | 1900-12-22 | 8530 | 0 | 46.1754 | 0
356 | 1900-12-22 | 8531 | 0 | 42.0573 | 0
356 | 1900-12-22 | 8532 | 0 | 41.8355 | 0
356 | 1900-12-22 | 8533 | 0 | 37.9495 | 0
356 | 1900-12-22 | 8534 | 0 | 37.6448 | 0
356 | 1900-12-22 | 8535 | 0 | 37.3127 | 0
356 | 1900-12-22 | 8536 | 0 | 44.4715 | 0
356 | 1900-12-22 | 8537 | 0 | 50.7947 | 0
356 | 1900-12-22 | 8538 | 0 | 37.594 | 0
356 | 1900-12-22 | 8539 | 0 | 38.9118 | 0
356 | 1900-12-22 | 8540 | 0 | 24.9614 | 0
356 | 1900-12-22 | 8541 | 0 | 29.2321 | 0
356 | 1900-12-22 | 8542 | 0 | 28.2424 | 0
356 | 1900-12-22 | 8543 | 0 | 23.2191 | 0
356 | 1900-12-22 | 8544 | 0 | 39.1023 | 0
357 | 1900-12-23 | 8545 | 0 | 41.3942 | 0
357 | 1900-12-23 | 8546 | 0 | 29.3625 | 0
357 | 1900-12-23 | 8547 | 0 | 32.2566 | 0
357 | 1900-12-23 | 8548 | 0 | 35.0146 | 0
357 | 1900-12-23 | 8549 | 0 | 28.9906 | 0
357 | 1900-12-23 | 8550 | 0 | 31.9485 | 0
357 | 1900-12-23 | 8551 | 0 | 25.4984 | 0
357 | 1900-12-23 | 8552 | 0 | 48.2724 | 0
357 | 1900-12-23 | 8553 | 0 | 241.7839 | 0
357 | 1900-12-23 | 8554 | 0 | 49.8417 | 0
357 | 1900-12-23 | 8555 | 0 | 42.173 | 0
357 | 1900-12-23 | 8556 | 0 | 34.1835 | 0
357 | 1900-12-23 | 8557 | 0 | 50.3572 | 0
357 | 1900-12-23 | 8558 | 0 | 29.2151 | 0
357 | 1900-12-23 | 8559 | 0 | 44.9509 | 0
357 | 1900-12-23 | 8560 | 0 | 36.2958 | 0
357 | 1900-12-23 | 8561 | 0 | 52.6594 | 0
357 | 1900-12-23 | 8562 | 0 | 29.0572 | 0
357 | 1900-12-23 | 8563 | 0 | 38.6096 | 0
357 | 1900-12-23 | 8564 | 0 | 25.8059 | 0
357 | 1900-12-23 | 8565 | 0 | 32.2146 | 0
357 | 1900-12-23 | 8566 | 0 | 26.827 | 0
357 | 1900-12-23 | 8567 | 0 | 28.7483 | 0
357 | 1900-12-23 | 8568 | 0 | 32.1541 | 0
358 | 1900-12-24 | 8569 | 0 | 225.5404 | 0
358 | 1900-12-24 | 8570 | 0 | 27.5207 | 0
358 | 1900-12-24 | 8571 | 0 | 22.594 | 0
358 | 1900-12-24 | 8572 | 0 | 30.6044 | 0
358 | 1900-12-24 | 8573 | 0 | 23.3474 | 0
358 | 1900-12-24 | 8574 | 0 | 25.9066 | 0
358 | 1900-12-24 | 8575 | 0 | 23.1477 | 0
358 | 1900-12-24 | 8576 | 0 | 39.4357 | 0
358 | 1900-12-24 | 8577 | 0 | 51.011 | 0
358 | 1900-12-24 | 8578 | 0 | 39.8325 | 0
358 | 1900-12-24 | 8579 | 0 | 46.9201 | 0
358 | 1900-12-24 | 8580 | 0 | 36.4446 | 0
358 | 1900-12-24 | 8581 | 0 | 49.6177 | 0
358 | 1900-12-24 | 8582 | 0 | 40.9403 | 0
358 | 1900-12-24 | 8583 | 0 | 53.2815 | 0
358 | 1900-12-24 | 8584 | 0 | 37.2602 | 0
358 | 1900-12-24 | 8585 | 0 | 37.1557 | 0
358 | 1900-12-24 | 8586 | 0 | 53.7084 | 0
358 | 1900-12-24 | 8587 | 0 | 30.7933 | 0
358 | 1900-12-24 | 8588 | 0 | 33.0721 | 0
358 | 1900-12-24 | 8589 | 0 | 18.7849 | 0
358 | 1900-12-24 | 8590 | 0 | 27.6093 | 0
358 | 1900-12-24 | 8591 | 0 | 25.6449 | 0
358 | 1900-12-24 | 8592 | 0 | 27.8111 | 0
359 | 1900-12-25 | 8593 | 0 | 20.5884 | 0
359 | 1900-12-25 | 8594 | 0 | 25.4483 | 0
359 | 1900-12-25 | 8595 | 0 | 26.1744 | 0
359 | 1900-12-25 | 8596 | 0 | 24.7669 | 0
359 | 1900-12-25 | 8597 | 0 | 31.3287 | 0
359 | 1900-12-25 | 8598 | 0 | 30.7598 | 0
359 | 1900-12-25 | 8599 | 0 | 32.7575 | 0
359 | 1900-12-25 | 8600 | 0 | 49.9593 | 0
359 | 1900-12-25 | 8601 | 0 | 231.5336 | 0
359 | 1900-12-25 | 8602 | 0 | 51.5644 | 0
359 | 1900-12-25 | 8603 | 0 | 50.0929 | 0
359 | 1900-12-25 | 8604 | 0 | 35.1169 | 0
359 | 1900-12-25 | 8605 | 0 | 52.7803 | 0
359 | 1900-12-25 | 8606 | 0 | 30.0918 | 0
359 | 1900-12-25 | 8607 | 0 | 53.5516 | 0
359 | 1900-12-25 | 8608 | 0 | 32.5194 | 0
359 | 1900-12-25 | 8609 | 0 | 48.276 | 0
359 | 1900-12-25 | 8610 | 0 | 42.812 | 0
359 | 1900-12-25 | 8611 | 0 | 44.5571 | 0
359 | 1900-12-25 | 8612 | 0 | 31.7671 | 0
359 | 1900-12-25 | 8613 | 0 | 31.0298 | 0
359 | 1900-12-25 | 8614 | 0 | 30.604 | 0
359 | 1900-12-25 | 8615 | 0 | 24.9789 | 0
359 | 1900-12-25 | 8616 | 0 | 28.7148 | 0
360 | 1900-12-26 | 8617 | 0 | 28.4794 | 0
360 | 1900-12-26 | 8618 | 0 | 25.4953 | 0
360 | 1900-12-26 | 8619 | 0 | 30.4608 | 0
360 | 1900-12-26 | 8620 | 0 | 22.3577 | 0
360 | 1900-12-26 | 8621 | 0 | 30.5587 | 0
360 | 1900-12-26 | 8622 | 0 | 33.2031 | 0
360 | 1900-12-26 | 8623 | 0 | 26.4644 | 0
360 | 1900-12-26 | 8624 | 0 | 29.0861 | 0
360 | 1900-12-26 | 8625 | 0 | 40.4249 | 0
360 | 1900-12-26 | 8626 | 0 | 50.6101 | 0
360 | 1900-12-26 | 8627 | 0 | 46.0935 | 0
360 | 1900-12-26 | 8628 | 0 | 46.6295 | 0
360 | 1900-12-26 | 8629 | 0 | 38.7559 | 0
360 | 1900-12-26 | 8630 | 0 | 37.3425 | 0
360 | 1900-12-26 | 8631 | 0 | 46.0966 | 0
360 | 1900-12-26 | 8632 | 0 | 230.5542 | 0
360 | 1900-12-26 | 8633 | 0 | 33.5357 | 0
360 | 1900-12-26 | 8634 | 0 | 248.1083 | 0
360 | 1900-12-26 | 8635 | 0 | 39.267 | 0
360 | 1900-12-26 | 8636 | 0 | 30.535 | 0
360 | 1900-12-26 | 8637 | 0 | 20.609 | 0
360 | 1900-12-26 | 8638 | 0 | 29.7363 | 0
360 | 1900-12-26 | 8639 | 0 | 27.6914 | 0
360 | 1900-12-26 | 8640 | 0 | 24.8046 | 0
361 | 1900-12-27 | 8641 | 0 | 34.4501 | 0
361 | 1900-12-27 | 8642 | 0 | 32.4558 | 0
361 | 1900-12-27 | 8643 | 0 | 31.4839 | 0
361 | 1900-12-27 | 8644 | 0 | 32.5246 | 0
361 | 1900-12-27 | 8645 | 0 | 23.0222 | 0
361 | 1900-12-27 | 8646 | 0 | 25.2573 | 0
361 | 1900-12-27 | 8647 | 0 | 37.344 | 0
361 | 1900-12-27 | 8648 | 0 | 45.6916 | 0
361 | 1900-12-27 | 8649 | 0 | 47.6431 | 0
361 | 1900-12-27 | 8650 | 0 | 41.3124 | 0
361 | 1900-12-27 | 8651 | 0 | 37.6975 | 0
361 | 1900-12-27 | 8652 | 0 | 37.8299 | 0
361 | 1900-12-27 | 8653 | 0 | 32.1998 | 0
361 | 1900-12-27 | 8654 | 0 | 45.6294 | 0
361 | 1900-12-27 | 8655 | 0 | 49.3057 | 0
361 | 1900-12-27 | 8656 | 0 | 40.1594 | 0
361 | 1900-12-27 | 8657 | 0 | 242.956 | 0
361 | 1900-12-27 | 8658 | 0 | 39.2208 | 0
361 | 1900-12-27 | 8659 | 0 | 47.6326 | 0
361 | 1900-12-27 | 8660 | 0 | 25.6242 | 0
361 | 1900-12-27 | 8661 | 0 | 24.2632 | 0
361 | 1900-12-27 | 8662 | 0 | 31.9416 | 0
361 | 1900-12-27 | 8663 | 0 | 27.5865 | 0
361 | 1900-12-27 | 8664 | 0 | 33.0859 | 0
362 | 1900-12-28 | 8665 | 0 | 29.74 | 0
362 | 1900-12-28 | 8666 | 0 | 23.0083 | 0
362 | 1900-12-28 | 8667 | 0 | 33.7736 | 0
362 | 1900-12-28 | 8668 | 0 | 34.8254 | 0
362 | 1900-12-28 | 8669 | 0 | 32.4075 | 0
362 | 1900-12-28 | 8670 | 0 | 22.4871 | 0
362 | 1900-12-28 | 8671 | 0 | 31.6149 | 0
362 | 1900-12-28 | 8672 | 0 | 48.8657 | 0
362 | 1900-12-28 | 8673 | 0 | 45.7068 | 0
362 | 1900-12-28 | 8674 | 0 | 47.0028 | 0
362 | 1900-12-28 | 8675 | 0 | 60.5665 | 0
362 | 1900-12-28 | 8676 | 0 | 38.982 | 0
362 | 1900-12-28 | 8677 | 0 | 45.0252 | 0
362 | 1900-12-28 | 8678 | 0 | 40.8714 | 0
362 | 1900-12-28 | 8679 | 0 | 38.5422 | 0
362 | 1900-12-28 | 8680 | 0 | 43.5233 | 0
362 | 1900-12-28 | 8681 | 0 | 34.7729 | 0
362 | 1900-12-28 | 8682 | 0 | 41.3215 | 0
362 | 1900-12-28 | 8683 | 0 | 241.6028 | 0
362 | 1900-12-28 | 8684 | 0 | 31.5194 | 0
362 | 1900-12-28 | 8685 | 0 | 24.3489 | 0
362 | 1900-12-28 | 8686 | 0 | 25.1146 | 0
362 | 1900-12-28 | 8687 | 0 | 21.4543 | 0
362 | 1900-12-28 | 8688 | 0 | 25.3157 | 0
363 | 1900-12-29 | 8689 | 0 | 31.854 | 0
363 | 1900-12-29 | 8690 | 0 | 35.0358 | 0
363 | 1900-12-29 | 8691 | 0 | 34.1222 | 0
363 | 1900-12-29 | 8692 | 0 | 28.3253 | 0
363 | 1900-12-29 | 8693 | 0 | 37.0006 | 0
363 | 1900-12-29 | 8694 | 0 | 27.1322 | 0
363 | 1900-12-29 | 8695 | 0 | 37.2157 | 0
363 | 1900-12-29 | 8696 | 0 | 41.19 | 0
363 | 1900-12-29 | 8697 | 0 | 36.754 | 0
363 | 1900-12-29 | 8698 | 0 | 47.7355 | 0
363 | 1900-12-29 | 8699 | 0 | 37.778 | 0
363 | 1900-12-29 | 8700 | 0 | 32.4288 | 0
363 | 1900-12-29 | 8701 | 0 | 52.2685 | 0
363 | 1900-12-29 | 8702 | 0 | 33.0305 | 0
363 | 1900-12-29 | 8703 | 0 | 42.3914 | 0
363 | 1900-12-29 | 8704 | 0 | 36.4591 | 0
363 | 1900-12-29 | 8705 | 0 | 31.4629 | 0
363 | 1900-12-29 | 8706 | 0 | 39.4057 | 0
363 | 1900-12-29 | 8707 | 0 | 42.7176 | 0
363 | 1900-12-29 | 8708 | 0 | 29.5816 | 0
363 | 1900-12-29 | 8709 | 0 | 24.9764 | 0
363 | 1900-12-29 | 8710 | 0 | 25.945 | 0
363 | 1900-12-29 | 8711 | 0 | 27.6922 | 0
363 | 1900-12-29 | 8712 | 0 | 223.9111 | 0
364 | 1900-12-30 | 8713 | 0 | 25.2247 | 0
364 | 1900-12-30 | 8714 | 0 | 22.5521 | 0
364 | 1900-12-30 | 8715 | 0 | 29.4063 | 0
364 | 1900-12-30 | 8716 | 0 | 30.213 | 0
364 | 1900-12-30 | 8717 | 0 | 39.4439 | 0
364 | 1900-12-30 | 8718 | 0 | 18.7759 | 0
364 | 1900-12-30 | 8719 | 0 | 29.6025 | 0
364 | 1900-12-30 | 8720 | 0 | 36.0572 | 0
364 | 1900-12-30 | 8721 | 0 | 40.5216 | 0
364 | 1900-12-30 | 8722 | 0 | 49.9062 | 0
364 | 1900-12-30 | 8723 | 0 | 48.6534 | 0
364 | 1900-12-30 | 8724 | 0 | 40.1889 | 0
364 | 1900-12-30 | 8725 | 0 | 51.1625 | 0
364 | 1900-12-30 | 8726 | 0 | 41.2959 | 0
364 | 1900-12-30 | 8727 | 0 | 43.9809 | 0
364 | 1900-12-30 | 8728 | 0 | 39.7524 | 0
364 | 1900-12-30 | 8729 | 0 | 40.9476 | 0
364 | 1900-12-30 | 8730 | 0 | 36.3843 | 0
364 | 1900-12-30 | 8731 | 0 | 52.2395 | 0
364 | 1900-12-30 | 8732 | 0 | 34.0235 | 0
364 | 1900-12-30 | 8733 | 0 | 25.2958 | 0
364 | 1900-12-30 | 8734 | 0 | 29.7686 | 0
364 | 1900-12-30 | 8735 | 0 | 24.3498 | 0
364 | 1900-12-30 | 8736 | 0 | 30.777 | 0
365 | 1900-12-31 | 8737 | 0 | 30.6664 | 0
365 | 1900-12-31 | 8738 | 0 | 35.3252 | 0
365 | 1900-12-31 | 8739 | 0 | 35.1235 | 0
365 | 1900-12-31 | 8740 | 0 | 29.872 | 0
365 | 1900-12-31 | 8741 | 0 | 229.9948 | 0
365 | 1900-12-31 | 8742 | 0 | 25.1175 | 0
365 | 1900-12-31 | 8743 | 0 | 24.5004 | 0
365 | 1900-12-31 | 8744 | 0 | 40.9353 | 0
365 | 1900-12-31 | 8745 | 0 | 51.1845 | 0
365 | 1900-12-31 | 8746 | 0 | 27.4644 | 0
365 | 1900-12-31 | 8747 | 0 | 41.1982 | 0
365 | 1900-12-31 | 8748 | 0 | 47.442 | 0
365 | 1900-12-31 | 8749 | 0 | 43.5471 | 0
365 | 1900-12-31 | 8750 | 0 | 53.3145 | 0
365 | 1900-12-31 | 8751 | 0 | 32.3741 | 0
365 | 1900-12-31 | 8752 | 0 | 42.1164 | 0
365 | 1900-12-31 | 8753 | 0 | 56.08 | 0
365 | 1900-12-31 | 8754 | 0 | 29.5645 | 0
365 | 1900-12-31 | 8755 | 0 | 46.1755 | 0
365 | 1900-12-31 | 8756 | 0 | 36.7694 | 0
365 | 1900-12-31 | 8757 | 0 | 31.655 | 0
365 | 1900-12-31 | 8758 | 0 | 30.5553 | 0
365 | 1900-12-31 | 8759 | 0 | 27.3242 | 0
365 | 1900-12-31 | 8760 | 0 | 26.9002 | 0
Formulas:
date = [day]
date = [day]+1

## production
| PV-production |  | Windturbine production |  |  |  | Electricity import |  | User may change green columns as desired!
| Qsolar | Ppv | vwind | vwind | Pturbine | Pw | profile | Price
hour | W/m2 | kWh | 0.1 m/s | m/s | kWh | kWh | kWh | euro/kWh | PV & wind production parameters
1 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.08392 | year | 2019
2 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07998 | climate database | Heino | Netherlands
3 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07527 | orientation
4 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06497 | tilt angle |  | degrees
5 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06266 | max. wind speed | 25 | m/s
6 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.063 | wind power factor | 94 | kW.s/m
7 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06475
8 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07012
9 | 8.3333 | 16.2223 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0598 | Total PV production | 2115060.3037 | kWh/y
10 | 55.5556 | 108.1485 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06458 | Total wind production | 0 | kWh/y
11 | 69.4444 | 135.1856 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07044
12 | 130.5556 | 254.149 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07762 | Peak PV production | 1779.0429 | kWh
13 | 88.8889 | 173.0376 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0724 | Peak wind production | 21.1847 | kWh
14 | 94.4444 | 183.8525 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06576
15 | 55.5556 | 108.1485 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06492 |  |  |  | v | Pturbine
16 | 5.5556 | 10.8149 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06505 |  |  |  | 0 | 0
17 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0656 |  |  |  | 1 | 0
18 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07572 |  |  |  | 2 | 0
19 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06551 |  |  |  | 3 | 50.4803
20 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06235 | z1 | 10 | [m] | 4 | 119.657
21 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0654 | z2 | 89 | [m] | 5 | 233.705
22 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06253 | a | 0.26 |  | 6 | 403.8423
23 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06606 |  |  |  | 7 | 641.2866
24 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06255 |  |  |  | 8 | 957.2558
25 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.064 |  |  |  | 9 | 1362.9678
26 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0616 |  |  |  | 10 | 1869.6403
27 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0616 |  |  |  | 11 | 2350
28 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06073 |  |  |  | 12 | 2350
29 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06101 | Cp | 0.45 |  | 13 | 2350
30 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06145 | D | 92 |  | 14 | 2350
31 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06286 | Vmax | 25 | m/s | 15 | 2350
32 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0645 | Vmin | 3 | m/s | 16 | 2350
33 | 19.4444 | 37.852 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06742 | Pmax | 2350 | kW | 17 | 2350
34 | 66.6667 | 129.7782 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06742 | scale factor | 0.5 |  | 18 | 2350
35 | 130.5556 | 254.149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06736 |  |  |  | 19 | 2350
36 | 208.3333 | 405.5569 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06694 |  |  |  | 20 | 2350
37 | 180.5556 | 351.4826 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06659 |  |  |  | 21 | 2350
38 | 161.1111 | 313.6307 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06677 | Electricity import |  |  | 22 | 2350
39 | 58.3333 | 113.5559 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06761 | maximum price | 0.13646 | euro/kWh | 23 | 2350
40 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.075 | average price | 0.056196 | euro/kWh | 24 | 2350
41 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08495 | max. solar | 1779.0429 | kWh | 25 | 2350
42 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.095 | max. wind | 0 | kWh | 26 | 0
43 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.09267 | penalty | 0.015 | euro/kWh | 27 | 0
44 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.09153 |  |  |  | 28 | 0
45 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08229 |  |  |  | 29 | 0
46 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07064 |  |  |  | 30 | 0
47 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06881
48 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06743
49 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06512
50 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0621
51 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0614
52 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.059
53 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05888
54 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06092
55 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06746
56 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07363
57 | 27.7778 | 54.0743 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08008
58 | 75 | 146.0005 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09058
59 | 141.6667 | 275.7787 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09468
60 | 144.4444 | 281.1861 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08929
61 | 177.7778 | 346.0752 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0887
62 | 63.8889 | 124.3708 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08531
63 | 41.6667 | 81.1114 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0849
64 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08345
65 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.085
66 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0887
67 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0987
68 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08634
69 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08338
70 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07672
71 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06881
72 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06498
73 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06663
74 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06211
75 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06207
76 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06121
77 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.062
78 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06191
79 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07454
80 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0834
81 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08919
82 | 11.1111 | 21.6297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.095
83 | 22.2222 | 43.2594 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.10038
84 | 27.7778 | 54.0743 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.09761
85 | 19.4444 | 37.852 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.08467
86 | 13.8889 | 27.0371 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.08473
87 | 8.3333 | 16.2223 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08473
88 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.088
89 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.091
90 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.1049
91 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0883
92 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07
93 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06773
94 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06712
95 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06643
96 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06564
97 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06502
98 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.061
99 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06068
100 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06049
101 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06
102 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0588
103 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0609
104 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06168
105 | 11.1111 | 21.6297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06665
106 | 30.5556 | 59.4817 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06741
107 | 55.5556 | 108.1485 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06762
108 | 58.3333 | 113.5559 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06771
109 | 50 | 97.3337 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.088
110 | 38.8889 | 75.704 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.088
111 | 16.6667 | 32.4446 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08396
112 | 2.7778 | 5.4074 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07912
113 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07461
114 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.09014
115 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0897
116 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.088
117 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08307
118 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06862
119 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06782
120 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07736
121 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06695
122 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.065
123 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06338
124 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06302
125 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06091
126 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06217
127 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06319
128 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06411
129 | 16.6667 | 32.4446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0657
130 | 69.4444 | 135.1856 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0684
131 | 63.8889 | 124.3708 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07155
132 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07502
133 | 88.8889 | 173.0376 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07522
134 | 86.1111 | 167.6302 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07
135 | 52.7778 | 102.7411 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06739
136 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06657
137 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06971
138 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07843
139 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08237
140 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0822
141 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08103
142 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07036
143 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07359
144 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06689
145 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06103
146 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06298
147 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06284
148 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06111
149 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06108
150 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06262
151 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07077
152 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08361
153 | 16.6667 | 32.4446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08915
154 | 38.8889 | 75.704 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08993
155 | 30.5556 | 59.4817 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08859
156 | 33.3333 | 64.8891 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08623
157 | 30.5556 | 59.4817 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08227
158 | 19.4444 | 37.852 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08014
159 | 8.3333 | 16.2223 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07756
160 | 2.7778 | 5.4074 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07256
161 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07199
162 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.08782
163 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06789
164 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.065
165 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.066
166 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.064
167 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06254
168 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0594
169 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0517
170 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06056
171 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.054
172 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.055
173 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0478
174 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.058
175 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06896
176 | 0 | 0 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.068
177 | 22.2222 | 43.2594 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0748
178 | 50 | 97.3337 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0751
179 | 69.4444 | 135.1856 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.07089
180 | 111.1111 | 216.297 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06848
181 | 108.3333 | 210.8896 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0637
182 | 94.4444 | 183.8525 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06401
183 | 47.2222 | 91.9262 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06738
184 | 5.5556 | 10.8149 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06737
185 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06784
186 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.09324
187 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06729
188 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06338
189 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0651
190 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06612
191 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06566
192 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06172
193 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0576
194 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0545
195 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.052
196 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0574
197 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05142
198 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.057
199 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06563
200 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07251
201 | 38.8889 | 75.704 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08169
202 | 141.6667 | 275.7787 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0809
203 | 188.8889 | 367.7049 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0832
204 | 236.1111 | 459.6311 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.069
205 | 208.3333 | 405.5569 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06609
206 | 133.3333 | 259.5564 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0651
207 | 69.4444 | 135.1856 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06756
208 | 8.3333 | 16.2223 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06895
209 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07937
210 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09064
211 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08922
212 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07098
213 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06973
214 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06502
215 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06764
216 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06531
217 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06607
218 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06461
219 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06363
220 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0638
221 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0635
222 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0648
223 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07429
224 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0876
225 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.09617
226 | 30.5556 | 59.4817 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.09679
227 | 38.8889 | 75.704 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.09615
228 | 55.5556 | 108.1485 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.095
229 | 52.7778 | 102.7411 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.09139
230 | 55.5556 | 108.1485 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09
231 | 33.3333 | 64.8891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09106
232 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0904
233 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09178
234 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.09845
235 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.10015
236 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.09316
237 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08692
238 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08225
239 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07704
240 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06607
241 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.061
242 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0592
243 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06043
244 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06142
245 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06
246 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0585
247 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.065
248 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06978
249 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07502
250 | 30.5556 | 59.4817 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08496
251 | 63.8889 | 124.3708 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08527
252 | 72.2222 | 140.5931 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08633
253 | 100 | 194.6673 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06861
254 | 52.7778 | 102.7411 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06748
255 | 27.7778 | 54.0743 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06596
256 | 5.5556 | 10.8149 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06569
257 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06617
258 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08
259 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06711
260 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06628
261 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06617
262 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06237
263 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06145
264 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06088
265 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0618
266 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06148
267 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.064
268 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05869
269 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06127
270 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0576
271 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05798
272 | 2.7778 | 5.4074 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06599
273 | 13.8889 | 27.0371 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0695
274 | 11.1111 | 21.6297 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07711
275 | 25 | 48.6668 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.08
276 | 36.1111 | 70.2965 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07901
277 | 38.8889 | 75.704 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06698
278 | 33.3333 | 64.8891 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.064
279 | 50 | 97.3337 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06675
280 | 5.5556 | 10.8149 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0675
281 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06781
282 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07447
283 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0649
284 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06459
285 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06342
286 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.064
287 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06258
288 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06255
289 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0674
290 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06293
291 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05844
292 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04848
293 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04963
294 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04963
295 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04397
296 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.055
297 | 5.5556 | 10.8149 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0533
298 | 25 | 48.6668 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06233
299 | 30.5556 | 59.4817 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0638
300 | 33.3333 | 64.8891 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0665
301 | 36.1111 | 70.2965 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06652
302 | 16.6667 | 32.4446 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06599
303 | 11.1111 | 21.6297 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.065
304 | 2.7778 | 5.4074 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06584
305 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06682
306 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0875
307 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06655
308 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06673
309 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06328
310 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06261
311 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0601
312 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0572
313 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06152
314 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0574
315 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06148
316 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06137
317 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06
318 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06167
319 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06541
320 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.073
321 | 58.3333 | 113.5559 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07814
322 | 113.8889 | 221.7044 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0813
323 | 205.5556 | 400.1495 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0805
324 | 180.5556 | 351.4826 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06694
325 | 197.2222 | 383.9272 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0633
326 | 83.3333 | 162.2228 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06657
327 | 77.7778 | 151.4079 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06673
328 | 22.2222 | 43.2594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07712
329 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08017
330 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.10074
331 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07814
332 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.071
333 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06714
334 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07
335 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06668
336 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06243
337 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06167
338 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.057
339 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0533
340 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.051
341 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0572
342 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0593
343 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0624
344 | 2.7778 | 5.4074 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07245
345 | 25 | 48.6668 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07736
346 | 58.3333 | 113.5559 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07672
347 | 69.4444 | 135.1856 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0752
348 | 63.8889 | 124.3708 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07182
349 | 88.8889 | 173.0376 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0707
350 | 83.3333 | 162.2228 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0699
351 | 30.5556 | 59.4817 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06937
352 | 5.5556 | 10.8149 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06712
353 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07
354 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0778
355 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06586
356 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06607
357 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06582
358 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06499
359 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06379
360 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0621
361 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0566
362 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0533
363 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0592
364 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0571
365 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0547
366 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.054
367 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06163
368 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07505
369 | 5.5556 | 10.8149 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07814
370 | 22.2222 | 43.2594 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0752
371 | 33.3333 | 64.8891 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07101
372 | 61.1111 | 118.9634 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07174
373 | 58.3333 | 113.5559 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.069
374 | 30.5556 | 59.4817 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06769
375 | 19.4444 | 37.852 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07032
376 | 2.7778 | 5.4074 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06872
377 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07539
378 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0781
379 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06767
380 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06592
381 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0647
382 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0645
383 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06308
384 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0632
385 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0636
386 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0616
387 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0619
388 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06176
389 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06194
390 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0636
391 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06958
392 | 2.7778 | 5.4074 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07855
393 | 16.6667 | 32.4446 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.08366
394 | 44.4444 | 86.5188 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.08485
395 | 44.4444 | 86.5188 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0799
396 | 44.4444 | 86.5188 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08057
397 | 130.5556 | 254.149 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.074
398 | 77.7778 | 151.4079 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07127
399 | 91.6667 | 178.445 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07181
400 | 13.8889 | 27.0371 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07275
401 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07432
402 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.09444
403 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07188
404 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06885
405 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.065
406 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06606
407 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0624
408 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06557
409 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0689
410 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06466
411 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06352
412 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06354
413 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0635
414 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06685
415 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07426
416 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08808
417 | 55.5556 | 108.1485 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.09186
418 | 194.4444 | 378.5198 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0894
419 | 272.2222 | 529.9277 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0894
420 | 255.5556 | 497.4831 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08628
421 | 244.4444 | 475.8534 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08425
422 | 197.2222 | 383.9272 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08027
423 | 80.5556 | 156.8153 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08244
424 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08314
425 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.084
426 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09004
427 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09113
428 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08746
429 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07683
430 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07319
431 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0717
432 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06816
433 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07278
434 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07232
435 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07018
436 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07
437 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06888
438 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06871
439 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06843
440 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07149
441 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07546
442 | 108.3333 | 210.8896 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07748
443 | 191.6667 | 373.1123 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07749
444 | 255.5556 | 497.4831 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07233
445 | 266.6667 | 519.1128 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07026
446 | 166.6667 | 324.4455 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07043
447 | 88.8889 | 173.0376 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07308
448 | 19.4444 | 37.852 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07348
449 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07793
450 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08215
451 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08391
452 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07842
453 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07522
454 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07353
455 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07352
456 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07146
457 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.071
458 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0691
459 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06883
460 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06635
461 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06545
462 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06547
463 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06396
464 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06517
465 | 69.4444 | 135.1856 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06741
466 | 194.4444 | 378.5198 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0719
467 | 291.6667 | 567.7796 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.072
468 | 422.2222 | 821.9286 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07151
469 | 375 | 730.0024 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07096
470 | 252.7778 | 492.0757 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0689
471 | 83.3333 | 162.2228 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07054
472 | 27.7778 | 54.0743 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07039
473 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07302
474 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08168
475 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08443
476 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.08491
477 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08378
478 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07616
479 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07726
480 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07247
481 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07054
482 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06802
483 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0671
484 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06631
485 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06614
486 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06823
487 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08216
488 | 2.7778 | 5.4074 | 0 | 0 | 0 | 0 | #DIV/0! | 0.09462
489 | 83.3333 | 162.2228 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.10306
490 | 191.6667 | 373.1123 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.10101
491 | 233.3333 | 454.2237 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.09504
492 | 338.8889 | 659.7059 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09
493 | 344.4444 | 670.5207 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08565
494 | 205.5556 | 400.1495 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08656
495 | 100 | 194.6673 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08703
496 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09149
497 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09608
498 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.10335
499 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.1035
500 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.09493
501 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08869
502 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08152
503 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0686
504 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0675
505 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0621
506 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06366
507 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06341
508 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0658
509 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06673
510 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06258
511 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07524
512 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08619
513 | 44.4444 | 86.5188 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.09108
514 | 108.3333 | 210.8896 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.09005
515 | 186.1111 | 362.2975 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.09164
516 | 108.3333 | 210.8896 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0878
517 | 44.4444 | 86.5188 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08623
518 | 63.8889 | 124.3708 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0878
519 | 30.5556 | 59.4817 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0893
520 | 11.1111 | 21.6297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.09004
521 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.09645
522 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.1047
523 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.10587
524 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.09776
525 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07334
526 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07038
527 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0677
528 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0649
529 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0607
530 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06541
531 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0649
532 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06619
533 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06602
534 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06981
535 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07686
536 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09711
537 | 22.2222 | 43.2594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.10715
538 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.10865
539 | 83.3333 | 162.2228 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.10693
540 | 125 | 243.3341 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.10813
541 | 105.5556 | 205.4822 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09996
542 | 66.6667 | 129.7782 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09899
543 | 36.1111 | 70.2965 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.10059
544 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.10187
545 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09996
546 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.10501
547 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.10915
548 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.10554
549 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09343
550 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08304
551 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07488
552 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0656
553 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0749
554 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07265
555 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0724
556 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07113
557 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07195
558 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07653
559 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08575
560 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.11407
561 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.12807
562 | 58.3333 | 113.5559 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.12623
563 | 94.4444 | 183.8525 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.12325
564 | 105.5556 | 205.4822 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.11869
565 | 94.4444 | 183.8525 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.11333
566 | 83.3333 | 162.2228 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.10763
567 | 52.7778 | 102.7411 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.10486
568 | 16.6667 | 32.4446 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.10545
569 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.11001
570 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.12182
571 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.13646
572 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.11706
573 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.10434
574 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08943
575 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08463
576 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0761
577 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07963
578 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07564
579 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0728
580 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07019
581 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07028
582 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07398
583 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07951
584 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.09948
585 | 33.3333 | 64.8891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.112
586 | 91.6667 | 178.445 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.10864
587 | 105.5556 | 205.4822 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.1
588 | 125 | 243.3341 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.093
589 | 100 | 194.6673 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08681
590 | 69.4444 | 135.1856 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08487
591 | 47.2222 | 91.9262 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08364
592 | 11.1111 | 21.6297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08058
593 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.08008
594 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.08587
595 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.08652
596 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06633
597 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0645
598 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0648
599 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06221
600 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.058
601 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0639
602 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06988
603 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0649
604 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05696
605 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05665
606 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05572
607 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05653
608 | 2.7778 | 5.4074 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0625
609 | 13.8889 | 27.0371 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06637
610 | 22.2222 | 43.2594 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07133
611 | 27.7778 | 54.0743 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07362
612 | 44.4444 | 86.5188 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07418
613 | 38.8889 | 75.704 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07172
614 | 41.6667 | 81.1114 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07244
615 | 36.1111 | 70.2965 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06832
616 | 11.1111 | 21.6297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0678
617 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06744
618 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07095
619 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07292
620 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06775
621 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0624
622 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05999
623 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05904
624 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0554
625 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06
626 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.063
627 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0596
628 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0539
629 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04858
630 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0349
631 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.041
632 | 2.7778 | 5.4074 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0524
633 | 19.4444 | 37.852 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04997
634 | 41.6667 | 81.1114 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0581
635 | 61.1111 | 118.9634 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06935
636 | 55.5556 | 108.1485 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07
637 | 36.1111 | 70.2965 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06197
638 | 41.6667 | 81.1114 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05825
639 | 88.8889 | 173.0376 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05625
640 | 22.2222 | 43.2594 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05567
641 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05626
642 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06225
643 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06764
644 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06796
645 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06544
646 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06278
647 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06582
648 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05985
649 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06439
650 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05597
651 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05542
652 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0528
653 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05309
654 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05683
655 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06809
656 | 8.3333 | 16.2223 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07904
657 | 33.3333 | 64.8891 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07965
658 | 47.2222 | 91.9262 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07492
659 | 58.3333 | 113.5559 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06843
660 | 94.4444 | 183.8525 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07078
661 | 130.5556 | 254.149 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06879
662 | 102.7778 | 200.0747 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.065
663 | 77.7778 | 151.4079 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06396
664 | 36.1111 | 70.2965 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0624
665 | 2.7778 | 5.4074 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06674
666 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.077
667 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0749
668 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06885
669 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0649
670 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06535
671 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06136
672 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0599
673 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0626
674 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06366
675 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06309
676 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06022
677 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06097
678 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0624
679 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07093
680 | 16.6667 | 32.4446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08078
681 | 108.3333 | 210.8896 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08798
682 | 241.6667 | 470.446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08758
683 | 252.7778 | 492.0757 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08636
684 | 294.4444 | 573.1871 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.08514
685 | 266.6667 | 519.1128 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.08099
686 | 236.1111 | 459.6311 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08177
687 | 130.5556 | 254.149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08156
688 | 41.6667 | 81.1114 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.081
689 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08433
690 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08645
691 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08782
692 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08481
693 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07122
694 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06847
695 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06
696 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.063
697 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.058
698 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06136
699 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0601
700 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05785
701 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05774
702 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06134
703 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06712
704 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07999
705 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08317
706 | 108.3333 | 210.8896 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08747
707 | 127.7778 | 248.7416 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0986
708 | 158.3333 | 308.2232 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09783
709 | 230.5556 | 448.8163 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.09932
710 | 141.6667 | 275.7787 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.10038
711 | 86.1111 | 167.6302 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0896
712 | 22.2222 | 43.2594 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0938
713 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.09143
714 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08796
715 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.10959
716 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.075
717 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.073
718 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07123
719 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0651
720 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0621
721 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0589
722 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06184
723 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06178
724 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06182
725 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06008
726 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0637
727 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07727
728 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0867
729 | 36.1111 | 70.2965 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.09349
730 | 63.8889 | 124.3708 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.09436
731 | 91.6667 | 178.445 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09296
732 | 102.7778 | 200.0747 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08659
733 | 116.6667 | 227.1119 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08181
734 | 177.7778 | 346.0752 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08122
735 | 155.5556 | 302.8158 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08116
736 | 36.1111 | 70.2965 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08116
737 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08035
738 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08168
739 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08198
740 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0804
741 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0749
742 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06784
743 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06636
744 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06236
745 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05909
746 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06047
747 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0581
748 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0561
749 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05651
750 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06076
751 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06744
752 | 2.7778 | 5.4074 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.08144
753 | 16.6667 | 32.4446 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08794
754 | 44.4444 | 86.5188 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.09925
755 | 52.7778 | 102.7411 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.09881
756 | 58.3333 | 113.5559 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09923
757 | 66.6667 | 129.7782 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09549
758 | 66.6667 | 129.7782 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09364
759 | 52.7778 | 102.7411 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08052
760 | 19.4444 | 37.852 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07955
761 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07891
762 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08271
763 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08525
764 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0849
765 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07799
766 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07105
767 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06901
768 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06592
769 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06421
770 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06207
771 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0607
772 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05814
773 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05771
774 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0576
775 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05847
776 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06268
777 | 16.6667 | 32.4446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06647
778 | 38.8889 | 75.704 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07079
779 | 44.4444 | 86.5188 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0745
780 | 44.4444 | 86.5188 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07415
781 | 41.6667 | 81.1114 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07108
782 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06533
783 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06409
784 | 30.5556 | 59.4817 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0636
785 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06439
786 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07186
787 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07291
788 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06959
789 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06543
790 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06348
791 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06349
792 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06106
793 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0573
794 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05629
795 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05548
796 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.054
797 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0539
798 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05347
799 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05488
800 | 19.4444 | 37.852 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05597
801 | 127.7778 | 248.7416 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0588
802 | 194.4444 | 378.5198 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06205
803 | 288.8889 | 562.3722 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06433
804 | 341.6667 | 665.1133 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06611
805 | 277.7778 | 540.7425 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06535
806 | 255.5556 | 497.4831 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06209
807 | 150 | 292.001 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06014
808 | 72.2222 | 140.5931 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0594
809 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06079
810 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06694
811 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07454
812 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07567
813 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0724
814 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06694
815 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06125
816 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05676
817 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.055
818 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05511
819 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05442
820 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05421
821 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05355
822 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05563
823 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06216
824 | 16.6667 | 32.4446 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07074
825 | 50 | 97.3337 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07034
826 | 88.8889 | 173.0376 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.074
827 | 138.8889 | 270.3713 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.068
828 | 111.1111 | 216.297 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0597
829 | 86.1111 | 167.6302 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05669
830 | 47.2222 | 91.9262 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0558
831 | 38.8889 | 75.704 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0604
832 | 27.7778 | 54.0743 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06049
833 | 2.7778 | 5.4074 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06159
834 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0649
835 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06178
836 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05708
837 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05559
838 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0549
839 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0547
840 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0499
841 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0523
842 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0524
843 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05342
844 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0549
845 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0549
846 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05799
847 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06913
848 | 5.5556 | 10.8149 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07722
849 | 25 | 48.6668 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0853
850 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.09019
851 | 50 | 97.3337 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08496
852 | 47.2222 | 91.9262 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07785
853 | 63.8889 | 124.3708 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07393
854 | 83.3333 | 162.2228 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07296
855 | 83.3333 | 162.2228 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07296
856 | 25 | 48.6668 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07304
857 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07535
858 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07806
859 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08079
860 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07763
861 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07677
862 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06793
863 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06103
864 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0576
865 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0578
866 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05663
867 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0555
868 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0554
869 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05638
870 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05731
871 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06566
872 | 8.3333 | 16.2223 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0683
873 | 25 | 48.6668 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07093
874 | 44.4444 | 86.5188 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06845
875 | 66.6667 | 129.7782 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07037
876 | 86.1111 | 167.6302 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07009
877 | 69.4444 | 135.1856 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06994
878 | 55.5556 | 108.1485 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06955
879 | 30.5556 | 59.4817 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06793
880 | 16.6667 | 32.4446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0693
881 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07173
882 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07527
883 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0774
884 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07394
885 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06937
886 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06549
887 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0645
888 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06118
889 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06125
890 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06021
891 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05624
892 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05305
893 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.052
894 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05404
895 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06306
896 | 2.7778 | 5.4074 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06577
897 | 50 | 97.3337 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06979
898 | 208.3333 | 405.5569 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0687
899 | 286.1111 | 556.9648 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06817
900 | 297.2222 | 578.5945 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.065
901 | 180.5556 | 351.4826 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.06445
902 | 233.3333 | 454.2237 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.06109
903 | 141.6667 | 275.7787 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05758
904 | 36.1111 | 70.2965 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05832
905 | 2.7778 | 5.4074 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.06128
906 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06665
907 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06476
908 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0604
909 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05819
910 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0607
911 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05855
912 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.057
913 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06185
914 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06
915 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.061
916 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06
917 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0524
918 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05449
919 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0615
920 | 5.5556 | 10.8149 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07087
921 | 22.2222 | 43.2594 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07283
922 | 38.8889 | 75.704 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07331
923 | 50 | 97.3337 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07404
924 | 66.6667 | 129.7782 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07256
925 | 66.6667 | 129.7782 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06913
926 | 58.3333 | 113.5559 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06648
927 | 30.5556 | 59.4817 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06331
928 | 16.6667 | 32.4446 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06045
929 | 2.7778 | 5.4074 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0608
930 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.065
931 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06734
932 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06259
933 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0624
934 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06166
935 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06143
936 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06149
937 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0612
938 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.055
939 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05487
940 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0521
941 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.04818
942 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04513
943 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.053
944 | 25 | 48.6668 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05612
945 | 86.1111 | 167.6302 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05882
946 | 108.3333 | 210.8896 | 110 | 19.4193 | 2350 | 0 | #DIV/0! | 0.06354
947 | 197.2222 | 383.9272 | 110 | 19.4193 | 2350 | 0 | #DIV/0! | 0.0649
948 | 136.1111 | 264.9638 | 110 | 19.4193 | 2350 | 0 | #DIV/0! | 0.06209
949 | 283.3333 | 551.5574 | 110 | 19.4193 | 2350 | 0 | #DIV/0! | 0.06182
950 | 80.5556 | 156.8153 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.0586
951 | 52.7778 | 102.7411 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.0539
952 | 30.5556 | 59.4817 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.0574
953 | 2.7778 | 5.4074 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05835
954 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06937
955 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06598
956 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06501
957 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06701
958 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0586
959 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0613
960 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06118
961 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06055
962 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0596
963 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0596
964 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.055
965 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0522
966 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0521
967 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.065
968 | 2.7778 | 5.4074 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06021
969 | 11.1111 | 21.6297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06
970 | 44.4444 | 86.5188 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06385
971 | 88.8889 | 173.0376 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06429
972 | 41.6667 | 81.1114 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.065
973 | 50 | 97.3337 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0699
974 | 69.4444 | 135.1856 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0596
975 | 22.2222 | 43.2594 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0604
976 | 11.1111 | 21.6297 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0596
977 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06167
978 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06605
979 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06637
980 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06612
981 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06473
982 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06074
983 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0593
984 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0596
985 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05759
986 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0564
987 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0548
988 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0548
989 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0566
990 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06003
991 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07263
992 | 11.1111 | 21.6297 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.08559
993 | 86.1111 | 167.6302 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.08
994 | 236.1111 | 459.6311 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.08621
995 | 325 | 632.6688 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08621
996 | 283.3333 | 551.5574 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07343
997 | 197.2222 | 383.9272 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0649
998 | 341.6667 | 665.1133 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0567
999 | 158.3333 | 308.2232 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06481
1000 | 97.2222 | 189.2599 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.062
1001 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07283
1002 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.089
1003 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.10023
1004 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.10931
1005 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0949
1006 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07526
1007 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06
1008 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0548
1009 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0553
1010 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.052
1011 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05232
1012 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0524
1013 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0523
1014 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05502
1015 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0615
1016 | 16.6667 | 32.4446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07622
1017 | 72.2222 | 140.5931 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0798
1018 | 127.7778 | 248.7416 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07974
1019 | 186.1111 | 362.2975 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07528
1020 | 263.8889 | 513.7054 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07549
1021 | 275 | 535.3351 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06882
1022 | 250 | 486.6683 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06498
1023 | 147.2222 | 286.5935 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06498
1024 | 61.1111 | 118.9634 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06517
1025 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06784
1026 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07192
1027 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07547
1028 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06627
1029 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06096
1030 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0566
1031 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0599
1032 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0552
1033 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0549
1034 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0526
1035 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0513
1036 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.051
1037 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05258
1038 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05218
1039 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06062
1040 | 11.1111 | 21.6297 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0679
1041 | 44.4444 | 86.5188 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07985
1042 | 69.4444 | 135.1856 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07797
1043 | 55.5556 | 108.1485 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.065
1044 | 61.1111 | 118.9634 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06363
1045 | 75 | 146.0005 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06349
1046 | 55.5556 | 108.1485 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0626
1047 | 52.7778 | 102.7411 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0613
1048 | 52.7778 | 102.7411 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06182
1049 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06471
1050 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06894
1051 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07155
1052 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06934
1053 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06513
1054 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06176
1055 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0595
1056 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05785
1057 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0536
1058 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05415
1059 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0536
1060 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.054
1061 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05347
1062 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05804
1063 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0629
1064 | 33.3333 | 64.8891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07573
1065 | 136.1111 | 264.9638 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07867
1066 | 252.7778 | 492.0757 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08025
1067 | 347.2222 | 675.9282 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.073
1068 | 394.4444 | 767.8544 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06112
1069 | 388.8889 | 757.0395 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.059
1070 | 336.1111 | 654.2985 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05965
1071 | 233.3333 | 454.2237 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05962
1072 | 127.7778 | 248.7416 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06212
1073 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06739
1074 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07063
1075 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0752
1076 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07693
1077 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06997
1078 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06469
1079 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06239
1080 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05651
1081 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0573
1082 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05719
1083 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05672
1084 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05519
1085 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0561
1086 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05867
1087 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06798
1088 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07498
1089 | 186.1111 | 362.2975 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07673
1090 | 291.6667 | 567.7796 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0724
1091 | 377.7778 | 735.4098 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06525
1092 | 422.2222 | 821.9286 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05584
1093 | 411.1111 | 800.2989 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05605
1094 | 352.7778 | 686.743 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.056
1095 | 250 | 486.6683 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05752
1096 | 133.3333 | 259.5564 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05941
1097 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06318
1098 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06861
1099 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07154
1100 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07049
1101 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0649
1102 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05615
1103 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06086
1104 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05693
1105 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05617
1106 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05479
1107 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.051
1108 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05129
1109 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05152
1110 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.055
1111 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0581
1112 | 55.5556 | 108.1485 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06
1113 | 186.1111 | 362.2975 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06534
1114 | 277.7778 | 540.7425 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07007
1115 | 391.6667 | 762.447 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07273
1116 | 388.8889 | 757.0395 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0538
1117 | 350 | 681.3356 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05062
1118 | 316.6667 | 616.4465 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.051
1119 | 222.2222 | 432.594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05221
1120 | 116.6667 | 227.1119 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05461
1121 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05711
1122 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06183
1123 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06813
1124 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.09092
1125 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06147
1126 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05567
1127 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05733
1128 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0557
1129 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.054
1130 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05497
1131 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05224
1132 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05127
1133 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05113
1134 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05174
1135 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05152
1136 | 44.4444 | 86.5188 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05382
1137 | 175 | 340.6678 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.055
1138 | 277.7778 | 540.7425 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05388
1139 | 366.6667 | 713.7801 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05191
1140 | 411.1111 | 800.2989 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0515
1141 | 366.6667 | 713.7801 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05241
1142 | 330.5556 | 643.4836 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05009
1143 | 225 | 438.0014 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05012
1144 | 130.5556 | 254.149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05127
1145 | 27.7778 | 54.0743 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05436
1146 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05903
1147 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0646
1148 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06507
1149 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06115
1150 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.055
1151 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05783
1152 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05375
1153 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05441
1154 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05378
1155 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05378
1156 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0532
1157 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0538
1158 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.055
1159 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06672
1160 | 55.5556 | 108.1485 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07237
1161 | 177.7778 | 346.0752 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07101
1162 | 291.6667 | 567.7796 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06761
1163 | 375 | 730.0024 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06343
1164 | 413.8889 | 805.7064 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05996
1165 | 400 | 778.6692 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05826
1166 | 316.6667 | 616.4465 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05807
1167 | 241.6667 | 470.446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05973
1168 | 113.8889 | 221.7044 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06235
1169 | 25 | 48.6668 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0659
1170 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06794
1171 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07194
1172 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07076
1173 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06691
1174 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05898
1175 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.055
1176 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0535
1177 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0511
1178 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05043
1179 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05042
1180 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.051
1181 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05108
1182 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0531
1183 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06036
1184 | 55.5556 | 108.1485 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06372
1185 | 188.8889 | 367.7049 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06217
1186 | 241.6667 | 470.446 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07666
1187 | 277.7778 | 540.7425 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0724
1188 | 175 | 340.6678 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05705
1189 | 202.7778 | 394.742 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0536
1190 | 136.1111 | 264.9638 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0536
1191 | 125 | 243.3341 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0536
1192 | 88.8889 | 173.0376 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0574
1193 | 11.1111 | 21.6297 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0589
1194 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06592
1195 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06909
1196 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06742
1197 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0599
1198 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05663
1199 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05698
1200 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05069
1201 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.051
1202 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0504
1203 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04795
1204 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0505
1205 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05106
1206 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05306
1207 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06405
1208 | 44.4444 | 86.5188 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06954
1209 | 138.8889 | 270.3713 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06958
1210 | 219.4444 | 427.1866 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06808
1211 | 277.7778 | 540.7425 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06709
1212 | 341.6667 | 665.1133 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06401
1213 | 283.3333 | 551.5574 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05826
1214 | 250 | 486.6683 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06005
1215 | 163.8889 | 319.0381 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06058
1216 | 72.2222 | 140.5931 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06101
1217 | 22.2222 | 43.2594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06479
1218 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06696
1219 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06925
1220 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06905
1221 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06497
1222 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05559
1223 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05407
1224 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0506
1225 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05213
1226 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.051
1227 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05049
1228 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05036
1229 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05108
1230 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0529
1231 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0549
1232 | 38.8889 | 75.704 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.058
1233 | 80.5556 | 156.8153 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0655
1234 | 80.5556 | 156.8153 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0768
1235 | 163.8889 | 319.0381 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0549
1236 | 230.5556 | 448.8163 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0532
1237 | 133.3333 | 259.5564 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0517
1238 | 97.2222 | 189.2599 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05245
1239 | 44.4444 | 86.5188 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05423
1240 | 19.4444 | 37.852 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05794
1241 | 8.3333 | 16.2223 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0613
1242 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06561
1243 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0681
1244 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06798
1245 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06639
1246 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06113
1247 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06008
1248 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05769
1249 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05658
1250 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05532
1251 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05484
1252 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05459
1253 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05435
1254 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.057
1255 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06531
1256 | 13.8889 | 27.0371 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06993
1257 | 50 | 97.3337 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07285
1258 | 141.6667 | 275.7787 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07062
1259 | 191.6667 | 373.1123 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06914
1260 | 213.8889 | 416.3717 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06806
1261 | 208.3333 | 405.5569 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06645
1262 | 247.2222 | 481.2608 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06399
1263 | 172.2222 | 335.2604 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06088
1264 | 72.2222 | 140.5931 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06038
1265 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06423
1266 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06733
1267 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06848
1268 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06458
1269 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0593
1270 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05802
1271 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05841
1272 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0546
1273 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05304
1274 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05154
1275 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05106
1276 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05101
1277 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05061
1278 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05103
1279 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0523
1280 | 75 | 146.0005 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05611
1281 | 186.1111 | 362.2975 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05857
1282 | 311.1111 | 605.6316 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06616
1283 | 383.3333 | 746.2247 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05594
1284 | 438.8889 | 854.3732 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05302
1285 | 441.6667 | 859.7806 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05066
1286 | 366.6667 | 713.7801 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05032
1287 | 297.2222 | 578.5945 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05062
1288 | 183.3333 | 356.8901 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0505
1289 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06047
1290 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06249
1291 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0672
1292 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06597
1293 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06199
1294 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05535
1295 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05659
1296 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.054
1297 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05282
1298 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05248
1299 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05248
1300 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05121
1301 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05121
1302 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05204
1303 | 8.3333 | 16.2223 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0523
1304 | 122.2222 | 237.9267 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05298
1305 | 241.6667 | 470.446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05411
1306 | 355.5556 | 692.1504 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05479
1307 | 430.5556 | 838.1509 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05265
1308 | 483.3333 | 940.892 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05206
1309 | 477.7778 | 930.0771 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05214
1310 | 416.6667 | 811.1138 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05
1311 | 280.5556 | 546.1499 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04954
1312 | 152.7778 | 297.4084 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05025
1313 | 33.3333 | 64.8891 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05357
1314 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06075
1315 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06668
1316 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06647
1317 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.065
1318 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05946
1319 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06265
1320 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0591
1321 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0537
1322 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05202
1323 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.052
1324 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05137
1325 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05106
1326 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05507
1327 | 5.5556 | 10.8149 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06502
1328 | 97.2222 | 189.2599 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07188
1329 | 244.4444 | 475.8534 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07059
1330 | 366.6667 | 713.7801 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06572
1331 | 441.6667 | 859.7806 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05503
1332 | 494.4444 | 962.5217 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05397
1333 | 491.6667 | 957.1143 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0524
1334 | 386.1111 | 751.6321 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05398
1335 | 294.4444 | 573.1871 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05288
1336 | 197.2222 | 383.9272 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.057
1337 | 63.8889 | 124.3708 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0594
1338 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06824
1339 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07192
1340 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0694
1341 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06561
1342 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05809
1343 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0574
1344 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0554
1345 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0521
1346 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.052
1347 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05184
1348 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05088
1349 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05177
1350 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05441
1351 | 8.3333 | 16.2223 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06374
1352 | 111.1111 | 216.297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06804
1353 | 244.4444 | 475.8534 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06688
1354 | 363.8889 | 708.3727 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06492
1355 | 436.1111 | 848.9658 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.057
1356 | 488.8889 | 951.7068 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05408
1357 | 472.2222 | 919.2623 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05428
1358 | 411.1111 | 800.2989 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.054
1359 | 311.1111 | 605.6316 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05291
1360 | 186.1111 | 362.2975 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05645
1361 | 50 | 97.3337 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06014
1362 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07024
1363 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07798
1364 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06994
1365 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06619
1366 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06257
1367 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0618
1368 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05641
1369 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05598
1370 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05442
1371 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05358
1372 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05299
1373 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05359
1374 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05648
1375 | 13.8889 | 27.0371 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06575
1376 | 133.3333 | 259.5564 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07484
1377 | 250 | 486.6683 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06919
1378 | 375 | 730.0024 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06495
1379 | 444.4444 | 865.188 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05957
1380 | 500 | 973.3365 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05579
1381 | 494.4444 | 962.5217 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05463
1382 | 433.3333 | 843.5583 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05458
1383 | 322.2222 | 627.2613 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05506
1384 | 191.6667 | 373.1123 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05562
1385 | 55.5556 | 108.1485 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05892
1386 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06816
1387 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06948
1388 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06682
1389 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06169
1390 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05658
1391 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05639
1392 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0524
1393 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0525
1394 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05298
1395 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0525
1396 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0536
1397 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0514
1398 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0499
1399 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05745
1400 | 86.1111 | 167.6302 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06459
1401 | 136.1111 | 264.9638 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07149
1402 | 230.5556 | 448.8163 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0723
1403 | 300 | 584.0019 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05766
1404 | 294.4444 | 573.1871 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05389
1405 | 316.6667 | 616.4465 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.053
1406 | 341.6667 | 665.1133 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05208
1407 | 200 | 389.3346 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05305
1408 | 33.3333 | 64.8891 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05968
1409 | 19.4444 | 37.852 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06245
1410 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06867
1411 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06876
1412 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06597
1413 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0642
1414 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0592
1415 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05821
1416 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05644
1417 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0544
1418 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0527
1419 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05223
1420 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05272
1421 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05506
1422 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05696
1423 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06175
1424 | 11.1111 | 21.6297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06298
1425 | 22.2222 | 43.2594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06562
1426 | 47.2222 | 91.9262 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06608
1427 | 83.3333 | 162.2228 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06721
1428 | 52.7778 | 102.7411 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06703
1429 | 97.2222 | 189.2599 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06356
1430 | 100 | 194.6673 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0624
1431 | 63.8889 | 124.3708 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06191
1432 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06231
1433 | 11.1111 | 21.6297 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06504
1434 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06859
1435 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07
1436 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06749
1437 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06366
1438 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06153
1439 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06065
1440 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05941
1441 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05919
1442 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05828
1443 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05609
1444 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05449
1445 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05563
1446 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05497
1447 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05642
1448 | 19.4444 | 37.852 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05892
1449 | 33.3333 | 64.8891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06289
1450 | 52.7778 | 102.7411 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0636
1451 | 238.8889 | 465.0386 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0629
1452 | 313.8889 | 611.0391 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06084
1453 | 425 | 827.3361 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0589
1454 | 325 | 632.6688 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05521
1455 | 272.2222 | 529.9277 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05568
1456 | 83.3333 | 162.2228 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05604
1457 | 11.1111 | 21.6297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05691
1458 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0601
1459 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06149
1460 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0618
1461 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05546
1462 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0549
1463 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0549
1464 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05357
1465 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0549
1466 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05519
1467 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0519
1468 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05226
1469 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0517
1470 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05071
1471 | 2.7778 | 5.4074 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05383
1472 | 13.8889 | 27.0371 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05637
1473 | 38.8889 | 75.704 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.053
1474 | 44.4444 | 86.5188 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06012
1475 | 58.3333 | 113.5559 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06702
1476 | 83.3333 | 162.2228 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07344
1477 | 61.1111 | 118.9634 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06616
1478 | 66.6667 | 129.7782 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05833
1479 | 30.5556 | 59.4817 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05475
1480 | 27.7778 | 54.0743 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0533
1481 | 5.5556 | 10.8149 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0488
1482 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.055
1483 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.054
1484 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0568
1485 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05909
1486 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05588
1487 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0569
1488 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05784
1489 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05525
1490 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05531
1491 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0548
1492 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05497
1493 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0512
1494 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05476
1495 | 0 | 0 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.0551
1496 | 33.3333 | 64.8891 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05657
1497 | 80.5556 | 156.8153 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.06048
1498 | 113.8889 | 221.7044 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.06943
1499 | 250 | 486.6683 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0735
1500 | 202.7778 | 394.742 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05953
1501 | 230.5556 | 448.8163 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.05658
1502 | 175 | 340.6678 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.05759
1503 | 244.4444 | 475.8534 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.05925
1504 | 202.7778 | 394.742 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.0599
1505 | 58.3333 | 113.5559 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.06264
1506 | 2.7778 | 5.4074 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05965
1507 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05952
1508 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05944
1509 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0591
1510 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05925
1511 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05586
1512 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05529
1513 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0515
1514 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0507
1515 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0521
1516 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0507
1517 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.052
1518 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.055
1519 | 13.8889 | 27.0371 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05597
1520 | 119.4444 | 232.5193 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06071
1521 | 263.8889 | 513.7054 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0765
1522 | 180.5556 | 351.4826 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.07841
1523 | 350 | 681.3356 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0649
1524 | 286.1111 | 556.9648 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06086
1525 | 238.8889 | 465.0386 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05759
1526 | 313.8889 | 611.0391 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05739
1527 | 152.7778 | 297.4084 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05737
1528 | 163.8889 | 319.0381 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05909
1529 | 72.2222 | 140.5931 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06139
1530 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06427
1531 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07145
1532 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07023
1533 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0661
1534 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06309
1535 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06109
1536 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05654
1537 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05108
1538 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.051
1539 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04998
1540 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.051
1541 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.049
1542 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05
1543 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0582
1544 | 25 | 48.6668 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06464
1545 | 80.5556 | 156.8153 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06437
1546 | 138.8889 | 270.3713 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06926
1547 | 205.5556 | 400.1495 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07298
1548 | 216.6667 | 421.7792 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07225
1549 | 166.6667 | 324.4455 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06285
1550 | 113.8889 | 221.7044 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06259
1551 | 86.1111 | 167.6302 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06214
1552 | 38.8889 | 75.704 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06153
1553 | 22.2222 | 43.2594 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06185
1554 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06224
1555 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0624
1556 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06735
1557 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.065
1558 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0576
1559 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0561
1560 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05561
1561 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.052
1562 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05453
1563 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05226
1564 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0524
1565 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0507
1566 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05009
1567 | 2.7778 | 5.4074 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05406
1568 | 25 | 48.6668 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.06332
1569 | 66.6667 | 129.7782 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.066
1570 | 230.5556 | 448.8163 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06419
1571 | 227.7778 | 443.4089 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06402
1572 | 197.2222 | 383.9272 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.0602
1573 | 252.7778 | 492.0757 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0549
1574 | 316.6667 | 616.4465 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.057
1575 | 288.8889 | 562.3722 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05303
1576 | 144.4444 | 281.1861 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.054
1577 | 41.6667 | 81.1114 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05657
1578 | 2.7778 | 5.4074 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05827
1579 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05895
1580 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06149
1581 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0573
1582 | 0 | 0 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.055
1583 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05623
1584 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0541
1585 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.049
1586 | 0 | 0 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.055
1587 | 0 | 0 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05
1588 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0537
1589 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.055
1590 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0493
1591 | 11.1111 | 21.6297 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06179
1592 | 102.7778 | 200.0747 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06008
1593 | 227.7778 | 443.4089 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.08423
1594 | 227.7778 | 443.4089 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0742
1595 | 397.2222 | 773.2618 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.063
1596 | 308.3333 | 600.2242 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05731
1597 | 411.1111 | 800.2989 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05649
1598 | 430.5556 | 838.1509 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0549
1599 | 316.6667 | 616.4465 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05472
1600 | 116.6667 | 227.1119 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0549
1601 | 41.6667 | 81.1114 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0541
1602 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05807
1603 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06349
1604 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06544
1605 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05904
1606 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05557
1607 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05424
1608 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0513
1609 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05
1610 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.049
1611 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05
1612 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0474
1613 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.03764
1614 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0398
1615 | 22.2222 | 43.2594 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.052
1616 | 80.5556 | 156.8153 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0467
1617 | 91.6667 | 178.445 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05152
1618 | 213.8889 | 416.3717 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.06636
1619 | 269.4444 | 524.5202 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06476
1620 | 194.4444 | 378.5198 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0572
1621 | 177.7778 | 346.0752 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0545
1622 | 130.5556 | 254.149 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.0555
1623 | 63.8889 | 124.3708 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.052
1624 | 180.5556 | 351.4826 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.0501
1625 | 61.1111 | 118.9634 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.05695
1626 | 2.7778 | 5.4074 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05733
1627 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0544
1628 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0649
1629 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06
1630 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.063
1631 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07
1632 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0759
1633 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07805
1634 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0759
1635 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0759
1636 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07715
1637 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0694
1638 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05994
1639 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05688
1640 | 25 | 48.6668 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04305
1641 | 91.6667 | 178.445 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0568
1642 | 122.2222 | 237.9267 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0573
1643 | 91.6667 | 178.445 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05718
1644 | 58.3333 | 113.5559 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05726
1645 | 55.5556 | 108.1485 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0627
1646 | 55.5556 | 108.1485 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05
1647 | 58.3333 | 113.5559 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04895
1648 | 33.3333 | 64.8891 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04851
1649 | 16.6667 | 32.4446 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04895
1650 | 2.7778 | 5.4074 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05236
1651 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0564
1652 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05592
1653 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.051
1654 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0524
1655 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05462
1656 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04896
1657 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0493
1658 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0549
1659 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05638
1660 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0504
1661 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04896
1662 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0499
1663 | 16.6667 | 32.4446 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05553
1664 | 52.7778 | 102.7411 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06296
1665 | 130.5556 | 254.149 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06306
1666 | 316.6667 | 616.4465 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06184
1667 | 294.4444 | 573.1871 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.06031
1668 | 252.7778 | 492.0757 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05766
1669 | 227.7778 | 443.4089 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.05495
1670 | 130.5556 | 254.149 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.05369
1671 | 155.5556 | 302.8158 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.0519
1672 | 58.3333 | 113.5559 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05211
1673 | 80.5556 | 156.8153 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0551
1674 | 5.5556 | 10.8149 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06128
1675 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06529
1676 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0729
1677 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06506
1678 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06291
1679 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06261
1680 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05901
1681 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05598
1682 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05397
1683 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05191
1684 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05
1685 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04792
1686 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0513
1687 | 11.1111 | 21.6297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06183
1688 | 38.8889 | 75.704 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06705
1689 | 116.6667 | 227.1119 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06637
1690 | 133.3333 | 259.5564 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06302
1691 | 211.1111 | 410.9643 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06052
1692 | 241.6667 | 470.446 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05934
1693 | 300 | 584.0019 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05882
1694 | 188.8889 | 367.7049 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05883
1695 | 88.8889 | 173.0376 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05852
1696 | 58.3333 | 113.5559 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05819
1697 | 19.4444 | 37.852 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05737
1698 | 2.7778 | 5.4074 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.057
1699 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05902
1700 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.065
1701 | 0 | 0 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.06273
1702 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0549
1703 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0546
1704 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0524
1705 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0496
1706 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0514
1707 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0506
1708 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0524
1709 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0498
1710 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.045
1711 | 11.1111 | 21.6297 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0524
1712 | 33.3333 | 64.8891 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05916
1713 | 86.1111 | 167.6302 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.07033
1714 | 122.2222 | 237.9267 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.065
1715 | 66.6667 | 129.7782 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06027
1716 | 61.1111 | 118.9634 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05991
1717 | 97.2222 | 189.2599 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05959
1718 | 147.2222 | 286.5935 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05938
1719 | 238.8889 | 465.0386 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.05653
1720 | 163.8889 | 319.0381 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.05653
1721 | 86.1111 | 167.6302 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.05675
1722 | 11.1111 | 21.6297 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05906
1723 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0551
1724 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06336
1725 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05639
1726 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.056
1727 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05556
1728 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0524
1729 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05211
1730 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0511
1731 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0533
1732 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.048
1733 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0425
1734 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04259
1735 | 8.3333 | 16.2223 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05269
1736 | 19.4444 | 37.852 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06101
1737 | 50 | 97.3337 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06152
1738 | 80.5556 | 156.8153 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06238
1739 | 94.4444 | 183.8525 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06071
1740 | 41.6667 | 81.1114 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06006
1741 | 97.2222 | 189.2599 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05987
1742 | 161.1111 | 313.6307 | 120 | 21.1847 | 2350 | 0 | #DIV/0! | 0.05668
1743 | 166.6667 | 324.4455 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.054
1744 | 194.4444 | 378.5198 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.0545
1745 | 122.2222 | 237.9267 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.056
1746 | 8.3333 | 16.2223 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05732
1747 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05676
1748 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06409
1749 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06175
1750 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0534
1751 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.055
1752 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.055
1753 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04507
1754 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05411
1755 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0528
1756 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05
1757 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0511
1758 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0467
1759 | 19.4444 | 37.852 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.051
1760 | 44.4444 | 86.5188 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06
1761 | 55.5556 | 108.1485 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05872
1762 | 63.8889 | 124.3708 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05759
1763 | 202.7778 | 394.742 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05654
1764 | 144.4444 | 281.1861 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05597
1765 | 163.8889 | 319.0381 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05491
1766 | 163.8889 | 319.0381 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0514
1767 | 147.2222 | 286.5935 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05675
1768 | 166.6667 | 324.4455 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05664
1769 | 88.8889 | 173.0376 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05674
1770 | 11.1111 | 21.6297 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0575
1771 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.055
1772 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06175
1773 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05899
1774 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0551
1775 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05518
1776 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05488
1777 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05498
1778 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05486
1779 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0549
1780 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05442
1781 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05454
1782 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05465
1783 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0514
1784 | 30.5556 | 59.4817 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.047
1785 | 44.4444 | 86.5188 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0504
1786 | 66.6667 | 129.7782 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05243
1787 | 91.6667 | 178.445 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05322
1788 | 141.6667 | 275.7787 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.0524
1789 | 144.4444 | 281.1861 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.0499
1790 | 72.2222 | 140.5931 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.04137
1791 | 61.1111 | 118.9634 | 110 | 19.4193 | 2350 | 0 | #DIV/0! | 0.0475
1792 | 52.7778 | 102.7411 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.04824
1793 | 25 | 48.6668 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.0475
1794 | 5.5556 | 10.8149 | 110 | 19.4193 | 2350 | 0 | #DIV/0! | 0.053
1795 | 0 | 0 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.0549
1796 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0535
1797 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0514
1798 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0499
1799 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0467
1800 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05
1801 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05
1802 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0415
1803 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0351
1804 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0151
1805 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.024
1806 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05
1807 | 19.4444 | 37.852 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05364
1808 | 152.7778 | 297.4084 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0512
1809 | 155.5556 | 302.8158 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0511
1810 | 350 | 681.3356 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.054
1811 | 308.3333 | 600.2242 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0528
1812 | 150 | 292.001 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05135
1813 | 508.3333 | 989.5588 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0524
1814 | 486.1111 | 946.2994 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0519
1815 | 411.1111 | 800.2989 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0495
1816 | 252.7778 | 492.0757 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0501
1817 | 100 | 194.6673 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0502
1818 | 13.8889 | 27.0371 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05481
1819 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05254
1820 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06472
1821 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06
1822 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05382
1823 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05432
1824 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0545
1825 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.048
1826 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.049
1827 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05
1828 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0527
1829 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05295
1830 | 2.7778 | 5.4074 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05466
1831 | 72.2222 | 140.5931 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05716
1832 | 152.7778 | 297.4084 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06329
1833 | 380.5556 | 740.8173 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0718
1834 | 355.5556 | 692.1504 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06134
1835 | 300 | 584.0019 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0576
1836 | 541.6667 | 1054.4479 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0551
1837 | 547.2222 | 1065.2628 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05
1838 | 580.5556 | 1130.1519 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0512
1839 | 258.3333 | 502.8905 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0512
1840 | 166.6667 | 324.4455 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05277
1841 | 77.7778 | 151.4079 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.053
1842 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0624
1843 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06112
1844 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.068
1845 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.061
1846 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05939
1847 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0567
1848 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05574
1849 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05408
1850 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05349
1851 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05245
1852 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05147
1853 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05142
1854 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05529
1855 | 83.3333 | 162.2228 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06196
1856 | 233.3333 | 454.2237 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06627
1857 | 386.1111 | 751.6321 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06938
1858 | 508.3333 | 989.5588 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06469
1859 | 588.8889 | 1146.3741 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06131
1860 | 580.5556 | 1130.1519 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05955
1861 | 308.3333 | 600.2242 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05831
1862 | 452.7778 | 881.4103 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05789
1863 | 305.5556 | 594.8168 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05748
1864 | 169.4444 | 329.8529 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05874
1865 | 66.6667 | 129.7782 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05961
1866 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06396
1867 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07017
1868 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07573
1869 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06755
1870 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06146
1871 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05972
1872 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05608
1873 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05328
1874 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0513
1875 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05005
1876 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04933
1877 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04969
1878 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0522
1879 | 47.2222 | 91.9262 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05623
1880 | 80.5556 | 156.8153 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06056
1881 | 163.8889 | 319.0381 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06794
1882 | 163.8889 | 319.0381 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06136
1883 | 202.7778 | 394.742 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05889
1884 | 211.1111 | 410.9643 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05486
1885 | 150 | 292.001 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05259
1886 | 116.6667 | 227.1119 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05247
1887 | 141.6667 | 275.7787 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05316
1888 | 69.4444 | 135.1856 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05536
1889 | 27.7778 | 54.0743 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0571
1890 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06049
1891 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.066
1892 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07055
1893 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06374
1894 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05924
1895 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05774
1896 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05365
1897 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05047
1898 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0497
1899 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04851
1900 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04804
1901 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0481
1902 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05093
1903 | 61.1111 | 118.9634 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.059
1904 | 141.6667 | 275.7787 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05831
1905 | 241.6667 | 470.446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06026
1906 | 258.3333 | 502.8905 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06055
1907 | 275 | 535.3351 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0535
1908 | 455.5556 | 886.8177 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05089
1909 | 441.6667 | 859.7806 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05043
1910 | 425 | 827.3361 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0495
1911 | 341.6667 | 665.1133 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0499
1912 | 219.4444 | 427.1866 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05181
1913 | 133.3333 | 259.5564 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05427
1914 | 19.4444 | 37.852 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0584
1915 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0617
1916 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07
1917 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06253
1918 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05892
1919 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05694
1920 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05409
1921 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.054
1922 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05095
1923 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05169
1924 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05139
1925 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05128
1926 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05495
1927 | 19.4444 | 37.852 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06101
1928 | 69.4444 | 135.1856 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06598
1929 | 141.6667 | 275.7787 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0642
1930 | 394.4444 | 767.8544 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05997
1931 | 561.1111 | 1092.2999 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05541
1932 | 594.4444 | 1157.189 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05157
1933 | 597.2222 | 1162.5964 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05
1934 | 550 | 1070.6702 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0493
1935 | 447.2222 | 870.5955 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04946
1936 | 300 | 584.0019 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05
1937 | 147.2222 | 286.5935 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05278
1938 | 22.2222 | 43.2594 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05861
1939 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06191
1940 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06517
1941 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.061
1942 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05561
1943 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0549
1944 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05212
1945 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05053
1946 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04994
1947 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0499
1948 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0481
1949 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04805
1950 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0496
1951 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05164
1952 | 66.6667 | 129.7782 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05386
1953 | 105.5556 | 205.4822 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05343
1954 | 138.8889 | 270.3713 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05536
1955 | 155.5556 | 302.8158 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05234
1956 | 152.7778 | 297.4084 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05162
1957 | 150 | 292.001 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.051
1958 | 116.6667 | 227.1119 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0461
1959 | 175 | 340.6678 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0451
1960 | 208.3333 | 405.5569 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0461
1961 | 133.3333 | 259.5564 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04758
1962 | 30.5556 | 59.4817 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05371
1963 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05627
1964 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05999
1965 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05725
1966 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0541
1967 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05535
1968 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05293
1969 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05415
1970 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05105
1971 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04945
1972 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04861
1973 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04885
1974 | 5.5556 | 10.8149 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0492
1975 | 105.5556 | 205.4822 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04932
1976 | 252.7778 | 492.0757 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04998
1977 | 311.1111 | 605.6316 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0516
1978 | 247.2222 | 481.2608 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05081
1979 | 419.4444 | 816.5212 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04878
1980 | 508.3333 | 989.5588 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04701
1981 | 625 | 1216.6707 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0461
1982 | 575 | 1119.337 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04008
1983 | 491.6667 | 957.1143 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03913
1984 | 358.3333 | 697.5579 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03879
1985 | 133.3333 | 259.5564 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0401
1986 | 22.2222 | 43.2594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0516
1987 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05437
1988 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05793
1989 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05555
1990 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0526
1991 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.055
1992 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0532
1993 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.03934
1994 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0375
1995 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04
1996 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0374
1997 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0426
1998 | 2.7778 | 5.4074 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.043
1999 | 33.3333 | 64.8891 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04945
2000 | 144.4444 | 281.1861 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.057
2001 | 300 | 584.0019 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05618
2002 | 416.6667 | 811.1138 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05469
2003 | 425 | 827.3361 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04961
2004 | 405.5556 | 789.4841 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.049
2005 | 308.3333 | 600.2242 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04806
2006 | 344.4444 | 670.5207 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0474
2007 | 350 | 681.3356 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0462
2008 | 150 | 292.001 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04652
2009 | 80.5556 | 156.8153 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0474
2010 | 27.7778 | 54.0743 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05168
2011 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0562
2012 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0635
2013 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05822
2014 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05481
2015 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05499
2016 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05256
2017 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04825
2018 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0463
2019 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0462
2020 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0463
2021 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0463
2022 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0475
2023 | 66.6667 | 129.7782 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.054
2024 | 133.3333 | 259.5564 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0578
2025 | 225 | 438.0014 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05775
2026 | 200 | 389.3346 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.055
2027 | 247.2222 | 481.2608 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.057
2028 | 300 | 584.0019 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05405
2029 | 261.1111 | 508.298 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05378
2030 | 302.7778 | 589.4093 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0524
2031 | 205.5556 | 400.1495 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0511
2032 | 122.2222 | 237.9267 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0489
2033 | 72.2222 | 140.5931 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.049
2034 | 25 | 48.6668 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05476
2035 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.058
2036 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0644
2037 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06141
2038 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05837
2039 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05728
2040 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05342
2041 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05162
2042 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04981
2043 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04927
2044 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04837
2045 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04914
2046 | 8.3333 | 16.2223 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05182
2047 | 111.1111 | 216.297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05701
2048 | 277.7778 | 540.7425 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.061
2049 | 422.2222 | 821.9286 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06204
2050 | 472.2222 | 919.2623 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05894
2051 | 619.4444 | 1205.8558 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05648
2052 | 577.7778 | 1124.7444 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05561
2053 | 541.6667 | 1054.4479 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.055
2054 | 441.6667 | 859.7806 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05458
2055 | 216.6667 | 421.7792 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05375
2056 | 158.3333 | 308.2232 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05375
2057 | 77.7778 | 151.4079 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05418
2058 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05649
2059 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05917
2060 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06268
2061 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05899
2062 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05622
2063 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05583
2064 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05192
2065 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04773
2066 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04867
2067 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04838
2068 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04829
2069 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04812
2070 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05167
2071 | 25 | 48.6668 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05948
2072 | 111.1111 | 216.297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06406
2073 | 161.1111 | 313.6307 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06353
2074 | 180.5556 | 351.4826 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06178
2075 | 233.3333 | 454.2237 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05912
2076 | 319.4444 | 621.8539 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05836
2077 | 261.1111 | 508.298 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05754
2078 | 150 | 292.001 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05739
2079 | 105.5556 | 205.4822 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05674
2080 | 100 | 194.6673 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05694
2081 | 69.4444 | 135.1856 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05753
2082 | 19.4444 | 37.852 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06074
2083 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06265
2084 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06766
2085 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06136
2086 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0583
2087 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05738
2088 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05432
2089 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05428
2090 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0491
2091 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04944
2092 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04947
2093 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04999
2094 | 13.8889 | 27.0371 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05304
2095 | 113.8889 | 221.7044 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06056
2096 | 266.6667 | 519.1128 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06333
2097 | 422.2222 | 821.9286 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06262
2098 | 530.5556 | 1032.8182 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05807
2099 | 605.5556 | 1178.8187 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0532
2100 | 636.1111 | 1238.3004 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04949
2101 | 636.1111 | 1238.3004 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04843
2102 | 572.2222 | 1113.9296 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04787
2103 | 458.3333 | 892.2252 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0474
2104 | 308.3333 | 600.2242 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04813
2105 | 147.2222 | 286.5935 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05101
2106 | 36.1111 | 70.2965 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05827
2107 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06351
2108 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06407
2109 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06262
2110 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05804
2111 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05775
2112 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05432
2113 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05249
2114 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05168
2115 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04936
2116 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04961
2117 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0499
2118 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05002
2119 | 133.3333 | 259.5564 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04851
2120 | 291.6667 | 567.7796 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05189
2121 | 438.8889 | 854.3732 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0521
2122 | 541.6667 | 1054.4479 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04817
2123 | 591.6667 | 1151.7816 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04663
2124 | 550 | 1070.6702 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0485
2125 | 333.3333 | 648.891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0497
2126 | 230.5556 | 448.8163 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0474
2127 | 225 | 438.0014 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0494
2128 | 175 | 340.6678 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04585
2129 | 125 | 243.3341 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0494
2130 | 41.6667 | 81.1114 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05529
2131 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06181
2132 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06162
2133 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05808
2134 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05553
2135 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05586
2136 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05185
2137 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0551
2138 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05233
2139 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05503
2140 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05238
2141 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04867
2142 | 8.3333 | 16.2223 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.047
2143 | 41.6667 | 81.1114 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04898
2144 | 116.6667 | 227.1119 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04807
2145 | 338.8889 | 659.7059 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05128
2146 | 594.4444 | 1157.189 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05242
2147 | 561.1111 | 1092.2999 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05238
2148 | 694.4444 | 1351.8563 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04015
2149 | 575 | 1119.337 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0458
2150 | 588.8889 | 1146.3741 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0399
2151 | 508.3333 | 989.5588 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0251
2152 | 352.7778 | 686.743 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03506
2153 | 177.7778 | 346.0752 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04173
2154 | 47.2222 | 91.9262 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04897
2155 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05369
2156 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0568
2157 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05408
2158 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0553
2159 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05251
2160 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04606
2161 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04496
2162 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04607
2163 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04563
2164 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0455
2165 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05157
2166 | 27.7778 | 54.0743 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06093
2167 | 152.7778 | 297.4084 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07056
2168 | 325 | 632.6688 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06856
2169 | 477.7778 | 930.0771 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06095
2170 | 588.8889 | 1146.3741 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0572
2171 | 666.6667 | 1297.7821 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05411
2172 | 694.4444 | 1351.8563 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0493
2173 | 688.8889 | 1341.0415 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04729
2174 | 630.5556 | 1227.4855 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0461
2175 | 516.6667 | 1005.7811 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04655
2176 | 363.8889 | 708.3727 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0468
2177 | 180.5556 | 351.4826 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05074
2178 | 50 | 97.3337 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05894
2179 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0601
2180 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06006
2181 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05441
2182 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0508
2183 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05181
2184 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04923
2185 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.049
2186 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05
2187 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0459
2188 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0459
2189 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04604
2190 | 36.1111 | 70.2965 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05529
2191 | 130.5556 | 254.149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05878
2192 | 294.4444 | 573.1871 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06058
2193 | 427.7778 | 832.7435 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06411
2194 | 472.2222 | 919.2623 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.065
2195 | 558.3333 | 1086.8925 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05497
2196 | 447.2222 | 870.5955 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0637
2197 | 311.1111 | 605.6316 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05788
2198 | 80.5556 | 156.8153 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05402
2199 | 44.4444 | 86.5188 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05266
2200 | 169.4444 | 329.8529 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05
2201 | 138.8889 | 270.3713 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05008
2202 | 8.3333 | 16.2223 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05573
2203 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05815
2204 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05774
2205 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0532
2206 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05008
2207 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04601
2208 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0469
2209 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0465
2210 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04608
2211 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04619
2212 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04757
2213 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05
2214 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05798
2215 | 91.6667 | 178.445 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06325
2216 | 130.5556 | 254.149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06742
2217 | 266.6667 | 519.1128 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06972
2218 | 252.7778 | 492.0757 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06447
2219 | 277.7778 | 540.7425 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06287
2220 | 269.4444 | 524.5202 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05989
2221 | 294.4444 | 573.1871 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05811
2222 | 213.8889 | 416.3717 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05677
2223 | 200 | 389.3346 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05648
2224 | 105.5556 | 205.4822 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05673
2225 | 55.5556 | 108.1485 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05768
2226 | 13.8889 | 27.0371 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06044
2227 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06632
2228 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06734
2229 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05908
2230 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0541
2231 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05158
2232 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0506
2233 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05002
2234 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.048
2235 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04759
2236 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04913
2237 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05186
2238 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05967
2239 | 44.4444 | 86.5188 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06864
2240 | 94.4444 | 183.8525 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07486
2241 | 116.6667 | 227.1119 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0625
2242 | 127.7778 | 248.7416 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07076
2243 | 194.4444 | 378.5198 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06515
2244 | 205.5556 | 400.1495 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06
2245 | 163.8889 | 319.0381 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05632
2246 | 127.7778 | 248.7416 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05359
2247 | 66.6667 | 129.7782 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0533
2248 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0531
2249 | 55.5556 | 108.1485 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05508
2250 | 27.7778 | 54.0743 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06023
2251 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0655
2252 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06393
2253 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05881
2254 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05347
2255 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0518
2256 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05036
2257 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0499
2258 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04949
2259 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04876
2260 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05117
2261 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05353
2262 | 19.4444 | 37.852 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05984
2263 | 72.2222 | 140.5931 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06704
2264 | 266.6667 | 519.1128 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07367
2265 | 422.2222 | 821.9286 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06864
2266 | 347.2222 | 675.9282 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06158
2267 | 300 | 584.0019 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05765
2268 | 216.6667 | 421.7792 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0549
2269 | 238.8889 | 465.0386 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05472
2270 | 147.2222 | 286.5935 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05354
2271 | 175 | 340.6678 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05334
2272 | 144.4444 | 281.1861 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05364
2273 | 75 | 146.0005 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05596
2274 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05935
2275 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06223
2276 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06194
2277 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05699
2278 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05633
2279 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05533
2280 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05665
2281 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05486
2282 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05331
2283 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0511
2284 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05113
2285 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05227
2286 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0542
2287 | 27.7778 | 54.0743 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05703
2288 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05906
2289 | 97.2222 | 189.2599 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06151
2290 | 105.5556 | 205.4822 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05772
2291 | 216.6667 | 421.7792 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05591
2292 | 450 | 876.0029 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05287
2293 | 300 | 584.0019 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05289
2294 | 258.3333 | 502.8905 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0496
2295 | 183.3333 | 356.8901 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0512
2296 | 186.1111 | 362.2975 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05238
2297 | 111.1111 | 216.297 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0536
2298 | 30.5556 | 59.4817 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05662
2299 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05791
2300 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08
2301 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0624
2302 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.063
2303 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06053
2304 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05678
2305 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05363
2306 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0524
2307 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0505
2308 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05064
2309 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05117
2310 | 38.8889 | 75.704 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05169
2311 | 158.3333 | 308.2232 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05443
2312 | 305.5556 | 594.8168 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05551
2313 | 447.2222 | 870.5955 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05566
2314 | 577.7778 | 1124.7444 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05163
2315 | 650 | 1265.3375 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04999
2316 | 677.7778 | 1319.4118 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04968
2317 | 661.1111 | 1286.9672 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0465
2318 | 608.3333 | 1184.2261 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04303
2319 | 505.5556 | 984.1514 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04392
2320 | 358.3333 | 697.5579 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0464
2321 | 194.4444 | 378.5198 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04987
2322 | 58.3333 | 113.5559 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0579
2323 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06165
2324 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06465
2325 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06127
2326 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06055
2327 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05901
2328 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05384
2329 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0527
2330 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05173
2331 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0513
2332 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0522
2333 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0566
2334 | 44.4444 | 86.5188 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06996
2335 | 177.7778 | 346.0752 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07447
2336 | 358.3333 | 697.5579 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.075
2337 | 502.7778 | 978.744 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07362
2338 | 608.3333 | 1184.2261 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0641
2339 | 677.7778 | 1319.4118 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0594
2340 | 700 | 1362.6712 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.056
2341 | 666.6667 | 1297.7821 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05551
2342 | 611.1111 | 1189.6336 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05425
2343 | 477.7778 | 930.0771 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05517
2344 | 350 | 681.3356 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05473
2345 | 158.3333 | 308.2232 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05784
2346 | 58.3333 | 113.5559 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06005
2347 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06346
2348 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06158
2349 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05878
2350 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05737
2351 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05244
2352 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04975
2353 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04969
2354 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0506
2355 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04996
2356 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05012
2357 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05247
2358 | 41.6667 | 81.1114 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0622
2359 | 169.4444 | 329.8529 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06708
2360 | 311.1111 | 605.6316 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07032
2361 | 516.6667 | 1005.7811 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06447
2362 | 611.1111 | 1189.6336 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06211
2363 | 708.3333 | 1378.8934 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05979
2364 | 725 | 1411.338 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05677
2365 | 694.4444 | 1351.8563 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05594
2366 | 644.4444 | 1254.5227 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05459
2367 | 550 | 1070.6702 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05238
2368 | 413.8889 | 805.7064 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05239
2369 | 216.6667 | 421.7792 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05571
2370 | 69.4444 | 135.1856 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05909
2371 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06201
2372 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06094
2373 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05776
2374 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05701
2375 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05407
2376 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0515
2377 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05218
2378 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05154
2379 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05078
2380 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05163
2381 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05355
2382 | 63.8889 | 124.3708 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06199
2383 | 208.3333 | 405.5569 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06943
2384 | 391.6667 | 762.447 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07302
2385 | 541.6667 | 1054.4479 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06559
2386 | 650 | 1265.3375 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05968
2387 | 725 | 1411.338 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05634
2388 | 744.4444 | 1449.19 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0515
2389 | 711.1111 | 1384.3009 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05241
2390 | 655.5556 | 1276.1524 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05314
2391 | 566.6667 | 1103.1147 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0526
2392 | 425 | 827.3361 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05312
2393 | 236.1111 | 459.6311 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0576
2394 | 80.5556 | 156.8153 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0615
2395 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0622
2396 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06197
2397 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05956
2398 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0576
2399 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05423
2400 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0525
2401 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05207
2402 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05207
2403 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05152
2404 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0521
2405 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05387
2406 | 63.8889 | 124.3708 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06291
2407 | 205.5556 | 400.1495 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0714
2408 | 386.1111 | 751.6321 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07424
2409 | 530.5556 | 1032.8182 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0667
2410 | 625 | 1216.6707 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06355
2411 | 413.8889 | 805.7064 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06098
2412 | 363.8889 | 708.3727 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05895
2413 | 338.8889 | 659.7059 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05486
2414 | 458.3333 | 892.2252 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0539
2415 | 413.8889 | 805.7064 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05428
2416 | 325 | 632.6688 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.054
2417 | 144.4444 | 281.1861 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05892
2418 | 38.8889 | 75.704 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06269
2419 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06902
2420 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06799
2421 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06402
2422 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0622
2423 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05905
2424 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05459
2425 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05401
2426 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05295
2427 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05222
2428 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0525
2429 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05605
2430 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06462
2431 | 147.2222 | 286.5935 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07398
2432 | 322.2222 | 627.2613 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07508
2433 | 350 | 681.3356 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06655
2434 | 405.5556 | 789.4841 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06397
2435 | 363.8889 | 708.3727 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06199
2436 | 244.4444 | 475.8534 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0601
2437 | 275 | 535.3351 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05911
2438 | 205.5556 | 400.1495 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05711
2439 | 208.3333 | 405.5569 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05567
2440 | 188.8889 | 367.7049 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05357
2441 | 150 | 292.001 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05673
2442 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06143
2443 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06343
2444 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06308
2445 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06036
2446 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06027
2447 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05827
2448 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05978
2449 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05847
2450 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05736
2451 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05511
2452 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05445
2453 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05593
2454 | 80.5556 | 156.8153 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05878
2455 | 222.2222 | 432.594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0601
2456 | 397.2222 | 773.2618 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06228
2457 | 505.5556 | 984.1514 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06196
2458 | 544.4444 | 1059.8553 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05745
2459 | 377.7778 | 735.4098 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05485
2460 | 605.5556 | 1178.8187 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05357
2461 | 297.2222 | 578.5945 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05302
2462 | 322.2222 | 627.2613 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05211
2463 | 272.2222 | 529.9277 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05142
2464 | 352.7778 | 686.743 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05065
2465 | 113.8889 | 221.7044 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05283
2466 | 36.1111 | 70.2965 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05803
2467 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06109
2468 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06128
2469 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06057
2470 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06004
2471 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05964
2472 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0546
2473 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.055
2474 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0547
2475 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05161
2476 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05223
2477 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0547
2478 | 52.7778 | 102.7411 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05236
2479 | 127.7778 | 248.7416 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05318
2480 | 369.4444 | 719.1876 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05536
2481 | 513.8889 | 1000.3737 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05476
2482 | 641.6667 | 1249.1152 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0521
2483 | 661.1111 | 1286.9672 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0546
2484 | 758.3333 | 1476.2271 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05
2485 | 725 | 1411.338 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0541
2486 | 619.4444 | 1205.8558 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05
2487 | 416.6667 | 811.1138 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05523
2488 | 311.1111 | 605.6316 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0547
2489 | 155.5556 | 302.8158 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0505
2490 | 38.8889 | 75.704 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05687
2491 | 5.5556 | 10.8149 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0597
2492 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06174
2493 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05828
2494 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06118
2495 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0601
2496 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06064
2497 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05661
2498 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05572
2499 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0539
2500 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05299
2501 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0576
2502 | 66.6667 | 129.7782 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06523
2503 | 200 | 389.3346 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07376
2504 | 372.2222 | 724.595 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07686
2505 | 513.8889 | 1000.3737 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06984
2506 | 616.6667 | 1200.4484 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.061
2507 | 700 | 1362.6712 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05625
2508 | 725 | 1411.338 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0509
2509 | 708.3333 | 1378.8934 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0515
2510 | 650 | 1265.3375 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.054
2511 | 530.5556 | 1032.8182 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05226
2512 | 411.1111 | 800.2989 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05166
2513 | 236.1111 | 459.6311 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05596
2514 | 80.5556 | 156.8153 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06201
2515 | 8.3333 | 16.2223 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06427
2516 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06356
2517 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0607
2518 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05743
2519 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0516
2520 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0518
2521 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05081
2522 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05166
2523 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05103
2524 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05006
2525 | 5.5556 | 10.8149 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05242
2526 | 97.2222 | 189.2599 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06122
2527 | 236.1111 | 459.6311 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06706
2528 | 400 | 778.6692 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06716
2529 | 541.6667 | 1054.4479 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06162
2530 | 650 | 1265.3375 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05572
2531 | 722.2222 | 1405.9306 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0514
2532 | 738.8889 | 1438.3751 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0504
2533 | 711.1111 | 1384.3009 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05079
2534 | 650 | 1265.3375 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0506
2535 | 544.4444 | 1059.8553 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05187
2536 | 330.5556 | 643.4836 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05428
2537 | 155.5556 | 302.8158 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0595
2538 | 55.5556 | 108.1485 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06474
2539 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06795
2540 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06532
2541 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06294
2542 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0589
2543 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0538
2544 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0485
2545 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0487
2546 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05002
2547 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05002
2548 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05036
2549 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05294
2550 | 50 | 97.3337 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06182
2551 | 163.8889 | 319.0381 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06543
2552 | 358.3333 | 697.5579 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06723
2553 | 494.4444 | 962.5217 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0654
2554 | 566.6667 | 1103.1147 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06301
2555 | 675 | 1314.0043 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06105
2556 | 608.3333 | 1184.2261 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06037
2557 | 358.3333 | 697.5579 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05689
2558 | 261.1111 | 508.298 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05112
2559 | 186.1111 | 362.2975 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05005
2560 | 161.1111 | 313.6307 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05049
2561 | 80.5556 | 156.8153 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05373
2562 | 33.3333 | 64.8891 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06109
2563 | 8.3333 | 16.2223 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06449
2564 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06309
2565 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05983
2566 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05603
2567 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05229
2568 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05293
2569 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0523
2570 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05224
2571 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05002
2572 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05006
2573 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05307
2574 | 88.8889 | 173.0376 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06282
2575 | 236.1111 | 459.6311 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06695
2576 | 411.1111 | 800.2989 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07361
2577 | 555.5556 | 1081.485 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06493
2578 | 661.1111 | 1286.9672 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05957
2579 | 608.3333 | 1184.2261 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05539
2580 | 708.3333 | 1378.8934 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05279
2581 | 713.8889 | 1389.7083 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0524
2582 | 602.7778 | 1173.4113 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.051
2583 | 436.1111 | 848.9658 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05
2584 | 341.6667 | 665.1133 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05
2585 | 230.5556 | 448.8163 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0544
2586 | 83.3333 | 162.2228 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06009
2587 | 8.3333 | 16.2223 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06431
2588 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06319
2589 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06081
2590 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05819
2591 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05665
2592 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05529
2593 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05528
2594 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0517
2595 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0491
2596 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04707
2597 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0499
2598 | 100 | 194.6673 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05534
2599 | 244.4444 | 475.8534 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05797
2600 | 413.8889 | 805.7064 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06436
2601 | 555.5556 | 1081.485 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05949
2602 | 666.6667 | 1297.7821 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05659
2603 | 741.6667 | 1443.7825 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05639
2604 | 761.1111 | 1481.6345 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0573
2605 | 733.3333 | 1427.5603 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05651
2606 | 680.5556 | 1324.8192 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05651
2607 | 572.2222 | 1113.9296 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05467
2608 | 397.2222 | 773.2618 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0451
2609 | 250 | 486.6683 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05783
2610 | 91.6667 | 178.445 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06297
2611 | 11.1111 | 21.6297 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06702
2612 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0582
2613 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06054
2614 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05908
2615 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05737
2616 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05609
2617 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04657
2618 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.045
2619 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0475
2620 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0475
2621 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04933
2622 | 102.7778 | 200.0747 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05492
2623 | 255.5556 | 497.4831 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0551
2624 | 425 | 827.3361 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0563
2625 | 561.1111 | 1092.2999 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0527
2626 | 675 | 1314.0043 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04603
2627 | 744.4444 | 1449.19 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04338
2628 | 758.3333 | 1476.2271 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04191
2629 | 736.1111 | 1432.9677 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0378
2630 | 677.7778 | 1319.4118 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03603
2631 | 558.3333 | 1086.8925 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0487
2632 | 386.1111 | 751.6321 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05416
2633 | 247.2222 | 481.2608 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05781
2634 | 91.6667 | 178.445 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05879
2635 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06449
2636 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07063
2637 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05841
2638 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0575
2639 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05637
2640 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05195
2641 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04902
2642 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.048
2643 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0507
2644 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05347
2645 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0554
2646 | 108.3333 | 210.8896 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0507
2647 | 266.6667 | 519.1128 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05196
2648 | 438.8889 | 854.3732 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.049
2649 | 583.3333 | 1135.5593 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04723
2650 | 691.6667 | 1346.4489 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0441
2651 | 769.4444 | 1497.8568 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04405
2652 | 783.3333 | 1524.8939 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04247
2653 | 758.3333 | 1476.2271 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.025
2654 | 697.2222 | 1357.2637 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.02127
2655 | 580.5556 | 1130.1519 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0247
2656 | 402.7778 | 784.0767 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0374
2657 | 255.5556 | 497.4831 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05399
2658 | 94.4444 | 183.8525 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06027
2659 | 13.8889 | 27.0371 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0648
2660 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06108
2661 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05916
2662 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05638
2663 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05334
2664 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04279
2665 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.03418
2666 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.028
2667 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.02501
2668 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0427
2669 | 11.1111 | 21.6297 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03836
2670 | 108.3333 | 210.8896 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.042
2671 | 261.1111 | 508.298 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.047
2672 | 430.5556 | 838.1509 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0399
2673 | 572.2222 | 1113.9296 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0427
2674 | 625 | 1216.6707 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0599
2675 | 733.3333 | 1427.5603 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06997
2676 | 766.6667 | 1492.4494 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05651
2677 | 741.6667 | 1443.7825 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05309
2678 | 672.2222 | 1308.5969 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05146
2679 | 563.8889 | 1097.7073 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04865
2680 | 402.7778 | 784.0767 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.053
2681 | 236.1111 | 459.6311 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0575
2682 | 63.8889 | 124.3708 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06144
2683 | 13.8889 | 27.0371 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06533
2684 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.068
2685 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.08006
2686 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0674
2687 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05786
2688 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0547
2689 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0529
2690 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05276
2691 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05305
2692 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05275
2693 | 16.6667 | 32.4446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05338
2694 | 122.2222 | 237.9267 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0535
2695 | 275 | 535.3351 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06168
2696 | 441.6667 | 859.7806 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.064
2697 | 577.7778 | 1124.7444 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.07
2698 | 688.8889 | 1341.0415 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.0574
2699 | 750 | 1460.0048 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05891
2700 | 697.2222 | 1357.2637 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.0549
2701 | 772.2222 | 1503.2642 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05416
2702 | 691.6667 | 1346.4489 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.05314
2703 | 519.4444 | 1011.1885 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.04865
2704 | 200 | 389.3346 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05267
2705 | 222.2222 | 432.594 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05548
2706 | 86.1111 | 167.6302 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05987
2707 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06196
2708 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0651
2709 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07446
2710 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05914
2711 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05572
2712 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.053
2713 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04914
2714 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04905
2715 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0479
2716 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0476
2717 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04725
2718 | 86.1111 | 167.6302 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05459
2719 | 166.6667 | 324.4455 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05818
2720 | 211.1111 | 410.9643 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0652
2721 | 222.2222 | 432.594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05697
2722 | 552.7778 | 1076.0776 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05465
2723 | 736.1111 | 1432.9677 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05356
2724 | 672.2222 | 1308.5969 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0478
2725 | 691.6667 | 1346.4489 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04752
2726 | 672.2222 | 1308.5969 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0466
2727 | 505.5556 | 984.1514 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.047
2728 | 275 | 535.3351 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04894
2729 | 205.5556 | 400.1495 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05536
2730 | 41.6667 | 81.1114 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06038
2731 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06148
2732 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05936
2733 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05807
2734 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05365
2735 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05195
2736 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0539
2737 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05046
2738 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04843
2739 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04952
2740 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04449
2741 | 19.4444 | 37.852 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05099
2742 | 116.6667 | 227.1119 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0575
2743 | 197.2222 | 383.9272 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06503
2744 | 369.4444 | 719.1876 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06288
2745 | 277.7778 | 540.7425 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05918
2746 | 480.5556 | 935.4846 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05596
2747 | 630.5556 | 1227.4855 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05265
2748 | 780.5556 | 1519.4865 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0519
2749 | 672.2222 | 1308.5969 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0501
2750 | 469.4444 | 913.8549 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0474
2751 | 330.5556 | 643.4836 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05301
2752 | 147.2222 | 286.5935 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0493
2753 | 91.6667 | 178.445 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05552
2754 | 38.8889 | 75.704 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06122
2755 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07359
2756 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0749
2757 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06353
2758 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05721
2759 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05404
2760 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.052
2761 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05
2762 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04841
2763 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04929
2764 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05059
2765 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05392
2766 | 22.2222 | 43.2594 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06009
2767 | 61.1111 | 118.9634 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0686
2768 | 133.3333 | 259.5564 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07138
2769 | 202.7778 | 394.742 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06794
2770 | 325 | 632.6688 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06493
2771 | 355.5556 | 692.1504 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06194
2772 | 408.3333 | 794.8915 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05896
2773 | 408.3333 | 794.8915 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05716
2774 | 275 | 535.3351 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05535
2775 | 219.4444 | 427.1866 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05538
2776 | 175 | 340.6678 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05586
2777 | 141.6667 | 275.7787 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05942
2778 | 136.1111 | 264.9638 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05968
2779 | 22.2222 | 43.2594 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06375
2780 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06397
2781 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06104
2782 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05697
2783 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05205
2784 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04702
2785 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0451
2786 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04405
2787 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04304
2788 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04534
2789 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04463
2790 | 27.7778 | 54.0743 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04391
2791 | 63.8889 | 124.3708 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04987
2792 | 77.7778 | 151.4079 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.055
2793 | 94.4444 | 183.8525 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0555
2794 | 130.5556 | 254.149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0499
2795 | 272.2222 | 529.9277 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05137
2796 | 361.1111 | 702.9653 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04548
2797 | 527.7778 | 1027.4108 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.045
2798 | 455.5556 | 886.8177 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0449
2799 | 352.7778 | 686.743 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04547
2800 | 191.6667 | 373.1123 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04964
2801 | 127.7778 | 248.7416 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05268
2802 | 50 | 97.3337 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05574
2803 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05511
2804 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05358
2805 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0531
2806 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05136
2807 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04657
2808 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0523
2809 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05166
2810 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.045
2811 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.044
2812 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0477
2813 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.049
2814 | 111.1111 | 216.297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05533
2815 | 211.1111 | 410.9643 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05418
2816 | 327.7778 | 638.0762 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04705
2817 | 263.8889 | 513.7054 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0537
2818 | 525 | 1022.0034 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0542
2819 | 322.2222 | 627.2613 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0523
2820 | 222.2222 | 432.594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0523
2821 | 138.8889 | 270.3713 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0547
2822 | 191.6667 | 373.1123 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0523
2823 | 97.2222 | 189.2599 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04987
2824 | 158.3333 | 308.2232 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04972
2825 | 136.1111 | 264.9638 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05247
2826 | 91.6667 | 178.445 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05706
2827 | 27.7778 | 54.0743 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06159
2828 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0652
2829 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06107
2830 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06276
2831 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05956
2832 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05353
2833 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05122
2834 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05057
2835 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05001
2836 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04918
2837 | 13.8889 | 27.0371 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05157
2838 | 105.5556 | 205.4822 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06182
2839 | 294.4444 | 573.1871 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06777
2840 | 450 | 876.0029 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07171
2841 | 536.1111 | 1043.6331 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0663
2842 | 633.3333 | 1232.893 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06199
2843 | 727.7778 | 1416.7454 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06061
2844 | 647.2222 | 1259.9301 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05906
2845 | 458.3333 | 892.2252 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.058
2846 | 516.6667 | 1005.7811 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05567
2847 | 272.2222 | 529.9277 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05441
2848 | 108.3333 | 210.8896 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05449
2849 | 72.2222 | 140.5931 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05791
2850 | 27.7778 | 54.0743 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06227
2851 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06226
2852 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06407
2853 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06181
2854 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05986
2855 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05343
2856 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.049
2857 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05107
2858 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05
2859 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05024
2860 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04944
2861 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05201
2862 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06062
2863 | 33.3333 | 64.8891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06714
2864 | 72.2222 | 140.5931 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.075
2865 | 125 | 243.3341 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06647
2866 | 138.8889 | 270.3713 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06243
2867 | 169.4444 | 329.8529 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05985
2868 | 230.5556 | 448.8163 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05585
2869 | 261.1111 | 508.298 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05149
2870 | 344.4444 | 670.5207 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04998
2871 | 600 | 1168.0038 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04994
2872 | 422.2222 | 821.9286 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05034
2873 | 286.1111 | 556.9648 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0563
2874 | 147.2222 | 286.5935 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06209
2875 | 27.7778 | 54.0743 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0694
2876 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06676
2877 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06371
2878 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06128
2879 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05841
2880 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.053
2881 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0502
2882 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04764
2883 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04616
2884 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0483
2885 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0457
2886 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04598
2887 | 108.3333 | 210.8896 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04998
2888 | 158.3333 | 308.2232 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0545
2889 | 211.1111 | 410.9643 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05205
2890 | 275 | 535.3351 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05195
2891 | 333.3333 | 648.891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04789
2892 | 477.7778 | 930.0771 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05831
2893 | 566.6667 | 1103.1147 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06827
2894 | 602.7778 | 1173.4113 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06327
2895 | 605.5556 | 1178.8187 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05716
2896 | 455.5556 | 886.8177 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05266
2897 | 286.1111 | 556.9648 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0501
2898 | 147.2222 | 286.5935 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04966
2899 | 41.6667 | 81.1114 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0544
2900 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0549
2901 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0705
2902 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06701
2903 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05659
2904 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0505
2905 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05164
2906 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05081
2907 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04945
2908 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04197
2909 | 19.4444 | 37.852 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04693
2910 | 80.5556 | 156.8153 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05675
2911 | 175 | 340.6678 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06052
2912 | 338.8889 | 659.7059 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06218
2913 | 447.2222 | 870.5955 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0583
2914 | 400 | 778.6692 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06045
2915 | 180.5556 | 351.4826 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.059
2916 | 52.7778 | 102.7411 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05674
2917 | 91.6667 | 178.445 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05667
2918 | 205.5556 | 400.1495 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05474
2919 | 169.4444 | 329.8529 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.052
2920 | 108.3333 | 210.8896 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05248
2921 | 208.3333 | 405.5569 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05541
2922 | 127.7778 | 248.7416 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06098
2923 | 16.6667 | 32.4446 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06218
2924 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06356
2925 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06196
2926 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05972
2927 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05671
2928 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04829
2929 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0499
2930 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0486
2931 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04748
2932 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0481
2933 | 33.3333 | 64.8891 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05096
2934 | 158.3333 | 308.2232 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05695
2935 | 272.2222 | 529.9277 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06199
2936 | 302.7778 | 589.4093 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0651
2937 | 369.4444 | 719.1876 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06294
2938 | 455.5556 | 886.8177 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0619
2939 | 563.8889 | 1097.7073 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06147
2940 | 658.3333 | 1281.5598 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0587
2941 | 441.6667 | 859.7806 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05624
2942 | 269.4444 | 524.5202 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05405
2943 | 238.8889 | 465.0386 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05061
2944 | 163.8889 | 319.0381 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05047
2945 | 91.6667 | 178.445 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05389
2946 | 19.4444 | 37.852 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05701
2947 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05896
2948 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05957
2949 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05992
2950 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06037
2951 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05701
2952 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05472
2953 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05415
2954 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05056
2955 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0499
2956 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04998
2957 | 33.3333 | 64.8891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04951
2958 | 105.5556 | 205.4822 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05059
2959 | 225 | 438.0014 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05587
2960 | 275 | 535.3351 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06
2961 | 325 | 632.6688 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06007
2962 | 386.1111 | 751.6321 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05862
2963 | 344.4444 | 670.5207 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05765
2964 | 361.1111 | 702.9653 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05556
2965 | 411.1111 | 800.2989 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05198
2966 | 433.3333 | 843.5583 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04995
2967 | 550 | 1070.6702 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05011
2968 | 491.6667 | 957.1143 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0525
2969 | 269.4444 | 524.5202 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0542
2970 | 202.7778 | 394.742 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05603
2971 | 33.3333 | 64.8891 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05953
2972 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05981
2973 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0605
2974 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06092
2975 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0593
2976 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05019
2977 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04702
2978 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.045
2979 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0471
2980 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0471
2981 | 33.3333 | 64.8891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05357
2982 | 72.2222 | 140.5931 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05
2983 | 102.7778 | 200.0747 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05066
2984 | 233.3333 | 454.2237 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04893
2985 | 216.6667 | 421.7792 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05186
2986 | 305.5556 | 594.8168 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.053
2987 | 313.8889 | 611.0391 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0499
2988 | 255.5556 | 497.4831 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0553
2989 | 302.7778 | 589.4093 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05512
2990 | 272.2222 | 529.9277 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.045
2991 | 611.1111 | 1189.6336 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0449
2992 | 288.8889 | 562.3722 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0503
2993 | 183.3333 | 356.8901 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05503
2994 | 105.5556 | 205.4822 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.055
2995 | 33.3333 | 64.8891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05558
2996 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06
2997 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07475
2998 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07762
2999 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06702
3000 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06733
3001 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05766
3002 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0549
3003 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05456
3004 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05119
3005 | 19.4444 | 37.852 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05135
3006 | 63.8889 | 124.3708 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06085
3007 | 133.3333 | 259.5564 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06663
3008 | 258.3333 | 502.8905 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06384
3009 | 488.8889 | 951.7068 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06022
3010 | 677.7778 | 1319.4118 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06042
3011 | 344.4444 | 670.5207 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06121
3012 | 222.2222 | 432.594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06087
3013 | 202.7778 | 394.742 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05919
3014 | 94.4444 | 183.8525 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05708
3015 | 180.5556 | 351.4826 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05609
3016 | 63.8889 | 124.3708 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05616
3017 | 66.6667 | 129.7782 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05887
3018 | 63.8889 | 124.3708 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06219
3019 | 19.4444 | 37.852 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0694
3020 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07114
3021 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07114
3022 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07
3023 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06033
3024 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05732
3025 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05598
3026 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0558
3027 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05503
3028 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05503
3029 | 38.8889 | 75.704 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05771
3030 | 141.6667 | 275.7787 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06659
3031 | 277.7778 | 540.7425 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07516
3032 | 491.6667 | 957.1143 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0789
3033 | 322.2222 | 627.2613 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07253
3034 | 522.2222 | 1016.5959 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07387
3035 | 286.1111 | 556.9648 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0714
3036 | 475 | 924.6697 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06907
3037 | 494.4444 | 962.5217 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06394
3038 | 600 | 1168.0038 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.063
3039 | 191.6667 | 373.1123 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06177
3040 | 119.4444 | 232.5193 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0621
3041 | 144.4444 | 281.1861 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06394
3042 | 44.4444 | 86.5188 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07422
3043 | 38.8889 | 75.704 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08068
3044 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08287
3045 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07
3046 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06598
3047 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06
3048 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05918
3049 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05403
3050 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05096
3051 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05079
3052 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05008
3053 | 19.4444 | 37.852 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05137
3054 | 72.2222 | 140.5931 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05867
3055 | 133.3333 | 259.5564 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06409
3056 | 275 | 535.3351 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06392
3057 | 397.2222 | 773.2618 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0612
3058 | 516.6667 | 1005.7811 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05966
3059 | 394.4444 | 767.8544 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0585
3060 | 352.7778 | 686.743 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05787
3061 | 197.2222 | 383.9272 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05319
3062 | 200 | 389.3346 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05078
3063 | 66.6667 | 129.7782 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0499
3064 | 50 | 97.3337 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04938
3065 | 80.5556 | 156.8153 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05045
3066 | 44.4444 | 86.5188 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05235
3067 | 30.5556 | 59.4817 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05419
3068 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05461
3069 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05301
3070 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06
3071 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05519
3072 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04892
3073 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04701
3074 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04526
3075 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04569
3076 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0481
3077 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05207
3078 | 150 | 292.001 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06099
3079 | 311.1111 | 605.6316 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06492
3080 | 486.1111 | 946.2994 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06966
3081 | 533.3333 | 1038.2256 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06719
3082 | 536.1111 | 1043.6331 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06495
3083 | 727.7778 | 1416.7454 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06493
3084 | 466.6667 | 908.4474 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06405
3085 | 480.5556 | 935.4846 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06276
3086 | 488.8889 | 951.7068 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06076
3087 | 283.3333 | 551.5574 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06033
3088 | 158.3333 | 308.2232 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06054
3089 | 77.7778 | 151.4079 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06641
3090 | 105.5556 | 205.4822 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06605
3091 | 25 | 48.6668 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07198
3092 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07
3093 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0649
3094 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06407
3095 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.059
3096 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0551
3097 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05383
3098 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05254
3099 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05225
3100 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05217
3101 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05402
3102 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06263
3103 | 58.3333 | 113.5559 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06958
3104 | 55.5556 | 108.1485 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07117
3105 | 188.8889 | 367.7049 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06807
3106 | 336.1111 | 654.2985 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06541
3107 | 302.7778 | 589.4093 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06193
3108 | 472.2222 | 919.2623 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06011
3109 | 230.5556 | 448.8163 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05698
3110 | 219.4444 | 427.1866 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05594
3111 | 347.2222 | 675.9282 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.053
3112 | 466.6667 | 908.4474 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05238
3113 | 272.2222 | 529.9277 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0577
3114 | 130.5556 | 254.149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0639
3115 | 41.6667 | 81.1114 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06548
3116 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06681
3117 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06645
3118 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06622
3119 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06347
3120 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05906
3121 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.055
3122 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05294
3123 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05508
3124 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05196
3125 | 33.3333 | 64.8891 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05162
3126 | 150 | 292.001 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05216
3127 | 263.8889 | 513.7054 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05365
3128 | 452.7778 | 881.4103 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05655
3129 | 619.4444 | 1205.8558 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0574
3130 | 713.8889 | 1389.7083 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06158
3131 | 552.7778 | 1076.0776 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06023
3132 | 591.6667 | 1151.7816 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05487
3133 | 647.2222 | 1259.9301 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05109
3134 | 519.4444 | 1011.1885 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04819
3135 | 497.2222 | 967.9291 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04679
3136 | 522.2222 | 1016.5959 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0467
3137 | 372.2222 | 724.595 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04946
3138 | 188.8889 | 367.7049 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05236
3139 | 63.8889 | 124.3708 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0549
3140 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05288
3141 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06031
3142 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0727
3143 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06791
3144 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05876
3145 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0558
3146 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0555
3147 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05488
3148 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05544
3149 | 58.3333 | 113.5559 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0524
3150 | 202.7778 | 394.742 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0431
3151 | 369.4444 | 719.1876 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05539
3152 | 547.2222 | 1065.2628 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05556
3153 | 433.3333 | 843.5583 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0556
3154 | 255.5556 | 497.4831 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0539
3155 | 591.6667 | 1151.7816 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0532
3156 | 827.7778 | 1611.4127 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.054
3157 | 602.7778 | 1173.4113 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0524
3158 | 511.1111 | 994.9662 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05
3159 | 461.1111 | 897.6326 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0499
3160 | 388.8889 | 757.0395 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05553
3161 | 344.4444 | 670.5207 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0482
3162 | 205.5556 | 400.1495 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05588
3163 | 69.4444 | 135.1856 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05298
3164 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.055
3165 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05587
3166 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0591
3167 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05909
3168 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05994
3169 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05759
3170 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0549
3171 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0518
3172 | 2.7778 | 5.4074 | 0 | 0 | 0 | 0 | #DIV/0! | 0.046
3173 | 58.3333 | 113.5559 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05073
3174 | 161.1111 | 313.6307 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06116
3175 | 316.6667 | 616.4465 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06801
3176 | 527.7778 | 1027.4108 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06801
3177 | 680.5556 | 1324.8192 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06226
3178 | 777.7778 | 1514.0791 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.055
3179 | 827.7778 | 1611.4127 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0517
3180 | 852.7778 | 1660.0795 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0497
3181 | 722.2222 | 1405.9306 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04774
3182 | 586.1111 | 1140.9667 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04633
3183 | 588.8889 | 1146.3741 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04598
3184 | 527.7778 | 1027.4108 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04706
3185 | 366.6667 | 713.7801 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05394
3186 | 194.4444 | 378.5198 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0586
3187 | 63.8889 | 124.3708 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06395
3188 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06621
3189 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06261
3190 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06188
3191 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05626
3192 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05334
3193 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05083
3194 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05032
3195 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04996
3196 | 2.7778 | 5.4074 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0506
3197 | 61.1111 | 118.9634 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05379
3198 | 200 | 389.3346 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06322
3199 | 344.4444 | 670.5207 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06961
3200 | 472.2222 | 919.2623 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07053
3201 | 638.8889 | 1243.7078 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06198
3202 | 652.7778 | 1270.7449 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05571
3203 | 805.5556 | 1568.1533 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0513
3204 | 833.3333 | 1622.2276 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04926
3205 | 833.3333 | 1622.2276 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.049
3206 | 694.4444 | 1351.8563 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04884
3207 | 611.1111 | 1189.6336 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04904
3208 | 411.1111 | 800.2989 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04993
3209 | 327.7778 | 638.0762 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0523
3210 | 175 | 340.6678 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05895
3211 | 63.8889 | 124.3708 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06291
3212 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06329
3213 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06322
3214 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06019
3215 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05536
3216 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0521
3217 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05068
3218 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05057
3219 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05044
3220 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04938
3221 | 61.1111 | 118.9634 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05121
3222 | 205.5556 | 400.1495 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0591
3223 | 386.1111 | 751.6321 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06599
3224 | 483.3333 | 940.892 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07007
3225 | 680.5556 | 1324.8192 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06282
3226 | 777.7778 | 1514.0791 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05984
3227 | 838.8889 | 1633.0424 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05594
3228 | 861.1111 | 1676.3018 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05377
3229 | 752.7778 | 1465.4122 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05067
3230 | 636.1111 | 1238.3004 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05057
3231 | 527.7778 | 1027.4108 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04928
3232 | 438.8889 | 854.3732 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05052
3233 | 300 | 584.0019 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.055
3234 | 177.7778 | 346.0752 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05911
3235 | 77.7778 | 151.4079 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0608
3236 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05937
3237 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05823
3238 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0585
3239 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05391
3240 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0495
3241 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0495
3242 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04901
3243 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04707
3244 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04809
3245 | 22.2222 | 43.2594 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05005
3246 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0577
3247 | 108.3333 | 210.8896 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06221
3248 | 166.6667 | 324.4455 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0643
3249 | 391.6667 | 762.447 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06006
3250 | 555.5556 | 1081.485 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05923
3251 | 761.1111 | 1481.6345 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05893
3252 | 697.2222 | 1357.2637 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0567
3253 | 638.8889 | 1243.7078 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05497
3254 | 513.8889 | 1000.3737 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05387
3255 | 238.8889 | 465.0386 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05297
3256 | 236.1111 | 459.6311 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0509
3257 | 94.4444 | 183.8525 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05405
3258 | 50 | 97.3337 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05597
3259 | 30.5556 | 59.4817 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0578
3260 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05658
3261 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05638
3262 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05583
3263 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05179
3264 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0507
3265 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05018
3266 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04925
3267 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04879
3268 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.049
3269 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05109
3270 | 77.7778 | 151.4079 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05613
3271 | 116.6667 | 227.1119 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06171
3272 | 202.7778 | 394.742 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06589
3273 | 352.7778 | 686.743 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06417
3274 | 305.5556 | 594.8168 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06127
3275 | 252.7778 | 492.0757 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06103
3276 | 297.2222 | 578.5945 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05986
3277 | 308.3333 | 600.2242 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0566
3278 | 180.5556 | 351.4826 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05415
3279 | 116.6667 | 227.1119 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05349
3280 | 152.7778 | 297.4084 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05404
3281 | 80.5556 | 156.8153 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05753
3282 | 36.1111 | 70.2965 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06336
3283 | 13.8889 | 27.0371 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06761
3284 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06755
3285 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06383
3286 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06332
3287 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05847
3288 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05237
3289 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04939
3290 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04985
3291 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04911
3292 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04976
3293 | 58.3333 | 113.5559 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04842
3294 | 191.6667 | 373.1123 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04892
3295 | 350 | 681.3356 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05124
3296 | 458.3333 | 892.2252 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05399
3297 | 516.6667 | 1005.7811 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05252
3298 | 655.5556 | 1276.1524 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05012
3299 | 575 | 1119.337 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04979
3300 | 783.3333 | 1524.8939 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0489
3301 | 602.7778 | 1173.4113 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04805
3302 | 669.4444 | 1303.1895 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04736
3303 | 608.3333 | 1184.2261 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04825
3304 | 411.1111 | 800.2989 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0491
3305 | 205.5556 | 400.1495 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05036
3306 | 205.5556 | 400.1495 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0579
3307 | 63.8889 | 124.3708 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05993
3308 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06017
3309 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05975
3310 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05996
3311 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.057
3312 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05466
3313 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05102
3314 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05
3315 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04903
3316 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04918
3317 | 50 | 97.3337 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04891
3318 | 141.6667 | 275.7787 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04837
3319 | 250 | 486.6683 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04904
3320 | 425 | 827.3361 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05007
3321 | 569.4444 | 1108.5222 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05002
3322 | 613.8889 | 1195.041 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04908
3323 | 661.1111 | 1286.9672 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0491
3324 | 811.1111 | 1578.9682 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0488
3325 | 586.1111 | 1140.9667 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04464
3326 | 741.6667 | 1443.7825 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04241
3327 | 530.5556 | 1032.8182 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04249
3328 | 355.5556 | 692.1504 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04528
3329 | 19.4444 | 37.852 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04947
3330 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05328
3331 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05728
3332 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05734
3333 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05671
3334 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05833
3335 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05394
3336 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0523
3337 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05
3338 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04955
3339 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0499
3340 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04877
3341 | 38.8889 | 75.704 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05104
3342 | 75 | 146.0005 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0628
3343 | 133.3333 | 259.5564 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0754
3344 | 177.7778 | 346.0752 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07767
3345 | 277.7778 | 540.7425 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0727
3346 | 636.1111 | 1238.3004 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07163
3347 | 550 | 1070.6702 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0705
3348 | 502.7778 | 978.744 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06699
3349 | 597.2222 | 1162.5964 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06529
3350 | 458.3333 | 892.2252 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06259
3351 | 363.8889 | 708.3727 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06063
3352 | 330.5556 | 643.4836 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05937
3353 | 225 | 438.0014 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06109
3354 | 105.5556 | 205.4822 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06291
3355 | 25 | 48.6668 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06439
3356 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06118
3357 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0608
3358 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05917
3359 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05266
3360 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0502
3361 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04944
3362 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04812
3363 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04649
3364 | 2.7778 | 5.4074 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04737
3365 | 13.8889 | 27.0371 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04925
3366 | 41.6667 | 81.1114 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05552
3367 | 58.3333 | 113.5559 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06492
3368 | 100 | 194.6673 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07261
3369 | 141.6667 | 275.7787 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07
3370 | 211.1111 | 410.9643 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06752
3371 | 183.3333 | 356.8901 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06615
3372 | 169.4444 | 329.8529 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06485
3373 | 152.7778 | 297.4084 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06127
3374 | 127.7778 | 248.7416 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05895
3375 | 91.6667 | 178.445 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05614
3376 | 91.6667 | 178.445 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05552
3377 | 52.7778 | 102.7411 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05745
3378 | 16.6667 | 32.4446 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06095
3379 | 8.3333 | 16.2223 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06196
3380 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05987
3381 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05911
3382 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05649
3383 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05018
3384 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04766
3385 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0475
3386 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04466
3387 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.044
3388 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04461
3389 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04809
3390 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0526
3391 | 119.4444 | 232.5193 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0616
3392 | 302.7778 | 589.4093 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06535
3393 | 558.3333 | 1086.8925 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06337
3394 | 663.8889 | 1292.3746 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06077
3395 | 844.4444 | 1643.8573 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05741
3396 | 858.3333 | 1670.8944 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05599
3397 | 669.4444 | 1303.1895 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05365
3398 | 758.3333 | 1476.2271 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05199
3399 | 638.8889 | 1243.7078 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05102
3400 | 516.6667 | 1005.7811 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05071
3401 | 375 | 730.0024 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.054
3402 | 175 | 340.6678 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05785
3403 | 47.2222 | 91.9262 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06247
3404 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06399
3405 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06314
3406 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06345
3407 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05616
3408 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0508
3409 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04832
3410 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04737
3411 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04615
3412 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04572
3413 | 88.8889 | 173.0376 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04872
3414 | 219.4444 | 427.1866 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05418
3415 | 366.6667 | 713.7801 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06177
3416 | 530.5556 | 1032.8182 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06206
3417 | 641.6667 | 1249.1152 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05586
3418 | 713.8889 | 1389.7083 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05085
3419 | 725 | 1411.338 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0506
3420 | 802.7778 | 1562.7459 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05056
3421 | 755.5556 | 1470.8197 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05074
3422 | 675 | 1314.0043 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05055
3423 | 608.3333 | 1184.2261 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05176
3424 | 538.8889 | 1049.0405 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05257
3425 | 363.8889 | 708.3727 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05804
3426 | 222.2222 | 432.594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06355
3427 | 69.4444 | 135.1856 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06738
3428 | 5.5556 | 10.8149 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06995
3429 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06698
3430 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06441
3431 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06008
3432 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0549
3433 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05024
3434 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04993
3435 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04887
3436 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04946
3437 | 61.1111 | 118.9634 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04998
3438 | 211.1111 | 410.9643 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05516
3439 | 325 | 632.6688 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06474
3440 | 430.5556 | 838.1509 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06595
3441 | 658.3333 | 1281.5598 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06094
3442 | 769.4444 | 1497.8568 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05878
3443 | 855.5556 | 1665.487 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05454
3444 | 838.8889 | 1633.0424 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05248
3445 | 802.7778 | 1562.7459 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05085
3446 | 752.7778 | 1465.4122 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05035
3447 | 663.8889 | 1292.3746 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05
3448 | 544.4444 | 1059.8553 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05008
3449 | 397.2222 | 773.2618 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05164
3450 | 233.3333 | 454.2237 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05664
3451 | 91.6667 | 178.445 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05988
3452 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06055
3453 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06051
3454 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06006
3455 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05689
3456 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05697
3457 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05215
3458 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05007
3459 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04903
3460 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04884
3461 | 30.5556 | 59.4817 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04809
3462 | 102.7778 | 200.0747 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04905
3463 | 222.2222 | 432.594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05011
3464 | 333.3333 | 648.891 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0527
3465 | 272.2222 | 529.9277 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05256
3466 | 291.6667 | 567.7796 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05132
3467 | 586.1111 | 1140.9667 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0502
3468 | 525 | 1022.0034 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04924
3469 | 658.3333 | 1281.5598 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04801
3470 | 594.4444 | 1157.189 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04642
3471 | 561.1111 | 1092.2999 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04635
3472 | 369.4444 | 719.1876 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04708
3473 | 375 | 730.0024 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04919
3474 | 208.3333 | 405.5569 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05248
3475 | 47.2222 | 91.9262 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05612
3476 | 2.7778 | 5.4074 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05947
3477 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05971
3478 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05947
3479 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05558
3480 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0514
3481 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04804
3482 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04437
3483 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04281
3484 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03801
3485 | 33.3333 | 64.8891 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03315
3486 | 122.2222 | 237.9267 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.02963
3487 | 250 | 486.6683 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03365
3488 | 355.5556 | 692.1504 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03958
3489 | 505.5556 | 984.1514 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0433
3490 | 400 | 778.6692 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.03369
3491 | 441.6667 | 859.7806 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0433
3492 | 497.2222 | 967.9291 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0441
3493 | 505.5556 | 984.1514 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0424
3494 | 358.3333 | 697.5579 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0304
3495 | 336.1111 | 654.2985 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.02
3496 | 280.5556 | 546.1499 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.01967
3497 | 169.4444 | 329.8529 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04674
3498 | 77.7778 | 151.4079 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04801
3499 | 25 | 48.6668 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05163
3500 | 2.7778 | 5.4074 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05216
3501 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05159
3502 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05137
3503 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04745
3504 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04823
3505 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0424
3506 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04063
3507 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03825
3508 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03851
3509 | 77.7778 | 151.4079 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04376
3510 | 166.6667 | 324.4455 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05165
3511 | 402.7778 | 784.0767 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06117
3512 | 505.5556 | 984.1514 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05835
3513 | 677.7778 | 1319.4118 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05737
3514 | 683.3333 | 1330.2266 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05474
3515 | 516.6667 | 1005.7811 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05427
3516 | 336.1111 | 654.2985 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05303
3517 | 397.2222 | 773.2618 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.053
3518 | 263.8889 | 513.7054 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05143
3519 | 263.8889 | 513.7054 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05089
3520 | 119.4444 | 232.5193 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05046
3521 | 233.3333 | 454.2237 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05227
3522 | 183.3333 | 356.8901 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05548
3523 | 80.5556 | 156.8153 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06039
3524 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.063
3525 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0607
3526 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05779
3527 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05364
3528 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04907
3529 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0481
3530 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04771
3531 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04829
3532 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04812
3533 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04945
3534 | 27.7778 | 54.0743 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06123
3535 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06548
3536 | 72.2222 | 140.5931 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07183
3537 | 111.1111 | 216.297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07271
3538 | 122.2222 | 237.9267 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06566
3539 | 183.3333 | 356.8901 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06308
3540 | 494.4444 | 962.5217 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05995
3541 | 627.7778 | 1222.0781 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0599
3542 | 180.5556 | 351.4826 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05521
3543 | 627.7778 | 1222.0781 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05465
3544 | 372.2222 | 724.595 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05467
3545 | 377.7778 | 735.4098 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05717
3546 | 136.1111 | 264.9638 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05729
3547 | 100 | 194.6673 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05764
3548 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0581
3549 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05679
3550 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05377
3551 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04907
3552 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0494
3553 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04807
3554 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04557
3555 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0458
3556 | 13.8889 | 27.0371 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04788
3557 | 105.5556 | 205.4822 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0481
3558 | 222.2222 | 432.594 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05605
3559 | 400 | 778.6692 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06267
3560 | 558.3333 | 1086.8925 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06562
3561 | 713.8889 | 1389.7083 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0628
3562 | 797.2222 | 1551.931 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06097
3563 | 875 | 1703.3389 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05965
3564 | 897.2222 | 1746.5983 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05589
3565 | 875 | 1703.3389 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0549
3566 | 786.1111 | 1530.3013 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05492
3567 | 708.3333 | 1378.8934 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05329
3568 | 527.7778 | 1027.4108 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05515
3569 | 369.4444 | 719.1876 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06024
3570 | 194.4444 | 378.5198 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06463
3571 | 72.2222 | 140.5931 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06689
3572 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.067
3573 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06213
3574 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05577
3575 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04955
3576 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0471
3577 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0443
3578 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04571
3579 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04176
3580 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03836
3581 | 8.3333 | 16.2223 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03517
3582 | 27.7778 | 54.0743 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03989
3583 | 58.3333 | 113.5559 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04638
3584 | 105.5556 | 205.4822 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04638
3585 | 111.1111 | 216.297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04811
3586 | 158.3333 | 308.2232 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05107
3587 | 213.8889 | 416.3717 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05104
3588 | 238.8889 | 465.0386 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05151
3589 | 372.2222 | 724.595 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05051
3590 | 430.5556 | 838.1509 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04984
3591 | 411.1111 | 800.2989 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04638
3592 | 297.2222 | 578.5945 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0449
3593 | 152.7778 | 297.4084 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0441
3594 | 72.2222 | 140.5931 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04949
3595 | 25 | 48.6668 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05117
3596 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05202
3597 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05301
3598 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05534
3599 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05169
3600 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04702
3601 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04449
3602 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04338
3603 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0436
3604 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04407
3605 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04407
3606 | 113.8889 | 221.7044 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05
3607 | 169.4444 | 329.8529 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05605
3608 | 386.1111 | 751.6321 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05649
3609 | 508.3333 | 989.5588 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05478
3610 | 694.4444 | 1351.8563 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.052
3611 | 516.6667 | 1005.7811 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05063
3612 | 627.7778 | 1222.0781 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04917
3613 | 533.3333 | 1038.2256 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04551
3614 | 575 | 1119.337 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.045
3615 | 380.5556 | 740.8173 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04414
3616 | 441.6667 | 859.7806 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04851
3617 | 375 | 730.0024 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05204
3618 | 216.6667 | 421.7792 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0556
3619 | 69.4444 | 135.1856 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0608
3620 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06226
3621 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06019
3622 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05898
3623 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.055
3624 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04863
3625 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04603
3626 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04323
3627 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04262
3628 | 8.3333 | 16.2223 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04229
3629 | 83.3333 | 162.2228 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.042
3630 | 219.4444 | 427.1866 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0438
3631 | 347.2222 | 675.9282 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04651
3632 | 486.1111 | 946.2994 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04716
3633 | 633.3333 | 1232.893 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04969
3634 | 730.5556 | 1422.1528 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04883
3635 | 788.8889 | 1535.7088 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04774
3636 | 775 | 1508.6716 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04705
3637 | 775 | 1508.6716 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.045
3638 | 727.7778 | 1416.7454 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0449
3639 | 644.4444 | 1254.5227 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0445
3640 | 525 | 1022.0034 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04257
3641 | 308.3333 | 600.2242 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04409
3642 | 163.8889 | 319.0381 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05187
3643 | 94.4444 | 183.8525 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05515
3644 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0568
3645 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05594
3646 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05536
3647 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0526
3648 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04349
3649 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04399
3650 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04652
3651 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04788
3652 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0425
3653 | 86.1111 | 167.6302 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03952
3654 | 222.2222 | 432.594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03898
3655 | 352.7778 | 686.743 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03774
3656 | 480.5556 | 935.4846 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0425
3657 | 611.1111 | 1189.6336 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04354
3658 | 738.8889 | 1438.3751 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.02676
3659 | 805.5556 | 1568.1533 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0269
3660 | 830.5556 | 1616.8201 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.02391
3661 | 794.4444 | 1546.5236 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0185
3662 | 694.4444 | 1351.8563 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.00598
3663 | 544.4444 | 1059.8553 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.01452
3664 | 416.6667 | 811.1138 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0185
3665 | 330.5556 | 643.4836 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04527
3666 | 244.4444 | 475.8534 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04674
3667 | 97.2222 | 189.2599 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05241
3668 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05313
3669 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05214
3670 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05212
3671 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04485
3672 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0418
3673 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.03851
3674 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.03578
3675 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03484
3676 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.03433
3677 | 61.1111 | 118.9634 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.03887
3678 | 138.8889 | 270.3713 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05422
3679 | 275 | 535.3351 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05964
3680 | 361.1111 | 702.9653 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06002
3681 | 450 | 876.0029 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05681
3682 | 416.6667 | 811.1138 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05436
3683 | 327.7778 | 638.0762 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05271
3684 | 333.3333 | 648.891 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05125
3685 | 297.2222 | 578.5945 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05046
3686 | 288.8889 | 562.3722 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05023
3687 | 133.3333 | 259.5564 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05068
3688 | 125 | 243.3341 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05069
3689 | 238.8889 | 465.0386 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0571
3690 | 75 | 146.0005 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06042
3691 | 36.1111 | 70.2965 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0655
3692 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06398
3693 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06312
3694 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06096
3695 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0564
3696 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04974
3697 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04799
3698 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04686
3699 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04599
3700 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04723
3701 | 63.8889 | 124.3708 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04829
3702 | 208.3333 | 405.5569 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.057
3703 | 358.3333 | 697.5579 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0569
3704 | 488.8889 | 951.7068 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0697
3705 | 663.8889 | 1292.3746 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06193
3706 | 763.8889 | 1487.0419 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05724
3707 | 830.5556 | 1616.8201 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.056
3708 | 536.1111 | 1043.6331 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05256
3709 | 363.8889 | 708.3727 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0515
3710 | 550 | 1070.6702 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05019
3711 | 472.2222 | 919.2623 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04947
3712 | 394.4444 | 767.8544 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05165
3713 | 313.8889 | 611.0391 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05686
3714 | 222.2222 | 432.594 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06013
3715 | 41.6667 | 81.1114 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06117
3716 | 8.3333 | 16.2223 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05972
3717 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05328
3718 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04883
3719 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04301
3720 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04248
3721 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04106
3722 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03955
3723 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03954
3724 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04031
3725 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04253
3726 | 44.4444 | 86.5188 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05166
3727 | 266.6667 | 519.1128 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05927
3728 | 288.8889 | 562.3722 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05999
3729 | 233.3333 | 454.2237 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05897
3730 | 430.5556 | 838.1509 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05638
3731 | 450 | 876.0029 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05546
3732 | 416.6667 | 811.1138 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05385
3733 | 583.3333 | 1135.5593 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05132
3734 | 638.8889 | 1243.7078 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05119
3735 | 566.6667 | 1103.1147 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05301
3736 | 508.3333 | 989.5588 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.054
3737 | 313.8889 | 611.0391 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05837
3738 | 227.7778 | 443.4089 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06328
3739 | 108.3333 | 210.8896 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07152
3740 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06441
3741 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05822
3742 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05499
3743 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04709
3744 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0435
3745 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0415
3746 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03964
3747 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03903
3748 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03906
3749 | 13.8889 | 27.0371 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04254
3750 | 36.1111 | 70.2965 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04716
3751 | 97.2222 | 189.2599 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05573
3752 | 111.1111 | 216.297 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05791
3753 | 166.6667 | 324.4455 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05493
3754 | 222.2222 | 432.594 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04911
3755 | 277.7778 | 540.7425 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04862
3756 | 277.7778 | 540.7425 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04731
3757 | 388.8889 | 757.0395 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.047
3758 | 288.8889 | 562.3722 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.047
3759 | 327.7778 | 638.0762 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04753
3760 | 244.4444 | 475.8534 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04858
3761 | 419.4444 | 816.5212 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05076
3762 | 169.4444 | 329.8529 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05775
3763 | 116.6667 | 227.1119 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06662
3764 | 16.6667 | 32.4446 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07343
3765 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0696
3766 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06266
3767 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0564
3768 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05538
3769 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04905
3770 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04746
3771 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04814
3772 | 19.4444 | 37.852 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04709
3773 | 88.8889 | 173.0376 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04741
3774 | 208.3333 | 405.5569 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05112
3775 | 397.2222 | 773.2618 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05804
3776 | 433.3333 | 843.5583 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06617
3777 | 547.2222 | 1065.2628 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06082
3778 | 752.7778 | 1465.4122 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05221
3779 | 811.1111 | 1578.9682 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04839
3780 | 752.7778 | 1465.4122 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04509
3781 | 855.5556 | 1665.487 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0427
3782 | 752.7778 | 1465.4122 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04207
3783 | 333.3333 | 648.891 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04221
3784 | 69.4444 | 135.1856 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04357
3785 | 83.3333 | 162.2228 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04627
3786 | 33.3333 | 64.8891 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05399
3787 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05628
3788 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05507
3789 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04702
3790 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04504
3791 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0438
3792 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0576
3793 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05
3794 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0421
3795 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0431
3796 | 2.7778 | 5.4074 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0421
3797 | 11.1111 | 21.6297 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0405
3798 | 36.1111 | 70.2965 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0385
3799 | 58.3333 | 113.5559 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0421
3800 | 75 | 146.0005 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0431
3801 | 69.4444 | 135.1856 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0449
3802 | 58.3333 | 113.5559 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0424
3803 | 166.6667 | 324.4455 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0412
3804 | 288.8889 | 562.3722 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0376
3805 | 180.5556 | 351.4826 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0382
3806 | 94.4444 | 183.8525 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0351
3807 | 147.2222 | 286.5935 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0315
3808 | 391.6667 | 762.447 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.031
3809 | 308.3333 | 600.2242 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0413
3810 | 166.6667 | 324.4455 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0417
3811 | 100 | 194.6673 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0408
3812 | 16.6667 | 32.4446 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0499
3813 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.054
3814 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.063
3815 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.056
3816 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0427
3817 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04824
3818 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05143
3819 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05309
3820 | 16.6667 | 32.4446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.045
3821 | 97.2222 | 189.2599 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0427
3822 | 188.8889 | 367.7049 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03435
3823 | 291.6667 | 567.7796 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04
3824 | 444.4444 | 865.188 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04157
3825 | 586.1111 | 1140.9667 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04529
3826 | 669.4444 | 1303.1895 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0451
3827 | 700 | 1362.6712 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04266
3828 | 850 | 1654.6721 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0449
3829 | 769.4444 | 1497.8568 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0384
3830 | 691.6667 | 1346.4489 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03347
3831 | 486.1111 | 946.2994 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.03294
3832 | 269.4444 | 524.5202 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04349
3833 | 125 | 243.3341 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05314
3834 | 41.6667 | 81.1114 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05881
3835 | 13.8889 | 27.0371 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06377
3836 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0731
3837 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07211
3838 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05649
3839 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0506
3840 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04832
3841 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04384
3842 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04278
3843 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.042
3844 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04201
3845 | 69.4444 | 135.1856 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04083
3846 | 197.2222 | 383.9272 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04184
3847 | 308.3333 | 600.2242 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04503
3848 | 411.1111 | 800.2989 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04854
3849 | 661.1111 | 1286.9672 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04592
3850 | 744.4444 | 1449.19 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04506
3851 | 822.2222 | 1600.5979 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04455
3852 | 802.7778 | 1562.7459 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04369
3853 | 813.8889 | 1584.3756 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04303
3854 | 486.1111 | 946.2994 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0423
3855 | 472.2222 | 919.2623 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04245
3856 | 244.4444 | 475.8534 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04308
3857 | 294.4444 | 573.1871 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04619
3858 | 91.6667 | 178.445 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05152
3859 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.055
3860 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05604
3861 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0549
3862 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.055
3863 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05006
3864 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05865
3865 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04421
3866 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04328
3867 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04214
3868 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04153
3869 | 19.4444 | 37.852 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04413
3870 | 19.4444 | 37.852 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05732
3871 | 100 | 194.6673 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06207
3872 | 136.1111 | 264.9638 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06741
3873 | 250 | 486.6683 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06503
3874 | 411.1111 | 800.2989 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06722
3875 | 755.5556 | 1470.8197 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06837
3876 | 727.7778 | 1416.7454 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06238
3877 | 691.6667 | 1346.4489 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06072
3878 | 697.2222 | 1357.2637 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06
3879 | 552.7778 | 1076.0776 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06119
3880 | 502.7778 | 978.744 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06412
3881 | 286.1111 | 556.9648 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07071
3882 | 158.3333 | 308.2232 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07438
3883 | 44.4444 | 86.5188 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07493
3884 | 13.8889 | 27.0371 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.069
3885 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06625
3886 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0611
3887 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05593
3888 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05269
3889 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05065
3890 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04843
3891 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04804
3892 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04764
3893 | 44.4444 | 86.5188 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04974
3894 | 150 | 292.001 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06166
3895 | 291.6667 | 567.7796 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07072
3896 | 350 | 681.3356 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07761
3897 | 383.3333 | 746.2247 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07286
3898 | 69.4444 | 135.1856 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06731
3899 | 47.2222 | 91.9262 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06554
3900 | 52.7778 | 102.7411 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06098
3901 | 44.4444 | 86.5188 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05791
3902 | 197.2222 | 383.9272 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05405
3903 | 397.2222 | 773.2618 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04909
3904 | 494.4444 | 962.5217 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0499
3905 | 355.5556 | 692.1504 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05714
3906 | 202.7778 | 394.742 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0635
3907 | 125 | 243.3341 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06644
3908 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06556
3909 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0627
3910 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05964
3911 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0537
3912 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04478
3913 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04334
3914 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04232
3915 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04235
3916 | 25 | 48.6668 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04245
3917 | 119.4444 | 232.5193 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0441
3918 | 216.6667 | 421.7792 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05156
3919 | 319.4444 | 621.8539 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06032
3920 | 352.7778 | 686.743 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05949
3921 | 547.2222 | 1065.2628 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05142
3922 | 577.7778 | 1124.7444 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0479
3923 | 722.2222 | 1405.9306 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04518
3924 | 525 | 1022.0034 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04342
3925 | 580.5556 | 1130.1519 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04366
3926 | 602.7778 | 1173.4113 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04385
3927 | 427.7778 | 832.7435 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04495
3928 | 205.5556 | 400.1495 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04611
3929 | 302.7778 | 589.4093 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04868
3930 | 138.8889 | 270.3713 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06371
3931 | 44.4444 | 86.5188 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07706
3932 | 13.8889 | 27.0371 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.08787
3933 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07528
3934 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06256
3935 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05603
3936 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04844
3937 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04478
3938 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04322
3939 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04298
3940 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04299
3941 | 105.5556 | 205.4822 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04455
3942 | 152.7778 | 297.4084 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05426
3943 | 252.7778 | 492.0757 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06687
3944 | 269.4444 | 524.5202 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07368
3945 | 380.5556 | 740.8173 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06404
3946 | 177.7778 | 346.0752 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05791
3947 | 208.3333 | 405.5569 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05601
3948 | 408.3333 | 794.8915 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0499
3949 | 625 | 1216.6707 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04802
3950 | 680.5556 | 1324.8192 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04828
3951 | 519.4444 | 1011.1885 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04906
3952 | 333.3333 | 648.891 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05134
3953 | 213.8889 | 416.3717 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06279
3954 | 169.4444 | 329.8529 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07182
3955 | 100 | 194.6673 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07776
3956 | 27.7778 | 54.0743 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07236
3957 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06407
3958 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05849
3959 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05294
3960 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04829
3961 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04647
3962 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04492
3963 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04326
3964 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04248
3965 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04098
3966 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04168
3967 | 47.2222 | 91.9262 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04499
3968 | 75 | 146.0005 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.048
3969 | 283.3333 | 551.5574 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.055
3970 | 202.7778 | 394.742 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0545
3971 | 488.8889 | 951.7068 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0628
3972 | 555.5556 | 1081.485 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05566
3973 | 825 | 1606.0053 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.041
3974 | 619.4444 | 1205.8558 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.03931
3975 | 547.2222 | 1065.2628 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03942
3976 | 366.6667 | 713.7801 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03992
3977 | 311.1111 | 605.6316 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04737
3978 | 172.2222 | 335.2604 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05034
3979 | 102.7778 | 200.0747 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0551
3980 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06602
3981 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06519
3982 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05779
3983 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04931
3984 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04517
3985 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04343
3986 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04546
3987 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04285
3988 | 8.3333 | 16.2223 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0431
3989 | 69.4444 | 135.1856 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04279
3990 | 233.3333 | 454.2237 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04403
3991 | 405.5556 | 789.4841 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04841
3992 | 552.7778 | 1076.0776 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0476
3993 | 661.1111 | 1286.9672 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04655
3994 | 627.7778 | 1222.0781 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04335
3995 | 686.1111 | 1335.634 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04298
3996 | 883.3333 | 1719.5612 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04217
3997 | 516.6667 | 1005.7811 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.03892
3998 | 330.5556 | 643.4836 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04093
3999 | 533.3333 | 1038.2256 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04251
4000 | 466.6667 | 908.4474 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04448
4001 | 130.5556 | 254.149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0492
4002 | 213.8889 | 416.3717 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05275
4003 | 50 | 97.3337 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05944
4004 | 16.6667 | 32.4446 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06426
4005 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06715
4006 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0628
4007 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05591
4008 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04806
4009 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04528
4010 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0455
4011 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04546
4012 | 16.6667 | 32.4446 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04452
4013 | 113.8889 | 221.7044 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04569
4014 | 250 | 486.6683 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05922
4015 | 405.5556 | 789.4841 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0658
4016 | 563.8889 | 1097.7073 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06402
4017 | 691.6667 | 1346.4489 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05419
4018 | 788.8889 | 1535.7088 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04964
4019 | 811.1111 | 1578.9682 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0487
4020 | 838.8889 | 1633.0424 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04899
4021 | 708.3333 | 1378.8934 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05016
4022 | 733.3333 | 1427.5603 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04976
4023 | 719.4444 | 1400.5231 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0505
4024 | 505.5556 | 984.1514 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05417
4025 | 300 | 584.0019 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05997
4026 | 141.6667 | 275.7787 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07055
4027 | 83.3333 | 162.2228 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0851
4028 | 13.8889 | 27.0371 | 0 | 0 | 0 | 0 | #DIV/0! | 0.08452
4029 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07324
4030 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06167
4031 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0541
4032 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04797
4033 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04785
4034 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04671
4035 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04787
4036 | 11.1111 | 21.6297 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0476
4037 | 63.8889 | 124.3708 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04703
4038 | 177.7778 | 346.0752 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05516
4039 | 272.2222 | 529.9277 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06674
4040 | 438.8889 | 854.3732 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06475
4041 | 550 | 1070.6702 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06011
4042 | 588.8889 | 1146.3741 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05492
4043 | 688.8889 | 1341.0415 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0539
4044 | 602.7778 | 1173.4113 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05212
4045 | 552.7778 | 1076.0776 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0511
4046 | 477.7778 | 930.0771 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05106
4047 | 338.8889 | 659.7059 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05337
4048 | 283.3333 | 551.5574 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05792
4049 | 230.5556 | 448.8163 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06874
4050 | 147.2222 | 286.5935 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0738
4051 | 91.6667 | 178.445 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08116
4052 | 11.1111 | 21.6297 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08212
4053 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0682
4054 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.062
4055 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05208
4056 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04912
4057 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05032
4058 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05006
4059 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05039
4060 | 13.8889 | 27.0371 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05001
4061 | 113.8889 | 221.7044 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04704
4062 | 230.5556 | 448.8163 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05596
4063 | 341.6667 | 665.1133 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0673
4064 | 413.8889 | 805.7064 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07342
4065 | 394.4444 | 767.8544 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06383
4066 | 94.4444 | 183.8525 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05798
4067 | 383.3333 | 746.2247 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05581
4068 | 605.5556 | 1178.8187 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05201
4069 | 744.4444 | 1449.19 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05193
4070 | 313.8889 | 611.0391 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05129
4071 | 305.5556 | 594.8168 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05109
4072 | 447.2222 | 870.5955 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04991
4073 | 216.6667 | 421.7792 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05678
4074 | 33.3333 | 64.8891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06494
4075 | 13.8889 | 27.0371 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06817
4076 | 13.8889 | 27.0371 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06607
4077 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06064
4078 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05508
4079 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04999
4080 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0458
4081 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04623
4082 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04508
4083 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.045
4084 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0467
4085 | 19.4444 | 37.852 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04503
4086 | 83.3333 | 162.2228 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04698
4087 | 111.1111 | 216.297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05109
4088 | 213.8889 | 416.3717 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05676
4089 | 300 | 584.0019 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06507
4090 | 450 | 876.0029 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0599
4091 | 702.7778 | 1368.0786 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05429
4092 | 725 | 1411.338 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05108
4093 | 772.2222 | 1503.2642 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04909
4094 | 661.1111 | 1286.9672 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04817
4095 | 413.8889 | 805.7064 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04893
4096 | 477.7778 | 930.0771 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04854
4097 | 383.3333 | 746.2247 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05171
4098 | 247.2222 | 481.2608 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05462
4099 | 105.5556 | 205.4822 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05982
4100 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06696
4101 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.065
4102 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06152
4103 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05428
4104 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0493
4105 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04703
4106 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04652
4107 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04681
4108 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04704
4109 | 108.3333 | 210.8896 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04819
4110 | 236.1111 | 459.6311 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05451
4111 | 369.4444 | 719.1876 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06038
4112 | 427.7778 | 832.7435 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06209
4113 | 552.7778 | 1076.0776 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05941
4114 | 677.7778 | 1319.4118 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05893
4115 | 594.4444 | 1157.189 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05604
4116 | 725 | 1411.338 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05121
4117 | 461.1111 | 897.6326 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04853
4118 | 380.5556 | 740.8173 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04741
4119 | 372.2222 | 724.595 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04726
4120 | 408.3333 | 794.8915 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04722
4121 | 316.6667 | 616.4465 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04998
4122 | 255.5556 | 497.4831 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05579
4123 | 105.5556 | 205.4822 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0595
4124 | 30.5556 | 59.4817 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06284
4125 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06491
4126 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05926
4127 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05195
4128 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05058
4129 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04684
4130 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04444
4131 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04428
4132 | 16.6667 | 32.4446 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04398
4133 | 88.8889 | 173.0376 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04359
4134 | 150 | 292.001 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04448
4135 | 275 | 535.3351 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04736
4136 | 261.1111 | 508.298 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04946
4137 | 583.3333 | 1135.5593 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04686
4138 | 713.8889 | 1389.7083 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04592
4139 | 780.5556 | 1519.4865 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04479
4140 | 772.2222 | 1503.2642 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04497
4141 | 888.8889 | 1730.3761 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04355
4142 | 516.6667 | 1005.7811 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04318
4143 | 552.7778 | 1076.0776 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04321
4144 | 461.1111 | 897.6326 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04441
4145 | 388.8889 | 757.0395 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04737
4146 | 263.8889 | 513.7054 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04937
4147 | 119.4444 | 232.5193 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05291
4148 | 27.7778 | 54.0743 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05038
4149 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04763
4150 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04903
4151 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04458
4152 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0431
4153 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04194
4154 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04662
4155 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05139
4156 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05262
4157 | 80.5556 | 156.8153 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04712
4158 | 238.8889 | 465.0386 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04653
4159 | 383.3333 | 746.2247 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0498
4160 | 444.4444 | 865.188 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04764
4161 | 552.7778 | 1076.0776 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04759
4162 | 741.6667 | 1443.7825 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0398
4163 | 752.7778 | 1465.4122 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0398
4164 | 638.8889 | 1243.7078 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.034
4165 | 616.6667 | 1200.4484 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0299
4166 | 516.6667 | 1005.7811 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03186
4167 | 625 | 1216.6707 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03755
4168 | 575 | 1119.337 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03959
4169 | 358.3333 | 697.5579 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04713
4170 | 230.5556 | 448.8163 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04744
4171 | 80.5556 | 156.8153 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05618
4172 | 19.4444 | 37.852 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06287
4173 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04795
4174 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04919
4175 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0494
4176 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04197
4177 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04068
4178 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.039
4179 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03971
4180 | 16.6667 | 32.4446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04285
4181 | 100 | 194.6673 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04103
4182 | 155.5556 | 302.8158 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05027
4183 | 319.4444 | 621.8539 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06318
4184 | 438.8889 | 854.3732 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05778
4185 | 538.8889 | 1049.0405 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05124
4186 | 708.3333 | 1378.8934 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04767
4187 | 713.8889 | 1389.7083 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04774
4188 | 636.1111 | 1238.3004 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04956
4189 | 597.2222 | 1162.5964 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04913
4190 | 600 | 1168.0038 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04891
4191 | 533.3333 | 1038.2256 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04828
4192 | 419.4444 | 816.5212 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04887
4193 | 305.5556 | 594.8168 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05095
4194 | 152.7778 | 297.4084 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06309
4195 | 77.7778 | 151.4079 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0724
4196 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07343
4197 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05947
4198 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0493
4199 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.044
4200 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04571
4201 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0406
4202 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03948
4203 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04069
4204 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.042
4205 | 55.5556 | 108.1485 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04409
4206 | 166.6667 | 324.4455 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04811
4207 | 261.1111 | 508.298 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05891
4208 | 452.7778 | 881.4103 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06418
4209 | 466.6667 | 908.4474 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05596
4210 | 705.5556 | 1373.486 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05277
4211 | 719.4444 | 1400.5231 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05145
4212 | 616.6667 | 1200.4484 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05007
4213 | 605.5556 | 1178.8187 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04992
4214 | 586.1111 | 1140.9667 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05002
4215 | 516.6667 | 1005.7811 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04991
4216 | 447.2222 | 870.5955 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05193
4217 | 336.1111 | 654.2985 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07088
4218 | 197.2222 | 383.9272 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0865
4219 | 108.3333 | 210.8896 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09862
4220 | 19.4444 | 37.852 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.095
4221 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08174
4222 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0615
4223 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0524
4224 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05495
4225 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04896
4226 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0498
4227 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05081
4228 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04936
4229 | 22.2222 | 43.2594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0493
4230 | 105.5556 | 205.4822 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05888
4231 | 350 | 681.3356 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07508
4232 | 436.1111 | 848.9658 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07444
4233 | 541.6667 | 1054.4479 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06683
4234 | 711.1111 | 1384.3009 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05365
4235 | 686.1111 | 1335.634 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0517
4236 | 527.7778 | 1027.4108 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05008
4237 | 580.5556 | 1130.1519 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04809
4238 | 583.3333 | 1135.5593 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04688
4239 | 544.4444 | 1059.8553 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04589
4240 | 519.4444 | 1011.1885 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04647
4241 | 422.2222 | 821.9286 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04927
4242 | 272.2222 | 529.9277 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05398
4243 | 133.3333 | 259.5564 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06492
4244 | 30.5556 | 59.4817 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0651
4245 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05795
4246 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0517
4247 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04545
4248 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.043
4249 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.042
4250 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04231
4251 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04322
4252 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04442
4253 | 50 | 97.3337 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04478
4254 | 169.4444 | 329.8529 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05006
4255 | 408.3333 | 794.8915 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05829
4256 | 427.7778 | 832.7435 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0571
4257 | 541.6667 | 1054.4479 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0515
4258 | 733.3333 | 1427.5603 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04956
4259 | 747.2222 | 1454.5974 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04947
4260 | 702.7778 | 1368.0786 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04697
4261 | 683.3333 | 1330.2266 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04695
4262 | 636.1111 | 1238.3004 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04591
4263 | 541.6667 | 1054.4479 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04631
4264 | 550 | 1070.6702 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04694
4265 | 447.2222 | 870.5955 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05098
4266 | 297.2222 | 578.5945 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0569
4267 | 144.4444 | 281.1861 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06911
4268 | 30.5556 | 59.4817 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06723
4269 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05902
4270 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05617
4271 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05058
4272 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04633
4273 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04646
4274 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04771
4275 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04838
4276 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04738
4277 | 30.5556 | 59.4817 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04758
4278 | 66.6667 | 129.7782 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0594
4279 | 130.5556 | 254.149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07251
4280 | 225 | 438.0014 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0752
4281 | 483.3333 | 940.892 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06382
4282 | 725 | 1411.338 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05899
4283 | 750 | 1460.0048 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05453
4284 | 677.7778 | 1319.4118 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05175
4285 | 677.7778 | 1319.4118 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04933
4286 | 641.6667 | 1249.1152 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04889
4287 | 566.6667 | 1103.1147 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04891
4288 | 547.2222 | 1065.2628 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0494
4289 | 452.7778 | 881.4103 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05404
4290 | 297.2222 | 578.5945 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06864
4291 | 147.2222 | 286.5935 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08063
4292 | 30.5556 | 59.4817 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08
4293 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06925
4294 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06354
4295 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05405
4296 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05024
4297 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04664
4298 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04526
4299 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04415
4300 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04458
4301 | 111.1111 | 216.297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04379
4302 | 252.7778 | 492.0757 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04516
4303 | 405.5556 | 789.4841 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04648
4304 | 477.7778 | 930.0771 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04511
4305 | 600 | 1168.0038 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04515
4306 | 769.4444 | 1497.8568 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04307
4307 | 811.1111 | 1578.9682 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04301
4308 | 747.2222 | 1454.5974 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04301
4309 | 730.5556 | 1422.1528 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04082
4310 | 705.5556 | 1373.486 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04006
4311 | 636.1111 | 1238.3004 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04019
4312 | 566.6667 | 1103.1147 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04139
4313 | 466.6667 | 908.4474 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04518
4314 | 300 | 584.0019 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.055
4315 | 144.4444 | 281.1861 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06746
4316 | 25 | 48.6668 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07123
4317 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06489
4318 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05603
4319 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05061
4320 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04541
4321 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0419
4322 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04239
4323 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03978
4324 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0346
4325 | 97.2222 | 189.2599 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.02516
4326 | 225 | 438.0014 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.02727
4327 | 358.3333 | 697.5579 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.02955
4328 | 447.2222 | 870.5955 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.03567
4329 | 572.2222 | 1113.9296 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.03224
4330 | 730.5556 | 1422.1528 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0324
4331 | 694.4444 | 1351.8563 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0351
4332 | 727.7778 | 1416.7454 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04805
4333 | 727.7778 | 1416.7454 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.03936
4334 | 572.2222 | 1113.9296 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03672
4335 | 386.1111 | 751.6321 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04084
4336 | 558.3333 | 1086.8925 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0375
4337 | 419.4444 | 816.5212 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03505
4338 | 291.6667 | 567.7796 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04383
4339 | 138.8889 | 270.3713 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05163
4340 | 27.7778 | 54.0743 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05294
4341 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05207
4342 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05819
4343 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05172
4344 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04398
4345 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04123
4346 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04002
4347 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03987
4348 | 11.1111 | 21.6297 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0409
4349 | 94.4444 | 183.8525 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04189
4350 | 225 | 438.0014 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0533
4351 | 355.5556 | 692.1504 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06655
4352 | 447.2222 | 870.5955 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06734
4353 | 502.7778 | 978.744 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05613
4354 | 319.4444 | 621.8539 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05257
4355 | 697.2222 | 1357.2637 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04785
4356 | 650 | 1265.3375 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04446
4357 | 686.1111 | 1335.634 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04241
4358 | 688.8889 | 1341.0415 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04228
4359 | 630.5556 | 1227.4855 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.042
4360 | 391.6667 | 762.447 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0426
4361 | 361.1111 | 702.9653 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04341
4362 | 205.5556 | 400.1495 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04603
4363 | 63.8889 | 124.3708 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05149
4364 | 11.1111 | 21.6297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05132
4365 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04993
4366 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0539
4367 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04697
4368 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0439
4369 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04197
4370 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04048
4371 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.03975
4372 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03991
4373 | 105.5556 | 205.4822 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04199
4374 | 250 | 486.6683 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.046
4375 | 352.7778 | 686.743 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05112
4376 | 533.3333 | 1038.2256 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0511
4377 | 636.1111 | 1238.3004 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05494
4378 | 741.6667 | 1443.7825 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0565
4379 | 877.7778 | 1708.7464 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05648
4380 | 619.4444 | 1205.8558 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05598
4381 | 616.6667 | 1200.4484 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0551
4382 | 847.2222 | 1649.2647 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05326
4383 | 694.4444 | 1351.8563 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.048
4384 | 513.8889 | 1000.3737 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04496
4385 | 469.4444 | 913.8549 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04805
4386 | 286.1111 | 556.9648 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05302
4387 | 133.3333 | 259.5564 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.059
4388 | 27.7778 | 54.0743 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06742
4389 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06265
4390 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05714
4391 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05205
4392 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04594
4393 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04307
4394 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0426
4395 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04233
4396 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04293
4397 | 52.7778 | 102.7411 | 0 | 0 | 0 | 0 | #DIV/0! | 0.044
4398 | 191.6667 | 373.1123 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05322
4399 | 405.5556 | 789.4841 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0626
4400 | 427.7778 | 832.7435 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.063
4401 | 333.3333 | 648.891 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05253
4402 | 300 | 584.0019 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04868
4403 | 433.3333 | 843.5583 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0484
4404 | 569.4444 | 1108.5222 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04619
4405 | 580.5556 | 1130.1519 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04514
4406 | 588.8889 | 1146.3741 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0451
4407 | 605.5556 | 1178.8187 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04498
4408 | 336.1111 | 654.2985 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04508
4409 | 425 | 827.3361 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.048
4410 | 252.7778 | 492.0757 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05149
4411 | 130.5556 | 254.149 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05807
4412 | 25 | 48.6668 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06569
4413 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0564
4414 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05257
4415 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04841
4416 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04493
4417 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04383
4418 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04298
4419 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04389
4420 | 13.8889 | 27.0371 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04442
4421 | 80.5556 | 156.8153 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04571
4422 | 216.6667 | 421.7792 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0517
4423 | 386.1111 | 751.6321 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05931
4424 | 536.1111 | 1043.6331 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05472
4425 | 658.3333 | 1281.5598 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04977
4426 | 763.8889 | 1487.0419 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04688
4427 | 794.4444 | 1546.5236 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04589
4428 | 766.6667 | 1492.4494 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04497
4429 | 655.5556 | 1276.1524 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04465
4430 | 755.5556 | 1470.8197 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04453
4431 | 680.5556 | 1324.8192 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04485
4432 | 541.6667 | 1054.4479 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0448
4433 | 350 | 681.3356 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04798
4434 | 197.2222 | 383.9272 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05192
4435 | 86.1111 | 167.6302 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05858
4436 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05998
4437 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0549
4438 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05406
4439 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0499
4440 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0448
4441 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.044
4442 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0428
4443 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04264
4444 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0429
4445 | 44.4444 | 86.5188 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04408
4446 | 138.8889 | 270.3713 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04962
4447 | 283.3333 | 551.5574 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05789
4448 | 297.2222 | 578.5945 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06092
4449 | 511.1111 | 994.9662 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0584
4450 | 619.4444 | 1205.8558 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.053
4451 | 822.2222 | 1600.5979 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0516
4452 | 797.2222 | 1551.931 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04802
4453 | 663.8889 | 1292.3746 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04605
4454 | 775 | 1508.6716 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04468
4455 | 708.3333 | 1378.8934 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04423
4456 | 575 | 1119.337 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0454
4457 | 422.2222 | 821.9286 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04797
4458 | 258.3333 | 502.8905 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05035
4459 | 102.7778 | 200.0747 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05515
4460 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06086
4461 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06075
4462 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05707
4463 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05309
4464 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05297
4465 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0491
4466 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04599
4467 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04552
4468 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.045
4469 | 55.5556 | 108.1485 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04423
4470 | 94.4444 | 183.8525 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04421
4471 | 341.6667 | 665.1133 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04474
4472 | 327.7778 | 638.0762 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04605
4473 | 416.6667 | 811.1138 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04625
4474 | 394.4444 | 767.8544 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04568
4475 | 413.8889 | 805.7064 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04447
4476 | 300 | 584.0019 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04343
4477 | 236.1111 | 459.6311 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04307
4478 | 91.6667 | 178.445 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0427
4479 | 119.4444 | 232.5193 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04216
4480 | 138.8889 | 270.3713 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0427
4481 | 83.3333 | 162.2228 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04495
4482 | 44.4444 | 86.5188 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04573
4483 | 30.5556 | 59.4817 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0499
4484 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0549
4485 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0524
4486 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06451
4487 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.055
4488 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06234
4489 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05242
4490 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.044
4491 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03927
4492 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0391
4493 | 33.3333 | 64.8891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04021
4494 | 175 | 340.6678 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04146
4495 | 177.7778 | 346.0752 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0417
4496 | 191.6667 | 373.1123 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04278
4497 | 350 | 681.3356 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04393
4498 | 461.1111 | 897.6326 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04453
4499 | 561.1111 | 1092.2999 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.044
4500 | 533.3333 | 1038.2256 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04206
4501 | 544.4444 | 1059.8553 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04185
4502 | 494.4444 | 962.5217 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04
4503 | 155.5556 | 302.8158 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04112
4504 | 316.6667 | 616.4465 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0416
4505 | 177.7778 | 346.0752 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0441
4506 | 130.5556 | 254.149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0442
4507 | 47.2222 | 91.9262 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04647
4508 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04725
4509 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04806
4510 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05202
4511 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04802
4512 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04993
4513 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04511
4514 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04455
4515 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04528
4516 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04504
4517 | 36.1111 | 70.2965 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04502
4518 | 130.5556 | 254.149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04976
4519 | 216.6667 | 421.7792 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05406
4520 | 372.2222 | 724.595 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05499
4521 | 425 | 827.3361 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05359
4522 | 552.7778 | 1076.0776 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05229
4523 | 613.8889 | 1195.041 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05494
4524 | 594.4444 | 1157.189 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05368
4525 | 141.6667 | 275.7787 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05009
4526 | 108.3333 | 210.8896 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04848
4527 | 255.5556 | 497.4831 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04876
4528 | 244.4444 | 475.8534 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04947
4529 | 208.3333 | 405.5569 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04992
4530 | 100 | 194.6673 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.053
4531 | 55.5556 | 108.1485 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0579
4532 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05335
4533 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05293
4534 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05443
4535 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04963
4536 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04656
4537 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04519
4538 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04481
4539 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04448
4540 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04519
4541 | 100 | 194.6673 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04555
4542 | 216.6667 | 421.7792 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05116
4543 | 380.5556 | 740.8173 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05895
4544 | 552.7778 | 1076.0776 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05906
4545 | 572.2222 | 1113.9296 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05609
4546 | 602.7778 | 1173.4113 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05317
4547 | 611.1111 | 1189.6336 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05304
4548 | 625 | 1216.6707 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05206
4549 | 680.5556 | 1324.8192 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05015
4550 | 622.2222 | 1211.2633 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04975
4551 | 397.2222 | 773.2618 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04924
4552 | 425 | 827.3361 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04974
4553 | 363.8889 | 708.3727 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05171
4554 | 266.6667 | 519.1128 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05534
4555 | 127.7778 | 248.7416 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.062
4556 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0629
4557 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06099
4558 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05888
4559 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05166
4560 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05091
4561 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04854
4562 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04798
4563 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04792
4564 | 5.5556 | 10.8149 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0483
4565 | 41.6667 | 81.1114 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04838
4566 | 144.4444 | 281.1861 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0568
4567 | 302.7778 | 589.4093 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06445
4568 | 447.2222 | 870.5955 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0638
4569 | 577.7778 | 1124.7444 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05899
4570 | 627.7778 | 1222.0781 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05634
4571 | 263.8889 | 513.7054 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05713
4572 | 205.5556 | 400.1495 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05416
4573 | 222.2222 | 432.594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05232
4574 | 197.2222 | 383.9272 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05199
4575 | 166.6667 | 324.4455 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05205
4576 | 138.8889 | 270.3713 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05384
4577 | 158.3333 | 308.2232 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05908
4578 | 66.6667 | 129.7782 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06395
4579 | 27.7778 | 54.0743 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06819
4580 | 8.3333 | 16.2223 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06647
4581 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06306
4582 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06273
4583 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05765
4584 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05152
4585 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05099
4586 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05012
4587 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04988
4588 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04986
4589 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0509
4590 | 127.7778 | 248.7416 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05734
4591 | 172.2222 | 335.2604 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06577
4592 | 80.5556 | 156.8153 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06673
4593 | 127.7778 | 248.7416 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06784
4594 | 233.3333 | 454.2237 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06678
4595 | 430.5556 | 838.1509 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06899
4596 | 325 | 632.6688 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06642
4597 | 161.1111 | 313.6307 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.065
4598 | 247.2222 | 481.2608 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06165
4599 | 308.3333 | 600.2242 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06051
4600 | 386.1111 | 751.6321 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.061
4601 | 180.5556 | 351.4826 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06472
4602 | 225 | 438.0014 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06728
4603 | 83.3333 | 162.2228 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06834
4604 | 13.8889 | 27.0371 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06671
4605 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0639
4606 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06276
4607 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05517
4608 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05394
4609 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05289
4610 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05238
4611 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0522
4612 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05245
4613 | 38.8889 | 75.704 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05271
4614 | 116.6667 | 227.1119 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05797
4615 | 152.7778 | 297.4084 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06873
4616 | 286.1111 | 556.9648 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0733
4617 | 402.7778 | 784.0767 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07177
4618 | 427.7778 | 832.7435 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0674
4619 | 266.6667 | 519.1128 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06597
4620 | 25 | 48.6668 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05954
4621 | 230.5556 | 448.8163 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05673
4622 | 186.1111 | 362.2975 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05573
4623 | 188.8889 | 367.7049 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.053
4624 | 175 | 340.6678 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05364
4625 | 169.4444 | 329.8529 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05689
4626 | 127.7778 | 248.7416 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06581
4627 | 83.3333 | 162.2228 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06884
4628 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06881
4629 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06321
4630 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05888
4631 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05642
4632 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05605
4633 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05338
4634 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05187
4635 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05114
4636 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05208
4637 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05038
4638 | 41.6667 | 81.1114 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0511
4639 | 83.3333 | 162.2228 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05279
4640 | 169.4444 | 329.8529 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05346
4641 | 266.6667 | 519.1128 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05483
4642 | 244.4444 | 475.8534 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05482
4643 | 525 | 1022.0034 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.054
4644 | 508.3333 | 989.5588 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05287
4645 | 600 | 1168.0038 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0497
4646 | 525 | 1022.0034 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04894
4647 | 622.2222 | 1211.2633 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04851
4648 | 469.4444 | 913.8549 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04856
4649 | 241.6667 | 470.446 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04971
4650 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05191
4651 | 25 | 48.6668 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05298
4652 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05279
4653 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05272
4654 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0562
4655 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05317
4656 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05085
4657 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05004
4658 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04877
4659 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04769
4660 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04715
4661 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04714
4662 | 61.1111 | 118.9634 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04731
4663 | 152.7778 | 297.4084 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05141
4664 | 177.7778 | 346.0752 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05224
4665 | 216.6667 | 421.7792 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.053
4666 | 422.2222 | 821.9286 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05368
4667 | 455.5556 | 886.8177 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.055
4668 | 355.5556 | 692.1504 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05143
4669 | 327.7778 | 638.0762 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04904
4670 | 327.7778 | 638.0762 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04871
4671 | 380.5556 | 740.8173 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04704
4672 | 277.7778 | 540.7425 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04901
4673 | 188.8889 | 367.7049 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05297
4674 | 72.2222 | 140.5931 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05437
4675 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05596
4676 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05585
4677 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05472
4678 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05872
4679 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05411
4680 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0528
4681 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05147
4682 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05136
4683 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04991
4684 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04973
4685 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05175
4686 | 27.7778 | 54.0743 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0594
4687 | 91.6667 | 178.445 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06478
4688 | 186.1111 | 362.2975 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06506
4689 | 252.7778 | 492.0757 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06294
4690 | 316.6667 | 616.4465 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0612
4691 | 311.1111 | 605.6316 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0603
4692 | 500 | 973.3365 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.059
4693 | 483.3333 | 940.892 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.056
4694 | 300 | 584.0019 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05419
4695 | 411.1111 | 800.2989 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05403
4696 | 408.3333 | 794.8915 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05349
4697 | 191.6667 | 373.1123 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05402
4698 | 180.5556 | 351.4826 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05756
4699 | 38.8889 | 75.704 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06094
4700 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05908
4701 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05844
4702 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0596
4703 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05347
4704 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05304
4705 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05127
4706 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04993
4707 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04889
4708 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04813
4709 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05011
4710 | 41.6667 | 81.1114 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05421
4711 | 75 | 146.0005 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06195
4712 | 108.3333 | 210.8896 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06414
4713 | 125 | 243.3341 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06295
4714 | 150 | 292.001 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06213
4715 | 191.6667 | 373.1123 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06192
4716 | 238.8889 | 465.0386 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05707
4717 | 211.1111 | 410.9643 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0549
4718 | 222.2222 | 432.594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05446
4719 | 175 | 340.6678 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05404
4720 | 133.3333 | 259.5564 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0543
4721 | 94.4444 | 183.8525 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06038
4722 | 91.6667 | 178.445 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06381
4723 | 75 | 146.0005 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06764
4724 | 16.6667 | 32.4446 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06696
4725 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06419
4726 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.064
4727 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06019
4728 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05502
4729 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05387
4730 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05312
4731 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05228
4732 | 5.5556 | 10.8149 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0529
4733 | 33.3333 | 64.8891 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0541
4734 | 69.4444 | 135.1856 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05903
4735 | 191.6667 | 373.1123 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06878
4736 | 261.1111 | 508.298 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06968
4737 | 383.3333 | 746.2247 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06523
4738 | 644.4444 | 1254.5227 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06378
4739 | 780.5556 | 1519.4865 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0627
4740 | 880.5556 | 1714.1538 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06
4741 | 850 | 1654.6721 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05814
4742 | 591.6667 | 1151.7816 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05552
4743 | 372.2222 | 724.595 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05555
4744 | 511.1111 | 994.9662 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0566
4745 | 375 | 730.0024 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.063
4746 | 208.3333 | 405.5569 | 0 | 0 | 0 | 0 | #DIV/0! | 0.067
4747 | 116.6667 | 227.1119 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06901
4748 | 13.8889 | 27.0371 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06982
4749 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06888
4750 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06564
4751 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0609
4752 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05547
4753 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.054
4754 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05101
4755 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04933
4756 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04757
4757 | 50 | 97.3337 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04852
4758 | 108.3333 | 210.8896 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05619
4759 | 258.3333 | 502.8905 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06447
4760 | 444.4444 | 865.188 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06396
4761 | 572.2222 | 1113.9296 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0625
4762 | 647.2222 | 1259.9301 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05991
4763 | 675 | 1314.0043 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05849
4764 | 636.1111 | 1238.3004 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05541
4765 | 483.3333 | 940.892 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05425
4766 | 438.8889 | 854.3732 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05399
4767 | 433.3333 | 843.5583 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05472
4768 | 300 | 584.0019 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05421
4769 | 250 | 486.6683 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06272
4770 | 138.8889 | 270.3713 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06484
4771 | 41.6667 | 81.1114 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0695
4772 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06862
4773 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06416
4774 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06301
4775 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05873
4776 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05286
4777 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05087
4778 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05035
4779 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04807
4780 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04841
4781 | 41.6667 | 81.1114 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05
4782 | 111.1111 | 216.297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05777
4783 | 255.5556 | 497.4831 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06684
4784 | 397.2222 | 773.2618 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06733
4785 | 591.6667 | 1151.7816 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06443
4786 | 725 | 1411.338 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06286
4787 | 791.6667 | 1541.1162 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06203
4788 | 663.8889 | 1292.3746 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05901
4789 | 433.3333 | 843.5583 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05459
4790 | 655.5556 | 1276.1524 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0544
4791 | 275 | 535.3351 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0542
4792 | 377.7778 | 735.4098 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05436
4793 | 275 | 535.3351 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06121
4794 | 130.5556 | 254.149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06615
4795 | 36.1111 | 70.2965 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06656
4796 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06661
4797 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06416
4798 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0656
4799 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05992
4800 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05621
4801 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05308
4802 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05181
4803 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05054
4804 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04932
4805 | 33.3333 | 64.8891 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04898
4806 | 113.8889 | 221.7044 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04991
4807 | 241.6667 | 470.446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05079
4808 | 180.5556 | 351.4826 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05166
4809 | 419.4444 | 816.5212 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0518
4810 | 155.5556 | 302.8158 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05004
4811 | 66.6667 | 129.7782 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04791
4812 | 25 | 48.6668 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04663
4813 | 361.1111 | 702.9653 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04279
4814 | 555.5556 | 1081.485 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04298
4815 | 486.1111 | 946.2994 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04381
4816 | 486.1111 | 946.2994 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04683
4817 | 83.3333 | 162.2228 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05054
4818 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05189
4819 | 97.2222 | 189.2599 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05338
4820 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05253
4821 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05272
4822 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0542
4823 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05229
4824 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0495
4825 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0474
4826 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04698
4827 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04527
4828 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.045
4829 | 41.6667 | 81.1114 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04503
4830 | 152.7778 | 297.4084 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04488
4831 | 333.3333 | 648.891 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04567
4832 | 458.3333 | 892.2252 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04602
4833 | 625 | 1216.6707 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04601
4834 | 708.3333 | 1378.8934 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04469
4835 | 694.4444 | 1351.8563 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04513
4836 | 625 | 1216.6707 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04429
4837 | 666.6667 | 1297.7821 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04
4838 | 666.6667 | 1297.7821 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0412
4839 | 527.7778 | 1027.4108 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.03586
4840 | 416.6667 | 811.1138 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04304
4841 | 361.1111 | 702.9653 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04702
4842 | 208.3333 | 405.5569 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0509
4843 | 83.3333 | 162.2228 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05742
4844 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0586
4845 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05992
4846 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06162
4847 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.055
4848 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05247
4849 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05011
4850 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04814
4851 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04507
4852 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04315
4853 | 33.3333 | 64.8891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04598
4854 | 69.4444 | 135.1856 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05291
4855 | 166.6667 | 324.4455 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06195
4856 | 250 | 486.6683 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.063
4857 | 333.3333 | 648.891 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05897
4858 | 388.8889 | 757.0395 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05836
4859 | 566.6667 | 1103.1147 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05578
4860 | 488.8889 | 951.7068 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05027
4861 | 808.3333 | 1573.5607 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05092
4862 | 694.4444 | 1351.8563 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0509
4863 | 461.1111 | 897.6326 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05152
4864 | 391.6667 | 762.447 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05391
4865 | 319.4444 | 621.8539 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05998
4866 | 227.7778 | 443.4089 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06398
4867 | 100 | 194.6673 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06894
4868 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06834
4869 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06559
4870 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06687
4871 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05836
4872 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05361
4873 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05258
4874 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05198
4875 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05152
4876 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04959
4877 | 75 | 146.0005 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0527
4878 | 183.3333 | 356.8901 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06015
4879 | 338.8889 | 659.7059 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06304
4880 | 477.7778 | 930.0771 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06598
4881 | 622.2222 | 1211.2633 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06465
4882 | 736.1111 | 1432.9677 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0614
4883 | 811.1111 | 1578.9682 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05818
4884 | 841.6667 | 1638.4498 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05537
4885 | 827.7778 | 1611.4127 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05523
4886 | 769.4444 | 1497.8568 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05461
4887 | 669.4444 | 1303.1895 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05539
4888 | 533.3333 | 1038.2256 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05984
4889 | 383.3333 | 746.2247 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06797
4890 | 227.7778 | 443.4089 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07271
4891 | 88.8889 | 173.0376 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07782
4892 | 8.3333 | 16.2223 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0756
4893 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07434
4894 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07
4895 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0605
4896 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05725
4897 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05465
4898 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05348
4899 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05192
4900 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0516
4901 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05324
4902 | 166.6667 | 324.4455 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06055
4903 | 322.2222 | 627.2613 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0678
4904 | 500 | 973.3365 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07235
4905 | 616.6667 | 1200.4484 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07275
4906 | 725 | 1411.338 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06502
4907 | 800 | 1557.3385 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0574
4908 | 819.4444 | 1595.1904 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05455
4909 | 794.4444 | 1546.5236 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05551
4910 | 736.1111 | 1432.9677 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05491
4911 | 636.1111 | 1238.3004 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05795
4912 | 483.3333 | 940.892 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0634
4913 | 316.6667 | 616.4465 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07275
4914 | 194.4444 | 378.5198 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08313
4915 | 77.7778 | 151.4079 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08906
4916 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08316
4917 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07436
4918 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07281
4919 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0648
4920 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06062
4921 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05705
4922 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05458
4923 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05409
4924 | 2.7778 | 5.4074 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0539
4925 | 47.2222 | 91.9262 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05567
4926 | 158.3333 | 308.2232 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06191
4927 | 272.2222 | 529.9277 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07394
4928 | 422.2222 | 821.9286 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0703
4929 | 544.4444 | 1059.8553 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0717
4930 | 688.8889 | 1341.0415 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06778
4931 | 775 | 1508.6716 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06497
4932 | 780.5556 | 1519.4865 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06216
4933 | 722.2222 | 1405.9306 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0617
4934 | 719.4444 | 1400.5231 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05843
4935 | 622.2222 | 1211.2633 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06278
4936 | 519.4444 | 1011.1885 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06515
4937 | 361.1111 | 702.9653 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07185
4938 | 175 | 340.6678 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07705
4939 | 61.1111 | 118.9634 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08458
4940 | 5.5556 | 10.8149 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07686
4941 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07175
4942 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06574
4943 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05688
4944 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05361
4945 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05273
4946 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05219
4947 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05157
4948 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05137
4949 | 55.5556 | 108.1485 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05349
4950 | 158.3333 | 308.2232 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05808
4951 | 305.5556 | 594.8168 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06466
4952 | 450 | 876.0029 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06918
4953 | 597.2222 | 1162.5964 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0708
4954 | 700 | 1362.6712 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06861
4955 | 783.3333 | 1524.8939 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06331
4956 | 827.7778 | 1611.4127 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0574
4957 | 808.3333 | 1573.5607 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05775
4958 | 747.2222 | 1454.5974 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05623
4959 | 644.4444 | 1254.5227 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05513
4960 | 511.1111 | 994.9662 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05795
4961 | 361.1111 | 702.9653 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06415
4962 | 205.5556 | 400.1495 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06707
4963 | 47.2222 | 91.9262 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06862
4964 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06706
4965 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06397
4966 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06505
4967 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05495
4968 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05401
4969 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05259
4970 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05201
4971 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05104
4972 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0501
4973 | 47.2222 | 91.9262 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05028
4974 | 169.4444 | 329.8529 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0492
4975 | 252.7778 | 492.0757 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04993
4976 | 466.6667 | 908.4474 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05242
4977 | 622.2222 | 1211.2633 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05443
4978 | 741.6667 | 1443.7825 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05316
4979 | 750 | 1460.0048 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05189
4980 | 816.6667 | 1589.783 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0499
4981 | 808.3333 | 1573.5607 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04871
4982 | 788.8889 | 1535.7088 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04834
4983 | 644.4444 | 1254.5227 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04774
4984 | 400 | 778.6692 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04885
4985 | 308.3333 | 600.2242 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05062
4986 | 138.8889 | 270.3713 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05379
4987 | 66.6667 | 129.7782 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05394
4988 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05291
4989 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05119
4990 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05119
4991 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.049
4992 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04598
4993 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04502
4994 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0432
4995 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04127
4996 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0421
4997 | 33.3333 | 64.8891 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0418
4998 | 147.2222 | 286.5935 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0406
4999 | 288.8889 | 562.3722 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0431
5000 | 405.5556 | 789.4841 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04505
5001 | 533.3333 | 1038.2256 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04528
5002 | 700 | 1362.6712 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04706
5003 | 780.5556 | 1519.4865 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04761
5004 | 841.6667 | 1638.4498 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04668
5005 | 655.5556 | 1276.1524 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04432
5006 | 186.1111 | 362.2975 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04345
5007 | 133.3333 | 259.5564 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04345
5008 | 191.6667 | 373.1123 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04808
5009 | 236.1111 | 459.6311 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05569
5010 | 86.1111 | 167.6302 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05458
5011 | 25 | 48.6668 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05503
5012 | 2.7778 | 5.4074 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0553
5013 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05587
5014 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05646
5015 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05401
5016 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05077
5017 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04905
5018 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04765
5019 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04827
5020 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04869
5021 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05009
5022 | 100 | 194.6673 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05542
5023 | 297.2222 | 578.5945 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06137
5024 | 455.5556 | 886.8177 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06297
5025 | 600 | 1168.0038 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0649
5026 | 719.4444 | 1400.5231 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0614
5027 | 750 | 1460.0048 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06034
5028 | 913.8889 | 1779.0429 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05948
5029 | 472.2222 | 919.2623 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0565
5030 | 572.2222 | 1113.9296 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05414
5031 | 577.7778 | 1124.7444 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0534
5032 | 536.1111 | 1043.6331 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0556
5033 | 197.2222 | 383.9272 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06021
5034 | 155.5556 | 302.8158 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06437
5035 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.075
5036 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07475
5037 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06787
5038 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06438
5039 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05825
5040 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05
5041 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05212
5042 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04995
5043 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04882
5044 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04717
5045 | 44.4444 | 86.5188 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04673
5046 | 166.6667 | 324.4455 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06191
5047 | 313.8889 | 611.0391 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06827
5048 | 466.6667 | 908.4474 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06989
5049 | 602.7778 | 1173.4113 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06846
5050 | 713.8889 | 1389.7083 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06512
5051 | 783.3333 | 1524.8939 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06144
5052 | 794.4444 | 1546.5236 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0571
5053 | 750 | 1460.0048 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05624
5054 | 736.1111 | 1432.9677 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05541
5055 | 444.4444 | 865.188 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05528
5056 | 144.4444 | 281.1861 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05494
5057 | 138.8889 | 270.3713 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05704
5058 | 105.5556 | 205.4822 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06191
5059 | 58.3333 | 113.5559 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06741
5060 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06654
5061 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06193
5062 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05866
5063 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05366
5064 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05176
5065 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04784
5066 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04473
5067 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04219
5068 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04107
5069 | 38.8889 | 75.704 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04566
5070 | 158.3333 | 308.2232 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04999
5071 | 250 | 486.6683 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05956
5072 | 411.1111 | 800.2989 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06
5073 | 494.4444 | 962.5217 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05949
5074 | 477.7778 | 930.0771 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05624
5075 | 480.5556 | 935.4846 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05644
5076 | 558.3333 | 1086.8925 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05622
5077 | 291.6667 | 567.7796 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0545
5078 | 144.4444 | 281.1861 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05307
5079 | 191.6667 | 373.1123 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05301
5080 | 225 | 438.0014 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05279
5081 | 133.3333 | 259.5564 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.055
5082 | 97.2222 | 189.2599 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06702
5083 | 27.7778 | 54.0743 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06968
5084 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07687
5085 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06998
5086 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06415
5087 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0572
5088 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.054
5089 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05207
5090 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05125
5091 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04989
5092 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04886
5093 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05166
5094 | 61.1111 | 118.9634 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0558
5095 | 116.6667 | 227.1119 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05945
5096 | 236.1111 | 459.6311 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05909
5097 | 327.7778 | 638.0762 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05743
5098 | 425 | 827.3361 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05576
5099 | 425 | 827.3361 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05429
5100 | 244.4444 | 475.8534 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05348
5101 | 202.7778 | 394.742 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05378
5102 | 441.6667 | 859.7806 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05375
5103 | 433.3333 | 843.5583 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05478
5104 | 277.7778 | 540.7425 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05513
5105 | 238.8889 | 465.0386 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06033
5106 | 158.3333 | 308.2232 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07064
5107 | 61.1111 | 118.9634 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0785
5108 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0812
5109 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0736
5110 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06653
5111 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05954
5112 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.055
5113 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05389
5114 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05238
5115 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04918
5116 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04903
5117 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0513
5118 | 127.7778 | 248.7416 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05697
5119 | 308.3333 | 600.2242 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06036
5120 | 280.5556 | 546.1499 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06356
5121 | 261.1111 | 508.298 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06547
5122 | 255.5556 | 497.4831 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06295
5123 | 347.2222 | 675.9282 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05996
5124 | 177.7778 | 346.0752 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05731
5125 | 83.3333 | 162.2228 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05628
5126 | 72.2222 | 140.5931 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05508
5127 | 316.6667 | 616.4465 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05522
5128 | 530.5556 | 1032.8182 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05421
5129 | 269.4444 | 524.5202 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05779
5130 | 127.7778 | 248.7416 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06095
5131 | 86.1111 | 167.6302 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06451
5132 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06472
5133 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06217
5134 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05896
5135 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05612
5136 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05396
5137 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05194
5138 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05184
5139 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05153
5140 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0464
5141 | 19.4444 | 37.852 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05166
5142 | 36.1111 | 70.2965 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05061
5143 | 66.6667 | 129.7782 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0529
5144 | 116.6667 | 227.1119 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05272
5145 | 225 | 438.0014 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05351
5146 | 361.1111 | 702.9653 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05204
5147 | 200 | 389.3346 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05063
5148 | 469.4444 | 913.8549 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05004
5149 | 419.4444 | 816.5212 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04743
5150 | 363.8889 | 708.3727 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0451
5151 | 302.7778 | 589.4093 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0454
5152 | 100 | 194.6673 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04552
5153 | 155.5556 | 302.8158 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04909
5154 | 158.3333 | 308.2232 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05395
5155 | 33.3333 | 64.8891 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05608
5156 | 2.7778 | 5.4074 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05602
5157 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05658
5158 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05696
5159 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05447
5160 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05269
5161 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05
5162 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05041
5163 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05099
5164 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05087
5165 | 22.2222 | 43.2594 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04885
5166 | 72.2222 | 140.5931 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0512
5167 | 113.8889 | 221.7044 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0493
5168 | 250 | 486.6683 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04816
5169 | 416.6667 | 811.1138 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0461
5170 | 611.1111 | 1189.6336 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04326
5171 | 669.4444 | 1303.1895 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04336
5172 | 558.3333 | 1086.8925 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04406
5173 | 655.5556 | 1276.1524 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04412
5174 | 663.8889 | 1292.3746 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04402
5175 | 536.1111 | 1043.6331 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04329
5176 | 497.2222 | 967.9291 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04497
5177 | 327.7778 | 638.0762 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04923
5178 | 108.3333 | 210.8896 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05402
5179 | 44.4444 | 86.5188 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.057
5180 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05899
5181 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.062
5182 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06176
5183 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05724
5184 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05346
5185 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04826
5186 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04667
5187 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04444
5188 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0454
5189 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0478
5190 | 50 | 97.3337 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05549
5191 | 88.8889 | 173.0376 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0638
5192 | 136.1111 | 264.9638 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06296
5193 | 111.1111 | 216.297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06655
5194 | 497.2222 | 967.9291 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06691
5195 | 563.8889 | 1097.7073 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0643
5196 | 580.5556 | 1130.1519 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06022
5197 | 616.6667 | 1200.4484 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05958
5198 | 569.4444 | 1108.5222 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05429
5199 | 419.4444 | 816.5212 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05322
5200 | 350 | 681.3356 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05321
5201 | 183.3333 | 356.8901 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0547
5202 | 91.6667 | 178.445 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0574
5203 | 30.5556 | 59.4817 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06533
5204 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0684
5205 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0649
5206 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06
5207 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05487
5208 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05348
5209 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05192
5210 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04962
5211 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04869
5212 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0485
5213 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05168
5214 | 144.4444 | 281.1861 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05253
5215 | 252.7778 | 492.0757 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05858
5216 | 433.3333 | 843.5583 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06
5217 | 466.6667 | 908.4474 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.059
5218 | 591.6667 | 1151.7816 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05696
5219 | 625 | 1216.6707 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05637
5220 | 575 | 1119.337 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05502
5221 | 522.2222 | 1016.5959 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05387
5222 | 552.7778 | 1076.0776 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05397
5223 | 488.8889 | 951.7068 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05399
5224 | 352.7778 | 686.743 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05504
5225 | 227.7778 | 443.4089 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05884
5226 | 113.8889 | 221.7044 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06393
5227 | 58.3333 | 113.5559 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06938
5228 | 2.7778 | 5.4074 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06852
5229 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06769
5230 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06412
5231 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05597
5232 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05203
5233 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04817
5234 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04653
5235 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04592
5236 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04574
5237 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04787
5238 | 88.8889 | 173.0376 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05168
5239 | 255.5556 | 497.4831 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05777
5240 | 450 | 876.0029 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05971
5241 | 450 | 876.0029 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05998
5242 | 563.8889 | 1097.7073 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05893
5243 | 400 | 778.6692 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05931
5244 | 597.2222 | 1162.5964 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05716
5245 | 213.8889 | 416.3717 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05509
5246 | 597.2222 | 1162.5964 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05293
5247 | 533.3333 | 1038.2256 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05083
5248 | 463.8889 | 903.04 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05075
5249 | 338.8889 | 659.7059 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0545
5250 | 186.1111 | 362.2975 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0577
5251 | 55.5556 | 108.1485 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05815
5252 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05762
5253 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05694
5254 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05555
5255 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05264
5256 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04774
5257 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04634
5258 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04252
5259 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04185
5260 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04251
5261 | 16.6667 | 32.4446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04511
5262 | 100 | 194.6673 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04957
5263 | 172.2222 | 335.2604 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05494
5264 | 288.8889 | 562.3722 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05498
5265 | 316.6667 | 616.4465 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05247
5266 | 311.1111 | 605.6316 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04756
5267 | 497.2222 | 967.9291 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04546
5268 | 722.2222 | 1405.9306 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04355
5269 | 508.3333 | 989.5588 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0435
5270 | 744.4444 | 1449.19 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04337
5271 | 594.4444 | 1157.189 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0437
5272 | 491.6667 | 957.1143 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04576
5273 | 338.8889 | 659.7059 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05099
5274 | 163.8889 | 319.0381 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05404
5275 | 55.5556 | 108.1485 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05805
5276 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05837
5277 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05863
5278 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0571
5279 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05312
5280 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04992
5281 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04888
5282 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04446
5283 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04252
5284 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04092
5285 | 30.5556 | 59.4817 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0431
5286 | 61.1111 | 118.9634 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0567
5287 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06467
5288 | 75 | 146.0005 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06317
5289 | 152.7778 | 297.4084 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05787
5290 | 163.8889 | 319.0381 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05527
5291 | 91.6667 | 178.445 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0554
5292 | 108.3333 | 210.8896 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0542
5293 | 75 | 146.0005 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05423
5294 | 197.2222 | 383.9272 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05468
5295 | 283.3333 | 551.5574 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05371
5296 | 197.2222 | 383.9272 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05157
5297 | 108.3333 | 210.8896 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0545
5298 | 55.5556 | 108.1485 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05764
5299 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0607
5300 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05418
5301 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05194
5302 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04926
5303 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04626
5304 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04875
5305 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04857
5306 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04287
5307 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0384
5308 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03179
5309 | 19.4444 | 37.852 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03166
5310 | 125 | 243.3341 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.034
5311 | 261.1111 | 508.298 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04198
5312 | 283.3333 | 551.5574 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04911
5313 | 186.1111 | 362.2975 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0499
5314 | 202.7778 | 394.742 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0435
5315 | 566.6667 | 1103.1147 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0427
5316 | 716.6667 | 1395.1157 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0401
5317 | 391.6667 | 762.447 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0398
5318 | 511.1111 | 994.9662 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.034
5319 | 450 | 876.0029 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.03
5320 | 377.7778 | 735.4098 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.03968
5321 | 302.7778 | 589.4093 | 100 | 17.6539 | 2350 | 0 | #DIV/0! | 0.04445
5322 | 152.7778 | 297.4084 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.0435
5323 | 47.2222 | 91.9262 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04792
5324 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05012
5325 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04639
5326 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04683
5327 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04807
5328 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04201
5329 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.03687
5330 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0316
5331 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0277
5332 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.02813
5333 | 16.6667 | 32.4446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.02862
5334 | 105.5556 | 205.4822 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.02944
5335 | 275 | 535.3351 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03551
5336 | 444.4444 | 865.188 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04317
5337 | 583.3333 | 1135.5593 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04596
5338 | 461.1111 | 897.6326 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.044
5339 | 455.5556 | 886.8177 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.043
5340 | 638.8889 | 1243.7078 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0461
5341 | 430.5556 | 838.1509 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04594
5342 | 536.1111 | 1043.6331 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04561
5343 | 483.3333 | 940.892 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04643
5344 | 266.6667 | 519.1128 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.046
5345 | 186.1111 | 362.2975 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04792
5346 | 47.2222 | 91.9262 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04916
5347 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05437
5348 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05651
5349 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05696
5350 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.055
5351 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05229
5352 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04379
5353 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04407
5354 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04248
5355 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0411
5356 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0405
5357 | 19.4444 | 37.852 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04212
5358 | 108.3333 | 210.8896 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04916
5359 | 266.6667 | 519.1128 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05402
5360 | 394.4444 | 767.8544 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05407
5361 | 472.2222 | 919.2623 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05319
5362 | 611.1111 | 1189.6336 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0517
5363 | 705.5556 | 1373.486 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0529
5364 | 580.5556 | 1130.1519 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05118
5365 | 611.1111 | 1189.6336 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05079
5366 | 533.3333 | 1038.2256 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05146
5367 | 363.8889 | 708.3727 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05077
5368 | 36.1111 | 70.2965 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04988
5369 | 33.3333 | 64.8891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05906
5370 | 27.7778 | 54.0743 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07299
5371 | 19.4444 | 37.852 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08286
5372 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08178
5373 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07696
5374 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05963
5375 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05163
5376 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0498
5377 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0487
5378 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0474
5379 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04743
5380 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04724
5381 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04775
5382 | 55.5556 | 108.1485 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05716
5383 | 277.7778 | 540.7425 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06621
5384 | 347.2222 | 675.9282 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06395
5385 | 466.6667 | 908.4474 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05585
5386 | 652.7778 | 1270.7449 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05396
5387 | 388.8889 | 757.0395 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05102
5388 | 705.5556 | 1373.486 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0471
5389 | 230.5556 | 448.8163 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04594
5390 | 252.7778 | 492.0757 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04434
5391 | 475 | 924.6697 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04478
5392 | 197.2222 | 383.9272 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0499
5393 | 266.6667 | 519.1128 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05267
5394 | 136.1111 | 264.9638 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05317
5395 | 30.5556 | 59.4817 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06134
5396 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0639
5397 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0626
5398 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05682
5399 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0513
5400 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04739
5401 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04535
5402 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04325
5403 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04318
5404 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04432
5405 | 16.6667 | 32.4446 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0453
5406 | 111.1111 | 216.297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05293
5407 | 258.3333 | 502.8905 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06224
5408 | 425 | 827.3361 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06022
5409 | 561.1111 | 1092.2999 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05277
5410 | 680.5556 | 1324.8192 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05067
5411 | 716.6667 | 1395.1157 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04929
5412 | 688.8889 | 1341.0415 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04702
5413 | 630.5556 | 1227.4855 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.045
5414 | 550 | 1070.6702 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04601
5415 | 494.4444 | 962.5217 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04732
5416 | 377.7778 | 735.4098 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04884
5417 | 200 | 389.3346 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05283
5418 | 44.4444 | 86.5188 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06287
5419 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0772
5420 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06735
5421 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.066
5422 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05482
5423 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05095
5424 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04415
5425 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04274
5426 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0434
5427 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04181
5428 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0401
5429 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03643
5430 | 33.3333 | 64.8891 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0419
5431 | 72.2222 | 140.5931 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04699
5432 | 100 | 194.6673 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05019
5433 | 144.4444 | 281.1861 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05847
5434 | 205.5556 | 400.1495 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05702
5435 | 313.8889 | 611.0391 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05028
5436 | 444.4444 | 865.188 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04928
5437 | 344.4444 | 670.5207 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04603
5438 | 419.4444 | 816.5212 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0429
5439 | 283.3333 | 551.5574 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0433
5440 | 297.2222 | 578.5945 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04692
5441 | 108.3333 | 210.8896 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05037
5442 | 69.4444 | 135.1856 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05076
5443 | 19.4444 | 37.852 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05361
5444 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05568
5445 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05115
5446 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05007
5447 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04833
5448 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04483
5449 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0423
5450 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04138
5451 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0407
5452 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04065
5453 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04354
5454 | 125 | 243.3341 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04968
5455 | 250 | 486.6683 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05552
5456 | 355.5556 | 692.1504 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05833
5457 | 522.2222 | 1016.5959 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05465
5458 | 527.7778 | 1027.4108 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05173
5459 | 463.8889 | 903.04 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0499
5460 | 505.5556 | 984.1514 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04806
5461 | 586.1111 | 1140.9667 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04554
5462 | 558.3333 | 1086.8925 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04697
5463 | 411.1111 | 800.2989 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0449
5464 | 341.6667 | 665.1133 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04601
5465 | 188.8889 | 367.7049 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0524
5466 | 55.5556 | 108.1485 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06084
5467 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07094
5468 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06576
5469 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05942
5470 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05176
5471 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04619
5472 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0444
5473 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03759
5474 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03313
5475 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03171
5476 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.028
5477 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.02751
5478 | 38.8889 | 75.704 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03157
5479 | 58.3333 | 113.5559 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03257
5480 | 61.1111 | 118.9634 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04013
5481 | 97.2222 | 189.2599 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04921
5482 | 113.8889 | 221.7044 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04726
5483 | 202.7778 | 394.742 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04694
5484 | 222.2222 | 432.594 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0418
5485 | 241.6667 | 470.446 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04107
5486 | 197.2222 | 383.9272 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03907
5487 | 119.4444 | 232.5193 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03904
5488 | 66.6667 | 129.7782 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0401
5489 | 47.2222 | 91.9262 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04667
5490 | 52.7778 | 102.7411 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04945
5491 | 19.4444 | 37.852 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05076
5492 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05295
5493 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.055
5494 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05752
5495 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04939
5496 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04729
5497 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04613
5498 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0461
5499 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04982
5500 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0449
5501 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04442
5502 | 30.5556 | 59.4817 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04741
5503 | 63.8889 | 124.3708 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04978
5504 | 133.3333 | 259.5564 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04931
5505 | 158.3333 | 308.2232 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04817
5506 | 208.3333 | 405.5569 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0488
5507 | 213.8889 | 416.3717 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04875
5508 | 300 | 584.0019 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04524
5509 | 316.6667 | 616.4465 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0423
5510 | 236.1111 | 459.6311 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03714
5511 | 266.6667 | 519.1128 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.02887
5512 | 286.1111 | 556.9648 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03325
5513 | 211.1111 | 410.9643 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04823
5514 | 133.3333 | 259.5564 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05082
5515 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05279
5516 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05517
5517 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05368
5518 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05197
5519 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04881
5520 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04364
5521 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04245
5522 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.041
5523 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04079
5524 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04206
5525 | 11.1111 | 21.6297 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0431
5526 | 100 | 194.6673 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04735
5527 | 244.4444 | 475.8534 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05731
5528 | 402.7778 | 784.0767 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05687
5529 | 513.8889 | 1000.3737 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05198
5530 | 472.2222 | 919.2623 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04919
5531 | 652.7778 | 1270.7449 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04706
5532 | 375 | 730.0024 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0449
5533 | 350 | 681.3356 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0429
5534 | 458.3333 | 892.2252 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0428
5535 | 555.5556 | 1081.485 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04273
5536 | 325 | 632.6688 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04228
5537 | 258.3333 | 502.8905 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04806
5538 | 52.7778 | 102.7411 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.053
5539 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05896
5540 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0657
5541 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06181
5542 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0555
5543 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04992
5544 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04638
5545 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04474
5546 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0444
5547 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04331
5548 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0445
5549 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04675
5550 | 94.4444 | 183.8525 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05216
5551 | 236.1111 | 459.6311 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0595
5552 | 361.1111 | 702.9653 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06253
5553 | 477.7778 | 930.0771 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05973
5554 | 588.8889 | 1146.3741 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05451
5555 | 672.2222 | 1308.5969 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05391
5556 | 347.2222 | 675.9282 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05293
5557 | 330.5556 | 643.4836 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05235
5558 | 605.5556 | 1178.8187 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05255
5559 | 472.2222 | 919.2623 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05298
5560 | 219.4444 | 427.1866 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05252
5561 | 169.4444 | 329.8529 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05911
5562 | 86.1111 | 167.6302 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06434
5563 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.068
5564 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06829
5565 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06335
5566 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05561
5567 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05085
5568 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04807
5569 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04796
5570 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04684
5571 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0458
5572 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04653
5573 | 8.3333 | 16.2223 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04563
5574 | 91.6667 | 178.445 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05642
5575 | 233.3333 | 454.2237 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07074
5576 | 388.8889 | 757.0395 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07023
5577 | 508.3333 | 989.5588 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05695
5578 | 619.4444 | 1205.8558 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.053
5579 | 750 | 1460.0048 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05197
5580 | 711.1111 | 1384.3009 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05072
5581 | 611.1111 | 1189.6336 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04905
5582 | 625 | 1216.6707 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04817
5583 | 283.3333 | 551.5574 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04799
5584 | 200 | 389.3346 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05044
5585 | 225 | 438.0014 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05514
5586 | 94.4444 | 183.8525 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06426
5587 | 22.2222 | 43.2594 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08036
5588 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.08232
5589 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06721
5590 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05958
5591 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05294
5592 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04826
5593 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04687
5594 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04504
5595 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04479
5596 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04291
5597 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04391
5598 | 108.3333 | 210.8896 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05094
5599 | 233.3333 | 454.2237 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05612
5600 | 388.8889 | 757.0395 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05564
5601 | 508.3333 | 989.5588 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0529
5602 | 600 | 1168.0038 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04991
5603 | 683.3333 | 1330.2266 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04801
5604 | 736.1111 | 1432.9677 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04701
5605 | 711.1111 | 1384.3009 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04553
5606 | 638.8889 | 1243.7078 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04621
5607 | 538.8889 | 1049.0405 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04614
5608 | 413.8889 | 805.7064 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04694
5609 | 241.6667 | 470.446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05199
5610 | 108.3333 | 210.8896 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05747
5611 | 13.8889 | 27.0371 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0696
5612 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06607
5613 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0604
5614 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05348
5615 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04895
5616 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04528
5617 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04508
5618 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04479
5619 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04462
5620 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.045
5621 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.047
5622 | 83.3333 | 162.2228 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05447
5623 | 241.6667 | 470.446 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0584
5624 | 377.7778 | 735.4098 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05575
5625 | 486.1111 | 946.2994 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05168
5626 | 563.8889 | 1097.7073 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0498
5627 | 677.7778 | 1319.4118 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04913
5628 | 683.3333 | 1330.2266 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04695
5629 | 650 | 1265.3375 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04623
5630 | 566.6667 | 1103.1147 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04581
5631 | 541.6667 | 1054.4479 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04657
5632 | 377.7778 | 735.4098 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04728
5633 | 233.3333 | 454.2237 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05477
5634 | 111.1111 | 216.297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0624
5635 | 16.6667 | 32.4446 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07233
5636 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07056
5637 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05983
5638 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05197
5639 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04968
5640 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04907
5641 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04686
5642 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04586
5643 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04582
5644 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04503
5645 | 5.5556 | 10.8149 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04525
5646 | 80.5556 | 156.8153 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04779
5647 | 227.7778 | 443.4089 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04896
5648 | 383.3333 | 746.2247 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05095
5649 | 508.3333 | 989.5588 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05025
5650 | 616.6667 | 1200.4484 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04451
5651 | 711.1111 | 1384.3009 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0425
5652 | 750 | 1460.0048 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04183
5653 | 719.4444 | 1400.5231 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04184
5654 | 644.4444 | 1254.5227 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04201
5655 | 538.8889 | 1049.0405 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04303
5656 | 411.1111 | 800.2989 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04303
5657 | 261.1111 | 508.298 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04829
5658 | 108.3333 | 210.8896 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05193
5659 | 11.1111 | 21.6297 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05739
5660 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05375
5661 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05129
5662 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04995
5663 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04667
5664 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04408
5665 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04365
5666 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0437
5667 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04349
5668 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0437
5669 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04303
5670 | 77.7778 | 151.4079 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04328
5671 | 227.7778 | 443.4089 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04664
5672 | 380.5556 | 740.8173 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04611
5673 | 497.2222 | 967.9291 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04648
5674 | 594.4444 | 1157.189 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04089
5675 | 686.1111 | 1335.634 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04088
5676 | 733.3333 | 1427.5603 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04083
5677 | 708.3333 | 1378.8934 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04003
5678 | 633.3333 | 1232.893 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04001
5679 | 536.1111 | 1043.6331 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04039
5680 | 391.6667 | 762.447 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0414
5681 | 244.4444 | 475.8534 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04698
5682 | 102.7778 | 200.0747 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05585
5683 | 11.1111 | 21.6297 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06131
5684 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06144
5685 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05805
5686 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05249
5687 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04952
5688 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04867
5689 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04795
5690 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04706
5691 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04686
5692 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0471
5693 | 5.5556 | 10.8149 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04765
5694 | 61.1111 | 118.9634 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06391
5695 | 188.8889 | 367.7049 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08155
5696 | 336.1111 | 654.2985 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07561
5697 | 452.7778 | 881.4103 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06394
5698 | 558.3333 | 1086.8925 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0607
5699 | 647.2222 | 1259.9301 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05874
5700 | 680.5556 | 1324.8192 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05591
5701 | 661.1111 | 1286.9672 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05396
5702 | 586.1111 | 1140.9667 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05325
5703 | 491.6667 | 957.1143 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05339
5704 | 358.3333 | 697.5579 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05846
5705 | 211.1111 | 410.9643 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06738
5706 | 86.1111 | 167.6302 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07014
5707 | 8.3333 | 16.2223 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08027
5708 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07336
5709 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07001
5710 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06287
5711 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05444
5712 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05333
5713 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05026
5714 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04979
5715 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0495
5716 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04971
5717 | 5.5556 | 10.8149 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05074
5718 | 63.8889 | 124.3708 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05975
5719 | 202.7778 | 394.742 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07113
5720 | 352.7778 | 686.743 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06869
5721 | 477.7778 | 930.0771 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06853
5722 | 577.7778 | 1124.7444 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06595
5723 | 663.8889 | 1292.3746 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06382
5724 | 691.6667 | 1346.4489 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06015
5725 | 652.7778 | 1270.7449 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05993
5726 | 611.1111 | 1189.6336 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06006
5727 | 458.3333 | 892.2252 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06011
5728 | 369.4444 | 719.1876 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06308
5729 | 211.1111 | 410.9643 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06622
5730 | 41.6667 | 81.1114 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07199
5731 | 5.5556 | 10.8149 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07807
5732 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07105
5733 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0662
5734 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06118
5735 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05249
5736 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05308
5737 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05055
5738 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04992
5739 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04966
5740 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04908
5741 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05033
5742 | 38.8889 | 75.704 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06276
5743 | 188.8889 | 367.7049 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0791
5744 | 344.4444 | 670.5207 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08041
5745 | 466.6667 | 908.4474 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07075
5746 | 563.8889 | 1097.7073 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06779
5747 | 633.3333 | 1232.893 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0667
5748 | 666.6667 | 1297.7821 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06155
5749 | 550 | 1070.6702 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05973
5750 | 422.2222 | 821.9286 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06
5751 | 480.5556 | 935.4846 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0606
5752 | 288.8889 | 562.3722 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06383
5753 | 205.5556 | 400.1495 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07152
5754 | 77.7778 | 151.4079 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.086
5755 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.09283
5756 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.08691
5757 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07229
5758 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06579
5759 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05892
5760 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05454
5761 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05064
5762 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04915
5763 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04725
5764 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04722
5765 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04773
5766 | 33.3333 | 64.8891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05784
5767 | 127.7778 | 248.7416 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0671
5768 | 211.1111 | 410.9643 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07316
5769 | 291.6667 | 567.7796 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07156
5770 | 455.5556 | 886.8177 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0669
5771 | 594.4444 | 1157.189 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06501
5772 | 347.2222 | 675.9282 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05712
5773 | 355.5556 | 692.1504 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05462
5774 | 541.6667 | 1054.4479 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05277
5775 | 522.2222 | 1016.5959 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05188
5776 | 311.1111 | 605.6316 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05242
5777 | 227.7778 | 443.4089 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.059
5778 | 69.4444 | 135.1856 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06585
5779 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07564
5780 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07119
5781 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06596
5782 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05995
5783 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0524
5784 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04933
5785 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0465
5786 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04441
5787 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04384
5788 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04375
5789 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0451
5790 | 66.6667 | 129.7782 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05627
5791 | 227.7778 | 443.4089 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06607
5792 | 344.4444 | 670.5207 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06576
5793 | 447.2222 | 870.5955 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06104
5794 | 622.2222 | 1211.2633 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05636
5795 | 705.5556 | 1373.486 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05319
5796 | 727.7778 | 1416.7454 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04994
5797 | 700 | 1362.6712 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04933
5798 | 605.5556 | 1178.8187 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04903
5799 | 477.7778 | 930.0771 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05027
5800 | 338.8889 | 659.7059 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05122
5801 | 222.2222 | 432.594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0584
5802 | 108.3333 | 210.8896 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06549
5803 | 5.5556 | 10.8149 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06734
5804 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06749
5805 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06651
5806 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06314
5807 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05372
5808 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05239
5809 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04766
5810 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04564
5811 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04312
5812 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04276
5813 | 2.7778 | 5.4074 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04213
5814 | 55.5556 | 108.1485 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04311
5815 | 188.8889 | 367.7049 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0428
5816 | 358.3333 | 697.5579 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04706
5817 | 508.3333 | 989.5588 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04872
5818 | 622.2222 | 1211.2633 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04629
5819 | 663.8889 | 1292.3746 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04544
5820 | 719.4444 | 1400.5231 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0436
5821 | 675 | 1314.0043 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0435
5822 | 616.6667 | 1200.4484 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04303
5823 | 494.4444 | 962.5217 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04313
5824 | 350 | 681.3356 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04487
5825 | 150 | 292.001 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04759
5826 | 33.3333 | 64.8891 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05568
5827 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06334
5828 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06245
5829 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05642
5830 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05207
5831 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04802
5832 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0422
5833 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0417
5834 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04147
5835 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04093
5836 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04034
5837 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04099
5838 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04149
5839 | 75 | 146.0005 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04149
5840 | 225 | 438.0014 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04184
5841 | 241.6667 | 470.446 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0451
5842 | 394.4444 | 767.8544 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0447
5843 | 427.7778 | 832.7435 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04517
5844 | 344.4444 | 670.5207 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04601
5845 | 327.7778 | 638.0762 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04523
5846 | 461.1111 | 897.6326 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04339
5847 | 333.3333 | 648.891 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04274
5848 | 341.6667 | 665.1133 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0422
5849 | 205.5556 | 400.1495 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04494
5850 | 75 | 146.0005 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04907
5851 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05152
5852 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05467
5853 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05376
5854 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05233
5855 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04935
5856 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04428
5857 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04197
5858 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04096
5859 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04
5860 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04063
5861 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04273
5862 | 47.2222 | 91.9262 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05288
5863 | 166.6667 | 324.4455 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06109
5864 | 344.4444 | 670.5207 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06455
5865 | 466.6667 | 908.4474 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06329
5866 | 644.4444 | 1254.5227 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05907
5867 | 355.5556 | 692.1504 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05681
5868 | 519.4444 | 1011.1885 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05383
5869 | 486.1111 | 946.2994 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05315
5870 | 525 | 1022.0034 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0517
5871 | 355.5556 | 692.1504 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05099
5872 | 333.3333 | 648.891 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05257
5873 | 197.2222 | 383.9272 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05584
5874 | 72.2222 | 140.5931 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06041
5875 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06729
5876 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06753
5877 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06192
5878 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05576
5879 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05022
5880 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04681
5881 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04312
5882 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04195
5883 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0393
5884 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0391
5885 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04323
5886 | 11.1111 | 21.6297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04744
5887 | 91.6667 | 178.445 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05574
5888 | 255.5556 | 497.4831 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05588
5889 | 219.4444 | 427.1866 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05296
5890 | 202.7778 | 394.742 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04795
5891 | 105.5556 | 205.4822 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04708
5892 | 166.6667 | 324.4455 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0449
5893 | 283.3333 | 551.5574 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04615
5894 | 208.3333 | 405.5569 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04671
5895 | 72.2222 | 140.5931 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04701
5896 | 61.1111 | 118.9634 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04829
5897 | 47.2222 | 91.9262 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05476
5898 | 16.6667 | 32.4446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05996
5899 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06583
5900 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0681
5901 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06112
5902 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0559
5903 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05108
5904 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04631
5905 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.044
5906 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.044
5907 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04275
5908 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04307
5909 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03915
5910 | 25 | 48.6668 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05452
5911 | 97.2222 | 189.2599 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05781
5912 | 308.3333 | 600.2242 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06029
5913 | 333.3333 | 648.891 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05796
5914 | 361.1111 | 702.9653 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05273
5915 | 222.2222 | 432.594 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04757
5916 | 152.7778 | 297.4084 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04548
5917 | 130.5556 | 254.149 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04437
5918 | 72.2222 | 140.5931 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04442
5919 | 83.3333 | 162.2228 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0439
5920 | 30.5556 | 59.4817 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04386
5921 | 102.7778 | 200.0747 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04668
5922 | 19.4444 | 37.852 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05305
5923 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0553
5924 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05567
5925 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05325
5926 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0503
5927 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04454
5928 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.043
5929 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04096
5930 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04005
5931 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03832
5932 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.03794
5933 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04134
5934 | 25 | 48.6668 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04868
5935 | 108.3333 | 210.8896 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05462
5936 | 275 | 535.3351 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05548
5937 | 250 | 486.6683 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05149
5938 | 450 | 876.0029 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04694
5939 | 416.6667 | 811.1138 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04366
5940 | 380.5556 | 740.8173 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04076
5941 | 316.6667 | 616.4465 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0403
5942 | 447.2222 | 870.5955 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04084
5943 | 258.3333 | 502.8905 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0422
5944 | 255.5556 | 497.4831 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04416
5945 | 163.8889 | 319.0381 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04726
5946 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05109
5947 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05495
5948 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05592
5949 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05395
5950 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05121
5951 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04595
5952 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04128
5953 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04064
5954 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03936
5955 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03931
5956 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04046
5957 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04118
5958 | 22.2222 | 43.2594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04844
5959 | 102.7778 | 200.0747 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05323
5960 | 202.7778 | 394.742 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05407
5961 | 280.5556 | 546.1499 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05396
5962 | 358.3333 | 697.5579 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05233
5963 | 461.1111 | 897.6326 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04661
5964 | 433.3333 | 843.5583 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.042
5965 | 475 | 924.6697 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0415
5966 | 313.8889 | 611.0391 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04335
5967 | 147.2222 | 286.5935 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04344
5968 | 116.6667 | 227.1119 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04411
5969 | 33.3333 | 64.8891 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04849
5970 | 11.1111 | 21.6297 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05326
5971 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05431
5972 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05507
5973 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0534
5974 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05289
5975 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04907
5976 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04701
5977 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.045
5978 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04444
5979 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04369
5980 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04432
5981 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04484
5982 | 27.7778 | 54.0743 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04757
5983 | 108.3333 | 210.8896 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05009
5984 | 288.8889 | 562.3722 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05127
5985 | 433.3333 | 843.5583 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05483
5986 | 416.6667 | 811.1138 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0547
5987 | 222.2222 | 432.594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05199
5988 | 475 | 924.6697 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.051
5989 | 372.2222 | 724.595 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05005
5990 | 480.5556 | 935.4846 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04896
5991 | 261.1111 | 508.298 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04717
5992 | 219.4444 | 427.1866 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04839
5993 | 55.5556 | 108.1485 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0524
5994 | 25 | 48.6668 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.059
5995 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06171
5996 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06473
5997 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.054
5998 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05298
5999 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04978
6000 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04946
6001 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04761
6002 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04736
6003 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04701
6004 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04692
6005 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.046
6006 | 22.2222 | 43.2594 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04739
6007 | 97.2222 | 189.2599 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0482
6008 | 183.3333 | 356.8901 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05
6009 | 333.3333 | 648.891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05227
6010 | 411.1111 | 800.2989 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05131
6011 | 377.7778 | 735.4098 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05119
6012 | 430.5556 | 838.1509 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05046
6013 | 572.2222 | 1113.9296 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0472
6014 | 358.3333 | 697.5579 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0473
6015 | 200 | 389.3346 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04737
6016 | 177.7778 | 346.0752 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04926
6017 | 147.2222 | 286.5935 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0543
6018 | 63.8889 | 124.3708 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0601
6019 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06688
6020 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07228
6021 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06049
6022 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0575
6023 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05327
6024 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05333
6025 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04909
6026 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04803
6027 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04709
6028 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04744
6029 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04914
6030 | 41.6667 | 81.1114 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06298
6031 | 172.2222 | 335.2604 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07753
6032 | 322.2222 | 627.2613 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08544
6033 | 463.8889 | 903.04 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07084
6034 | 555.5556 | 1081.485 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06367
6035 | 380.5556 | 740.8173 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06241
6036 | 566.6667 | 1103.1147 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.061
6037 | 391.6667 | 762.447 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06023
6038 | 163.8889 | 319.0381 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05764
6039 | 233.3333 | 454.2237 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05723
6040 | 288.8889 | 562.3722 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0566
6041 | 91.6667 | 178.445 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06014
6042 | 22.2222 | 43.2594 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06499
6043 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07564
6044 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07243
6045 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06094
6046 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05538
6047 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04935
6048 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04801
6049 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04745
6050 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.046
6051 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04463
6052 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04401
6053 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0468
6054 | 22.2222 | 43.2594 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0552
6055 | 80.5556 | 156.8153 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05995
6056 | 247.2222 | 481.2608 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06093
6057 | 438.8889 | 854.3732 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.056
6058 | 297.2222 | 578.5945 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.051
6059 | 336.1111 | 654.2985 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0476
6060 | 663.8889 | 1292.3746 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04604
6061 | 652.7778 | 1270.7449 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0457
6062 | 480.5556 | 935.4846 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0463
6063 | 344.4444 | 670.5207 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04701
6064 | 219.4444 | 427.1866 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0491
6065 | 111.1111 | 216.297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05418
6066 | 33.3333 | 64.8891 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05953
6067 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06244
6068 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06567
6069 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05775
6070 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05089
6071 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0467
6072 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04625
6073 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04523
6074 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0435
6075 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0421
6076 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03997
6077 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04261
6078 | 36.1111 | 70.2965 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05229
6079 | 183.3333 | 356.8901 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05757
6080 | 158.3333 | 308.2232 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05825
6081 | 191.6667 | 373.1123 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05482
6082 | 130.5556 | 254.149 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05129
6083 | 147.2222 | 286.5935 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04894
6084 | 119.4444 | 232.5193 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04555
6085 | 94.4444 | 183.8525 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04379
6086 | 111.1111 | 216.297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04368
6087 | 72.2222 | 140.5931 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04502
6088 | 47.2222 | 91.9262 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04433
6089 | 22.2222 | 43.2594 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04806
6090 | 5.5556 | 10.8149 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05234
6091 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05467
6092 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0561
6093 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05337
6094 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04804
6095 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0451
6096 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04288
6097 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04221
6098 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04253
6099 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04201
6100 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04303
6101 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04574
6102 | 13.8889 | 27.0371 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05966
6103 | 83.3333 | 162.2228 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06565
6104 | 286.1111 | 556.9648 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07025
6105 | 386.1111 | 751.6321 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06296
6106 | 563.8889 | 1097.7073 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05893
6107 | 602.7778 | 1173.4113 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05697
6108 | 483.3333 | 940.892 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05599
6109 | 652.7778 | 1270.7449 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05028
6110 | 413.8889 | 805.7064 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04768
6111 | 344.4444 | 670.5207 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04772
6112 | 275 | 535.3351 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04775
6113 | 130.5556 | 254.149 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0549
6114 | 25 | 48.6668 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.057
6115 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05927
6116 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05917
6117 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05651
6118 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05129
6119 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0451
6120 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04505
6121 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04331
6122 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04211
6123 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04124
6124 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04205
6125 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04501
6126 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05501
6127 | 69.4444 | 135.1856 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05898
6128 | 255.5556 | 497.4831 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06072
6129 | 358.3333 | 697.5579 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05969
6130 | 563.8889 | 1097.7073 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05865
6131 | 522.2222 | 1016.5959 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05721
6132 | 488.8889 | 951.7068 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05583
6133 | 466.6667 | 908.4474 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05302
6134 | 483.3333 | 940.892 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05203
6135 | 369.4444 | 719.1876 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05125
6136 | 277.7778 | 540.7425 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05253
6137 | 147.2222 | 286.5935 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05748
6138 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06113
6139 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0661
6140 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06743
6141 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05991
6142 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05702
6143 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.054
6144 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0547
6145 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0475
6146 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04707
6147 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0469
6148 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04683
6149 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04693
6150 | 22.2222 | 43.2594 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04785
6151 | 150 | 292.001 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0549
6152 | 291.6667 | 567.7796 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05649
6153 | 430.5556 | 838.1509 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05677
6154 | 558.3333 | 1086.8925 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05149
6155 | 619.4444 | 1205.8558 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04754
6156 | 641.6667 | 1249.1152 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04628
6157 | 563.8889 | 1097.7073 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04501
6158 | 552.7778 | 1076.0776 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04303
6159 | 427.7778 | 832.7435 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04302
6160 | 258.3333 | 502.8905 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.045
6161 | 83.3333 | 162.2228 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05048
6162 | 19.4444 | 37.852 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05792
6163 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06585
6164 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06299
6165 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05905
6166 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05595
6167 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04789
6168 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04808
6169 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0444
6170 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04035
6171 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03286
6172 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0318
6173 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.034
6174 | 27.7778 | 54.0743 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03954
6175 | 136.1111 | 264.9638 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04714
6176 | 227.7778 | 443.4089 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04305
6177 | 327.7778 | 638.0762 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04715
6178 | 488.8889 | 951.7068 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04316
6179 | 552.7778 | 1076.0776 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04
6180 | 625 | 1216.6707 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.043
6181 | 297.2222 | 578.5945 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0453
6182 | 350 | 681.3356 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0453
6183 | 125 | 243.3341 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0453
6184 | 33.3333 | 64.8891 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0444
6185 | 30.5556 | 59.4817 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0474
6186 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05675
6187 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05896
6188 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0639
6189 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06299
6190 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06091
6191 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05617
6192 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04745
6193 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04757
6194 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04709
6195 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04543
6196 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04592
6197 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0483
6198 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06338
6199 | 25 | 48.6668 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06769
6200 | 55.5556 | 108.1485 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07469
6201 | 88.8889 | 173.0376 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07031
6202 | 127.7778 | 248.7416 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06579
6203 | 236.1111 | 459.6311 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06969
6204 | 297.2222 | 578.5945 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.065
6205 | 200 | 389.3346 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06532
6206 | 161.1111 | 313.6307 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06439
6207 | 147.2222 | 286.5935 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06391
6208 | 205.5556 | 400.1495 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06311
6209 | 66.6667 | 129.7782 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06693
6210 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07167
6211 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07591
6212 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07516
6213 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06609
6214 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06285
6215 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.053
6216 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05188
6217 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04802
6218 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04591
6219 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0455
6220 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04557
6221 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04788
6222 | 33.3333 | 64.8891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0609
6223 | 130.5556 | 254.149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06591
6224 | 244.4444 | 475.8534 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06703
6225 | 247.2222 | 481.2608 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06082
6226 | 375 | 730.0024 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05132
6227 | 113.8889 | 221.7044 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04523
6228 | 305.5556 | 594.8168 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0427
6229 | 294.4444 | 573.1871 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04251
6230 | 300 | 584.0019 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0421
6231 | 319.4444 | 621.8539 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0425
6232 | 200 | 389.3346 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.043
6233 | 111.1111 | 216.297 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04474
6234 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05032
6235 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05673
6236 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05632
6237 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05151
6238 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04823
6239 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04503
6240 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04253
6241 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04216
6242 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.042
6243 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04174
6244 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0427
6245 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04518
6246 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05477
6247 | 72.2222 | 140.5931 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06495
6248 | 252.7778 | 492.0757 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06622
6249 | 266.6667 | 519.1128 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06136
6250 | 330.5556 | 643.4836 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04766
6251 | 350 | 681.3356 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04699
6252 | 386.1111 | 751.6321 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04356
6253 | 411.1111 | 800.2989 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0437
6254 | 519.4444 | 1011.1885 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0437
6255 | 186.1111 | 362.2975 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0449
6256 | 200 | 389.3346 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0449
6257 | 88.8889 | 173.0376 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05291
6258 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06329
6259 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06727
6260 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06817
6261 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06307
6262 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06019
6263 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.052
6264 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04834
6265 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04615
6266 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04578
6267 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0444
6268 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04643
6269 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0495
6270 | 25 | 48.6668 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06373
6271 | 119.4444 | 232.5193 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06679
6272 | 280.5556 | 546.1499 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.069
6273 | 411.1111 | 800.2989 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.067
6274 | 525 | 1022.0034 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06519
6275 | 472.2222 | 919.2623 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0592
6276 | 583.3333 | 1135.5593 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05273
6277 | 516.6667 | 1005.7811 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0513
6278 | 472.2222 | 919.2623 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.051
6279 | 388.8889 | 757.0395 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05138
6280 | 280.5556 | 546.1499 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05388
6281 | 105.5556 | 205.4822 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.065
6282 | 16.6667 | 32.4446 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0672
6283 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.08504
6284 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07566
6285 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06624
6286 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06309
6287 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05358
6288 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05237
6289 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04783
6290 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04602
6291 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04451
6292 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04556
6293 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04694
6294 | 13.8889 | 27.0371 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06133
6295 | 119.4444 | 232.5193 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06847
6296 | 238.8889 | 465.0386 | 0 | 0 | 0 | 0 | #DIV/0! | 0.07573
6297 | 408.3333 | 794.8915 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06709
6298 | 525 | 1022.0034 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06448
6299 | 586.1111 | 1140.9667 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05652
6300 | 622.2222 | 1211.2633 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04837
6301 | 588.8889 | 1146.3741 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04615
6302 | 516.6667 | 1005.7811 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0459
6303 | 402.7778 | 784.0767 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04796
6304 | 255.5556 | 497.4831 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04898
6305 | 108.3333 | 210.8896 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06113
6306 | 11.1111 | 21.6297 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06541
6307 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07194
6308 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06622
6309 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05908
6310 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0535
6311 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04601
6312 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04807
6313 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04343
6314 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04272
6315 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04029
6316 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04142
6317 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0421
6318 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04449
6319 | 138.8889 | 270.3713 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04608
6320 | 277.7778 | 540.7425 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0515
6321 | 422.2222 | 821.9286 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0515
6322 | 530.5556 | 1032.8182 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04633
6323 | 594.4444 | 1157.189 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04483
6324 | 613.8889 | 1195.041 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04318
6325 | 591.6667 | 1151.7816 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04215
6326 | 519.4444 | 1011.1885 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04165
6327 | 400 | 778.6692 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0422
6328 | 255.5556 | 497.4831 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04232
6329 | 108.3333 | 210.8896 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.049
6330 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0583
6331 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.065
6332 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06132
6333 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04993
6334 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0481
6335 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04556
6336 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04262
6337 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04314
6338 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04416
6339 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04354
6340 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04487
6341 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04321
6342 | 19.4444 | 37.852 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04296
6343 | 136.1111 | 264.9638 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04347
6344 | 233.3333 | 454.2237 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.041
6345 | 388.8889 | 757.0395 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04307
6346 | 466.6667 | 908.4474 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04124
6347 | 508.3333 | 989.5588 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04191
6348 | 563.8889 | 1097.7073 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04158
6349 | 569.4444 | 1108.5222 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0399
6350 | 483.3333 | 940.892 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04005
6351 | 250 | 486.6683 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04149
6352 | 144.4444 | 281.1861 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04227
6353 | 36.1111 | 70.2965 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04999
6354 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05401
6355 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05597
6356 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0535
6357 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04944
6358 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0484
6359 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04699
6360 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04266
6361 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0422
6362 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04238
6363 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04133
6364 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04033
6365 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04631
6366 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05337
6367 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06399
6368 | 77.7778 | 151.4079 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.065
6369 | 113.8889 | 221.7044 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06484
6370 | 133.3333 | 259.5564 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06499
6371 | 225 | 438.0014 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06427
6372 | 250 | 486.6683 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06048
6373 | 344.4444 | 670.5207 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05837
6374 | 394.4444 | 767.8544 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05513
6375 | 266.6667 | 519.1128 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05559
6376 | 136.1111 | 264.9638 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0567
6377 | 52.7778 | 102.7411 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0651
6378 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06769
6379 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0763
6380 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06785
6381 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06421
6382 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05785
6383 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04771
6384 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0477
6385 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0454
6386 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04573
6387 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04526
6388 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04462
6389 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04757
6390 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0551
6391 | 61.1111 | 118.9634 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0651
6392 | 158.3333 | 308.2232 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08019
6393 | 175 | 340.6678 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06804
6394 | 236.1111 | 459.6311 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06693
6395 | 441.6667 | 859.7806 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06586
6396 | 397.2222 | 773.2618 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06246
6397 | 136.1111 | 264.9638 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05957
6398 | 66.6667 | 129.7782 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05722
6399 | 55.5556 | 108.1485 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05676
6400 | 38.8889 | 75.704 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06304
6401 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06996
6402 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0752
6403 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06906
6404 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.065
6405 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06042
6406 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05023
6407 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0472
6408 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04609
6409 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04517
6410 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04444
6411 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04319
6412 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04222
6413 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04576
6414 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05188
6415 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06306
6416 | 94.4444 | 183.8525 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07708
6417 | 86.1111 | 167.6302 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07164
6418 | 127.7778 | 248.7416 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06486
6419 | 216.6667 | 421.7792 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0574
6420 | 200 | 389.3346 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0556
6421 | 136.1111 | 264.9638 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0549
6422 | 241.6667 | 470.446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05417
6423 | 269.4444 | 524.5202 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0549
6424 | 130.5556 | 254.149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0556
6425 | 30.5556 | 59.4817 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06499
6426 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06919
6427 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07466
6428 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06674
6429 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0556
6430 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04858
6431 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0483
6432 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04461
6433 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04757
6434 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0451
6435 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04136
6436 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04203
6437 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04535
6438 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0585
6439 | 38.8889 | 75.704 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06529
6440 | 66.6667 | 129.7782 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06651
6441 | 47.2222 | 91.9262 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06538
6442 | 94.4444 | 183.8525 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06369
6443 | 105.5556 | 205.4822 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06132
6444 | 108.3333 | 210.8896 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0574
6445 | 80.5556 | 156.8153 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05293
6446 | 66.6667 | 129.7782 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0518
6447 | 50 | 97.3337 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05011
6448 | 33.3333 | 64.8891 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05035
6449 | 22.2222 | 43.2594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05622
6450 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06
6451 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.054
6452 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05159
6453 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04814
6454 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04561
6455 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04477
6456 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04405
6457 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04274
6458 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04241
6459 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0398
6460 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03926
6461 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04158
6462 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0561
6463 | 41.6667 | 81.1114 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06337
6464 | 138.8889 | 270.3713 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06531
6465 | 186.1111 | 362.2975 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06504
6466 | 355.5556 | 692.1504 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06087
6467 | 400 | 778.6692 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05616
6468 | 277.7778 | 540.7425 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04968
6469 | 213.8889 | 416.3717 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0477
6470 | 200 | 389.3346 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04571
6471 | 130.5556 | 254.149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04689
6472 | 138.8889 | 270.3713 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04767
6473 | 38.8889 | 75.704 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0561
6474 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06013
6475 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06329
6476 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06249
6477 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05014
6478 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04808
6479 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04499
6480 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0415
6481 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0375
6482 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.038
6483 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03564
6484 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03586
6485 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03773
6486 | 5.5556 | 10.8149 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0398
6487 | 41.6667 | 81.1114 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04246
6488 | 202.7778 | 394.742 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0482
6489 | 305.5556 | 594.8168 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04958
6490 | 363.8889 | 708.3727 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04816
6491 | 483.3333 | 940.892 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04742
6492 | 269.4444 | 524.5202 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04583
6493 | 336.1111 | 654.2985 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04432
6494 | 238.8889 | 465.0386 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04404
6495 | 227.7778 | 443.4089 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04398
6496 | 94.4444 | 183.8525 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04212
6497 | 58.3333 | 113.5559 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04728
6498 | 2.7778 | 5.4074 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05319
6499 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05869
6500 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0499
6501 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04512
6502 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04568
6503 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04583
6504 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04675
6505 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04608
6506 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0432
6507 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.038
6508 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03257
6509 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.02808
6510 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03311
6511 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03809
6512 | 19.4444 | 37.852 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03902
6513 | 63.8889 | 124.3708 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04162
6514 | 94.4444 | 183.8525 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04701
6515 | 94.4444 | 183.8525 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04588
6516 | 141.6667 | 275.7787 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0468
6517 | 58.3333 | 113.5559 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04663
6518 | 61.1111 | 118.9634 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04665
6519 | 58.3333 | 113.5559 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04655
6520 | 27.7778 | 54.0743 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04672
6521 | 19.4444 | 37.852 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04744
6522 | 2.7778 | 5.4074 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04845
6523 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05181
6524 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.053
6525 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.049
6526 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.048
6527 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0447
6528 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0395
6529 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.038
6530 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0394
6531 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0402
6532 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0399
6533 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.039
6534 | 5.5556 | 10.8149 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0449
6535 | 80.5556 | 156.8153 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0607
6536 | 236.1111 | 459.6311 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05902
6537 | 300 | 584.0019 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06342
6538 | 466.6667 | 908.4474 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.046
6539 | 377.7778 | 735.4098 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0432
6540 | 513.8889 | 1000.3737 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0395
6541 | 450 | 876.0029 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0424
6542 | 394.4444 | 767.8544 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0432
6543 | 280.5556 | 546.1499 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04864
6544 | 191.6667 | 373.1123 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05513
6545 | 33.3333 | 64.8891 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06592
6546 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07015
6547 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07937
6548 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07234
6549 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06427
6550 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05958
6551 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0496
6552 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04809
6553 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04526
6554 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04266
6555 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0452
6556 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0408
6557 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04801
6558 | 2.7778 | 5.4074 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06044
6559 | 11.1111 | 21.6297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06598
6560 | 38.8889 | 75.704 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06604
6561 | 91.6667 | 178.445 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06463
6562 | 236.1111 | 459.6311 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06186
6563 | 241.6667 | 470.446 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05992
6564 | 166.6667 | 324.4455 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05717
6565 | 158.3333 | 308.2232 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05604
6566 | 186.1111 | 362.2975 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05449
6567 | 47.2222 | 91.9262 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05438
6568 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05788
6569 | 13.8889 | 27.0371 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0632
6570 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06516
6571 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06999
6572 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06792
6573 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06502
6574 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06006
6575 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05044
6576 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04849
6577 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04514
6578 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04425
6579 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04171
6580 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04174
6581 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0432
6582 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05875
6583 | 94.4444 | 183.8525 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06679
6584 | 230.5556 | 448.8163 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0674
6585 | 383.3333 | 746.2247 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06675
6586 | 383.3333 | 746.2247 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.065
6587 | 438.8889 | 854.3732 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06138
6588 | 466.6667 | 908.4474 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05196
6589 | 352.7778 | 686.743 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0499
6590 | 369.4444 | 719.1876 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04947
6591 | 252.7778 | 492.0757 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0495
6592 | 144.4444 | 281.1861 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04976
6593 | 30.5556 | 59.4817 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05547
6594 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06301
6595 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06661
6596 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06216
6597 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05213
6598 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04969
6599 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04375
6600 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04121
6601 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04141
6602 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0403
6603 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04035
6604 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04143
6605 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04431
6606 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05032
6607 | 66.6667 | 129.7782 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.064
6608 | 138.8889 | 270.3713 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0655
6609 | 219.4444 | 427.1866 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07074
6610 | 477.7778 | 930.0771 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06467
6611 | 425 | 827.3361 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06257
6612 | 350 | 681.3356 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05744
6613 | 511.1111 | 994.9662 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05282
6614 | 297.2222 | 578.5945 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05174
6615 | 250 | 486.6683 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05186
6616 | 102.7778 | 200.0747 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0554
6617 | 19.4444 | 37.852 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06293
6618 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06623
6619 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07006
6620 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06853
6621 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06306
6622 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06059
6623 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05093
6624 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05249
6625 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04557
6626 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04242
6627 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04242
6628 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04048
6629 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04294
6630 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0565
6631 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06375
6632 | 50 | 97.3337 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06506
6633 | 44.4444 | 86.5188 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06466
6634 | 86.1111 | 167.6302 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06348
6635 | 88.8889 | 173.0376 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06333
6636 | 72.2222 | 140.5931 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06387
6637 | 38.8889 | 75.704 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06197
6638 | 44.4444 | 86.5188 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0592
6639 | 44.4444 | 86.5188 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06126
6640 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06105
6641 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06505
6642 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06527
6643 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06852
6644 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06422
6645 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0555
6646 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05087
6647 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0499
6648 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0455
6649 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04776
6650 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04428
6651 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0434
6652 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0446
6653 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0448
6654 | 2.7778 | 5.4074 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0443
6655 | 61.1111 | 118.9634 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04651
6656 | 238.8889 | 465.0386 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05203
6657 | 394.4444 | 767.8544 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05825
6658 | 502.7778 | 978.744 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05496
6659 | 475 | 924.6697 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0527
6660 | 444.4444 | 865.188 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05218
6661 | 405.5556 | 789.4841 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05151
6662 | 338.8889 | 659.7059 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05024
6663 | 280.5556 | 546.1499 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05089
6664 | 113.8889 | 221.7044 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05305
6665 | 36.1111 | 70.2965 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05859
6666 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06311
6667 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06709
6668 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06475
6669 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.056
6670 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.055
6671 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0509
6672 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04922
6673 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04394
6674 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04243
6675 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04399
6676 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.042
6677 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04208
6678 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0421
6679 | 30.5556 | 59.4817 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04397
6680 | 97.2222 | 189.2599 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.045
6681 | 97.2222 | 189.2599 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0497
6682 | 127.7778 | 248.7416 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05155
6683 | 183.3333 | 356.8901 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05152
6684 | 127.7778 | 248.7416 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05108
6685 | 113.8889 | 221.7044 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04955
6686 | 100 | 194.6673 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.048
6687 | 83.3333 | 162.2228 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.044
6688 | 55.5556 | 108.1485 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04392
6689 | 8.3333 | 16.2223 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05046
6690 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05309
6691 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05835
6692 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05341
6693 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04993
6694 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05036
6695 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04906
6696 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04399
6697 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04207
6698 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.042
6699 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04219
6700 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04128
6701 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04523
6702 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06288
6703 | 72.2222 | 140.5931 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07149
6704 | 230.5556 | 448.8163 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07486
6705 | 327.7778 | 638.0762 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07151
6706 | 400 | 778.6692 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06808
6707 | 408.3333 | 794.8915 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06675
6708 | 438.8889 | 854.3732 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06491
6709 | 319.4444 | 621.8539 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0638
6710 | 136.1111 | 264.9638 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06257
6711 | 58.3333 | 113.5559 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06304
6712 | 55.5556 | 108.1485 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06378
6713 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0665
6714 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06991
6715 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07676
6716 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06693
6717 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05803
6718 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05386
6719 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0426
6720 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04564
6721 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04293
6722 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04
6723 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03798
6724 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03655
6725 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0395
6726 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04552
6727 | 22.2222 | 43.2594 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05715
6728 | 75 | 146.0005 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06219
6729 | 94.4444 | 183.8525 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06008
6730 | 136.1111 | 264.9638 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05649
6731 | 125 | 243.3341 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05493
6732 | 155.5556 | 302.8158 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05134
6733 | 127.7778 | 248.7416 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05077
6734 | 122.2222 | 237.9267 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.048
6735 | 113.8889 | 221.7044 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05031
6736 | 66.6667 | 129.7782 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0512
6737 | 27.7778 | 54.0743 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05562
6738 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05944
6739 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06515
6740 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0525
6741 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04816
6742 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0435
6743 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0413
6744 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03919
6745 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.03863
6746 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03725
6747 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03444
6748 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03692
6749 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04022
6750 | 2.7778 | 5.4074 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.046
6751 | 25 | 48.6668 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05851
6752 | 72.2222 | 140.5931 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06073
6753 | 113.8889 | 221.7044 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06206
6754 | 161.1111 | 313.6307 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05762
6755 | 152.7778 | 297.4084 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05549
6756 | 250 | 486.6683 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0524
6757 | 191.6667 | 373.1123 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0507
6758 | 194.4444 | 378.5198 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05049
6759 | 133.3333 | 259.5564 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05025
6760 | 61.1111 | 118.9634 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04849
6761 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05573
6762 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0601
6763 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06644
6764 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05827
6765 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05313
6766 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0492
6767 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04308
6768 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03888
6769 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03793
6770 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03677
6771 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03339
6772 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03395
6773 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0372
6774 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04973
6775 | 44.4444 | 86.5188 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06097
6776 | 147.2222 | 286.5935 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06265
6777 | 269.4444 | 524.5202 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0591
6778 | 352.7778 | 686.743 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0535
6779 | 366.6667 | 713.7801 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0507
6780 | 269.4444 | 524.5202 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04625
6781 | 416.6667 | 811.1138 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04904
6782 | 216.6667 | 421.7792 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.045
6783 | 152.7778 | 297.4084 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04689
6784 | 108.3333 | 210.8896 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04416
6785 | 22.2222 | 43.2594 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05195
6786 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0583
6787 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06279
6788 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05678
6789 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.044
6790 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04339
6791 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04023
6792 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.03854
6793 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.03734
6794 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.03265
6795 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.02757
6796 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.02954
6797 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.03517
6798 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04094
6799 | 11.1111 | 21.6297 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05366
6800 | 41.6667 | 81.1114 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05584
6801 | 58.3333 | 113.5559 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05242
6802 | 127.7778 | 248.7416 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04903
6803 | 144.4444 | 281.1861 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05113
6804 | 83.3333 | 162.2228 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0509
6805 | 88.8889 | 173.0376 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04832
6806 | 77.7778 | 151.4079 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04655
6807 | 30.5556 | 59.4817 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04294
6808 | 11.1111 | 21.6297 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0399
6809 | 2.7778 | 5.4074 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04538
6810 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04865
6811 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04992
6812 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04619
6813 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0398
6814 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.039
6815 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.038
6816 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0328
6817 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0364
6818 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.037
6819 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0377
6820 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0358
6821 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0399
6822 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04
6823 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04718
6824 | 33.3333 | 64.8891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04465
6825 | 75 | 146.0005 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05219
6826 | 108.3333 | 210.8896 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0549
6827 | 83.3333 | 162.2228 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0524
6828 | 88.8889 | 173.0376 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.056
6829 | 86.1111 | 167.6302 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0513
6830 | 66.6667 | 129.7782 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0495
6831 | 27.7778 | 54.0743 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0474
6832 | 8.3333 | 16.2223 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04743
6833 | 2.7778 | 5.4074 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05082
6834 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05698
6835 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05965
6836 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05513
6837 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04815
6838 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04859
6839 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04653
6840 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04644
6841 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04066
6842 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03905
6843 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0361
6844 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03962
6845 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.03704
6846 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.03708
6847 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04122
6848 | 44.4444 | 86.5188 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04285
6849 | 94.4444 | 183.8525 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04158
6850 | 200 | 389.3346 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0401
6851 | 202.7778 | 394.742 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.039
6852 | 380.5556 | 740.8173 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03808
6853 | 461.1111 | 897.6326 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0368
6854 | 225 | 438.0014 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0368
6855 | 97.2222 | 189.2599 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0368
6856 | 50 | 97.3337 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03629
6857 | 11.1111 | 21.6297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04294
6858 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.045
6859 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0625
6860 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0474
6861 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0401
6862 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0366
6863 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.035
6864 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0412
6865 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0412
6866 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.039
6867 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03017
6868 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.031
6869 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.03963
6870 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05106
6871 | 33.3333 | 64.8891 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06392
6872 | 97.2222 | 189.2599 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06524
6873 | 136.1111 | 264.9638 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07106
6874 | 222.2222 | 432.594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06885
6875 | 305.5556 | 594.8168 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.063
6876 | 175 | 340.6678 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06025
6877 | 122.2222 | 237.9267 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.058
6878 | 247.2222 | 481.2608 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0545
6879 | 155.5556 | 302.8158 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05818
6880 | 58.3333 | 113.5559 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06134
6881 | 11.1111 | 21.6297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06339
6882 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06509
6883 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06779
6884 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06393
6885 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05201
6886 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05
6887 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04018
6888 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.041
6889 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04072
6890 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04
6891 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03927
6892 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04
6893 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04499
6894 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05561
6895 | 27.7778 | 54.0743 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06764
6896 | 69.4444 | 135.1856 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07021
6897 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0698
6898 | 116.6667 | 227.1119 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06676
6899 | 194.4444 | 378.5198 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06562
6900 | 155.5556 | 302.8158 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0629
6901 | 166.6667 | 324.4455 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06164
6902 | 247.2222 | 481.2608 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05958
6903 | 80.5556 | 156.8153 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06019
6904 | 22.2222 | 43.2594 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06198
6905 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06737
6906 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07333
6907 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08295
6908 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07029
6909 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06097
6910 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0545
6911 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04485
6912 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04981
6913 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04802
6914 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04425
6915 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0434
6916 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0437
6917 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0453
6918 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05368
6919 | 11.1111 | 21.6297 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06497
6920 | 47.2222 | 91.9262 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0663
6921 | 205.5556 | 400.1495 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06514
6922 | 347.2222 | 675.9282 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06199
6923 | 327.7778 | 638.0762 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05759
6924 | 186.1111 | 362.2975 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.051
6925 | 113.8889 | 221.7044 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.051
6926 | 100 | 194.6673 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05109
6927 | 52.7778 | 102.7411 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05198
6928 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05303
6929 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06199
6930 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06507
6931 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06243
6932 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.055
6933 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04806
6934 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04886
6935 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04587
6936 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04265
6937 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0431
6938 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0416
6939 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04134
6940 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04343
6941 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04629
6942 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05474
6943 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06713
6944 | 52.7778 | 102.7411 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06942
6945 | 136.1111 | 264.9638 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06903
6946 | 202.7778 | 394.742 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06643
6947 | 225 | 438.0014 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06543
6948 | 216.6667 | 421.7792 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0637
6949 | 280.5556 | 546.1499 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.058
6950 | 255.5556 | 497.4831 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05645
6951 | 166.6667 | 324.4455 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05977
6952 | 38.8889 | 75.704 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06353
6953 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06683
6954 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07162
6955 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07896
6956 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06934
6957 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06053
6958 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0536
6959 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04944
6960 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04815
6961 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04605
6962 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04331
6963 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0425
6964 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0414
6965 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04458
6966 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0532
6967 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06204
6968 | 141.6667 | 275.7787 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06646
6969 | 136.1111 | 264.9638 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.062
6970 | 144.4444 | 281.1861 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0537
6971 | 88.8889 | 173.0376 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.051
6972 | 230.5556 | 448.8163 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04276
6973 | 94.4444 | 183.8525 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0416
6974 | 177.7778 | 346.0752 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04226
6975 | 133.3333 | 259.5564 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0431
6976 | 58.3333 | 113.5559 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04378
6977 | 8.3333 | 16.2223 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05142
6978 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05179
6979 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05203
6980 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0449
6981 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.044
6982 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0428
6983 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0429
6984 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04204
6985 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04256
6986 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0404
6987 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0389
6988 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0392
6989 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04009
6990 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04189
6991 | 16.6667 | 32.4446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0447
6992 | 52.7778 | 102.7411 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04797
6993 | 47.2222 | 91.9262 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05014
6994 | 130.5556 | 254.149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.051
6995 | 91.6667 | 178.445 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05153
6996 | 177.7778 | 346.0752 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0502
6997 | 241.6667 | 470.446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04908
6998 | 111.1111 | 216.297 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0483
6999 | 105.5556 | 205.4822 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04807
7000 | 63.8889 | 124.3708 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05004
7001 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05348
7002 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05908
7003 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0629
7004 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05419
7005 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05006
7006 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05005
7007 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04818
7008 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04499
7009 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04101
7010 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04201
7011 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0419
7012 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04151
7013 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0413
7014 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04203
7015 | 16.6667 | 32.4446 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04494
7016 | 105.5556 | 205.4822 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04674
7017 | 83.3333 | 162.2228 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05137
7018 | 83.3333 | 162.2228 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05247
7019 | 88.8889 | 173.0376 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05332
7020 | 88.8889 | 173.0376 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0529
7021 | 77.7778 | 151.4079 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05002
7022 | 91.6667 | 178.445 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04604
7023 | 58.3333 | 113.5559 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0478
7024 | 36.1111 | 70.2965 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05073
7025 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05538
7026 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06258
7027 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06606
7028 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0621
7029 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05462
7030 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05309
7031 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.051
7032 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04534
7033 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04211
7034 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04128
7035 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04079
7036 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0407
7037 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04139
7038 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05301
7039 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06693
7040 | 16.6667 | 32.4446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06743
7041 | 52.7778 | 102.7411 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06684
7042 | 163.8889 | 319.0381 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0646
7043 | 266.6667 | 519.1128 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06443
7044 | 172.2222 | 335.2604 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05975
7045 | 141.6667 | 275.7787 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05873
7046 | 83.3333 | 162.2228 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06016
7047 | 97.2222 | 189.2599 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06271
7048 | 19.4444 | 37.852 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06503
7049 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06911
7050 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07302
7051 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08151
7052 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0672
7053 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0639
7054 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05592
7055 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05068
7056 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05382
7057 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05088
7058 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04964
7059 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04684
7060 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04855
7061 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0512
7062 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06199
7063 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07143
7064 | 61.1111 | 118.9634 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0763
7065 | 94.4444 | 183.8525 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.075
7066 | 230.5556 | 448.8163 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07049
7067 | 205.5556 | 400.1495 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06772
7068 | 205.5556 | 400.1495 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05982
7069 | 180.5556 | 351.4826 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.055
7070 | 130.5556 | 254.149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.057
7071 | 158.3333 | 308.2232 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05788
7072 | 41.6667 | 81.1114 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06124
7073 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06693
7074 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.075
7075 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08047
7076 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06697
7077 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06015
7078 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0545
7079 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05148
7080 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05052
7081 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04731
7082 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04636
7083 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04509
7084 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04539
7085 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0494
7086 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0557
7087 | 8.3333 | 16.2223 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0674
7088 | 36.1111 | 70.2965 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07477
7089 | 94.4444 | 183.8525 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07212
7090 | 127.7778 | 248.7416 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06911
7091 | 222.2222 | 432.594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06623
7092 | 291.6667 | 567.7796 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05701
7093 | 363.8889 | 708.3727 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05446
7094 | 280.5556 | 546.1499 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05387
7095 | 175 | 340.6678 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0568
7096 | 55.5556 | 108.1485 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06087
7097 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06567
7098 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06849
7099 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0701
7100 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05545
7101 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05317
7102 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05238
7103 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04875
7104 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04855
7105 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04604
7106 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04502
7107 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04441
7108 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04506
7109 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04789
7110 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05455
7111 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06398
7112 | 58.3333 | 113.5559 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06911
7113 | 94.4444 | 183.8525 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06911
7114 | 161.1111 | 313.6307 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06608
7115 | 258.3333 | 502.8905 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06193
7116 | 200 | 389.3346 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05866
7117 | 200 | 389.3346 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05539
7118 | 263.8889 | 513.7054 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05297
7119 | 205.5556 | 400.1495 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05178
7120 | 44.4444 | 86.5188 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05281
7121 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0549
7122 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05841
7123 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05313
7124 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05067
7125 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04507
7126 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04521
7127 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04103
7128 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.042
7129 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04027
7130 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0402
7131 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03942
7132 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0402
7133 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04322
7134 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05106
7135 | 8.3333 | 16.2223 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0629
7136 | 66.6667 | 129.7782 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06652
7137 | 161.1111 | 313.6307 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06168
7138 | 183.3333 | 356.8901 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05949
7139 | 283.3333 | 551.5574 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05476
7140 | 358.3333 | 697.5579 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05065
7141 | 247.2222 | 481.2608 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05107
7142 | 236.1111 | 459.6311 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04978
7143 | 152.7778 | 297.4084 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05033
7144 | 50 | 97.3337 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05192
7145 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05883
7146 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06311
7147 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06169
7148 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05105
7149 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04821
7150 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04535
7151 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04051
7152 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0408
7153 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.041
7154 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0389
7155 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.035
7156 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.032
7157 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0389
7158 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0402
7159 | 5.5556 | 10.8149 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0418
7160 | 38.8889 | 75.704 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0465
7161 | 105.5556 | 205.4822 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05113
7162 | 280.5556 | 546.1499 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04432
7163 | 286.1111 | 556.9648 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.044
7164 | 369.4444 | 719.1876 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0418
7165 | 363.8889 | 708.3727 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0468
7166 | 280.5556 | 546.1499 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0468
7167 | 108.3333 | 210.8896 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.042
7168 | 25 | 48.6668 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04554
7169 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05122
7170 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05297
7171 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05237
7172 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05077
7173 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05005
7174 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04682
7175 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04181
7176 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04721
7177 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04211
7178 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04
7179 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0407
7180 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03786
7181 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03147
7182 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03439
7183 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03604
7184 | 61.1111 | 118.9634 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0417
7185 | 125 | 243.3341 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04398
7186 | 219.4444 | 427.1866 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0487
7187 | 261.1111 | 508.298 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05107
7188 | 308.3333 | 600.2242 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.045
7189 | 219.4444 | 427.1866 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04344
7190 | 238.8889 | 465.0386 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.043
7191 | 186.1111 | 362.2975 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.043
7192 | 63.8889 | 124.3708 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0461
7193 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0513
7194 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05944
7195 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05753
7196 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05632
7197 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05106
7198 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04906
7199 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04485
7200 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04082
7201 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0414
7202 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0416
7203 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0419
7204 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04264
7205 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04293
7206 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04597
7207 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05427
7208 | 105.5556 | 205.4822 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06347
7209 | 225 | 438.0014 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06093
7210 | 302.7778 | 589.4093 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05901
7211 | 241.6667 | 470.446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05806
7212 | 216.6667 | 421.7792 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05733
7213 | 263.8889 | 513.7054 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05558
7214 | 191.6667 | 373.1123 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05727
7215 | 144.4444 | 281.1861 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06383
7216 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06555
7217 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06999
7218 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07623
7219 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07862
7220 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07239
7221 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06369
7222 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05652
7223 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05466
7224 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05085
7225 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05192
7226 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0515
7227 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05083
7228 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0502
7229 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05017
7230 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.051
7231 | 8.3333 | 16.2223 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05826
7232 | 94.4444 | 183.8525 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0685
7233 | 216.6667 | 421.7792 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07081
7234 | 313.8889 | 611.0391 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07001
7235 | 369.4444 | 719.1876 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06537
7236 | 447.2222 | 870.5955 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06527
7237 | 255.5556 | 497.4831 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0601
7238 | 175 | 340.6678 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06164
7239 | 136.1111 | 264.9638 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0673
7240 | 44.4444 | 86.5188 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07001
7241 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0722
7242 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07744
7243 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08118
7244 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07575
7245 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06885
7246 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06076
7247 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05512
7248 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05234
7249 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05245
7250 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05139
7251 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05114
7252 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05058
7253 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05115
7254 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05272
7255 | 8.3333 | 16.2223 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0599
7256 | 113.8889 | 221.7044 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06912
7257 | 205.5556 | 400.1495 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0726
7258 | 305.5556 | 594.8168 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06892
7259 | 363.8889 | 708.3727 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0605
7260 | 388.8889 | 757.0395 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05748
7261 | 358.3333 | 697.5579 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05421
7262 | 269.4444 | 524.5202 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0542
7263 | 163.8889 | 319.0381 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05688
7264 | 41.6667 | 81.1114 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06731
7265 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07117
7266 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07657
7267 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0817
7268 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.075
7269 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06712
7270 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05842
7271 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05476
7272 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0479
7273 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04925
7274 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04923
7275 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04892
7276 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04816
7277 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04837
7278 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05023
7279 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0549
7280 | 83.3333 | 162.2228 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06019
7281 | 208.3333 | 405.5569 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05956
7282 | 313.8889 | 611.0391 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06021
7283 | 377.7778 | 735.4098 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05552
7284 | 388.8889 | 757.0395 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05382
7285 | 350 | 681.3356 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05204
7286 | 263.8889 | 513.7054 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05309
7287 | 158.3333 | 308.2232 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05771
7288 | 36.1111 | 70.2965 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0617
7289 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06608
7290 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07101
7291 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07044
7292 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06197
7293 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0599
7294 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05708
7295 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05393
7296 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05104
7297 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05094
7298 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04849
7299 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04399
7300 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04212
7301 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04117
7302 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04114
7303 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0441
7304 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04992
7305 | 47.2222 | 91.9262 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04927
7306 | 61.1111 | 118.9634 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05007
7307 | 69.4444 | 135.1856 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05346
7308 | 102.7778 | 200.0747 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04904
7309 | 66.6667 | 129.7782 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0509
7310 | 38.8889 | 75.704 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04843
7311 | 22.2222 | 43.2594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0465
7312 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04652
7313 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04659
7314 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.053
7315 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05308
7316 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05201
7317 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04698
7318 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04511
7319 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04549
7320 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04306
7321 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0465
7322 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04507
7323 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0411
7324 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04
7325 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03399
7326 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03686
7327 | 2.7778 | 5.4074 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04098
7328 | 36.1111 | 70.2965 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0507
7329 | 86.1111 | 167.6302 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05159
7330 | 116.6667 | 227.1119 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05295
7331 | 80.5556 | 156.8153 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05343
7332 | 275 | 535.3351 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0521
7333 | 311.1111 | 605.6316 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0453
7334 | 238.8889 | 465.0386 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.045
7335 | 116.6667 | 227.1119 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0426
7336 | 30.5556 | 59.4817 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04294
7337 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.045
7338 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04891
7339 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05444
7340 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05231
7341 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05188
7342 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04285
7343 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04381
7344 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.044
7345 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.036
7346 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0407
7347 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0417
7348 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0417
7349 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04
7350 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04086
7351 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04335
7352 | 33.3333 | 64.8891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0404
7353 | 119.4444 | 232.5193 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0392
7354 | 222.2222 | 432.594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04411
7355 | 300 | 584.0019 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04473
7356 | 175 | 340.6678 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04911
7357 | 75 | 146.0005 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05276
7358 | 102.7778 | 200.0747 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05126
7359 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05092
7360 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05098
7361 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05319
7362 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05622
7363 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05783
7364 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05604
7365 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05329
7366 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0493
7367 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04637
7368 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04146
7369 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04168
7370 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03994
7371 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03751
7372 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03382
7373 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03326
7374 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03881
7375 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0505
7376 | 30.5556 | 59.4817 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05856
7377 | 61.1111 | 118.9634 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06035
7378 | 130.5556 | 254.149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06007
7379 | 313.8889 | 611.0391 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05897
7380 | 213.8889 | 416.3717 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05833
7381 | 152.7778 | 297.4084 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05671
7382 | 136.1111 | 264.9638 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05865
7383 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05939
7384 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06138
7385 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06289
7386 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06789
7387 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06792
7388 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06391
7389 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05921
7390 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05295
7391 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0505
7392 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.045
7393 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0415
7394 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04064
7395 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04097
7396 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03999
7397 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04104
7398 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04294
7399 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05392
7400 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06052
7401 | 27.7778 | 54.0743 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06297
7402 | 41.6667 | 81.1114 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06243
7403 | 83.3333 | 162.2228 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06298
7404 | 180.5556 | 351.4826 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06343
7405 | 244.4444 | 475.8534 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06196
7406 | 91.6667 | 178.445 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06334
7407 | 41.6667 | 81.1114 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06491
7408 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.065
7409 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06504
7410 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07571
7411 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07789
7412 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0673
7413 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06256
7414 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0583
7415 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05621
7416 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0533
7417 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05197
7418 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05075
7419 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04927
7420 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04879
7421 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04945
7422 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05274
7423 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06063
7424 | 27.7778 | 54.0743 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07077
7425 | 141.6667 | 275.7787 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07277
7426 | 138.8889 | 270.3713 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07192
7427 | 152.7778 | 297.4084 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0718
7428 | 333.3333 | 648.891 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07144
7429 | 125 | 243.3341 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06942
7430 | 180.5556 | 351.4826 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0708
7431 | 88.8889 | 173.0376 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07228
7432 | 16.6667 | 32.4446 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07239
7433 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07571
7434 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.09108
7435 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.10212
7436 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.08
7437 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06947
7438 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06252
7439 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05959
7440 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0553
7441 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05407
7442 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05095
7443 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0484
7444 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04767
7445 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0479
7446 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05025
7447 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05749
7448 | 16.6667 | 32.4446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06312
7449 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06629
7450 | 47.2222 | 91.9262 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06356
7451 | 105.5556 | 205.4822 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06254
7452 | 108.3333 | 210.8896 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06136
7453 | 108.3333 | 210.8896 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05891
7454 | 27.7778 | 54.0743 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05957
7455 | 38.8889 | 75.704 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06061
7456 | 5.5556 | 10.8149 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06183
7457 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06368
7458 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06617
7459 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06319
7460 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06172
7461 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05998
7462 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0528
7463 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0523
7464 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0491
7465 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04582
7466 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0466
7467 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04707
7468 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04682
7469 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04819
7470 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05022
7471 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0599
7472 | 47.2222 | 91.9262 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06649
7473 | 175 | 340.6678 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06932
7474 | 266.6667 | 519.1128 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07041
7475 | 333.3333 | 648.891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06981
7476 | 350 | 681.3356 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06882
7477 | 316.6667 | 616.4465 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06744
7478 | 241.6667 | 470.446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06752
7479 | 125 | 243.3341 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06801
7480 | 16.6667 | 32.4446 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06719
7481 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0693
7482 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08147
7483 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07498
7484 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06697
7485 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06141
7486 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05869
7487 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0588
7488 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05434
7489 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05763
7490 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05478
7491 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05381
7492 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05194
7493 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0512
7494 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05113
7495 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05457
7496 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05656
7497 | 33.3333 | 64.8891 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05702
7498 | 83.3333 | 162.2228 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05957
7499 | 138.8889 | 270.3713 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05915
7500 | 61.1111 | 118.9634 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05755
7501 | 75 | 146.0005 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05642
7502 | 47.2222 | 91.9262 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05501
7503 | 33.3333 | 64.8891 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05496
7504 | 13.8889 | 27.0371 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05667
7505 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05881
7506 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06495
7507 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.066
7508 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06345
7509 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05775
7510 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05536
7511 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05466
7512 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05167
7513 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05257
7514 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0503
7515 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05013
7516 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04922
7517 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04886
7518 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05001
7519 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0506
7520 | 41.6667 | 81.1114 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05252
7521 | 163.8889 | 319.0381 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05252
7522 | 252.7778 | 492.0757 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05412
7523 | 327.7778 | 638.0762 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0534
7524 | 344.4444 | 670.5207 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05384
7525 | 316.6667 | 616.4465 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0551
7526 | 238.8889 | 465.0386 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0528
7527 | 125 | 243.3341 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05468
7528 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05635
7529 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06141
7530 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06717
7531 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06809
7532 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06751
7533 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06601
7534 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.062
7535 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05908
7536 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.054
7537 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05066
7538 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0508
7539 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05094
7540 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04975
7541 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0498
7542 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05158
7543 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.058
7544 | 16.6667 | 32.4446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06243
7545 | 52.7778 | 102.7411 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.066
7546 | 80.5556 | 156.8153 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06485
7547 | 116.6667 | 227.1119 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.063
7548 | 113.8889 | 221.7044 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06229
7549 | 105.5556 | 205.4822 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06
7550 | 36.1111 | 70.2965 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0606
7551 | 16.6667 | 32.4446 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05877
7552 | 8.3333 | 16.2223 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05892
7553 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05937
7554 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06339
7555 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06039
7556 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05536
7557 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05026
7558 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0504
7559 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0495
7560 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0496
7561 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0523
7562 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.051
7563 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0493
7564 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0476
7565 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0473
7566 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0503
7567 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05542
7568 | 11.1111 | 21.6297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05887
7569 | 33.3333 | 64.8891 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05899
7570 | 36.1111 | 70.2965 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.058
7571 | 38.8889 | 75.704 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05742
7572 | 152.7778 | 297.4084 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05703
7573 | 116.6667 | 227.1119 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0555
7574 | 63.8889 | 124.3708 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05601
7575 | 108.3333 | 210.8896 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05974
7576 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06604
7577 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06604
7578 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07405
7579 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.065
7580 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.058
7581 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05638
7582 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05464
7583 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05426
7584 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0496
7585 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.049
7586 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0489
7587 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0493
7588 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04968
7589 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04972
7590 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0499
7591 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05571
7592 | 16.6667 | 32.4446 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0627
7593 | 69.4444 | 135.1856 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06708
7594 | 197.2222 | 383.9272 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06656
7595 | 219.4444 | 427.1866 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06512
7596 | 211.1111 | 410.9643 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06559
7597 | 97.2222 | 189.2599 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06397
7598 | 72.2222 | 140.5931 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07012
7599 | 94.4444 | 183.8525 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07098
7600 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07342
7601 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07851
7602 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09559
7603 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07109
7604 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06794
7605 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06122
7606 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05791
7607 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05514
7608 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.053
7609 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05202
7610 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05285
7611 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05151
7612 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05037
7613 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05077
7614 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05314
7615 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05942
7616 | 16.6667 | 32.4446 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06622
7617 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06732
7618 | 86.1111 | 167.6302 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0641
7619 | 113.8889 | 221.7044 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06224
7620 | 213.8889 | 416.3717 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06295
7621 | 194.4444 | 378.5198 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06364
7622 | 105.5556 | 205.4822 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06562
7623 | 33.3333 | 64.8891 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0687
7624 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06912
7625 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07115
7626 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07614
7627 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0648
7628 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0601
7629 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05769
7630 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05705
7631 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05365
7632 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05038
7633 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0474
7634 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0471
7635 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.045
7636 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.048
7637 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.048
7638 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.048
7639 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0511
7640 | 11.1111 | 21.6297 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05473
7641 | 41.6667 | 81.1114 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05586
7642 | 33.3333 | 64.8891 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05561
7643 | 55.5556 | 108.1485 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05538
7644 | 38.8889 | 75.704 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0555
7645 | 38.8889 | 75.704 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05502
7646 | 27.7778 | 54.0743 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05512
7647 | 22.2222 | 43.2594 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05714
7648 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06041
7649 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.064
7650 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.076
7651 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06091
7652 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0588
7653 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05792
7654 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05635
7655 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05504
7656 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05346
7657 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05198
7658 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05207
7659 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05153
7660 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05219
7661 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05232
7662 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05249
7663 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05342
7664 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05401
7665 | 38.8889 | 75.704 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05747
7666 | 97.2222 | 189.2599 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05813
7667 | 105.5556 | 205.4822 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05651
7668 | 80.5556 | 156.8153 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0569
7669 | 61.1111 | 118.9634 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05397
7670 | 47.2222 | 91.9262 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05394
7671 | 36.1111 | 70.2965 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05512
7672 | 8.3333 | 16.2223 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05519
7673 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05761
7674 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05887
7675 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0572
7676 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05432
7677 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.052
7678 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04923
7679 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0493
7680 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0497
7681 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0479
7682 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0475
7683 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0497
7684 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04723
7685 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04786
7686 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04875
7687 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04749
7688 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04888
7689 | 63.8889 | 124.3708 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05185
7690 | 111.1111 | 216.297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05381
7691 | 216.6667 | 421.7792 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05472
7692 | 272.2222 | 529.9277 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05576
7693 | 188.8889 | 367.7049 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05515
7694 | 138.8889 | 270.3713 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05425
7695 | 66.6667 | 129.7782 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05406
7696 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05483
7697 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05615
7698 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06044
7699 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05867
7700 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0576
7701 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05518
7702 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0536
7703 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05006
7704 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0473
7705 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03976
7706 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04283
7707 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0415
7708 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04316
7709 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0449
7710 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.049
7711 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05502
7712 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05676
7713 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06087
7714 | 33.3333 | 64.8891 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06137
7715 | 63.8889 | 124.3708 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06338
7716 | 50 | 97.3337 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06479
7717 | 33.3333 | 64.8891 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06381
7718 | 19.4444 | 37.852 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06658
7719 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0648
7720 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06787
7721 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07
7722 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06994
7723 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05867
7724 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05662
7725 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05439
7726 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0503
7727 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04889
7728 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0478
7729 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0473
7730 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0478
7731 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0472
7732 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.047
7733 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.047
7734 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0502
7735 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05336
7736 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05832
7737 | 72.2222 | 140.5931 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05986
7738 | 158.3333 | 308.2232 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05838
7739 | 230.5556 | 448.8163 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05808
7740 | 283.3333 | 551.5574 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05815
7741 | 236.1111 | 459.6311 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05835
7742 | 147.2222 | 286.5935 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06297
7743 | 66.6667 | 129.7782 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0699
7744 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07681
7745 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08543
7746 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0951
7747 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.09109
7748 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.08653
7749 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07397
7750 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06195
7751 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05563
7752 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05303
7753 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0505
7754 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0484
7755 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0487
7756 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05028
7757 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0511
7758 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.053
7759 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06505
7760 | 13.8889 | 27.0371 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.074
7761 | 47.2222 | 91.9262 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0801
7762 | 80.5556 | 156.8153 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07945
7763 | 97.2222 | 189.2599 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07507
7764 | 88.8889 | 173.0376 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07427
7765 | 83.3333 | 162.2228 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07223
7766 | 52.7778 | 102.7411 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07261
7767 | 19.4444 | 37.852 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07482
7768 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07569
7769 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07764
7770 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08605
7771 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07606
7772 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0651
7773 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06366
7774 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05662
7775 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0504
7776 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0516
7777 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05
7778 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05
7779 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05086
7780 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0485
7781 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05121
7782 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05357
7783 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05851
7784 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07044
7785 | 27.7778 | 54.0743 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06672
7786 | 75 | 146.0005 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06929
7787 | 108.3333 | 210.8896 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07224
7788 | 188.8889 | 367.7049 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07239
7789 | 175 | 340.6678 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06833
7790 | 136.1111 | 264.9638 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07192
7791 | 77.7778 | 151.4079 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07122
7792 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07151
7793 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0737
7794 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07838
7795 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06811
7796 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06478
7797 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05855
7798 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05519
7799 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05292
7800 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0515
7801 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0485
7802 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0495
7803 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0492
7804 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0495
7805 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0504
7806 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05183
7807 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05041
7808 | 11.1111 | 21.6297 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06577
7809 | 38.8889 | 75.704 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06658
7810 | 108.3333 | 210.8896 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0649
7811 | 188.8889 | 367.7049 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06369
7812 | 277.7778 | 540.7425 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06223
7813 | 238.8889 | 465.0386 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0601
7814 | 147.2222 | 286.5935 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06091
7815 | 58.3333 | 113.5559 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06403
7816 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0645
7817 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06404
7818 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06691
7819 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05845
7820 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0535
7821 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05456
7822 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05427
7823 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05332
7824 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05049
7825 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04936
7826 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0505
7827 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0505
7828 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04817
7829 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04503
7830 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04322
7831 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04739
7832 | 13.8889 | 27.0371 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05114
7833 | 66.6667 | 129.7782 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05245
7834 | 88.8889 | 173.0376 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05998
7835 | 116.6667 | 227.1119 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06709
7836 | 188.8889 | 367.7049 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06763
7837 | 141.6667 | 275.7787 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0728
7838 | 86.1111 | 167.6302 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.065
7839 | 36.1111 | 70.2965 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06442
7840 | 5.5556 | 10.8149 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06323
7841 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06612
7842 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.07643
7843 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.069
7844 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0549
7845 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05254
7846 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0549
7847 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05194
7848 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0511
7849 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0516
7850 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.053
7851 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05174
7852 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0504
7853 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0546
7854 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0533
7855 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05143
7856 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06331
7857 | 72.2222 | 140.5931 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06012
7858 | 163.8889 | 319.0381 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06685
7859 | 197.2222 | 383.9272 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05255
7860 | 188.8889 | 367.7049 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05481
7861 | 191.6667 | 373.1123 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05481
7862 | 116.6667 | 227.1119 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05476
7863 | 55.5556 | 108.1485 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05505
7864 | 8.3333 | 16.2223 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05668
7865 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06001
7866 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.065
7867 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06677
7868 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06511
7869 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06496
7870 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0607
7871 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05964
7872 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0548
7873 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05319
7874 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0513
7875 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05102
7876 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0504
7877 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05038
7878 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05284
7879 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.065
7880 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07542
7881 | 13.8889 | 27.0371 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07337
7882 | 69.4444 | 135.1856 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07342
7883 | 186.1111 | 362.2975 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0723
7884 | 252.7778 | 492.0757 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07326
7885 | 211.1111 | 410.9643 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07377
7886 | 80.5556 | 156.8153 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0736
7887 | 44.4444 | 86.5188 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07205
7888 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07423
7889 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0734
7890 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07845
7891 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07436
7892 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07307
7893 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06893
7894 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06517
7895 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06028
7896 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05445
7897 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05407
7898 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05343
7899 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0512
7900 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05091
7901 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05098
7902 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05301
7903 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06021
7904 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06839
7905 | 27.7778 | 54.0743 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06979
7906 | 44.4444 | 86.5188 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06958
7907 | 72.2222 | 140.5931 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06979
7908 | 66.6667 | 129.7782 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06905
7909 | 77.7778 | 151.4079 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06791
7910 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06759
7911 | 19.4444 | 37.852 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06799
7912 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06734
7913 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06743
7914 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06955
7915 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06952
7916 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0679
7917 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06251
7918 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05853
7919 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05728
7920 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05274
7921 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0512
7922 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05032
7923 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04784
7924 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04523
7925 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04665
7926 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0498
7927 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05694
7928 | 2.7778 | 5.4074 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06568
7929 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06554
7930 | 69.4444 | 135.1856 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06821
7931 | 100 | 194.6673 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06326
7932 | 144.4444 | 281.1861 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06038
7933 | 66.6667 | 129.7782 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05912
7934 | 36.1111 | 70.2965 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05887
7935 | 30.5556 | 59.4817 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05867
7936 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0589
7937 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05988
7938 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06219
7939 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06272
7940 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.059
7941 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05755
7942 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0544
7943 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.054
7944 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05358
7945 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05534
7946 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05131
7947 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.049
7948 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04695
7949 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.043
7950 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04354
7951 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05302
7952 | 2.7778 | 5.4074 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.065
7953 | 11.1111 | 21.6297 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.06595
7954 | 30.5556 | 59.4817 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06693
7955 | 44.4444 | 86.5188 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.06405
7956 | 91.6667 | 178.445 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06427
7957 | 111.1111 | 216.297 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0622
7958 | 58.3333 | 113.5559 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06088
7959 | 16.6667 | 32.4446 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0593
7960 | 2.7778 | 5.4074 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06239
7961 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0627
7962 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.075
7963 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0711
7964 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0695
7965 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07464
7966 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0649
7967 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05949
7968 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05572
7969 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05657
7970 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05274
7971 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05239
7972 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05249
7973 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0523
7974 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0515
7975 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05935
7976 | 11.1111 | 21.6297 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06971
7977 | 88.8889 | 173.0376 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07149
7978 | 161.1111 | 313.6307 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07443
7979 | 216.6667 | 421.7792 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07294
7980 | 158.3333 | 308.2232 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.065
7981 | 183.3333 | 356.8901 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05665
7982 | 77.7778 | 151.4079 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05862
7983 | 38.8889 | 75.704 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06291
7984 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06604
7985 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06714
7986 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06913
7987 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06903
7988 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06413
7989 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06561
7990 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05778
7991 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05724
7992 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05428
7993 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05129
7994 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05379
7995 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05144
7996 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05039
7997 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05039
7998 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05103
7999 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05156
8000 | 11.1111 | 21.6297 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05908
8001 | 97.2222 | 189.2599 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05729
8002 | 180.5556 | 351.4826 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06035
8003 | 233.3333 | 454.2237 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.059
8004 | 255.5556 | 497.4831 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0577
8005 | 238.8889 | 465.0386 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0565
8006 | 163.8889 | 319.0381 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05577
8007 | 41.6667 | 81.1114 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05614
8008 | 2.7778 | 5.4074 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05802
8009 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06376
8010 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0679
8011 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.0681
8012 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06501
8013 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06235
8014 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05742
8015 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05694
8016 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05513
8017 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05355
8018 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05207
8019 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05126
8020 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05093
8021 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05086
8022 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05092
8023 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05113
8024 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05204
8025 | 30.5556 | 59.4817 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05374
8026 | 69.4444 | 135.1856 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05712
8027 | 88.8889 | 173.0376 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05977
8028 | 80.5556 | 156.8153 | 0 | 0 | 0 | 0 | #DIV/0! | 0.063
8029 | 91.6667 | 178.445 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06315
8030 | 72.2222 | 140.5931 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06076
8031 | 33.3333 | 64.8891 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0597
8032 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05998
8033 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06279
8034 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06545
8035 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0674
8036 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0651
8037 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0585
8038 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05707
8039 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0549
8040 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05283
8041 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05103
8042 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05193
8043 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0504
8044 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04946
8045 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0504
8046 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0513
8047 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05972
8048 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06797
8049 | 63.8889 | 124.3708 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07
8050 | 141.6667 | 275.7787 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06909
8051 | 197.2222 | 383.9272 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06181
8052 | 236.1111 | 459.6311 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06003
8053 | 211.1111 | 410.9643 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05696
8054 | 147.2222 | 286.5935 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05928
8055 | 33.3333 | 64.8891 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06471
8056 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06795
8057 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07405
8058 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08893
8059 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08122
8060 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.075
8061 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06943
8062 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06433
8063 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05799
8064 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05558
8065 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05504
8066 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05232
8067 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05324
8068 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05316
8069 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05442
8070 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05781
8071 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07007
8072 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.08228
8073 | 69.4444 | 135.1856 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.09147
8074 | 169.4444 | 329.8529 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.086
8075 | 197.2222 | 383.9272 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07549
8076 | 216.6667 | 421.7792 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07431
8077 | 133.3333 | 259.5564 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07024
8078 | 127.7778 | 248.7416 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0683
8079 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07163
8080 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07259
8081 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.075
8082 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.08684
8083 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0649
8084 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06232
8085 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05767
8086 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05648
8087 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05347
8088 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05205
8089 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05
8090 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05
8091 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05024
8092 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05058
8093 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05129
8094 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05194
8095 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05826
8096 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0684
8097 | 66.6667 | 129.7782 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06976
8098 | 166.6667 | 324.4455 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07301
8099 | 225 | 438.0014 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0724
8100 | 236.1111 | 459.6311 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06707
8101 | 216.6667 | 421.7792 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0649
8102 | 144.4444 | 281.1861 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06649
8103 | 36.1111 | 70.2965 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07111
8104 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0733
8105 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.07769
8106 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.09283
8107 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.09251
8108 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0751
8109 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.06793
8110 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06
8111 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05563
8112 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05257
8113 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05116
8114 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05073
8115 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05086
8116 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05075
8117 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05056
8118 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.051
8119 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05214
8120 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0633
8121 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07329
8122 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07666
8123 | 72.2222 | 140.5931 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07215
8124 | 94.4444 | 183.8525 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06072
8125 | 155.5556 | 302.8158 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05695
8126 | 113.8889 | 221.7044 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05686
8127 | 27.7778 | 54.0743 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05538
8128 | 2.7778 | 5.4074 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05774
8129 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0599
8130 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0599
8131 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05541
8132 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0549
8133 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05435
8134 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05145
8135 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05023
8136 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.047
8137 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04855
8138 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0462
8139 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.037
8140 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0304
8141 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.03614
8142 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04267
8143 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0479
8144 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0557
8145 | 8.3333 | 16.2223 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05631
8146 | 13.8889 | 27.0371 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0649
8147 | 25 | 48.6668 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0658
8148 | 27.7778 | 54.0743 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0635
8149 | 22.2222 | 43.2594 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05955
8150 | 13.8889 | 27.0371 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0586
8151 | 5.5556 | 10.8149 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05548
8152 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05725
8153 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05966
8154 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0591
8155 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05399
8156 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05218
8157 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0501
8158 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05098
8159 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.051
8160 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0483
8161 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0457
8162 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0489
8163 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.045
8164 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04286
8165 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0405
8166 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0465
8167 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0475
8168 | 2.7778 | 5.4074 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0489
8169 | 16.6667 | 32.4446 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.048
8170 | 50 | 97.3337 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05695
8171 | 75 | 146.0005 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05429
8172 | 69.4444 | 135.1856 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05416
8173 | 44.4444 | 86.5188 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0525
8174 | 30.5556 | 59.4817 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05126
8175 | 13.8889 | 27.0371 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05408
8176 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05441
8177 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05972
8178 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06346
8179 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0664
8180 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05813
8181 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05017
8182 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05005
8183 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05107
8184 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04548
8185 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.03697
8186 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.03576
8187 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.02209
8188 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.01614
8189 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.01501
8190 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.015
8191 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.01501
8192 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.01722
8193 | 5.5556 | 10.8149 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0449
8194 | 13.8889 | 27.0371 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04675
8195 | 33.3333 | 64.8891 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05179
8196 | 55.5556 | 108.1485 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05191
8197 | 55.5556 | 108.1485 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05166
8198 | 61.1111 | 118.9634 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05167
8199 | 36.1111 | 70.2965 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05183
8200 | 2.7778 | 5.4074 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05443
8201 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05373
8202 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.07416
8203 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06
8204 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.058
8205 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0512
8206 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05
8207 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0499
8208 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0456
8209 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0371
8210 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.03308
8211 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.02854
8212 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.015
8213 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.01153
8214 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0151
8215 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.045
8216 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0569
8217 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05833
8218 | 58.3333 | 113.5559 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06115
8219 | 147.2222 | 286.5935 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06127
8220 | 130.5556 | 254.149 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0592
8221 | 125 | 243.3341 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05623
8222 | 58.3333 | 113.5559 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05625
8223 | 13.8889 | 27.0371 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05629
8224 | 2.7778 | 5.4074 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05589
8225 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05649
8226 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06234
8227 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05484
8228 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05362
8229 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04912
8230 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0476
8231 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04695
8232 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0454
8233 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0456
8234 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.046
8235 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.046
8236 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04645
8237 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04709
8238 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04993
8239 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06111
8240 | 8.3333 | 16.2223 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0681
8241 | 52.7778 | 102.7411 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.07138
8242 | 130.5556 | 254.149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06993
8243 | 216.6667 | 421.7792 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.066
8244 | 225 | 438.0014 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0649
8245 | 216.6667 | 421.7792 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06234
8246 | 97.2222 | 189.2599 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06199
8247 | 33.3333 | 64.8891 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06183
8248 | 2.7778 | 5.4074 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06122
8249 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.06041
8250 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.06221
8251 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0479
8252 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0463
8253 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.04824
8254 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05
8255 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0451
8256 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.03994
8257 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.045
8258 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.0301
8259 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.036
8260 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04527
8261 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04531
8262 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04911
8263 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05214
8264 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05417
8265 | 8.3333 | 16.2223 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06664
8266 | 44.4444 | 86.5188 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06803
8267 | 58.3333 | 113.5559 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06803
8268 | 91.6667 | 178.445 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06438
8269 | 80.5556 | 156.8153 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06464
8270 | 66.6667 | 129.7782 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06682
8271 | 36.1111 | 70.2965 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06629
8272 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06679
8273 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06786
8274 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07523
8275 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.07136
8276 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06846
8277 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06222
8278 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0597
8279 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05263
8280 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05217
8281 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.052
8282 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05083
8283 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05002
8284 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04965
8285 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05018
8286 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05198
8287 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.064
8288 | 2.7778 | 5.4074 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07264
8289 | 44.4444 | 86.5188 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0766
8290 | 94.4444 | 183.8525 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0751
8291 | 133.3333 | 259.5564 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.069
8292 | 152.7778 | 297.4084 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06469
8293 | 166.6667 | 324.4455 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.064
8294 | 119.4444 | 232.5193 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06187
8295 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06215
8296 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06375
8297 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06269
8298 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06713
8299 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06205
8300 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05536
8301 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05304
8302 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05113
8303 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05007
8304 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04927
8305 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0451
8306 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04342
8307 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.044
8308 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0349
8309 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.036
8310 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0426
8311 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04783
8312 | 2.7778 | 5.4074 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05477
8313 | 13.8889 | 27.0371 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06
8314 | 22.2222 | 43.2594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0589
8315 | 33.3333 | 64.8891 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05582
8316 | 38.8889 | 75.704 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05665
8317 | 44.4444 | 86.5188 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05827
8318 | 16.6667 | 32.4446 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0558
8319 | 8.3333 | 16.2223 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05308
8320 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05374
8321 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05555
8322 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06556
8323 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06159
8324 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05779
8325 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05364
8326 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05151
8327 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05004
8328 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04896
8329 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04939
8330 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04762
8331 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04683
8332 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0405
8333 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03692
8334 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03492
8335 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03725
8336 | 2.7778 | 5.4074 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04315
8337 | 36.1111 | 70.2965 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04889
8338 | 119.4444 | 232.5193 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05056
8339 | 102.7778 | 200.0747 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0503
8340 | 211.1111 | 410.9643 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05006
8341 | 122.2222 | 237.9267 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05048
8342 | 69.4444 | 135.1856 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05098
8343 | 16.6667 | 32.4446 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05084
8344 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05102
8345 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05135
8346 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05567
8347 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05501
8348 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.054
8349 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0543
8350 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05002
8351 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.049
8352 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05
8353 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0499
8354 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05
8355 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0449
8356 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.03154
8357 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.02691
8358 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0307
8359 | 0 | 0 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.04194
8360 | 2.7778 | 5.4074 | 90 | 15.8885 | 2350 | 0 | #DIV/0! | 0.04658
8361 | 47.2222 | 91.9262 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.0441
8362 | 147.2222 | 286.5935 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.04915
8363 | 208.3333 | 405.5569 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05046
8364 | 202.7778 | 394.742 | 80 | 14.1231 | 2350 | 0 | #DIV/0! | 0.05045
8365 | 105.5556 | 205.4822 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05045
8366 | 47.2222 | 91.9262 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05048
8367 | 36.1111 | 70.2965 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05306
8368 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05856
8369 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0495
8370 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0541
8371 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05701
8372 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0574
8373 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05249
8374 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05032
8375 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0484
8376 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0501
8377 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05023
8378 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04868
8379 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04591
8380 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04449
8381 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04419
8382 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04677
8383 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05387
8384 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06501
8385 | 22.2222 | 43.2594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05943
8386 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0611
8387 | 50 | 97.3337 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05756
8388 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.063
8389 | 50 | 97.3337 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05924
8390 | 41.6667 | 81.1114 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05972
8391 | 16.6667 | 32.4446 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06103
8392 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06234
8393 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.065
8394 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06701
8395 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06696
8396 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06255
8397 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05717
8398 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0551
8399 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05308
8400 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.051
8401 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04771
8402 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0469
8403 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0455
8404 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04419
8405 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0444
8406 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04627
8407 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05074
8408 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05917
8409 | 22.2222 | 43.2594 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0645
8410 | 38.8889 | 75.704 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05753
8411 | 52.7778 | 102.7411 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05498
8412 | 113.8889 | 221.7044 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05292
8413 | 152.7778 | 297.4084 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0497
8414 | 127.7778 | 248.7416 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05036
8415 | 30.5556 | 59.4817 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.053
8416 | 2.7778 | 5.4074 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05752
8417 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05757
8418 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05783
8419 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05379
8420 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05174
8421 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0492
8422 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04839
8423 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0469
8424 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0451
8425 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04893
8426 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0455
8427 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.045
8428 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04183
8429 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04339
8430 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04522
8431 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05119
8432 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05705
8433 | 13.8889 | 27.0371 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0671
8434 | 66.6667 | 129.7782 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06697
8435 | 69.4444 | 135.1856 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05948
8436 | 83.3333 | 162.2228 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06303
8437 | 83.3333 | 162.2228 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06131
8438 | 86.1111 | 167.6302 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06169
8439 | 47.2222 | 91.9262 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06265
8440 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06175
8441 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06539
8442 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06919
8443 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.066
8444 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0613
8445 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05885
8446 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05415
8447 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0509
8448 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04697
8449 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04238
8450 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03936
8451 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03936
8452 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0374
8453 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03066
8454 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03327
8455 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04584
8456 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.055
8457 | 50 | 97.3337 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05795
8458 | 136.1111 | 264.9638 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05462
8459 | 188.8889 | 367.7049 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05286
8460 | 216.6667 | 421.7792 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05269
8461 | 197.2222 | 383.9272 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05187
8462 | 130.5556 | 254.149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05211
8463 | 30.5556 | 59.4817 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0518
8464 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05372
8465 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05449
8466 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05531
8467 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05491
8468 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05397
8469 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05068
8470 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05009
8471 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04914
8472 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0454
8473 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04156
8474 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04095
8475 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04078
8476 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03154
8477 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03622
8478 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04421
8479 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0491
8480 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05256
8481 | 16.6667 | 32.4446 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05439
8482 | 33.3333 | 64.8891 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0599
8483 | 50 | 97.3337 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05419
8484 | 58.3333 | 113.5559 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.062
8485 | 30.5556 | 59.4817 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05402
8486 | 66.6667 | 129.7782 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.069
8487 | 19.4444 | 37.852 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0599
8488 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05366
8489 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05369
8490 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0649
8491 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05371
8492 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.052
8493 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04901
8494 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.04996
8495 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.047
8496 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0449
8497 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0424
8498 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0425
8499 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.025
8500 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04583
8501 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04667
8502 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0456
8503 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0449
8504 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04918
8505 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04598
8506 | 138.8889 | 270.3713 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04976
8507 | 88.8889 | 173.0376 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.051
8508 | 100 | 194.6673 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05132
8509 | 41.6667 | 81.1114 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05123
8510 | 119.4444 | 232.5193 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05
8511 | 33.3333 | 64.8891 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0506
8512 | 2.7778 | 5.4074 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05199
8513 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05195
8514 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05493
8515 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05276
8516 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05192
8517 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.046
8518 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0452
8519 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.044
8520 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.044
8521 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03343
8522 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.039
8523 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0331
8524 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0435
8525 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0425
8526 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.038
8527 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.044
8528 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0415
8529 | 19.4444 | 37.852 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.046
8530 | 69.4444 | 135.1856 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05
8531 | 52.7778 | 102.7411 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05371
8532 | 58.3333 | 113.5559 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05514
8533 | 94.4444 | 183.8525 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05
8534 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05089
8535 | 11.1111 | 21.6297 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05114
8536 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05328
8537 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05252
8538 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05649
8539 | 0 | 0 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.05368
8540 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.052
8541 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04977
8542 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.047
8543 | 0 | 0 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.04762
8544 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.03367
8545 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.039
8546 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04581
8547 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.045
8548 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04516
8549 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04
8550 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.01759
8551 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0395
8552 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0456
8553 | 19.4444 | 37.852 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05258
8554 | 63.8889 | 124.3708 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05256
8555 | 80.5556 | 156.8153 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0524
8556 | 163.8889 | 319.0381 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0523
8557 | 133.3333 | 259.5564 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05094
8558 | 36.1111 | 70.2965 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0499
8559 | 30.5556 | 59.4817 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.0509
8560 | 5.5556 | 10.8149 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05242
8561 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05218
8562 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.055
8563 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05593
8564 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05422
8565 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05098
8566 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04963
8567 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04814
8568 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0474
8569 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05018
8570 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05005
8571 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04732
8572 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04209
8573 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.02587
8574 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.02752
8575 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04501
8576 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05024
8577 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05022
8578 | 11.1111 | 21.6297 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.052
8579 | 27.7778 | 54.0743 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04855
8580 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.052
8581 | 41.6667 | 81.1114 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05093
8582 | 52.7778 | 102.7411 | 70 | 12.3578 | 2350 | 0 | #DIV/0! | 0.0518
8583 | 19.4444 | 37.852 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05185
8584 | 2.7778 | 5.4074 | 60 | 10.5924 | 2221.9589 | 0 | #DIV/0! | 0.05131
8585 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05453
8586 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05663
8587 | 0 | 0 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05151
8588 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04903
8589 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05041
8590 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0465
8591 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0499
8592 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0455
8593 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.041
8594 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.041
8595 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03034
8596 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.02646
8597 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.02462
8598 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03071
8599 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.02456
8600 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03155
8601 | 30.5556 | 59.4817 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04285
8602 | 111.1111 | 216.297 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0481
8603 | 136.1111 | 264.9638 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.0496
8604 | 94.4444 | 183.8525 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04981
8605 | 77.7778 | 151.4079 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0475
8606 | 75 | 146.0005 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0494
8607 | 27.7778 | 54.0743 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04996
8608 | 5.5556 | 10.8149 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05028
8609 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05342
8610 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0623
8611 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05746
8612 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05353
8613 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04985
8614 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04963
8615 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04994
8616 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04709
8617 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04942
8618 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04901
8619 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04687
8620 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04656
8621 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04701
8622 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04116
8623 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04111
8624 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0413
8625 | 13.8889 | 27.0371 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04475
8626 | 58.3333 | 113.5559 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04931
8627 | 88.8889 | 173.0376 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04995
8628 | 97.2222 | 189.2599 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05071
8629 | 86.1111 | 167.6302 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0505
8630 | 55.5556 | 108.1485 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04996
8631 | 25 | 48.6668 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05111
8632 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05249
8633 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05406
8634 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05755
8635 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05764
8636 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05592
8637 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05224
8638 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05142
8639 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05096
8640 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04925
8641 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04581
8642 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04451
8643 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0428
8644 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0428
8645 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04292
8646 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04476
8647 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04698
8648 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05248
8649 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.053
8650 | 144.4444 | 281.1861 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05477
8651 | 219.4444 | 427.1866 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05483
8652 | 241.6667 | 470.446 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.05517
8653 | 225 | 438.0014 | 50 | 8.827 | 1285.8559 | 0 | #DIV/0! | 0.055
8654 | 163.8889 | 319.0381 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05504
8655 | 50 | 97.3337 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05627
8656 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05852
8657 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06006
8658 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.06319
8659 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05988
8660 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05899
8661 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05452
8662 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05167
8663 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05038
8664 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04857
8665 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04517
8666 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0445
8667 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04413
8668 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04292
8669 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0429
8670 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04205
8671 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04357
8672 | 2.7778 | 5.4074 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04586
8673 | 22.2222 | 43.2594 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04893
8674 | 77.7778 | 151.4079 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0516
8675 | 180.5556 | 351.4826 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05061
8676 | 150 | 292.001 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05005
8677 | 91.6667 | 178.445 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0497
8678 | 102.7778 | 200.0747 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04865
8679 | 36.1111 | 70.2965 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0502
8680 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05148
8681 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05419
8682 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05579
8683 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05875
8684 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05829
8685 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05462
8686 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05039
8687 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04975
8688 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04517
8689 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0456
8690 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0431
8691 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04192
8692 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03785
8693 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03597
8694 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03631
8695 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.03772
8696 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0401
8697 | 19.4444 | 37.852 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04252
8698 | 80.5556 | 156.8153 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04504
8699 | 100 | 194.6673 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05105
8700 | 175 | 340.6678 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05045
8701 | 88.8889 | 173.0376 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04703
8702 | 86.1111 | 167.6302 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04561
8703 | 30.5556 | 59.4817 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0458
8704 | 2.7778 | 5.4074 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04789
8705 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04897
8706 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05892
8707 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06109
8708 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06124
8709 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.06033
8710 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05568
8711 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05182
8712 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0454
8713 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04512
8714 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04503
8715 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04269
8716 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.03889
8717 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.03795
8718 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0399
8719 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0455
8720 | 2.7778 | 5.4074 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0551
8721 | 41.6667 | 81.1114 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05854
8722 | 108.3333 | 210.8896 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05742
8723 | 194.4444 | 378.5198 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.05742
8724 | 227.7778 | 443.4089 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05813
8725 | 227.7778 | 443.4089 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05405
8726 | 169.4444 | 329.8529 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05472
8727 | 52.7778 | 102.7411 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05195
8728 | 5.5556 | 10.8149 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0534
8729 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.05417
8730 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.07397
8731 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06378
8732 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.06827
8733 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.054
8734 | 0 | 0 | 40 | 7.0616 | 658.3582 | 0 | #DIV/0! | 0.04981
8735 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.04789
8736 | 0 | 0 | 30 | 5.2962 | 277.7449 | 0 | #DIV/0! | 0.0472
8737 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0444
8738 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.045
8739 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04531
8740 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.04787
8741 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.048
8742 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04787
8743 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.04829
8744 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0! | 0.04796
8745 | 36.1111 | 70.2965 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05156
8746 | 97.2222 | 189.2599 | 0 | 0 | 0 | 0 | #DIV/0! | 0.05685
8747 | 122.2222 | 237.9267 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06276
8748 | 180.5556 | 351.4826 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05398
8749 | 200 | 389.3346 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.0536
8750 | 158.3333 | 308.2232 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0529
8751 | 50 | 97.3337 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.053
8752 | 5.5556 | 10.8149 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05458
8753 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.05728
8754 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06106
8755 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.06273
8756 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.061
8757 | 0 | 0 | 10 | 1.7654 | 0 | 0 | #DIV/0! | 0.0572
8758 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05474
8759 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05388
8760 | 0 | 0 | 20 | 3.5308 | 82.2948 | 0 | #DIV/0! | 0.05221
Note on I2: Annelies Boerman: including CO2 penalty

## profiles
change these profiles according to local situation | [6 empty] | standard profiles (don't change)
Hour | Day-ahead Price [EUR/MWh] | De (kWh) | Dg (kg) | Dh (kWh) | CO2eq ton/MWh | standard profiles on the right may be scaled to larger amount of households | Hour | Day-ahead Price [EUR/MWh] | De (kWh) | Dg (kg) | Dh (kWh)
1 | 68.92 | 38.3276 | 28.9376 | 296.8172 | 0.4481 | standard profiles are based on: | 1 | 23.86 | 38.3276 | 2.2679 | 296.8172
2 | 64.98 | 31.4671 | 29.1815 | 288.5237 | 0.44566 | - Day-ahead prices is from ENTSOE APX database 2016, region the Netherlands | 2 | 22.39 | 31.4671 | 3 | 288.5237
3 | 60.27 | 30.1636 | 35.9061 | 292.0056 | 0.43458 | - Electricity demand profile is for 200 households simulated by ALPG tool | 3 | 20.59 | 30.1636 | 4 | 292.0056
4 | 49.97 | 28.8832 | 30.1971 | 295.9571 | 0.42789 | - hydrogen gas demand profile is a simple sinusoid profile for which parameters can be changed | 4 | 16.81 | 28.8832 | 5 | 295.9571
5 | 47.66 | 28.1217 | 39.6806 | 376.2182 | 0.41901 | - Heat demand profile is for 200 households simulated by degree day model | 5 | 17.41 | 28.1217 | 5.7321 | 376.2182
6 | 48 | 27.6981 | 28.9379 | 315.6036 | 0.42321 |  | 6 | 17.02 | 27.6981 | 6 | 315.6036
7 | 49.75 | 27.5018 | 34.4637 | 361.7192 | 0.42104 |  | 7 | 15.86 | 27.5018 | 5.7321 | 361.7192
8 | 55.12 | 30.8061 | 49.7149 | 337.4103 | 0.41793 |  | 8 | 18.16 | 30.8061 | 5 | 337.4103
9 | 44.8 | 54.1709 | 52.0359 | 317.1527 | 0.42635 | relevant websites: | 9 | 17.73 | 54.1709 | 4 | 317.1527
10 | 49.58 | 68.8209 | 39.1974 | 314.9595 | 0.43397 | for day-ahead prices: | 10 | 19.77 | 68.8209 | 3 | 314.9595
11 | 55.44 | 73.5034 | 42.405 | 291.8158 | 0.42243 | https://transparency.entsoe.eu/transmission-domain/r2/dayAheadPrices/show?name=&defaultValue=true&viewType=GRAPH&areaType=BZN&atch=false&dateTime.dateTime=21.08.2019+00:00¦CET¦DAY&biddingZone.values=CTY¦10YNL----------L!BZN¦10YNL----------L&dateTime.timezone=CET_CEST&dateTime.timezone_input=CET+(UTC+1)+/+CEST+(UTC+2) | 11 | 23.75 | 73.5034 | 2.2679 | 291.8158
12 | 62.62 | 72.7828 | 52.6496 | 266.0736 | 0.4205 |  | 12 | 26.03 | 72.7828 | 2 | 266.0736
13 | 57.4 | 81.4673 | 44.2398 | 243.3019 | 0.41933 | for ALPG tool: | 13 | 27.06 | 81.4673 | 2.2679 | 243.3019
14 | 50.76 | 77.549 | 49.0333 | 230.4981 | 0.41792 | https://www.utwente.nl/en/eemcs/energy/profile_generator/ | 14 | 26.59 | 77.549 | 3 | 230.4981
15 | 49.92 | 72.8614 | 46.7205 | 193.116 | 0.41488 |  | 15 | 25 | 72.8614 | 4 | 193.116
16 | 50.05 | 72.8042 | 55.1097 | 253.0422 | 0.41696 | kolommen B en F obv Entsoedata voor 2019 uit Actual Generation per Production Type_2019_kwartier&uur | 16 | 27.04 | 72.8042 | 5 | 253.0422
17 | 50.6 | 82.18 | 43.1132 | 234.9458 | 0.41788 |  | 17 | 34.46 | 82.18 | 5.7321 | 234.9458
18 | 60.72 | 121.3132 | 41.6424 | 258.8961 | 0.41699 |  | 18 | 45.14 | 121.3132 | 6 | 258.8961
19 | 50.51 | 137.7765 | 51.4645 | 298.071 | 0.41506 |  | 19 | 40 | 137.7765 | 5.7321 | 298.071
20 | 47.35 | 148.6146 | 23.9224 | 276.0306 | 0.4197 |  | 20 | 35.34 | 148.6146 | 5 | 276.0306
21 | 50.4 | 117.0026 | 27.3412 | 347.9643 | 0.42776 |  | 21 | 33.07 | 117.0026 | 4 | 347.9643
22 | 47.53 | 104.0861 | 35.8974 | 322.6094 | 0.43363 |  | 22 | 29.52 | 104.0861 | 3 | 322.6094
23 | 51.06 | 87.4348 | 22.2632 | 296.1828 | 0.43272 |  | 23 | 30.1 | 87.4348 | 2.2679 | 296.1828
24 | 47.55 | 39.5807 | 31.9763 | 246.0383 | 0.43582 |  | 24 | 24.57 | 39.5807 | 2 | 246.0383
25 | 49 | 35.3325 | 24.3883 | 271.515 | 0.43084 |  | 25 | 22.2 | 35.3325 | 2.2679 | 271.515
26 | 46.6 | 33.5531 | 32.4641 | 243.9173 | 0.42821 |  | 26 | 16.57 | 33.5531 | 3 | 243.9173
27 | 46.6 | 31.7617 | 24.5208 | 274.1364 | 0.431 |  | 27 | 15.35 | 31.7617 | 4 | 274.1364
28 | 45.73 | 30.2119 | 25.5111 | 313.043 | 0.43225 |  | 28 | 12.77 | 30.2119 | 5 | 313.043
29 | 46.01 | 29.1527 | 33.3961 | 340.6338 | 0.43616 |  | 29 | 11.27 | 29.1527 | 5.7321 | 340.6338
30 | 46.45 | 28.503 | 24.9132 | 368.4549 | 0.44548 |  | 30 | 11.91 | 28.503 | 6 | 368.4549
31 | 47.86 | 44.2276 | 29.3418 | 416.2796 | 0.45773 |  | 31 | 12.62 | 44.2276 | 5.7321 | 416.2796
32 | 49.5 | 66.2924 | 39.5093 | 364.1958 | 0.45133 |  | 32 | 15.27 | 66.2924 | 5 | 364.1958
33 | 52.42 | 51.5896 | 47.9677 | 325.3289 | 0.45929 |  | 33 | 22.34 | 51.5896 | 4 | 325.3289
34 | 52.42 | 43.0229 | 248.5421 | 329.785 | 0.46502 |  | 34 | 27.44 | 43.0229 | 3 | 329.785
35 | 52.36 | 44.954 | 45.9085 | 385.5676 | 0.46412 |  | 35 | 37 | 44.954 | 2.2679 | 385.5676
36 | 51.94 | 45.2758 | 48.5094 | 331.7671 | 0.46845 |  | 36 | 38 | 45.2758 | 2 | 331.7671
37 | 51.59 | 48.739 | 42.1889 | 367.8265 | 0.47743 |  | 37 | 46.68 | 48.739 | 2.2679 | 367.8265
38 | 51.77 | 49.6144 | 48.4479 | 322.4458 | 0.48431 |  | 38 | 42.44 | 49.6144 | 3 | 322.4458
39 | 52.61 | 56.2668 | 54.0008 | 267.7826 | 0.49189 |  | 39 | 34.94 | 56.2668 | 4 | 267.7826
40 | 60 | 68.9414 | 43.9271 | 317.6327 | 0.49435 |  | 40 | 29 | 68.9414 | 5 | 317.6327
41 | 69.95 | 99.6662 | 46.6585 | 379.5724 | 0.49608 |  | 41 | 32 | 99.6662 | 5.7321 | 379.5724
42 | 80 | 148.3871 | 43.5524 | 334.5579 | 0.49634 |  | 42 | 45 | 148.3871 | 6 | 334.5579
43 | 77.67 | 158.3851 | 43.9588 | 390.5488 | 0.4975 |  | 43 | 44.65 | 158.3851 | 5.7321 | 390.5488
44 | 76.53 | 151.3885 | 31.2894 | 427.9362 | 0.4984 |  | 44 | 39 | 151.3885 | 5 | 427.9362
45 | 67.29 | 116.7818 | 30.5482 | 331.9671 | 0.5004 |  | 45 | 35 | 116.7818 | 4 | 331.9671
46 | 55.64 | 104.7487 | 30.2655 | 347.3266 | 0.50438 |  | 46 | 27.54 | 104.7487 | 3 | 347.3266
47 | 53.81 | 75.8965 | 24.8339 | 346.2553 | 0.50181 |  | 47 | 32.18 | 75.8965 | 2.2679 | 346.2553
48 | 52.43 | 41.0681 | 28.2249 | 295.1686 | 0.49644 |  | 48 | 30.12 | 41.0681 | 2 | 295.1686
49 | 50.12 | 33.6175 | 23.9772 | 357.2243 | 0.50766 |  | 49 | 21.39 | 33.6175 | 2.2679 | 357.2243
50 | 47.1 | 32.0079 | 27.9619 | 350.0832 | 0.50554 |  | 50 | 18.91 | 32.0079 | 3 | 350.0832
51 | 46.4 | 30.5748 | 25.8889 | 349.4406 | 0.50475 |  | 51 | 19.07 | 30.5748 | 4 | 349.4406
52 | 44 | 29.3392 | 23.8979 | 322.4524 | 0.51007 |  | 52 | 16.1 | 29.3392 | 5 | 322.4524
53 | 43.88 | 28.4831 | 28.6893 | 457.9082 | 0.51152 |  | 53 | 13.97 | 28.4831 | 5.7321 | 457.9082
54 | 45.92 | 28.3494 | 30.9944 | 504.272 | 0.51365 |  | 54 | 15.37 | 28.3494 | 6 | 504.272
55 | 52.46 | 44.2266 | 36.1961 | 438.6548 | 0.50806 |  | 55 | 15.47 | 44.2266 | 5.7321 | 438.6548
56 | 58.63 | 65.2125 | 42.1813 | 413.7993 | 0.50668 |  | 56 | 16.04 | 65.2125 | 5 | 413.7993
57 | 65.08 | 51.3725 | 43.9248 | 461.8773 | 0.4992 |  | 57 | 18.44 | 51.3725 | 4 | 461.8773
58 | 75.58 | 44.0077 | 49.6227 | 368.8338 | 0.50184 |  | 58 | 23.1 | 44.0077 | 3 | 368.8338
59 | 79.68 | 46.1595 | 37.8531 | 365.3709 | 0.50353 |  | 59 | 32.44 | 46.1595 | 2.2679 | 365.3709
60 | 74.29 | 47.7311 | 231.6315 | 408.7501 | 0.50628 |  | 60 | 34.11 | 47.7311 | 2 | 408.7501
61 | 73.7 | 49.1317 | 41.9285 | 343.3509 | 0.50996 |  | 61 | 33.79 | 49.1317 | 2.2679 | 343.3509
62 | 70.31 | 51.154 | 28.5706 | 227.6533 | 0.50722 |  | 62 | 41.31 | 51.154 | 3 | 227.6533
63 | 69.9 | 59.4857 | 57.7758 | 201.7642 | 0.51075 |  | 63 | 26.18 | 59.4857 | 4 | 201.7642
64 | 68.45 | 73.4658 | 25.2863 | 237.3475 | 0.50995 |  | 64 | 23.34 | 73.4658 | 5 | 237.3475
65 | 70 | 103.4063 | 46.8403 | 354.1022 | 0.49964 |  | 65 | 21.68 | 103.4063 | 5.7321 | 354.1022
66 | 73.7 | 148.5552 | 48.7685 | 347.7102 | 0.50438 |  | 66 | 24.94 | 148.5552 | 6 | 347.7102
67 | 83.7 | 165.7199 | 44.783 | 391.9162 | 0.50103 |  | 67 | 26.76 | 165.7199 | 5.7321 | 391.9162
68 | 71.34 | 135.8221 | 29.8794 | 390.5999 | 0.50072 |  | 68 | 28 | 135.8221 | 5 | 390.5999
69 | 68.38 | 113.253 | 30.9745 | 440.1917 | 0.50066 |  | 69 | 25.33 | 113.253 | 4 | 440.1917
70 | 61.72 | 108.2216 | 29.0631 | 364.0364 | 0.50287 |  | 70 | 22.11 | 108.2216 | 3 | 364.0364
71 | 53.81 | 75.398 | 22.0088 | 419.6673 | 0.51166 |  | 71 | 29.94 | 75.398 | 2.2679 | 419.6673
72 | 49.98 | 38.7668 | 28.3787 | 312.3924 | 0.51023 |  | 72 | 23.1 | 38.7668 | 2 | 312.3924
73 | 51.63 | 35.6924 | 35.2363 | 400.1178 | 0.51038 |  | 73 | 13.78 | 35.6924 | 2.2679 | 400.1178
74 | 47.11 | 33.8485 | 22.4102 | 362.7242 | 0.51254 |  | 74 | 15.09 | 33.8485 | 3 | 362.7242
75 | 47.07 | 32.0238 | 31.9103 | 408.0953 | 0.5048 |  | 75 | 14.94 | 32.0238 | 4 | 408.0953
76 | 46.21 | 30.3249 | 24.9303 | 493.5606 | 0.49333 |  | 76 | 15.06 | 30.3249 | 5 | 493.5606
77 | 47 | 29.1932 | 35.8227 | 557.6549 | 0.48628 |  | 77 | 16.39 | 29.1932 | 5.7321 | 557.6549
78 | 46.91 | 28.9981 | 235.6684 | 574.8985 | 0.47496 |  | 78 | 16.43 | 28.9981 | 6 | 574.8985
79 | 59.54 | 43.6162 | 25.5531 | 440.5739 | 0.47383 |  | 79 | 22.99 | 43.6162 | 5.7321 | 440.5739
80 | 68.4 | 68.3456 | 33.4271 | 569.1222 | 0.48438 |  | 80 | 41.79 | 68.3456 | 5 | 569.1222
81 | 74.19 | 51.0007 | 28.2756 | 491.9233 | 0.4816 |  | 81 | 42.69 | 51.0007 | 4 | 491.9233
82 | 80 | 42.24 | 33.6969 | 448.0248 | 0.48134 |  | 82 | 33.46 | 42.24 | 3 | 448.0248
83 | 85.38 | 42.8118 | 45.5294 | 423.84 | 0.47627 |  | 83 | 33.24 | 42.8118 | 2.2679 | 423.84
84 | 82.61 | 44.8374 | 34.4547 | 462.5617 | 0.47526 |  | 84 | 35.09 | 44.8374 | 2 | 462.5617
85 | 69.67 | 48.5164 | 33.6957 | 411.964 | 0.47448 |  | 85 | 35 | 48.5164 | 2.2679 | 411.964
86 | 69.73 | 51.5081 | 52.75 | 385.9665 | 0.47645 |  | 86 | 35 | 51.5081 | 3 | 385.9665
87 | 69.73 | 59.365 | 36.0955 | 381.4988 | 0.47895 |  | 87 | 34.94 | 59.365 | 4 | 381.4988
88 | 73 | 79.6078 | 37.5425 | 376.0475 | 0.47758 |  | 88 | 34.92 | 79.6078 | 5 | 376.0475
89 | 76 | 107.9937 | 33.8665 | 496.951 | 0.47409 |  | 89 | 38 | 107.9937 | 5.7321 | 496.951
90 | 89.9 | 161.1027 | 47.4211 | 420.8626 | 0.46755 |  | 90 | 41.21 | 161.1027 | 6 | 420.8626
91 | 73.3 | 162.5415 | 53.5283 | 401.8019 | 0.46142 |  | 91 | 42.95 | 162.5415 | 5.7321 | 401.8019
92 | 55 | 148.9838 | 25.7104 | 437.713 | 0.46016 |  | 92 | 41.96 | 148.9838 | 5 | 437.713
93 | 52.73 | 120.9366 | 35.1875 | 430.5127 | 0.4573 |  | 93 | 34.94 | 120.9366 | 4 | 430.5127
94 | 52.12 | 108.8098 | 23.4989 | 466.1639 | 0.45832 |  | 94 | 30.66 | 108.8098 | 3 | 466.1639
95 | 51.43 | 79.9126 | 29.8849 | 404.8913 | 0.46447 |  | 95 | 30 | 79.9126 | 2.2679 | 404.8913
96 | 50.64 | 41.8092 | 27.9688 | 392.9008 | 0.46321 |  | 96 | 23.9 | 41.8092 | 2 | 392.9008
97 | 50.02 | 35.0623 | 31.2013 | 452.4768 | 0.46113 |  | 97 | 25.03 | 35.0623 | 2.2679 | 452.4768
98 | 46 | 33.3131 | 22.9091 | 397.2642 | 0.45767 |  | 98 | 24.42 | 33.3131 | 3 | 397.2642
99 | 45.68 | 31.4188 | 32.0143 | 408.5629 | 0.45307 |  | 99 | 22.34 | 31.4188 | 4 | 408.5629
100 | 45.49 | 29.8648 | 22.1166 | 458.4267 | 0.45018 |  | 100 | 21.5 | 29.8648 | 5 | 458.4267
101 | 45 | 28.8822 | 35.5603 | 482.7147 | 0.44748 |  | 101 | 20 | 28.8822 | 5.7321 | 482.7147
102 | 43.8 | 28.6353 | 22.1261 | 409.077 | 0.44727 |  | 102 | 23.53 | 28.6353 | 6 | 409.077
103 | 45.9 | 43.4258 | 23.3406 | 493.2074 | 0.44062 |  | 103 | 28.96 | 43.4258 | 5.7321 | 493.2074
104 | 46.68 | 65.1694 | 37.2854 | 416.5238 | 0.44161 |  | 104 | 38.32 | 65.1694 | 5 | 416.5238
105 | 51.65 | 52.5565 | 40.7334 | 411.8734 | 0.44973 |  | 105 | 41.45 | 52.5565 | 4 | 411.8734
106 | 52.41 | 45.3278 | 32.8957 | 458.5647 | 0.45448 |  | 106 | 40.72 | 45.3278 | 3 | 458.5647
107 | 52.62 | 47.1422 | 45.4595 | 465.2035 | 0.45614 |  | 107 | 40.66 | 47.1422 | 2.2679 | 465.2035
108 | 52.71 | 50.1921 | 37.5915 | 405.8159 | 0.45489 |  | 108 | 40.33 | 50.1921 | 2 | 405.8159
109 | 73 | 53.2144 | 41.8928 | 420.3399 | 0.4566 |  | 109 | 38.25 | 53.2144 | 2.2679 | 420.3399
110 | 73 | 53.876 | 48.7033 | 370.349 | 0.45711 |  | 110 | 36.98 | 53.876 | 3 | 370.349
111 | 68.96 | 60.5893 | 49.7054 | 374.1301 | 0.45748 |  | 111 | 34.91 | 60.5893 | 4 | 374.1301
112 | 64.12 | 72.6865 | 33.6307 | 440.973 | 0.4593 |  | 112 | 33.5 | 72.6865 | 5 | 440.973
113 | 59.61 | 102.6526 | 32.8219 | 380.9318 | 0.45917 |  | 113 | 35.1 | 102.6526 | 5.7321 | 380.9318
114 | 75.14 | 141.7673 | 43.4129 | 434.8611 | 0.45842 |  | 114 | 42.44 | 141.7673 | 6 | 434.8611
115 | 74.7 | 163.744 | 36.8413 | 448.7053 | 0.45934 |  | 115 | 42.94 | 163.744 | 5.7321 | 448.7053
116 | 73 | 147.2998 | 32.8393 | 423.3028 | 0.46441 |  | 116 | 40.5 | 147.2998 | 5 | 423.3028
117 | 68.07 | 120.6351 | 24.7761 | 336.2055 | 0.46472 |  | 117 | 34.49 | 120.6351 | 4 | 336.2055
118 | 53.62 | 110.4166 | 23.1862 | 306.774 | 0.46833 |  | 118 | 31.43 | 110.4166 | 3 | 306.774
119 | 52.82 | 76.9575 | 31.7762 | 357.5457 | 0.47127 |  | 119 | 30.54 | 76.9575 | 2.2679 | 357.5457
120 | 62.36 | 40.4118 | 431.6943 | 296.3865 | 0.47108 |  | 120 | 26.99 | 40.4118 | 2 | 296.3865
121 | 51.95 | 33.0744 | 33.0922 | 274.0885 | 0.47673 |  | 121 | 26.62 | 33.0744 | 2.2679 | 274.0885
122 | 50 | 31.558 | 18.9229 | 224.7161 | 0.48069 |  | 122 | 25.58 | 31.558 | 3 | 224.7161
123 | 48.38 | 30.2448 | 28.2923 | 263.6461 | 0.48363 |  | 123 | 24.59 | 30.2448 | 4 | 263.6461
124 | 48.02 | 28.9358 | 27.6968 | 296.481 | 0.4933 |  | 124 | 22.5 | 28.9358 | 5 | 296.481
125 | 45.91 | 28.2111 | 29.9238 | 394.1548 | 0.49912 |  | 125 | 23.16 | 28.2111 | 5.7321 | 394.1548
126 | 47.17 | 28.1125 | 26.377 | 357.6351 | 0.50049 |  | 126 | 24.99 | 28.1125 | 6 | 357.6351
127 | 48.19 | 43.2625 | 37.3332 | 390.2262 | 0.50741 |  | 127 | 26.62 | 43.2625 | 5.7321 | 390.2262
128 | 49.11 | 65.3784 | 43.1001 | 386.5625 | 0.50564 |  | 128 | 28.03 | 65.3784 | 5 | 386.5625
129 | 50.7 | 51.6221 | 52.5587 | 340.8917 | 0.50553 |  | 129 | 30.82 | 51.6221 | 4 | 340.8917
130 | 53.4 | 44.8671 | 42.8053 | 303.5401 | 0.506 |  | 130 | 34.22 | 44.8671 | 3 | 303.5401
131 | 56.55 | 46.9135 | 45.2001 | 321.8849 | 0.50712 |  | 131 | 37.9 | 46.9135 | 2.2679 | 321.8849
132 | 60.02 | 48.2849 | 48.3255 | 262.9261 | 0.51294 |  | 132 | 40.08 | 48.2849 | 2 | 262.9261
133 | 60.22 | 49.8379 | 32.9895 | 301.6666 | 0.5145 |  | 133 | 40.73 | 49.8379 | 2.2679 | 301.6666
134 | 55 | 52.8865 | 38.7787 | 294.4451 | 0.51677 |  | 134 | 38.26 | 52.8865 | 3 | 294.4451
135 | 52.39 | 60.3897 | 44.7976 | 273.2156 | 0.51356 |  | 135 | 35.44 | 60.3897 | 4 | 273.2156
136 | 51.57 | 76.3502 | 40.2855 | 269.6735 | 0.51475 |  | 136 | 36.92 | 76.3502 | 5 | 269.6735
137 | 54.71 | 106.8404 | 53.5259 | 292.2622 | 0.51261 |  | 137 | 41.28 | 106.8404 | 5.7321 | 292.2622
138 | 63.43 | 153.3711 | 40.4084 | 314.3771 | 0.50656 |  | 138 | 44.95 | 153.3711 | 6 | 314.3771
139 | 67.37 | 169.8415 | 42.761 | 332.0641 | 0.50098 |  | 139 | 46.9 | 169.8415 | 5.7321 | 332.0641
140 | 67.2 | 139.4081 | 30.1487 | 355.3422 | 0.50755 |  | 140 | 43.95 | 139.4081 | 5 | 355.3422
141 | 66.03 | 114.3973 | 36.1485 | 316.3078 | 0.51386 |  | 141 | 39.94 | 114.3973 | 4 | 316.3078
142 | 55.36 | 103.9433 | 31.3935 | 294.4504 | 0.51829 |  | 142 | 32.4 | 103.9433 | 3 | 294.4504
143 | 58.59 | 76.0047 | 23.0256 | 251.5506 | 0.51849 |  | 143 | 33.51 | 76.0047 | 2.2679 | 251.5506
144 | 51.89 | 37.8127 | 30.977 | 328.3929 | 0.51927 |  | 144 | 30.11 | 37.8127 | 2 | 328.3929
145 | 46.03 | 32.2309 | 30.4247 | 341.4161 | 0.52117 |  | 145 | 26.41 | 32.2309 | 2.2679 | 341.4161
146 | 47.98 | 31.0365 | 28.4062 | 273.59 | 0.52216 |  | 146 | 26.05 | 31.0365 | 3 | 273.59
147 | 47.84 | 29.7351 | 24.3526 | 308.1423 | 0.51883 |  | 147 | 24.93 | 29.7351 | 4 | 308.1423
148 | 46.11 | 28.7239 | 31.3259 | 356.3724 | 0.51437 |  | 148 | 22.39 | 28.7239 | 5 | 356.3724
149 | 46.08 | 27.9663 | 22.6671 | 422.5501 | 0.5141 |  | 149 | 22.32 | 27.9663 | 5.7321 | 422.5501
150 | 47.62 | 27.4953 | 22.858 | 451.1747 | 0.51493 |  | 150 | 24.2 | 27.4953 | 6 | 451.1747
151 | 55.77 | 27.3842 | 226.0971 | 506.7168 | 0.51001 |  | 151 | 31 | 27.3842 | 5.7321 | 506.7168
152 | 68.61 | 30.6178 | 39.7564 | 533.4412 | 0.5145 |  | 152 | 42.47 | 30.6178 | 5 | 533.4412
153 | 74.15 | 54.8435 | 44.0862 | 409.4929 | 0.51146 |  | 153 | 42.97 | 54.8435 | 4 | 409.4929
154 | 74.93 | 68.5533 | 38.9313 | 345.7677 | 0.50715 |  | 154 | 41.93 | 68.5533 | 3 | 345.7677
155 | 73.59 | 70.2377 | 46.1114 | 412.9273 | 0.49635 |  | 155 | 41.62 | 70.2377 | 2.2679 | 412.9273
156 | 71.23 | 70.5588 | 54.1144 | 375.3736 | 0.4853 |  | 156 | 41.5 | 70.5588 | 2 | 375.3736
157 | 67.27 | 74.144 | 34.1323 | 272.2755 | 0.48178 |  | 157 | 40.66 | 74.144 | 2.2679 | 272.2755
158 | 65.14 | 74.7823 | 41.958 | 137.8699 | 0.47334 |  | 158 | 40.33 | 74.7823 | 3 | 137.8699
159 | 62.56 | 68.5207 | 40.7691 | 112.7321 | 0.46105 |  | 159 | 36.51 | 68.5207 | 4 | 112.7321
160 | 57.56 | 72.3194 | 46.6282 | 161.2147 | 0.45726 |  | 160 | 33.49 | 72.3194 | 5 | 161.2147
161 | 56.99 | 85.1291 | 42.7553 | 261.4604 | 0.45174 |  | 161 | 34.19 | 85.1291 | 5.7321 | 261.4604
162 | 72.82 | 145.5104 | 41.2473 | 259.852 | 0.44629 |  | 162 | 40.66 | 145.5104 | 6 | 259.852
163 | 52.89 | 153.6514 | 51.7915 | 316.7558 | 0.4412 |  | 163 | 40.8 | 153.6514 | 5.7321 | 316.7558
164 | 50 | 136.4034 | 31.3043 | 347.0281 | 0.43975 |  | 164 | 37.19 | 136.4034 | 5 | 347.0281
165 | 51 | 114.7925 | 34.7601 | 326.7425 | 0.44183 |  | 165 | 31.94 | 114.7925 | 4 | 326.7425
166 | 49 | 101.708 | 21.5202 | 301.5727 | 0.44237 |  | 166 | 32.44 | 101.708 | 3 | 301.5727
167 | 47.54 | 88.9514 | 23.6005 | 244.758 | 0.43937 |  | 167 | 31.35 | 88.9514 | 2.2679 | 244.758
168 | 44.4 | 38.9672 | 33.523 | 218.5088 | 0.43962 |  | 168 | 29.94 | 38.9672 | 2 | 218.5088
169 | 36.7 | 35.6515 | 228.8656 | 294.2814 | 0.43836 |  | 169 | 12.12 | 35.6515 | 2.2679 | 294.2814
170 | 45.56 | 33.8767 | 25.3045 | 258.5609 | 0.43897 |  | 170 | 20.82 | 33.8767 | 3 | 258.5609
171 | 39 | 32.1234 | 35.6126 | 214.4968 | 0.43447 |  | 171 | 20.43 | 32.1234 | 4 | 214.4968
172 | 40 | 30.5044 | 23.8576 | 279.9445 | 0.43722 |  | 172 | 20.02 | 30.5044 | 5 | 279.9445
173 | 32.8 | 29.2378 | 23.7407 | 305.0205 | 0.43925 |  | 173 | 18.01 | 29.2378 | 5.7321 | 305.0205
174 | 43 | 28.2998 | 26.0575 | 353.2522 | 0.44424 |  | 174 | 19.68 | 28.2998 | 6 | 353.2522
175 | 53.96 | 27.537 | 27.2866 | 337.2205 | 0.43969 |  | 175 | 24.28 | 27.537 | 5.7321 | 337.2205
176 | 53 | 30.329 | 52.6294 | 332.7289 | 0.43878 |  | 176 | 33 | 30.329 | 5 | 332.7289
177 | 59.8 | 55.995 | 43.1389 | 341.0342 | 0.44523 |  | 177 | 46.13 | 55.995 | 4 | 341.0342
178 | 60.1 | 70.88 | 50.5542 | 294.9945 | 0.44286 |  | 178 | 35 | 70.88 | 3 | 294.9945
179 | 55.89 | 73.9062 | 51.7882 | 262.5869 | 0.44152 |  | 179 | 33 | 73.9062 | 2.2679 | 262.5869
180 | 53.48 | 74.2865 | 241.0379 | 297.4016 | 0.44542 |  | 180 | 36.91 | 74.2865 | 2 | 297.4016
181 | 48.7 | 77.9299 | 43.4748 | 286.0838 | 0.44896 |  | 181 | 36.13 | 77.9299 | 2.2679 | 286.0838
182 | 49.01 | 77.2917 | 40.2777 | 285.057 | 0.45472 |  | 182 | 36.13 | 77.2917 | 3 | 285.057
183 | 52.38 | 73.7719 | 41.0516 | 248.3785 | 0.45646 |  | 183 | 28.52 | 73.7719 | 4 | 248.3785
184 | 52.37 | 69.0904 | 44.0272 | 249.735 | 0.45774 |  | 184 | 32.08 | 69.0904 | 5 | 249.735
185 | 52.84 | 80.364 | 41.921 | 335.5825 | 0.45178 |  | 185 | 37.16 | 80.364 | 5.7321 | 335.5825
186 | 78.24 | 115.0356 | 42.9007 | 316.2188 | 0.45203 |  | 186 | 45 | 115.0356 | 6 | 316.2188
187 | 52.29 | 135.7677 | 43.9097 | 367.8299 | 0.44743 |  | 187 | 46.97 | 135.7677 | 5.7321 | 367.8299
188 | 48.38 | 147.8766 | 25.4261 | 284.2746 | 0.44559 |  | 188 | 40.09 | 147.8766 | 5 | 284.2746
189 | 50.1 | 120.6781 | 229.0005 | 323.667 | 0.4445 |  | 189 | 34.61 | 120.6781 | 4 | 323.667
190 | 51.12 | 107.0088 | 34.6662 | 283.5378 | 0.45064 |  | 190 | 31.52 | 107.0088 | 3 | 283.5378
191 | 50.66 | 90.498 | 32.2576 | 254.1168 | 0.45499 |  | 191 | 32.5 | 90.498 | 2.2679 | 254.1168
192 | 46.72 | 42.164 | 32.0297 | 240.8776 | 0.45819 |  | 192 | 28 | 42.164 | 2 | 240.8776
193 | 42.6 | 33.8154 | 33.0117 | 226.9071 | 0.46356 |  | 193 | 26.1 | 33.8154 | 2.2679 | 226.9071
194 | 39.5 | 32.307 | 24.3904 | 223.9061 | 0.46642 |  | 194 | 25.1 | 32.307 | 3 | 223.9061
195 | 37 | 30.7803 | 24.2588 | 222.1674 | 0.46707 |  | 195 | 24.3 | 30.7803 | 4 | 222.1674
196 | 42.4 | 29.4833 | 30.496 | 272.4654 | 0.46326 |  | 196 | 23.23 | 29.4833 | 5 | 272.4654
197 | 36.42 | 28.5578 | 27.5075 | 316.3182 | 0.46164 |  | 197 | 21.96 | 28.5578 | 5.7321 | 316.3182
198 | 42 | 28.2196 | 22.0403 | 344.7951 | 0.46511 |  | 198 | 22.45 | 28.2196 | 6 | 344.7951
199 | 50.63 | 44.7006 | 34.1844 | 375.99 | 0.46597 |  | 199 | 23.07 | 44.7006 | 5.7321 | 375.99
200 | 57.51 | 66.6432 | 45.2439 | 396.2161 | 0.47372 |  | 200 | 25 | 66.6432 | 5 | 396.2161
201 | 66.69 | 52.3641 | 48.1079 | 327.3887 | 0.4753 |  | 201 | 32.11 | 52.3641 | 4 | 327.3887
202 | 65.9 | 43.5718 | 38.6436 | 275.3142 | 0.47762 |  | 202 | 37.12 | 43.5718 | 3 | 275.3142
203 | 68.2 | 46.7369 | 49.0646 | 319.4499 | 0.48185 |  | 203 | 36.13 | 46.7369 | 2.2679 | 319.4499
204 | 54 | 46.6539 | 50.2374 | 333.1333 | 0.47726 |  | 204 | 35.76 | 46.6539 | 2 | 333.1333
205 | 51.09 | 51.0064 | 41.5301 | 240.9575 | 0.47352 |  | 205 | 34.06 | 51.0064 | 2.2679 | 240.9575
206 | 50.1 | 51.1996 | 54.9905 | 255.527 | 0.4728 |  | 206 | 31.54 | 51.1996 | 3 | 255.527
207 | 52.56 | 57.3 | 47.071 | 245.1887 | 0.47116 |  | 207 | 27.92 | 57.3 | 4 | 245.1887
208 | 53.95 | 72.4512 | 40.3432 | 285.1233 | 0.47285 |  | 208 | 27 | 72.4512 | 5 | 285.1233
209 | 64.37 | 100.3773 | 25.8587 | 365.9665 | 0.47359 |  | 209 | 30.5 | 100.3773 | 5.7321 | 365.9665
210 | 75.64 | 147.1845 | 240.5802 | 359.8589 | 0.47524 |  | 210 | 36.99 | 147.1845 | 6 | 359.8589
211 | 74.22 | 151.1746 | 51.385 | 313.145 | 0.47496 |  | 211 | 36.8 | 151.1746 | 5.7321 | 313.145
212 | 55.98 | 155.2994 | 27.6282 | 352.5543 | 0.47498 |  | 212 | 35 | 155.2994 | 5 | 352.5543
213 | 54.73 | 119.1783 | 19.5394 | 318.7254 | 0.4796 |  | 213 | 29 | 119.1783 | 4 | 318.7254
214 | 50.02 | 110.1273 | 31.887 | 323.129 | 0.48648 |  | 214 | 25.01 | 110.1273 | 3 | 323.129
215 | 52.64 | 76.7908 | 33.5202 | 286.2321 | 0.4924 |  | 215 | 25.1 | 76.7908 | 2.2679 | 286.2321
216 | 50.31 | 39.4045 | 36.0171 | 282.1331 | 0.49467 |  | 216 | 22.28 | 39.4045 | 2 | 282.1331
217 | 51.07 | 33.2244 | 28.021 | 266.1962 | 0.50976 |  | 217 | 15.58 | 33.2244 | 2.2679 | 266.1962
218 | 49.61 | 31.7983 | 41.0792 | 229.6155 | 0.51778 |  | 218 | 19.05 | 31.7983 | 3 | 229.6155
219 | 48.63 | 30.3593 | 30.1636 | 306.4216 | 0.52813 |  | 219 | 17.24 | 30.3593 | 4 | 306.4216
220 | 48.8 | 29.0769 | 28.0007 | 313.6925 | 0.53481 |  | 220 | 12.75 | 29.0769 | 5 | 313.6925
221 | 48.5 | 28.2356 | 27.146 | 449.5577 | 0.54065 |  | 221 | 10.81 | 28.2356 | 5.7321 | 449.5577
222 | 49.8 | 28.0573 | 30.2858 | 398.4495 | 0.54504 |  | 222 | 10.85 | 28.0573 | 6 | 398.4495
223 | 59.29 | 44.7802 | 30.6458 | 431.5363 | 0.54175 |  | 223 | 9.85 | 44.7802 | 5.7321 | 431.5363
224 | 72.6 | 64.802 | 42.6602 | 395.7854 | 0.54299 |  | 224 | 18.66 | 64.802 | 5 | 395.7854
225 | 81.17 | 51.1999 | 52.8529 | 509.3638 | 0.54294 |  | 225 | 18.87 | 51.1999 | 4 | 509.3638
226 | 81.79 | 43.4594 | 54.5596 | 448.0895 | 0.54559 |  | 226 | 20.82 | 43.4594 | 3 | 448.0895
227 | 81.15 | 46.7852 | 34.4641 | 340.1503 | 0.54555 |  | 227 | 21.65 | 46.7852 | 2.2679 | 340.1503
228 | 80 | 46.6257 | 41.5989 | 417.8682 | 0.54374 |  | 228 | 22.8 | 46.6257 | 2 | 417.8682
229 | 76.39 | 48.3629 | 43.4105 | 380.1275 | 0.54256 |  | 229 | 27 | 48.3629 | 2.2679 | 380.1275
230 | 75 | 53.3389 | 45.9566 | 331.0276 | 0.54245 |  | 230 | 22.8 | 53.3389 | 3 | 331.0276
231 | 76.06 | 56.1506 | 34.1904 | 360.0644 | 0.54212 |  | 231 | 22.44 | 56.1506 | 4 | 360.0644
232 | 75.4 | 72.088 | 47.7479 | 354.0944 | 0.53324 |  | 232 | 22.71 | 72.088 | 5 | 354.0944
233 | 76.78 | 95.9302 | 55.6522 | 346.2836 | 0.53018 |  | 233 | 23.92 | 95.9302 | 5.7321 | 346.2836
234 | 83.45 | 151.5349 | 42.5504 | 363.1684 | 0.53013 |  | 234 | 27.73 | 151.5349 | 6 | 363.1684
235 | 85.15 | 158.1374 | 46.5565 | 356.4024 | 0.52501 |  | 235 | 35 | 158.1374 | 5.7321 | 356.4024
236 | 78.16 | 138.0555 | 21.2737 | 445.544 | 0.52306 |  | 236 | 33 | 138.0555 | 5 | 445.544
237 | 71.92 | 111.5584 | 29.7703 | 360.7867 | 0.52067 |  | 237 | 33 | 111.5584 | 4 | 360.7867
238 | 67.25 | 102.6975 | 33.3671 | 357.5979 | 0.51785 |  | 238 | 30 | 102.6975 | 3 | 357.5979
239 | 62.04 | 75.3887 | 24.0949 | 306.0527 | 0.51702 |  | 239 | 26.93 | 75.3887 | 2.2679 | 306.0527
240 | 51.07 | 38.5266 | 25.7918 | 293.1808 | 0.51726 |  | 240 | 23.12 | 38.5266 | 2 | 293.1808
241 | 46 | 33.1811 | 29.9687 | 378.1682 | 0.52246 |  | 241 | 21.95 | 33.1811 | 2.2679 | 378.1682
242 | 44.2 | 31.6461 | 229.5169 | 283.4072 | 0.52471 |  | 242 | 20.04 | 31.6461 | 3 | 283.4072
243 | 45.43 | 30.2088 | 29.1475 | 352.7787 | 0.52312 |  | 243 | 19.78 | 30.2088 | 4 | 352.7787
244 | 46.42 | 28.9449 | 31.0844 | 354.535 | 0.51559 |  | 244 | 19.36 | 28.9449 | 5 | 354.535
245 | 45 | 28.2178 | 229.9448 | 349.2998 | 0.51451 |  | 245 | 19.56 | 28.2178 | 5.7321 | 349.2998
246 | 43.5 | 28.3152 | 27.6725 | 473.7494 | 0.51616 |  | 246 | 21.67 | 28.3152 | 6 | 473.7494
247 | 50 | 43.1567 | 33.4882 | 515.0505 | 0.5076 |  | 247 | 28.5 | 43.1567 | 5.7321 | 515.0505
248 | 54.78 | 65.8729 | 49.3691 | 550.0556 | 0.49915 |  | 248 | 41.61 | 65.8729 | 5 | 550.0556
249 | 60.02 | 51.3111 | 30.8677 | 509.4224 | 0.50265 |  | 249 | 45.93 | 51.3111 | 4 | 509.4224
250 | 69.96 | 42.675 | 35.6441 | 497.699 | 0.49776 |  | 250 | 44 | 42.675 | 3 | 497.699
251 | 70.27 | 43.2214 | 54.9441 | 463.9331 | 0.49765 |  | 251 | 41.94 | 43.2214 | 2.2679 | 463.9331
252 | 71.33 | 45.404 | 45.4064 | 437.8262 | 0.49319 |  | 252 | 41.96 | 45.404 | 2 | 437.8262
253 | 53.61 | 48.4916 | 28.2977 | 412.7052 | 0.49027 |  | 253 | 41.5 | 48.4916 | 2.2679 | 412.7052
254 | 52.48 | 48.7605 | 38.5729 | 326.1533 | 0.48647 |  | 254 | 41 | 48.7605 | 3 | 326.1533
255 | 50.96 | 57.1092 | 35.4517 | 385.6071 | 0.48306 |  | 255 | 39.88 | 57.1092 | 4 | 385.6071
256 | 50.69 | 75.7358 | 40.0605 | 435.0216 | 0.47602 |  | 256 | 37.5 | 75.7358 | 5 | 435.0216
257 | 51.17 | 102.8459 | 34.8538 | 457.9401 | 0.47139 |  | 257 | 37.95 | 102.8459 | 5.7321 | 457.9401
258 | 65 | 137.683 | 38.0373 | 424.6532 | 0.46869 |  | 258 | 42.97 | 137.683 | 6 | 424.6532
259 | 52.11 | 161.7832 | 42.5274 | 465.904 | 0.46946 |  | 259 | 42.88 | 161.7832 | 5.7321 | 465.904
260 | 51.28 | 144.0791 | 25.3995 | 422.3621 | 0.47186 |  | 260 | 40 | 144.0791 | 5 | 422.3621
261 | 51.17 | 117.8566 | 28.6898 | 509.1027 | 0.47527 |  | 261 | 33.09 | 117.8566 | 4 | 509.1027
262 | 47.37 | 111.0095 | 26.68 | 377.7999 | 0.4797 |  | 262 | 27.93 | 111.0095 | 3 | 377.7999
263 | 46.45 | 76.7994 | 32.5721 | 492.2336 | 0.48475 |  | 263 | 28 | 76.7994 | 2.2679 | 492.2336
264 | 45.88 | 38.1684 | 27.2078 | 367.2352 | 0.48461 |  | 264 | 24.15 | 38.1684 | 2 | 367.2352
265 | 46.8 | 34.2909 | 36.9587 | 452.4429 | 0.49284 |  | 265 | 21.51 | 34.2909 | 2.2679 | 452.4429
266 | 46.48 | 32.7871 | 27.7303 | 357.3082 | 0.49496 |  | 266 | 19.81 | 32.7871 | 3 | 357.3082
267 | 49 | 31.3053 | 29.9659 | 393.5065 | 0.49788 |  | 267 | 19.1 | 31.3053 | 4 | 393.5065
268 | 43.69 | 29.8889 | 31.0686 | 511.185 | 0.5039 |  | 268 | 15.74 | 29.8889 | 5 | 511.185
269 | 46.27 | 28.714 | 230.4364 | 477.2899 | 0.49332 |  | 269 | 15.22 | 28.714 | 5.7321 | 477.2899
270 | 42.6 | 28.2768 | 29.7964 | 610.0703 | 0.48924 |  | 270 | 20.19 | 28.2768 | 6 | 610.0703
271 | 42.98 | 43.1122 | 29.0842 | 522.1268 | 0.48324 |  | 271 | 24.38 | 43.1122 | 5.7321 | 522.1268
272 | 50.99 | 64.8055 | 49.5716 | 592.4239 | 0.47185 |  | 272 | 35.92 | 64.8055 | 5 | 592.4239
273 | 54.5 | 50.23 | 54.3311 | 453.8035 | 0.47472 |  | 273 | 40.5 | 50.23 | 4 | 453.8035
274 | 62.11 | 43.041 | 38.4665 | 448.8838 | 0.4743 |  | 274 | 41 | 43.041 | 3 | 448.8838
275 | 65 | 45.1842 | 36.1302 | 408.0261 | 0.47239 |  | 275 | 38.66 | 45.1842 | 2.2679 | 408.0261
276 | 64.01 | 45.6955 | 47.6277 | 520.6133 | 0.46888 |  | 276 | 36.46 | 45.6955 | 2 | 520.6133
277 | 51.98 | 49.2146 | 26.6245 | 436.179 | 0.4691 |  | 277 | 35 | 49.2146 | 2.2679 | 436.179
278 | 49 | 50.2176 | 39.5272 | 425.1814 | 0.46697 |  | 278 | 33.3 | 50.2176 | 3 | 425.1814
279 | 51.75 | 57.1113 | 43.897 | 461.1004 | 0.46704 |  | 279 | 32.21 | 57.1113 | 4 | 461.1004
280 | 52.5 | 72.7529 | 47.8077 | 460.8466 | 0.46972 |  | 280 | 33 | 72.7529 | 5 | 460.8466
281 | 52.81 | 97.2306 | 44.7449 | 505.0755 | 0.46807 |  | 281 | 36.08 | 97.2306 | 5.7321 | 505.0755
282 | 59.47 | 153.6653 | 46.293 | 476.2056 | 0.46743 |  | 282 | 41.94 | 153.6653 | 6 | 476.2056
283 | 49.9 | 149.5087 | 44.8239 | 465.3701 | 0.46242 |  | 283 | 41.77 | 149.5087 | 5.7321 | 465.3701
284 | 49.59 | 139.2648 | 24.8297 | 417.8503 | 0.46206 |  | 284 | 32.51 | 139.2648 | 5 | 417.8503
285 | 48.42 | 119.1871 | 26.8345 | 538.2128 | 0.46603 |  | 285 | 28.4 | 119.1871 | 4 | 538.2128
286 | 49 | 108.9093 | 32.4557 | 514.2728 | 0.47124 |  | 286 | 25.87 | 108.9093 | 3 | 514.2728
287 | 47.58 | 77.0835 | 25.1488 | 497.6465 | 0.47359 |  | 287 | 24.07 | 77.0835 | 2.2679 | 497.6465
288 | 47.55 | 40.2601 | 28.9378 | 388.4046 | 0.48139 |  | 288 | 26.3 | 40.2601 | 2 | 388.4046
289 | 52.4 | 36.3313 | 28.351 | 405.0404 | 0.48666 |  | 289 | 21 | 36.3313 | 2.2679 | 405.0404
290 | 47.93 | 34.3172 | 24.858 | 371.515 | 0.49537 |  | 290 | 19.66 | 34.3172 | 3 | 371.515
291 | 43.44 | 32.2974 | 34.4758 | 474.5291 | 0.50066 |  | 291 | 18.13 | 32.2974 | 4 | 474.5291
292 | 33.48 | 30.5299 | 29.2364 | 403.4141 | 0.4818 |  | 292 | 18.06 | 30.5299 | 5 | 403.4141
293 | 34.63 | 29.4937 | 26.0787 | 532.5359 | 0.45683 |  | 293 | 18.05 | 29.4937 | 5.7321 | 532.5359
294 | 34.63 | 29.1695 | 25.1098 | 512.1444 | 0.42871 |  | 294 | 20.83 | 29.1695 | 6 | 512.1444
295 | 28.97 | 43.6588 | 32.6647 | 572.3887 | 0.41981 |  | 295 | 24.1 | 43.6588 | 5.7321 | 572.3887
296 | 40 | 66.6298 | 39.8042 | 502.3069 | 0.42831 |  | 296 | 28.44 | 66.6298 | 5 | 502.3069
297 | 38.3 | 51.7497 | 54.5725 | 525.3368 | 0.44385 |  | 297 | 30.41 | 51.7497 | 4 | 525.3368
298 | 47.33 | 44.9997 | 52.0711 | 554.2029 | 0.44947 |  | 298 | 31.15 | 44.9997 | 3 | 554.2029
299 | 48.8 | 48.4421 | 34.9701 | 525.8125 | 0.44471 |  | 299 | 31.84 | 48.4421 | 2.2679 | 525.8125
300 | 51.5 | 50.5923 | 54.6123 | 442.6126 | 0.44109 |  | 300 | 33.88 | 50.5923 | 2 | 442.6126
301 | 51.52 | 52.9113 | 43.6734 | 386.8351 | 0.43762 |  | 301 | 34.18 | 52.9113 | 2.2679 | 386.8351
302 | 50.99 | 54.2717 | 452.8076 | 407.3879 | 0.43659 |  | 302 | 35.39 | 54.2717 | 3 | 407.3879
303 | 50 | 64.0953 | 43.0241 | 384.3948 | 0.43546 |  | 303 | 34.91 | 64.0953 | 4 | 384.3948
304 | 50.84 | 78.0371 | 39.5461 | 376.801 | 0.43399 |  | 304 | 37.44 | 78.0371 | 5 | 376.801
305 | 51.82 | 104.0906 | 49.749 | 368.1256 | 0.42927 |  | 305 | 39.58 | 104.0906 | 5.7321 | 368.1256
306 | 72.5 | 148.8075 | 32.325 | 443.7007 | 0.42707 |  | 306 | 43 | 148.8075 | 6 | 443.7007
307 | 51.55 | 163.3497 | 40.1412 | 372.2068 | 0.42517 |  | 307 | 43.32 | 163.3497 | 5.7321 | 372.2068
308 | 51.73 | 147.1114 | 33.0661 | 473.7492 | 0.42883 |  | 308 | 38.86 | 147.1114 | 5 | 473.7492
309 | 48.28 | 119.5023 | 30.2421 | 391.5483 | 0.43235 |  | 309 | 29.96 | 119.5023 | 4 | 391.5483
310 | 47.61 | 109.3341 | 22.2817 | 452.188 | 0.4399 |  | 310 | 27.96 | 109.3341 | 3 | 452.188
311 | 45.1 | 79.5447 | 28.1395 | 347.6745 | 0.44154 |  | 311 | 27.23 | 79.5447 | 2.2679 | 347.6745
312 | 42.2 | 41.8439 | 26.3932 | 345.2089 | 0.44037 |  | 312 | 23.52 | 41.8439 | 2 | 345.2089
313 | 46.52 | 34.4397 | 38.3196 | 413.0736 | 0.4381 |  | 313 | 24.29 | 34.4397 | 2.2679 | 413.0736
314 | 42.4 | 32.7453 | 29.669 | 313.5215 | 0.43893 |  | 314 | 23.06 | 32.7453 | 3 | 313.5215
315 | 46.48 | 31.1858 | 27.646 | 364.93 | 0.44109 |  | 315 | 22.22 | 31.1858 | 4 | 364.93
316 | 46.37 | 29.717 | 33.1385 | 323.6692 | 0.46497 |  | 316 | 22.03 | 29.717 | 5 | 323.6692
317 | 45 | 28.715 | 23.683 | 361.5662 | 0.47706 |  | 317 | 22.53 | 28.715 | 5.7321 | 361.5662
318 | 46.67 | 28.0817 | 25.2497 | 470.7602 | 0.47434 |  | 318 | 23.9 | 28.0817 | 6 | 470.7602
319 | 50.41 | 27.639 | 31.1686 | 461.4167 | 0.47187 |  | 319 | 29.84 | 27.639 | 5.7321 | 461.4167
320 | 58 | 30.0632 | 43.3721 | 497.8524 | 0.47159 |  | 320 | 38.06 | 30.0632 | 5 | 497.8524
321 | 63.14 | 55.375 | 50.3204 | 410.9469 | 0.47598 |  | 321 | 44.99 | 55.375 | 4 | 410.9469
322 | 66.3 | 68.2442 | 45.8122 | 339.408 | 0.47861 |  | 322 | 41.39 | 68.2442 | 3 | 339.408
323 | 65.5 | 73.7895 | 46.7834 | 334.2987 | 0.48021 |  | 323 | 36.37 | 73.7895 | 2.2679 | 334.2987
324 | 51.94 | 75.6179 | 42.5473 | 419.3477 | 0.47405 |  | 324 | 34.94 | 75.6179 | 2 | 419.3477
325 | 48.3 | 80.2903 | 50.8058 | 373.3116 | 0.4717 |  | 325 | 32.77 | 80.2903 | 2.2679 | 373.3116
326 | 51.57 | 77.6781 | 50.03 | 418.829 | 0.46868 |  | 326 | 35.06 | 77.6781 | 3 | 418.829
327 | 51.73 | 70.9876 | 40.7372 | 305.4981 | 0.47464 |  | 327 | 40.5 | 70.9876 | 4 | 305.4981
328 | 62.12 | 74.7841 | 51.8051 | 374.8329 | 0.47696 |  | 328 | 42.99 | 74.7841 | 5 | 374.8329
329 | 65.17 | 81.2516 | 244.6048 | 421.7692 | 0.47785 |  | 329 | 42.34 | 81.2516 | 5.7321 | 421.7692
330 | 85.74 | 130.4281 | 40.1052 | 414.2753 | 0.48277 |  | 330 | 45.76 | 130.4281 | 6 | 414.2753
331 | 63.14 | 166.782 | 46.6648 | 467.5952 | 0.48154 |  | 331 | 41.53 | 166.782 | 5.7321 | 467.5952
332 | 56 | 138.0248 | 28.7799 | 476.0548 | 0.48539 |  | 332 | 32.44 | 138.0248 | 5 | 476.0548
333 | 52.14 | 119.1811 | 27.929 | 413.6111 | 0.49115 |  | 333 | 34.1 | 119.1811 | 4 | 413.6111
334 | 55 | 106.6423 | 25.9792 | 400.6671 | 0.49536 |  | 334 | 30.86 | 106.6423 | 3 | 400.6671
335 | 51.68 | 90.1002 | 25.5159 | 399.6972 | 0.50096 |  | 335 | 28.46 | 90.1002 | 2.2679 | 399.6972
336 | 47.43 | 40.8853 | 27.8932 | 376.0366 | 0.50682 |  | 336 | 25.99 | 40.8853 | 2 | 376.0366
337 | 46.67 | 34.2913 | 26.0457 | 335.7077 | 0.5037 |  | 337 | 25.5 | 34.2913 | 2.2679 | 335.7077
338 | 42 | 32.71 | 23.4963 | 346.6946 | 0.48729 |  | 338 | 25.35 | 32.71 | 3 | 346.6946
339 | 38.3 | 31.0561 | 23.1824 | 316.8488 | 0.47773 |  | 339 | 24.36 | 31.0561 | 4 | 316.8488
340 | 36 | 29.6288 | 32.0736 | 420.8545 | 0.46683 |  | 340 | 23.5 | 29.6288 | 5 | 420.8545
341 | 42.2 | 28.7719 | 24.4647 | 378.6757 | 0.45961 |  | 341 | 22.94 | 28.7719 | 5.7321 | 378.6757
342 | 44.3 | 28.0671 | 38.4082 | 465.2538 | 0.4606 |  | 342 | 23.48 | 28.0671 | 6 | 465.2538
343 | 47.4 | 27.8331 | 30.9335 | 493.0544 | 0.46406 |  | 343 | 27.32 | 27.8331 | 5.7321 | 493.0544
344 | 57.45 | 31.1974 | 42.7928 | 457.0121 | 0.46717 |  | 344 | 41.22 | 31.1974 | 5 | 457.0121
345 | 62.36 | 55.3232 | 54.5577 | 512.0898 | 0.46269 |  | 345 | 45.53 | 55.3232 | 4 | 512.0898
346 | 61.72 | 69.2215 | 42.2026 | 405.2613 | 0.46105 |  | 346 | 45.86 | 69.2215 | 3 | 405.2613
347 | 60.2 | 76.4291 | 41.3912 | 317.5331 | 0.45921 |  | 347 | 46.35 | 76.4291 | 2.2679 | 317.5331
348 | 56.82 | 74.6649 | 41.7165 | 295.7056 | 0.45764 |  | 348 | 46.95 | 74.6649 | 2 | 295.7056
349 | 55.7 | 81.5582 | 47.9135 | 328.049 | 0.45368 |  | 349 | 44 | 81.5582 | 2.2679 | 328.049
350 | 54.9 | 80.0671 | 29.2914 | 203.0075 | 0.45423 |  | 350 | 42.05 | 80.0671 | 3 | 203.0075
351 | 54.37 | 82.353 | 46.3217 | 169.7406 | 0.45451 |  | 351 | 39.99 | 82.353 | 4 | 169.7406
352 | 52.12 | 80.0869 | 51.2278 | 267.7149 | 0.45395 |  | 352 | 37.65 | 80.0869 | 5 | 267.7149
353 | 55 | 84.0779 | 28.1498 | 306.6433 | 0.45355 |  | 353 | 38 | 84.0779 | 5.7321 | 306.6433
354 | 62.8 | 112.7864 | 30.7991 | 409.5073 | 0.45175 |  | 354 | 45.26 | 112.7864 | 6 | 409.5073
355 | 50.86 | 151.9706 | 37.9944 | 406.1977 | 0.4455 |  | 355 | 48.04 | 151.9706 | 5.7321 | 406.1977
356 | 51.07 | 163.9627 | 29.6628 | 524.8588 | 0.44467 |  | 356 | 44.76 | 163.9627 | 5 | 524.8588
357 | 50.82 | 119.346 | 26.6537 | 435.7419 | 0.44451 |  | 357 | 34.81 | 119.346 | 4 | 435.7419
358 | 49.99 | 103.0678 | 27.4278 | 373.4185 | 0.44901 |  | 358 | 30.61 | 103.0678 | 3 | 373.4185
359 | 48.79 | 90.6496 | 29.1334 | 416.0717 | 0.44832 |  | 359 | 30.76 | 90.6496 | 2.2679 | 416.0717
360 | 47.1 | 41.4835 | 224.1588 | 490.5651 | 0.44841 |  | 360 | 27.3 | 41.4835 | 2 | 490.5651
361 | 41.6 | 34.9564 | 28.7125 | 440.7812 | 0.44432 |  | 361 | 27.24 | 34.9564 | 2.2679 | 440.7812
362 | 38.3 | 33.1258 | 222.6216 | 469.8579 | 0.44105 |  | 362 | 26.55 | 33.1258 | 3 | 469.8579
363 | 44.2 | 31.4842 | 20.8378 | 448.5946 | 0.43261 |  | 363 | 25.58 | 31.4842 | 4 | 448.5946
364 | 42.1 | 29.9685 | 26.5316 | 509.2077 | 0.43072 |  | 364 | 24.73 | 29.9685 | 5 | 509.2077
365 | 39.7 | 28.9062 | 28.2154 | 528.197 | 0.43055 |  | 365 | 24.08 | 28.9062 | 5.7321 | 528.197
366 | 39 | 28.4566 | 29.3027 | 599.0559 | 0.43781 |  | 366 | 25.32 | 28.4566 | 6 | 599.0559
367 | 46.63 | 43.7138 | 32.4015 | 534.0008 | 0.44395 |  | 367 | 24.77 | 43.7138 | 5.7321 | 534.0008
368 | 60.05 | 66.157 | 44.9524 | 486.7846 | 0.44753 |  | 368 | 25.57 | 66.157 | 5 | 486.7846
369 | 63.14 | 51.1855 | 38.9096 | 478.2399 | 0.45088 |  | 369 | 28.87 | 51.1855 | 4 | 478.2399
370 | 60.2 | 42.4993 | 45.1064 | 447.1053 | 0.45015 |  | 370 | 32.67 | 42.4993 | 3 | 447.1053
371 | 56.01 | 43.3397 | 38.1916 | 355.1954 | 0.44923 |  | 371 | 34.49 | 43.3397 | 2.2679 | 355.1954
372 | 56.74 | 45.6032 | 26.4661 | 264.5232 | 0.44947 |  | 372 | 34.33 | 45.6032 | 2 | 264.5232
373 | 54 | 49.041 | 60.2435 | 242.9394 | 0.44944 |  | 373 | 30.84 | 49.041 | 2.2679 | 242.9394
374 | 52.69 | 51.8811 | 34.0384 | 185.0771 | 0.44993 |  | 374 | 28.39 | 51.8811 | 3 | 185.0771
375 | 55.32 | 58.2991 | 36.8046 | 201.6878 | 0.452 |  | 375 | 27.06 | 58.2991 | 4 | 201.6878
376 | 53.72 | 70.8857 | 47.3114 | 192.8386 | 0.45387 |  | 376 | 27.12 | 70.8857 | 5 | 192.8386
377 | 60.39 | 100.8177 | 44.5228 | 201.523 | 0.44754 |  | 377 | 31.12 | 100.8177 | 5.7321 | 201.523
378 | 63.1 | 150.8369 | 57.7534 | 340.9355 | 0.44133 |  | 378 | 39.77 | 150.8369 | 6 | 340.9355
379 | 52.67 | 163.6447 | 41.5012 | 428.4994 | 0.43701 |  | 379 | 40.03 | 163.6447 | 5.7321 | 428.4994
380 | 50.92 | 145.1237 | 31.717 | 390.1298 | 0.43305 |  | 380 | 31.29 | 145.1237 | 5 | 390.1298
381 | 49.7 | 119.6371 | 27.5847 | 416.7562 | 0.43888 |  | 381 | 27.04 | 119.6371 | 4 | 416.7562
382 | 49.5 | 108.8757 | 26.3845 | 476.3698 | 0.4447 |  | 382 | 25.9 | 108.8757 | 3 | 476.3698
383 | 48.08 | 77.2675 | 23.1147 | 487.072 | 0.45811 |  | 383 | 25.53 | 77.2675 | 2.2679 | 487.072
384 | 48.2 | 40.9358 | 225.928 | 466.9766 | 0.4866 |  | 384 | 24.32 | 40.9358 | 2 | 466.9766
385 | 48.6 | 32.7992 | 18.0538 | 442.5113 | 0.47289 |  | 385 | 22.6 | 32.7992 | 2.2679 | 442.5113
386 | 46.6 | 31.4697 | 28.6275 | 453.8271 | 0.4548 |  | 386 | 20.25 | 31.4697 | 3 | 453.8271
387 | 46.9 | 30.0611 | 28.882 | 461.8277 | 0.44993 |  | 387 | 20.76 | 30.0611 | 4 | 461.8277
388 | 46.76 | 28.8185 | 26.4434 | 496.3986 | 0.45246 |  | 388 | 20.97 | 28.8185 | 5 | 496.3986
389 | 46.94 | 28.0479 | 27.9837 | 496.5297 | 0.45262 |  | 389 | 20.89 | 28.0479 | 5.7321 | 496.5297
390 | 48.6 | 27.9172 | 37.1355 | 470.1234 | 0.4585 |  | 390 | 21.64 | 27.9172 | 6 | 470.1234
391 | 54.58 | 44.0472 | 28.4755 | 592.0604 | 0.46557 |  | 391 | 20.78 | 44.0472 | 5.7321 | 592.0604
392 | 63.55 | 65.65 | 39.7175 | 569.5255 | 0.46633 |  | 392 | 23.09 | 65.65 | 5 | 569.5255
393 | 68.66 | 51.3455 | 43.9915 | 496.69 | 0.46926 |  | 393 | 24.3 | 51.3455 | 4 | 496.69
394 | 69.85 | 43.319 | 38.4562 | 434.0021 | 0.47294 |  | 394 | 26.54 | 43.319 | 3 | 434.0021
395 | 64.9 | 44.3979 | 38.615 | 345.0396 | 0.46721 |  | 395 | 30.11 | 44.3979 | 2.2679 | 345.0396
396 | 65.57 | 47.2212 | 42.8996 | 263.9337 | 0.46129 |  | 396 | 36.29 | 47.2212 | 2 | 263.9337
397 | 59 | 50.8562 | 27.8984 | 191.3768 | 0.46556 |  | 397 | 32.44 | 50.8562 | 2.2679 | 191.3768
398 | 56.27 | 52.3763 | 33.8755 | 193.2255 | 0.46859 |  | 398 | 26.93 | 52.3763 | 3 | 193.2255
399 | 56.81 | 57.6087 | 45.4069 | 178.1878 | 0.46633 |  | 399 | 26.4 | 57.6087 | 4 | 178.1878
400 | 57.75 | 75.9754 | 47.8644 | 182.7897 | 0.46322 |  | 400 | 27.29 | 75.9754 | 5 | 182.7897
401 | 59.32 | 98.2529 | 30.5519 | 259.055 | 0.46102 |  | 401 | 31.94 | 98.2529 | 5.7321 | 259.055
402 | 79.44 | 156.7186 | 46.3837 | 316.0163 | 0.46077 |  | 402 | 39.49 | 156.7186 | 6 | 316.0163
403 | 56.88 | 149.487 | 40.8735 | 392.1497 | 0.4585 |  | 403 | 42.8 | 149.487 | 5.7321 | 392.1497
404 | 53.85 | 142.7051 | 19.4599 | 477.4908 | 0.45436 |  | 404 | 39.23 | 142.7051 | 5 | 477.4908
405 | 50 | 115.6917 | 25.8481 | 499.4532 | 0.45658 |  | 405 | 33.3 | 115.6917 | 4 | 499.4532
406 | 51.06 | 104.3233 | 25.161 | 516.8839 | 0.4575 |  | 406 | 27.04 | 104.3233 | 3 | 516.8839
407 | 47.4 | 74.3919 | 25.1178 | 430.77 | 0.46718 |  | 407 | 27.05 | 74.3919 | 2.2679 | 430.77
408 | 50.57 | 38.1479 | 29.8766 | 448.3784 | 0.4858 |  | 408 | 26.3 | 38.1479 | 2 | 448.3784
409 | 53.9 | 33.9962 | 32.6216 | 503.0998 | 0.49988 |  | 409 | 25.71 | 33.9962 | 2.2679 | 503.0998
410 | 49.66 | 32.4613 | 228.5986 | 419.4312 | 0.51549 |  | 410 | 25.54 | 32.4613 | 3 | 419.4312
411 | 48.52 | 30.8948 | 24.9925 | 492.4266 | 0.52152 |  | 411 | 24.99 | 30.8948 | 4 | 492.4266
412 | 48.54 | 29.5769 | 30.1636 | 518.6258 | 0.52991 |  | 412 | 23.9 | 29.5769 | 5 | 518.6258
413 | 48.5 | 28.5705 | 26.6804 | 457.6101 | 0.52619 |  | 413 | 23.51 | 28.5705 | 5.7321 | 457.6101
414 | 51.85 | 28.3957 | 35.4311 | 579.7125 | 0.52079 |  | 414 | 25.08 | 28.3957 | 6 | 579.7125
415 | 59.26 | 43.2945 | 27.2988 | 554.4687 | 0.51697 |  | 415 | 27.84 | 43.2945 | 5.7321 | 554.4687
416 | 73.08 | 66.3889 | 46.6907 | 612.4669 | 0.51441 |  | 416 | 45.99 | 66.3889 | 5 | 612.4669
417 | 76.86 | 50.7932 | 35.5752 | 518.2353 | 0.51189 |  | 417 | 49.98 | 50.7932 | 4 | 518.2353
418 | 74.4 | 41.8735 | 45.1896 | 583.4537 | 0.51683 |  | 418 | 50.54 | 41.8735 | 3 | 583.4537
419 | 74.4 | 43.4003 | 39.6697 | 440.0789 | 0.51312 |  | 419 | 49.91 | 43.4003 | 2.2679 | 440.0789
420 | 71.28 | 44.899 | 42.6932 | 384.1407 | 0.50559 |  | 420 | 48.44 | 44.899 | 2 | 384.1407
421 | 69.25 | 48.168 | 35.533 | 232.6112 | 0.51324 |  | 421 | 46.93 | 48.168 | 2.2679 | 232.6112
422 | 65.27 | 49.6389 | 243.5502 | 149.6718 | 0.51638 |  | 422 | 46.32 | 49.6389 | 3 | 149.6718
423 | 67.44 | 56.7919 | 38.6839 | 155.5034 | 0.51776 |  | 423 | 45.09 | 56.7919 | 4 | 155.5034
424 | 68.14 | 70.5386 | 35.5798 | 205.2187 | 0.51975 |  | 424 | 49.33 | 70.5386 | 5 | 205.2187
425 | 69 | 98.0393 | 36.0995 | 255.8864 | 0.52057 |  | 425 | 49.66 | 98.0393 | 5.7321 | 255.8864
426 | 75.04 | 148.2447 | 54.8848 | 350.7263 | 0.51579 |  | 426 | 62.55 | 148.2447 | 6 | 350.7263
427 | 76.13 | 163.3568 | 40.5868 | 408.2061 | 0.50909 |  | 427 | 57.64 | 163.3568 | 5.7321 | 408.2061
428 | 72.46 | 141.4877 | 28.6639 | 466.4314 | 0.50624 |  | 428 | 48.71 | 141.4877 | 5 | 466.4314
429 | 61.83 | 113.7662 | 31.2309 | 468.6475 | 0.50822 |  | 429 | 37.98 | 113.7662 | 4 | 468.6475
430 | 58.19 | 105.6646 | 21.9569 | 474.0635 | 0.51017 |  | 430 | 33.36 | 105.6646 | 3 | 474.0635
431 | 56.7 | 76.0256 | 25.6488 | 465.3437 | 0.51213 |  | 431 | 30.97 | 76.0256 | 2.2679 | 465.3437
432 | 53.16 | 39.8668 | 27.8855 | 523.5504 | 0.51127 |  | 432 | 27.99 | 39.8668 | 2 | 523.5504
433 | 57.78 | 35.1585 | 31.0568 | 540.7406 | 0.51716 |  | 433 | 32.44 | 35.1585 | 2.2679 | 540.7406
434 | 57.32 | 33.3805 | 223.5638 | 373.4324 | 0.51835 |  | 434 | 30 | 33.3805 | 3 | 373.4324
435 | 55.18 | 31.6608 | 29.576 | 496.805 | 0.51615 |  | 435 | 30.3 | 31.6608 | 4 | 496.805
436 | 55 | 30.1268 | 22.1916 | 549.4097 | 0.51367 |  | 436 | 28.99 | 30.1268 | 5 | 549.4097
437 | 53.88 | 29.1107 | 28.8184 | 511.8381 | 0.51468 |  | 437 | 27.33 | 29.1107 | 5.7321 | 511.8381
438 | 53.71 | 28.7341 | 31.8114 | 500.6856 | 0.51027 |  | 438 | 28.86 | 28.7341 | 6 | 500.6856
439 | 53.43 | 44.1411 | 26.8685 | 535.6929 | 0.50413 |  | 439 | 33.12 | 44.1411 | 5.7321 | 535.6929
440 | 56.49 | 65.7934 | 29.667 | 513.8729 | 0.49855 |  | 440 | 54.1 | 65.7934 | 5 | 513.8729
441 | 60.46 | 49.3878 | 52.0084 | 437.4893 | 0.49906 |  | 441 | 65.12 | 49.3878 | 4 | 437.4893
442 | 62.48 | 42.242 | 44.1484 | 432.8275 | 0.49692 |  | 442 | 65.35 | 42.242 | 3 | 432.8275
443 | 62.49 | 43.4083 | 37.1508 | 488.7529 | 0.49717 |  | 443 | 62.17 | 43.4083 | 2.2679 | 488.7529
444 | 57.33 | 45.3907 | 47.7366 | 438.9891 | 0.50166 |  | 444 | 61.59 | 45.3907 | 2 | 438.9891
445 | 55.26 | 48.8387 | 44.651 | 390.2576 | 0.50442 |  | 445 | 58.98 | 48.8387 | 2.2679 | 390.2576
446 | 55.43 | 50.6715 | 43.4521 | 367.6828 | 0.50598 |  | 446 | 58.53 | 50.6715 | 3 | 367.6828
447 | 58.08 | 55.9776 | 40.3799 | 335.9635 | 0.50954 |  | 447 | 55.81 | 55.9776 | 4 | 335.9635
448 | 58.48 | 71.1128 | 41.7261 | 381.2591 | 0.50248 |  | 448 | 55.5 | 71.1128 | 5 | 381.2591
449 | 62.93 | 96.4615 | 31.9703 | 389.7681 | 0.49289 |  | 449 | 56.21 | 96.4615 | 5.7321 | 389.7681
450 | 67.15 | 144.1223 | 43.717 | 423.2003 | 0.48536 |  | 450 | 70.07 | 144.1223 | 6 | 423.2003
451 | 68.91 | 162.0664 | 47.2854 | 462.1506 | 0.48018 |  | 451 | 81.82 | 162.0664 | 5.7321 | 462.1506
452 | 63.42 | 145.3716 | 33.1457 | 465.1191 | 0.48253 |  | 452 | 65.76 | 145.3716 | 5 | 465.1191
453 | 60.22 | 116.6911 | 24.3136 | 463.0888 | 0.47978 |  | 453 | 49.84 | 116.6911 | 4 | 463.0888
454 | 58.53 | 110.6869 | 34.9431 | 411.9449 | 0.4843 |  | 454 | 39.84 | 110.6869 | 3 | 411.9449
455 | 58.52 | 77.6756 | 27.0448 | 330.864 | 0.48913 |  | 455 | 35.92 | 77.6756 | 2.2679 | 330.864
456 | 56.46 | 40.7795 | 32.6608 | 279.9339 | 0.48967 |  | 456 | 32.64 | 40.7795 | 2 | 279.9339
457 | 56 | 35.4962 | 32.6593 | 279.3295 | 0.48893 |  | 457 | 27.22 | 35.4962 | 2.2679 | 279.3295
458 | 54.1 | 33.7585 | 22.2466 | 290.1853 | 0.49348 |  | 458 | 26.08 | 33.7585 | 3 | 290.1853
459 | 53.83 | 31.9475 | 27.7585 | 324.3116 | 0.4973 |  | 459 | 25.8 | 31.9475 | 4 | 324.3116
460 | 51.35 | 30.3508 | 219.481 | 418.3579 | 0.4996 |  | 460 | 25.46 | 30.3508 | 5 | 418.3579
461 | 50.45 | 29.1364 | 33.4539 | 393.2421 | 0.51129 |  | 461 | 25.9 | 29.1364 | 5.7321 | 393.2421
462 | 50.47 | 28.6317 | 25.7861 | 438.9774 | 0.51898 |  | 462 | 28.17 | 28.6317 | 6 | 438.9774
463 | 48.96 | 44.1489 | 27.1068 | 591.5679 | 0.51942 |  | 463 | 33.89 | 44.1489 | 5.7321 | 591.5679
464 | 50.17 | 65.3053 | 40.8722 | 586.1487 | 0.51767 |  | 464 | 55.08 | 65.3053 | 5 | 586.1487
465 | 52.41 | 51.1442 | 38.8998 | 519.7701 | 0.51596 |  | 465 | 61.08 | 51.1442 | 4 | 519.7701
466 | 56.9 | 43.7638 | 46.9709 | 495.025 | 0.51608 |  | 466 | 62.67 | 43.7638 | 3 | 495.025
467 | 57 | 47.3489 | 50.5895 | 324.0857 | 0.51718 |  | 467 | 64.81 | 47.3489 | 2.2679 | 324.0857
468 | 56.51 | 47.585 | 46.4616 | 259.8063 | 0.5176 |  | 468 | 61.92 | 47.585 | 2 | 259.8063
469 | 55.96 | 50.0264 | 38.264 | 221.441 | 0.51675 |  | 469 | 58.6 | 50.0264 | 2.2679 | 221.441
470 | 53.9 | 51.0585 | 46.9616 | 163.5134 | 0.51739 |  | 470 | 57.81 | 51.0585 | 3 | 163.5134
471 | 55.54 | 58.9848 | 45.3184 | 182.5318 | 0.51735 |  | 471 | 54.95 | 58.9848 | 4 | 182.5318
472 | 55.39 | 75.0194 | 46.5014 | 205.4213 | 0.5183 |  | 472 | 52.42 | 75.0194 | 5 | 205.4213
473 | 58.02 | 97.3846 | 43.866 | 339.8252 | 0.51614 |  | 473 | 72.01 | 97.3846 | 5.7321 | 339.8252
474 | 66.68 | 156.8919 | 45.1152 | 398.0751 | 0.51062 |  | 474 | 103.4 | 156.8919 | 6 | 398.0751
475 | 69.43 | 158.9313 | 31.8667 | 487.3412 | 0.50615 |  | 475 | 123.62 | 158.9313 | 5.7321 | 487.3412
476 | 69.91 | 135.8353 | 29.4772 | 438.8646 | 0.51163 |  | 476 | 75.54 | 135.8353 | 5 | 438.8646
477 | 68.78 | 113.8071 | 28.5616 | 405.2548 | 0.51532 |  | 477 | 52.45 | 113.8071 | 4 | 405.2548
478 | 61.16 | 105.2795 | 25.0183 | 366.3241 | 0.51787 |  | 478 | 41.73 | 105.2795 | 3 | 366.3241
479 | 62.26 | 78.8914 | 27.6388 | 334.2365 | 0.5198 |  | 479 | 39.48 | 78.8914 | 2.2679 | 334.2365
480 | 57.47 | 41.2653 | 33.5992 | 376.6267 | 0.52406 |  | 480 | 32.44 | 41.2653 | 2 | 376.6267
481 | 55.54 | 34.4562 | 25.0849 | 319.659 | 0.52694 |  | 481 | 29.84 | 34.4562 | 2.2679 | 319.659
482 | 53.02 | 32.9805 | 228.2249 | 320.1344 | 0.52728 |  | 482 | 28 | 32.9805 | 3 | 320.1344
483 | 52.1 | 31.4695 | 26.7338 | 342.6298 | 0.52778 |  | 483 | 25.8 | 31.4695 | 4 | 342.6298
484 | 51.31 | 29.9774 | 37.3053 | 356.6585 | 0.52727 |  | 484 | 26.1 | 29.9774 | 5 | 356.6585
485 | 51.14 | 28.7668 | 35.9388 | 490.4127 | 0.52519 |  | 485 | 26.59 | 28.7668 | 5.7321 | 490.4127
486 | 53.23 | 27.9564 | 35.081 | 450.0544 | 0.52311 |  | 486 | 28.16 | 27.9564 | 6 | 450.0544
487 | 67.16 | 27.4227 | 229.5625 | 515.0085 | 0.51747 |  | 487 | 39.47 | 27.4227 | 5.7321 | 515.0085
488 | 79.62 | 30.1113 | 58.7912 | 507.2236 | 0.51872 |  | 488 | 70.01 | 30.1113 | 5 | 507.2236
489 | 88.06 | 53.7567 | 35.6246 | 495.797 | 0.52192 |  | 489 | 85.33 | 53.7567 | 4 | 495.797
490 | 86.01 | 67.0044 | 47.9294 | 346.0027 | 0.52034 |  | 490 | 83.81 | 67.0044 | 3 | 346.0027
491 | 80.04 | 70.872 | 40.9674 | 404.5548 | 0.5197 |  | 491 | 74.94 | 70.872 | 2.2679 | 404.5548
492 | 75 | 71.3284 | 48.1968 | 413.9815 | 0.51656 |  | 492 | 70.12 | 71.3284 | 2 | 413.9815
493 | 70.65 | 77.6657 | 34.4666 | 374.7194 | 0.51553 |  | 493 | 59.91 | 77.6657 | 2.2679 | 374.7194
494 | 71.56 | 72.7352 | 51.0626 | 408.8947 | 0.51636 |  | 494 | 57.69 | 72.7352 | 3 | 408.8947
495 | 72.03 | 68.6369 | 41.8285 | 357.3795 | 0.51507 |  | 495 | 57.99 | 68.6369 | 4 | 357.3795
496 | 76.49 | 69.8234 | 49.594 | 403.8619 | 0.51537 |  | 496 | 61.05 | 69.8234 | 5 | 403.8619
497 | 81.08 | 79.0788 | 47.7888 | 406.814 | 0.51445 |  | 497 | 57.43 | 79.0788 | 5.7321 | 406.814
498 | 88.35 | 121.2257 | 42.4315 | 389.5063 | 0.50849 |  | 498 | 78.65 | 121.2257 | 6 | 389.5063
499 | 88.5 | 165.3559 | 42.167 | 460.6666 | 0.50169 |  | 499 | 86.01 | 165.3559 | 5.7321 | 460.6666
500 | 79.93 | 134.9458 | 31.6926 | 387.775 | 0.49778 |  | 500 | 60.13 | 134.9458 | 5 | 387.775
501 | 73.69 | 117.7735 | 32.3568 | 412.324 | 0.49828 |  | 501 | 48.6 | 117.7735 | 4 | 412.324
502 | 66.52 | 101.7524 | 28.9903 | 426.7606 | 0.49837 |  | 502 | 36.2 | 101.7524 | 3 | 426.7606
503 | 53.6 | 89.499 | 35.4996 | 332.5187 | 0.49621 |  | 503 | 29.55 | 89.499 | 2.2679 | 332.5187
504 | 52.5 | 40.8429 | 37.1881 | 330.8798 | 0.48821 |  | 504 | 27.44 | 40.8429 | 2 | 330.8798
505 | 47.1 | 33.0211 | 32.0932 | 364.5373 | 0.47638 |  | 505 | 24.02 | 33.0211 | 2.2679 | 364.5373
506 | 48.66 | 31.7268 | 23.4575 | 293.7673 | 0.46386 |  | 506 | 23.92 | 31.7268 | 3 | 293.7673
507 | 48.41 | 30.2345 | 34.6788 | 282.4106 | 0.46828 |  | 507 | 23.4 | 30.2345 | 4 | 282.4106
508 | 50.8 | 29.0345 | 26.4522 | 298.8115 | 0.46941 |  | 508 | 24.07 | 29.0345 | 5 | 298.8115
509 | 51.73 | 28.1776 | 27.7879 | 386.9513 | 0.46496 |  | 509 | 23.92 | 28.1776 | 5.7321 | 386.9513
510 | 47.58 | 27.6816 | 37.4635 | 475.7563 | 0.46535 |  | 510 | 23.11 | 27.6816 | 6 | 475.7563
511 | 60.24 | 27.4339 | 28.4818 | 415.8285 | 0.46559 |  | 511 | 27.59 | 27.4339 | 5.7321 | 415.8285
512 | 71.19 | 30.1841 | 252.56 | 406.037 | 0.46489 |  | 512 | 47.5 | 30.1841 | 5 | 406.037
513 | 76.08 | 53.6453 | 50.9635 | 370.7963 | 0.46289 |  | 513 | 52.5 | 53.6453 | 4 | 370.7963
514 | 75.05 | 67.2929 | 39.8017 | 395.6592 | 0.46379 |  | 514 | 49.94 | 67.2929 | 3 | 395.6592
515 | 76.64 | 72.1278 | 25.6067 | 308.0827 | 0.46277 |  | 515 | 46.86 | 72.1278 | 2.2679 | 308.0827
516 | 72.8 | 72.6732 | 48.857 | 352.6739 | 0.46605 |  | 516 | 46.3 | 72.6732 | 2 | 352.6739
517 | 71.23 | 78.6274 | 42.8959 | 325.4714 | 0.46917 |  | 517 | 44.65 | 78.6274 | 2.2679 | 325.4714
518 | 72.8 | 78.5047 | 50.8611 | 307.5274 | 0.47027 |  | 518 | 39.09 | 78.5047 | 3 | 307.5274
519 | 74.3 | 74.8602 | 31.5537 | 346.5392 | 0.47324 |  | 519 | 34.79 | 74.8602 | 4 | 346.5392
520 | 75.04 | 74.4106 | 45.8317 | 397.9454 | 0.47605 |  | 520 | 34.29 | 74.4106 | 5 | 397.9454
521 | 81.45 | 77.7392 | 33.9808 | 337.3849 | 0.47647 |  | 521 | 34.29 | 77.7392 | 5.7321 | 337.3849
522 | 89.7 | 132.3768 | 51.0422 | 399.4861 | 0.47522 |  | 522 | 35 | 132.3768 | 6 | 399.4861
523 | 90.87 | 132.825 | 49.0618 | 351.624 | 0.4717 |  | 523 | 30.18 | 132.825 | 5.7321 | 351.624
524 | 82.76 | 152.8718 | 28.4429 | 383.2464 | 0.47688 |  | 524 | 27.38 | 152.8718 | 5 | 383.2464
525 | 58.34 | 119.1925 | 28.7806 | 343.3555 | 0.48218 |  | 525 | 25.65 | 119.1925 | 4 | 343.3555
526 | 55.38 | 105.1787 | 35.0889 | 334.8389 | 0.48835 |  | 526 | 24.88 | 105.1787 | 3 | 334.8389
527 | 52.7 | 87.8826 | 27.3671 | 278.8427 | 0.49584 |  | 527 | 24.53 | 87.8826 | 2.2679 | 278.8427
528 | 49.9 | 40.3065 | 38.4743 | 293.5637 | 0.50088 |  | 528 | 23.81 | 40.3065 | 2 | 293.5637
529 | 45.7 | 33.2145 | 22.8722 | 347.7828 | 0.50907 |  | 529 | 24.44 | 33.2145 | 2.2679 | 347.7828
530 | 50.41 | 31.6149 | 26.6235 | 251.8149 | 0.50794 |  | 530 | 24.02 | 31.6149 | 3 | 251.8149
531 | 49.9 | 30.1603 | 19.6632 | 271.0307 | 0.50641 |  | 531 | 23.03 | 30.1603 | 4 | 271.0307
532 | 51.19 | 28.8795 | 29.835 | 404.4247 | 0.51161 |  | 532 | 22.99 | 28.8795 | 5 | 404.4247
533 | 51.02 | 28.2346 | 24.3884 | 339.3479 | 0.52294 |  | 533 | 22.68 | 28.2346 | 5.7321 | 339.3479
534 | 54.81 | 28.243 | 22.2841 | 473.4845 | 0.52471 |  | 534 | 22.44 | 28.243 | 6 | 473.4845
535 | 61.86 | 44.3743 | 30.2185 | 451.2864 | 0.52133 |  | 535 | 21.46 | 44.3743 | 5.7321 | 451.2864
536 | 82.11 | 67.8907 | 44.2324 | 437.1811 | 0.52079 |  | 536 | 23.35 | 67.8907 | 5 | 437.1811
537 | 92.15 | 51.6306 | 39.2411 | 442.3673 | 0.52123 |  | 537 | 24.68 | 51.6306 | 4 | 442.3673
538 | 93.65 | 42.5519 | 48.1178 | 456.6455 | 0.52298 |  | 538 | 28.9 | 42.5519 | 3 | 456.6455
539 | 91.93 | 44.8682 | 45.0172 | 483.5851 | 0.52366 |  | 539 | 31.32 | 44.8682 | 2.2679 | 483.5851
540 | 93.13 | 48.8508 | 48.1857 | 410.622 | 0.50946 |  | 540 | 34.75 | 48.8508 | 2 | 410.622
541 | 84.96 | 49.8656 | 39.4235 | 420.2493 | 0.50224 |  | 541 | 34.39 | 49.8656 | 2.2679 | 420.2493
542 | 83.99 | 53.6861 | 236.4306 | 447.0982 | 0.50431 |  | 542 | 30.45 | 53.6861 | 3 | 447.0982
543 | 85.59 | 57.4454 | 48.2079 | 383.4165 | 0.50461 |  | 543 | 28.04 | 57.4454 | 4 | 383.4165
544 | 86.87 | 76.4349 | 39.3884 | 410.7315 | 0.50414 |  | 544 | 29.1 | 76.4349 | 5 | 410.7315
545 | 84.96 | 98.0358 | 45.9874 | 382.6798 | 0.50098 |  | 545 | 29.7 | 98.0358 | 5.7321 | 382.6798
546 | 90.01 | 151.4499 | 54.9375 | 464.2411 | 0.49691 |  | 546 | 36.97 | 151.4499 | 6 | 464.2411
547 | 94.15 | 163.7677 | 36.1348 | 377.9947 | 0.49827 |  | 547 | 42.6 | 163.7677 | 5.7321 | 377.9947
548 | 90.54 | 144.5068 | 26.3085 | 441.4515 | 0.49916 |  | 548 | 35.83 | 144.5068 | 5 | 441.4515
549 | 78.43 | 116.71 | 26.6251 | 357.0738 | 0.50263 |  | 549 | 28.84 | 116.71 | 4 | 357.0738
550 | 68.04 | 103.2982 | 34.3396 | 350.3956 | 0.50942 |  | 550 | 25.4 | 103.2982 | 3 | 350.3956
551 | 59.88 | 75.8175 | 31.6426 | 384.4848 | 0.50548 |  | 551 | 26.27 | 75.8175 | 2.2679 | 384.4848
552 | 50.6 | 38.9017 | 33.4594 | 400.524 | 0.51283 |  | 552 | 24.94 | 38.9017 | 2 | 400.524
553 | 59.9 | 34.6021 | 30.141 | 335.092 | 0.5256 |  | 553 | 24.08 | 34.6021 | 2.2679 | 335.092
554 | 57.65 | 32.8281 | 29.2071 | 359.249 | 0.52671 |  | 554 | 23.99 | 32.8281 | 3 | 359.249
555 | 57.4 | 31.239 | 31.9416 | 338.5371 | 0.52762 |  | 555 | 21.4 | 31.239 | 4 | 338.5371
556 | 56.13 | 29.8293 | 30.5551 | 318.7273 | 0.52771 |  | 556 | 23.24 | 29.8293 | 5 | 318.7273
557 | 56.95 | 28.8194 | 29.2203 | 370.9416 | 0.52651 |  | 557 | 22.54 | 28.8194 | 5.7321 | 370.9416
558 | 61.53 | 28.4329 | 35.2845 | 502.8949 | 0.52722 |  | 558 | 23.41 | 28.4329 | 6 | 502.8949
559 | 70.75 | 43.6065 | 30.8354 | 473.48 | 0.52548 |  | 559 | 21.41 | 43.6065 | 5.7321 | 473.48
560 | 99.07 | 67.0517 | 52.2748 | 422.3771 | 0.52315 |  | 560 | 24.04 | 67.0517 | 5 | 422.3771
561 | 113.07 | 50.5315 | 34.4573 | 460.4428 | 0.52156 |  | 561 | 24.96 | 50.5315 | 4 | 460.4428
562 | 111.23 | 43.3259 | 47.8602 | 359.5197 | 0.52043 |  | 562 | 27.21 | 43.3259 | 3 | 359.5197
563 | 108.25 | 45.7636 | 255.7495 | 367.8949 | 0.51974 |  | 563 | 29.22 | 45.7636 | 2.2679 | 367.8949
564 | 103.69 | 49.6876 | 44.5893 | 319.0022 | 0.5194 |  | 564 | 33.09 | 49.6876 | 2 | 319.0022
565 | 98.33 | 50.229 | 39.3016 | 362.2336 | 0.52055 |  | 565 | 30.91 | 50.229 | 2.2679 | 362.2336
566 | 92.63 | 51.0493 | 50.6084 | 356.6622 | 0.52164 |  | 566 | 27.8 | 51.0493 | 3 | 356.6622
567 | 89.86 | 58.363 | 60.8995 | 306.5847 | 0.52289 |  | 567 | 24.84 | 58.363 | 4 | 306.5847
568 | 90.45 | 76.0461 | 52.3037 | 300.5478 | 0.52487 |  | 568 | 23.99 | 76.0461 | 5 | 300.5478
569 | 95.01 | 99.199 | 36.4347 | 308.6105 | 0.5264 |  | 569 | 25.04 | 99.199 | 5.7321 | 308.6105
570 | 106.82 | 150.3074 | 55.9964 | 344.2506 | 0.52414 |  | 570 | 32.88 | 150.3074 | 6 | 344.2506
571 | 121.46 | 152.7401 | 46.8078 | 314.8514 | 0.52131 |  | 571 | 36.09 | 152.7401 | 5.7321 | 314.8514
572 | 102.06 | 142.1914 | 30.2214 | 366.6949 | 0.52099 |  | 572 | 35.34 | 142.1914 | 5 | 366.6949
573 | 89.34 | 118.9009 | 30.6821 | 414.7225 | 0.52142 |  | 573 | 31.7 | 118.9009 | 4 | 414.7225
574 | 74.43 | 108.8511 | 19.7733 | 323.1121 | 0.52425 |  | 574 | 26 | 108.8511 | 3 | 323.1121
575 | 69.63 | 77.6958 | 29.8276 | 356.4715 | 0.52526 |  | 575 | 27.09 | 77.6958 | 2.2679 | 356.4715
576 | 61.1 | 39.7736 | 29.3929 | 292.8584 | 0.51643 |  | 576 | 22.44 | 39.7736 | 2 | 292.8584
577 | 64.63 | 34.0191 | 27.8476 | 278.3766 | 0.52548 |  | 577 | 20.07 | 34.0191 | 2.2679 | 278.3766
578 | 60.64 | 32.4978 | 26.4636 | 288.7137 | 0.53006 |  | 578 | 19.65 | 32.4978 | 3 | 288.7137
579 | 57.8 | 30.9781 | 23.5852 | 270.2903 | 0.53424 |  | 579 | 19.68 | 30.9781 | 4 | 270.2903
580 | 55.19 | 29.5685 | 22.7515 | 364.0509 | 0.53887 |  | 580 | 19.98 | 29.5685 | 5 | 364.0509
581 | 55.28 | 28.6962 | 29.1842 | 347.7599 | 0.53653 |  | 581 | 20.33 | 28.6962 | 5.7321 | 347.7599
582 | 58.98 | 28.5978 | 26.3707 | 408.3112 | 0.53651 |  | 582 | 21.32 | 28.5978 | 6 | 408.3112
583 | 64.51 | 43.8933 | 25.1949 | 416.0081 | 0.53341 |  | 583 | 25.01 | 43.8933 | 5.7321 | 416.0081
584 | 84.48 | 66.5153 | 41.5541 | 344.9662 | 0.53143 |  | 584 | 35.12 | 66.5153 | 5 | 344.9662
585 | 97 | 48.3185 | 46.4509 | 362.3121 | 0.52917 |  | 585 | 35 | 48.3185 | 4 | 362.3121
586 | 93.64 | 40.6161 | 32.7913 | 399.9899 | 0.52593 |  | 586 | 36.16 | 40.6161 | 3 | 399.9899
587 | 85 | 42.4178 | 34.586 | 317.0034 | 0.52268 |  | 587 | 36.62 | 42.4178 | 2.2679 | 317.0034
588 | 78 | 43.6695 | 47.6387 | 371.4144 | 0.51729 |  | 588 | 35.6 | 43.6695 | 2 | 371.4144
589 | 71.81 | 47.2953 | 46.2206 | 297.2139 | 0.51356 |  | 589 | 34.75 | 47.2953 | 2.2679 | 297.2139
590 | 69.87 | 47.8521 | 43.9036 | 193.6746 | 0.50913 |  | 590 | 32.26 | 47.8521 | 3 | 193.6746
591 | 68.64 | 57.8837 | 43.586 | 174.6571 | 0.50073 |  | 591 | 30.61 | 57.8837 | 4 | 174.6571
592 | 65.58 | 74.3195 | 50.4673 | 225.9509 | 0.49559 |  | 592 | 29.73 | 74.3195 | 5 | 225.9509
593 | 65.08 | 94.2889 | 46.9018 | 280.6364 | 0.48703 |  | 593 | 31.17 | 94.2889 | 5.7321 | 280.6364
594 | 70.87 | 146.6396 | 31.8215 | 328.3673 | 0.48243 |  | 594 | 34.96 | 146.6396 | 6 | 328.3673
595 | 71.52 | 161.3969 | 36.0014 | 364.5665 | 0.47529 |  | 595 | 36.4 | 161.3969 | 5.7321 | 364.5665
596 | 51.33 | 140.3224 | 32.1708 | 366.1825 | 0.47309 |  | 596 | 32.05 | 140.3224 | 5 | 366.1825
597 | 49.5 | 113.5135 | 26.9408 | 348.78 | 0.47087 |  | 597 | 26.8 | 113.5135 | 4 | 348.78
598 | 49.8 | 106.4724 | 23.3208 | 304.7771 | 0.46547 |  | 598 | 25.32 | 106.4724 | 3 | 304.7771
599 | 47.21 | 77.8912 | 23.849 | 330.0738 | 0.46236 |  | 599 | 23.93 | 77.8912 | 2.2679 | 330.0738
600 | 43 | 39.7089 | 26.3956 | 307.5698 | 0.45931 |  | 600 | 18.71 | 39.7089 | 2 | 307.5698
601 | 48.9 | 35.4147 | 24.1461 | 259.0512 | 0.46559 |  | 601 | 20.23 | 35.4147 | 2.2679 | 259.0512
602 | 54.88 | 33.6514 | 29.7635 | 272.9745 | 0.48109 |  | 602 | 18.02 | 33.6514 | 3 | 272.9745
603 | 49.9 | 31.85 | 230.1806 | 257.6681 | 0.48564 |  | 603 | 19.96 | 31.85 | 4 | 257.6681
604 | 41.96 | 30.2625 | 34.3061 | 352.2688 | 0.4788 |  | 604 | 21.2 | 30.2625 | 5 | 352.2688
605 | 41.65 | 29.0536 | 35.7783 | 306.3199 | 0.46989 |  | 605 | 21.72 | 29.0536 | 5.7321 | 306.3199
606 | 40.72 | 28.4915 | 225.6449 | 341.5383 | 0.4486 |  | 606 | 22.03 | 28.4915 | 6 | 341.5383
607 | 41.53 | 42.5668 | 20.5303 | 431.8719 | 0.44466 |  | 607 | 27.09 | 42.5668 | 5.7321 | 431.8719
608 | 47.5 | 65.3354 | 43.0221 | 437.6853 | 0.44757 |  | 608 | 39 | 65.3354 | 5 | 437.6853
609 | 51.37 | 48.6948 | 57.2012 | 314.4443 | 0.45736 |  | 609 | 39 | 48.6948 | 4 | 314.4443
610 | 56.33 | 41.5773 | 31.1815 | 320.4831 | 0.46343 |  | 610 | 43.45 | 41.5773 | 3 | 320.4831
611 | 58.62 | 44.6587 | 55.0157 | 315.0431 | 0.46276 |  | 611 | 40 | 44.6587 | 2.2679 | 315.0431
612 | 59.18 | 45.6725 | 38.7594 | 289.327 | 0.46399 |  | 612 | 38 | 45.6725 | 2 | 289.327
613 | 56.72 | 48.654 | 46.2114 | 206.144 | 0.46661 |  | 613 | 30.12 | 48.654 | 2.2679 | 206.144
614 | 57.44 | 49.9008 | 41.9285 | 148.5095 | 0.46391 |  | 614 | 34.4 | 49.9008 | 3 | 148.5095
615 | 53.32 | 55.7212 | 32.3537 | 165.9293 | 0.4624 |  | 615 | 28.07 | 55.7212 | 4 | 165.9293
616 | 52.8 | 71.3793 | 39.2805 | 228.7935 | 0.46178 |  | 616 | 30.09 | 71.3793 | 5 | 228.7935
617 | 52.44 | 90.6574 | 47.972 | 262.2138 | 0.45993 |  | 617 | 30.62 | 90.6574 | 5.7321 | 262.2138
618 | 55.95 | 148.6199 | 35.0916 | 298.592 | 0.45903 |  | 618 | 32.87 | 148.6199 | 6 | 298.592
619 | 57.92 | 149.3639 | 51.2306 | 291.1284 | 0.45406 |  | 619 | 35 | 149.3639 | 5.7321 | 291.1284
620 | 52.75 | 135.4289 | 31.4108 | 289.8154 | 0.44904 |  | 620 | 24.94 | 135.4289 | 5 | 289.8154
621 | 47.4 | 114.4301 | 30.1674 | 321.733 | 0.44762 |  | 621 | 29 | 114.4301 | 4 | 321.733
622 | 44.99 | 114.4415 | 27.2466 | 314.7501 | 0.4447 |  | 622 | 24 | 114.4415 | 3 | 314.7501
623 | 44.04 | 79.7494 | 31.0404 | 267.0052 | 0.44304 |  | 623 | 24.16 | 79.7494 | 2.2679 | 267.0052
624 | 40.4 | 40.7545 | 27.1061 | 220.1571 | 0.43165 |  | 624 | 34.35 | 40.7545 | 2 | 220.1571
625 | 45 | 32.9339 | 25.322 | 284.8253 | 0.41952 |  | 625 | 22.22 | 32.9339 | 2.2679 | 284.8253
626 | 48 | 31.6987 | 34.7981 | 272.6668 | 0.41764 |  | 626 | 20 | 31.6987 | 3 | 272.6668
627 | 44.6 | 30.4326 | 23.1989 | 287.202 | 0.41558 |  | 627 | 20 | 30.4326 | 4 | 287.202
628 | 38.9 | 29.1198 | 27.2568 | 334.9032 | 0.40481 |  | 628 | 14.59 | 29.1198 | 5 | 334.9032
629 | 33.58 | 28.1498 | 30.4834 | 340.1324 | 0.39784 |  | 629 | 12.45 | 28.1498 | 5.7321 | 340.1324
630 | 19.9 | 27.9884 | 29.3472 | 445.2131 | 0.39628 |  | 630 | 17.96 | 27.9884 | 6 | 445.2131
631 | 26 | 42.8919 | 31.6479 | 431.2583 | 0.40988 |  | 631 | 25.85 | 42.8919 | 5.7321 | 431.2583
632 | 37.4 | 63.9942 | 48.2197 | 349.4897 | 0.42007 |  | 632 | 31.17 | 63.9942 | 5 | 349.4897
633 | 34.97 | 49.1803 | 40.666 | 350.4055 | 0.44814 |  | 633 | 32.44 | 49.1803 | 4 | 350.4055
634 | 43.1 | 42.0894 | 30.9855 | 336.7659 | 0.47622 |  | 634 | 33 | 42.0894 | 3 | 336.7659
635 | 54.35 | 46.5005 | 48.4308 | 359.1703 | 0.49002 |  | 635 | 29.94 | 46.5005 | 2.2679 | 359.1703
636 | 55 | 45.44 | 32.3611 | 348.9216 | 0.48026 |  | 636 | 40.1 | 45.44 | 2 | 348.9216
637 | 46.97 | 49.1542 | 54.931 | 237.6978 | 0.46072 |  | 637 | 36.34 | 49.1542 | 2.2679 | 237.6978
638 | 43.25 | 49.9607 | 59.1787 | 287.6865 | 0.4502 |  | 638 | 29.96 | 49.9607 | 3 | 287.6865
639 | 41.25 | 57.6437 | 29.8432 | 247.6313 | 0.45798 |  | 639 | 27.06 | 57.6437 | 4 | 247.6313
640 | 40.67 | 72.1305 | 53.9323 | 239.2899 | 0.46197 |  | 640 | 27.44 | 72.1305 | 5 | 239.2899
641 | 41.26 | 92.9237 | 39.7132 | 336.5465 | 0.45415 |  | 641 | 26.87 | 92.9237 | 5.7321 | 336.5465
642 | 47.25 | 147.5183 | 44.2596 | 399.6205 | 0.45003 |  | 642 | 33.9 | 147.5183 | 6 | 399.6205
643 | 52.64 | 155.2192 | 43.0407 | 410.8787 | 0.44527 |  | 643 | 37.44 | 155.2192 | 5.7321 | 410.8787
644 | 52.96 | 143.1484 | 26.3463 | 327.2745 | 0.43967 |  | 644 | 29.96 | 143.1484 | 5 | 327.2745
645 | 50.44 | 116.4255 | 28.7287 | 319.3521 | 0.43622 |  | 645 | 30 | 116.4255 | 4 | 319.3521
646 | 47.78 | 104.7963 | 31.9707 | 378.7431 | 0.43555 |  | 646 | 24.96 | 104.7963 | 3 | 378.7431
647 | 50.82 | 74.2583 | 26.4573 | 360.5269 | 0.43375 |  | 647 | 27.44 | 74.2583 | 2.2679 | 360.5269
648 | 44.85 | 37.9168 | 38.6188 | 302.1315 | 0.43271 |  | 648 | 27.44 | 37.9168 | 2 | 302.1315
649 | 49.39 | 33.9279 | 31.0334 | 305.2475 | 0.4427 |  | 649 | 21 | 33.9279 | 2.2679 | 305.2475
650 | 40.97 | 32.4541 | 35.2486 | 278.2392 | 0.45147 |  | 650 | 22.79 | 32.4541 | 3 | 278.2392
651 | 40.42 | 30.9182 | 27.121 | 347.1648 | 0.43399 |  | 651 | 20.08 | 30.9182 | 4 | 347.1648
652 | 37.8 | 29.5565 | 29.3082 | 363.2921 | 0.42258 |  | 652 | 14.69 | 29.5565 | 5 | 363.2921
653 | 38.09 | 28.6923 | 28.6285 | 406.0203 | 0.41666 |  | 653 | 13.3 | 28.6923 | 5.7321 | 406.0203
654 | 41.83 | 27.8742 | 225.7937 | 411.7448 | 0.42183 |  | 654 | 17.39 | 27.8742 | 6 | 411.7448
655 | 53.09 | 27.4283 | 24.7345 | 478.7177 | 0.43164 |  | 655 | 23.41 | 27.4283 | 5.7321 | 478.7177
656 | 64.04 | 30.5198 | 44.1933 | 458.1071 | 0.44166 |  | 656 | 34.11 | 30.5198 | 5 | 458.1071
657 | 64.65 | 53.2912 | 38.2682 | 394.0106 | 0.44881 |  | 657 | 31.2 | 53.2912 | 4 | 394.0106
658 | 59.92 | 67.7756 | 41.3874 | 410.7322 | 0.45204 |  | 658 | 32 | 67.7756 | 3 | 410.7322
659 | 53.43 | 71.7952 | 41.6475 | 393.0075 | 0.45276 |  | 659 | 29.94 | 71.7952 | 2.2679 | 393.0075
660 | 55.78 | 73.7003 | 46.7255 | 295.2104 | 0.45085 |  | 660 | 26.22 | 73.7003 | 2 | 295.2104
661 | 53.79 | 76.2565 | 37.8249 | 290.8494 | 0.45273 |  | 661 | 24.44 | 76.2565 | 2.2679 | 290.8494
662 | 50 | 72.11 | 52.261 | 290.2689 | 0.45543 |  | 662 | 26.2 | 72.11 | 3 | 290.2689
663 | 48.96 | 68.9054 | 37.5801 | 359.0389 | 0.45778 |  | 663 | 27.16 | 68.9054 | 4 | 359.0389
664 | 47.4 | 74.7427 | 237.1252 | 301.9606 | 0.46328 |  | 664 | 31.02 | 74.7427 | 5 | 301.9606
665 | 51.74 | 80.329 | 25.5135 | 367.5173 | 0.46551 |  | 665 | 33.58 | 80.329 | 5.7321 | 367.5173
666 | 62 | 134.7935 | 35.0769 | 414.1847 | 0.46511 |  | 666 | 39.05 | 134.7935 | 6 | 414.1847
667 | 59.9 | 146.5588 | 35.1314 | 434.2131 | 0.46034 |  | 667 | 42.44 | 146.5588 | 5.7321 | 434.2131
668 | 53.85 | 149.3638 | 36.1082 | 379.2114 | 0.47023 |  | 668 | 35.81 | 149.3638 | 5 | 379.2114
669 | 49.9 | 115.2281 | 34.3977 | 403.4238 | 0.47332 |  | 669 | 29.96 | 115.2281 | 4 | 403.4238
670 | 50.35 | 101.3266 | 29.1056 | 324.5435 | 0.48494 |  | 670 | 27.42 | 101.3266 | 3 | 324.5435
671 | 46.36 | 88.755 | 28.4642 | 364.7039 | 0.49628 |  | 671 | 25 | 88.755 | 2.2679 | 364.7039
672 | 44.9 | 39.9042 | 34.7335 | 284.3734 | 0.49385 |  | 672 | 20.79 | 39.9042 | 2 | 284.3734
673 | 47.6 | 35.2252 | 26.9206 | 345.825 | 0.49789 |  | 673 | 21.1 | 35.2252 | 2.2679 | 345.825
674 | 48.66 | 33.2558 | 30.4782 | 307.945 | 0.51221 |  | 674 | 19.53 | 33.2558 | 3 | 307.945
675 | 48.09 | 31.5219 | 28.3494 | 291.9665 | 0.5145 |  | 675 | 19.06 | 31.5219 | 4 | 291.9665
676 | 45.22 | 30.0328 | 30.1916 | 359.4477 | 0.52076 |  | 676 | 18.08 | 30.0328 | 5 | 359.4477
677 | 45.97 | 28.9252 | 28.6293 | 443.1196 | 0.50991 |  | 677 | 16.14 | 28.9252 | 5.7321 | 443.1196
678 | 47.4 | 28.3213 | 32.9765 | 397.7347 | 0.49683 |  | 678 | 19.63 | 28.3213 | 6 | 397.7347
679 | 55.93 | 27.9537 | 24.2772 | 462.5882 | 0.49042 |  | 679 | 26 | 27.9537 | 5.7321 | 462.5882
680 | 65.78 | 31.1847 | 36.1468 | 481.4691 | 0.48588 |  | 680 | 34.91 | 31.1847 | 5 | 481.4691
681 | 72.98 | 53.307 | 34.0107 | 444.7001 | 0.4869 |  | 681 | 36.07 | 53.307 | 4 | 444.7001
682 | 72.58 | 69.8698 | 42.8377 | 427.4305 | 0.48689 |  | 682 | 35.1 | 69.8698 | 3 | 427.4305
683 | 71.36 | 75.3731 | 69.8699 | 347.9 | 0.48525 |  | 683 | 30.01 | 75.3731 | 2.2679 | 347.9
684 | 70.14 | 77.3863 | 32.4136 | 324.5338 | 0.4831 |  | 684 | 34 | 77.3863 | 2 | 324.5338
685 | 65.99 | 82.3437 | 49.7578 | 271.3582 | 0.48031 |  | 685 | 37 | 82.3437 | 2.2679 | 271.3582
686 | 66.77 | 83.1171 | 34.1743 | 243.0794 | 0.48393 |  | 686 | 37.01 | 83.1171 | 3 | 243.0794
687 | 66.56 | 79.6718 | 46.1379 | 177.2602 | 0.49074 |  | 687 | 32.93 | 79.6718 | 4 | 177.2602
688 | 66 | 79.1118 | 48.8282 | 138.4916 | 0.48592 |  | 688 | 27.81 | 79.1118 | 5 | 138.4916
689 | 69.33 | 80.4201 | 53.6402 | 176.8965 | 0.48146 |  | 689 | 29 | 80.4201 | 5.7321 | 176.8965
690 | 71.45 | 135.0238 | 33.0301 | 299.0155 | 0.4765 |  | 690 | 31.1 | 135.0238 | 6 | 299.0155
691 | 72.82 | 156.2988 | 37.1868 | 321.7317 | 0.46658 |  | 691 | 34.94 | 156.2988 | 5.7321 | 321.7317
692 | 69.81 | 156.3126 | 24.4988 | 302.483 | 0.4642 |  | 692 | 31.32 | 156.3126 | 5 | 302.483
693 | 56.22 | 120.2258 | 30.8055 | 346.3742 | 0.46396 |  | 693 | 28.1 | 120.2258 | 4 | 346.3742
694 | 53.47 | 106.7104 | 27.6854 | 302.5346 | 0.46692 |  | 694 | 29.38 | 106.7104 | 3 | 302.5346
695 | 45 | 90.7196 | 27.3404 | 252.5962 | 0.47734 |  | 695 | 27.11 | 90.7196 | 2.2679 | 252.5962
696 | 48 | 41.6522 | 34.6376 | 307.1467 | 0.48369 |  | 696 | 22 | 41.6522 | 2 | 307.1467
697 | 43 | 34.0123 | 25.831 | 266.7372 | 0.48965 |  | 697 | 14.08 | 34.0123 | 2.2679 | 266.7372
698 | 46.36 | 32.587 | 26.8909 | 272.7008 | 0.49384 |  | 698 | 18.17 | 32.587 | 3 | 272.7008
699 | 45.1 | 30.955 | 228.3825 | 301.0164 | 0.49766 |  | 699 | 18.67 | 30.955 | 4 | 301.0164
700 | 42.85 | 29.5231 | 33.6378 | 285.0571 | 0.50141 |  | 700 | 16.44 | 29.5231 | 5 | 285.0571
701 | 42.74 | 28.5961 | 22.4672 | 380.1896 | 0.50421 |  | 701 | 10.54 | 28.5961 | 5.7321 | 380.1896
702 | 46.34 | 28.2792 | 35.39 | 365.134 | 0.50719 |  | 702 | 12.45 | 28.2792 | 6 | 365.134
703 | 52.12 | 43.8009 | 40.2739 | 347.6824 | 0.5066 |  | 703 | 16.12 | 43.8009 | 5.7321 | 347.6824
704 | 64.99 | 67.9457 | 40.3111 | 339.0533 | 0.5084 |  | 704 | 20.88 | 67.9457 | 5 | 339.0533
705 | 68.17 | 50.549 | 43.6914 | 297.0156 | 0.50949 |  | 705 | 19.96 | 50.549 | 4 | 297.0156
706 | 72.47 | 43.1591 | 50.5462 | 317.1853 | 0.51186 |  | 706 | 25 | 43.1591 | 3 | 317.1853
707 | 83.6 | 45.2876 | 46.6464 | 292.1126 | 0.51386 |  | 707 | 30 | 45.2876 | 2.2679 | 292.1126
708 | 82.83 | 47.2983 | 45.9565 | 252.7418 | 0.51386 |  | 708 | 40.25 | 47.2983 | 2 | 252.7418
709 | 84.32 | 50.6749 | 52.8245 | 228.0932 | 0.51457 |  | 709 | 45.11 | 50.6749 | 2.2679 | 228.0932
710 | 85.38 | 51.7374 | 42.5111 | 171.1753 | 0.5164 |  | 710 | 36 | 51.7374 | 3 | 171.1753
711 | 74.6 | 57.6321 | 37.7791 | 112.4593 | 0.51744 |  | 711 | 30 | 57.6321 | 4 | 112.4593
712 | 78.8 | 74.0602 | 46.76 | 93.4882 | 0.51929 |  | 712 | 27.44 | 74.0602 | 5 | 93.4882
713 | 76.43 | 91.7196 | 39.0911 | 163.3439 | 0.51725 |  | 713 | 24.96 | 91.7196 | 5.7321 | 163.3439
714 | 72.96 | 148.334 | 41.9424 | 268.6496 | 0.51119 |  | 714 | 31.1 | 148.334 | 6 | 268.6496
715 | 94.59 | 159.4116 | 51.6467 | 315.3327 | 0.50147 |  | 715 | 30.12 | 159.4116 | 5.7321 | 315.3327
716 | 60 | 131.0383 | 28.7625 | 295.172 | 0.50078 |  | 716 | 27.3 | 131.0383 | 5 | 295.172
717 | 58 | 117.2297 | 27.6442 | 333.0956 | 0.50353 |  | 717 | 25 | 117.2297 | 4 | 333.0956
718 | 56.23 | 106.6633 | 24.1373 | 305.6255 | 0.50865 |  | 718 | 24.5 | 106.6633 | 3 | 305.6255
719 | 50.1 | 77.3382 | 23.9933 | 249.7824 | 0.51213 |  | 719 | 23.57 | 77.3382 | 2.2679 | 249.7824
720 | 47.1 | 39.266 | 34.2359 | 276.419 | 0.51929 |  | 720 | 24.75 | 39.266 | 2 | 276.419
721 | 43.9 | 35.1742 | 25.8696 | 280.2806 | 0.52873 |  | 721 | 19 | 35.1742 | 2.2679 | 280.2806
722 | 46.84 | 33.4081 | 27.0007 | 221.5626 | 0.52822 |  | 722 | 17.22 | 33.4081 | 3 | 221.5626
723 | 46.78 | 31.6603 | 29.368 | 237.1916 | 0.5271 |  | 723 | 15.66 | 31.6603 | 4 | 237.1916
724 | 46.82 | 30.1067 | 26.95 | 258.4598 | 0.52321 |  | 724 | 20.05 | 30.1067 | 5 | 258.4598
725 | 45.08 | 29.0297 | 223.8102 | 298.9156 | 0.51896 |  | 725 | 15.82 | 29.0297 | 5.7321 | 298.9156
726 | 48.7 | 28.7412 | 23.2456 | 357.5599 | 0.51861 |  | 726 | 15.93 | 28.7412 | 6 | 357.5599
727 | 62.27 | 43.9728 | 19.5995 | 379.3073 | 0.51432 |  | 727 | 20.68 | 43.9728 | 5.7321 | 379.3073
728 | 71.7 | 66.9417 | 43.3442 | 361.0264 | 0.51535 |  | 728 | 20.12 | 66.9417 | 5 | 361.0264
729 | 78.49 | 50.8293 | 32.5526 | 421.6794 | 0.51504 |  | 729 | 18 | 50.8293 | 4 | 421.6794
730 | 79.36 | 43.3285 | 236.7928 | 371.1513 | 0.5121 |  | 730 | 23.84 | 43.3285 | 3 | 371.1513
731 | 77.96 | 46.6716 | 36.9844 | 314.7368 | 0.51499 |  | 731 | 26 | 46.6716 | 2.2679 | 314.7368
732 | 71.59 | 47.8324 | 46.57 | 212.313 | 0.51571 |  | 732 | 29 | 47.8324 | 2 | 212.313
733 | 66.81 | 49.849 | 46.2068 | 204.7795 | 0.51332 |  | 733 | 33.12 | 49.849 | 2.2679 | 204.7795
734 | 66.22 | 51.5513 | 28.3922 | 161.4086 | 0.51118 |  | 734 | 27.3 | 51.5513 | 3 | 161.4086
735 | 66.16 | 58.4767 | 38.7682 | 170.2352 | 0.51268 |  | 735 | 22.82 | 58.4767 | 4 | 170.2352
736 | 66.16 | 73.5552 | 38.9071 | 186.8818 | 0.5062 |  | 736 | 20 | 73.5552 | 5 | 186.8818
737 | 65.35 | 93.6721 | 35.8076 | 223.5484 | 0.50687 |  | 737 | 20.12 | 93.6721 | 5.7321 | 223.5484
738 | 66.68 | 140.6102 | 37.3653 | 316.5624 | 0.50713 |  | 738 | 24.94 | 140.6102 | 6 | 316.5624
739 | 66.98 | 158.2278 | 50.7992 | 280.0888 | 0.50241 |  | 739 | 26.28 | 158.2278 | 5.7321 | 280.0888
740 | 65.4 | 137.0964 | 31.9679 | 312.213 | 0.49734 |  | 740 | 27.44 | 137.0964 | 5 | 312.213
741 | 59.9 | 115.2802 | 26.9057 | 288.9368 | 0.48743 |  | 741 | 27 | 115.2802 | 4 | 288.9368
742 | 52.84 | 105.6901 | 18.6215 | 249.9278 | 0.48451 |  | 742 | 20.89 | 105.6901 | 3 | 249.9278
743 | 51.36 | 76.3078 | 37.4248 | 220.9294 | 0.47564 |  | 743 | 18.79 | 76.3078 | 2.2679 | 220.9294
744 | 47.36 | 40.7229 | 31.8545 | 206.5786 | 0.4699 |  | 744 | 16.45 | 40.7229 | 2 | 206.5786
745 | 44.09 | 33.4703 | 27.7504 | 161.7019 | 0.46914 |  | 745 | 16.31 | 33.4703 | 2.2679 | 161.7019
746 | 45.47 | 32.0101 | 29.4674 | 155.5372 | 0.47022 |  | 746 | 14.42 | 32.0101 | 3 | 155.5372
747 | 43.1 | 30.548 | 21.0133 | 183.2092 | 0.46858 |  | 747 | 15.07 | 30.548 | 4 | 183.2092
748 | 41.1 | 29.3326 | 26.8104 | 195.7246 | 0.47262 |  | 748 | 15.24 | 29.3326 | 5 | 195.7246
749 | 41.51 | 28.4318 | 19.0031 | 232.5017 | 0.47559 |  | 749 | 12.81 | 28.4318 | 5.7321 | 232.5017
750 | 45.76 | 28.175 | 30.8492 | 263.2184 | 0.47407 |  | 750 | 14.12 | 28.175 | 6 | 263.2184
751 | 52.44 | 43.3154 | 29.3011 | 301.5525 | 0.47585 |  | 751 | 23.93 | 43.3154 | 5.7321 | 301.5525
752 | 66.44 | 68.1665 | 236.7833 | 278.1218 | 0.47436 |  | 752 | 35.9 | 68.1665 | 5 | 278.1218
753 | 72.94 | 47.8094 | 54.0525 | 264.0269 | 0.47487 |  | 753 | 37.99 | 47.8094 | 4 | 264.0269
754 | 84.25 | 41.028 | 49.5317 | 237.4724 | 0.47622 |  | 754 | 36.05 | 41.028 | 3 | 237.4724
755 | 83.81 | 44.8285 | 36.5187 | 246.2937 | 0.47961 |  | 755 | 33.34 | 44.8285 | 2.2679 | 246.2937
756 | 84.23 | 45.5947 | 37.3961 | 191.7559 | 0.48203 |  | 756 | 29.24 | 45.5947 | 2 | 191.7559
757 | 80.49 | 47.8439 | 42.5789 | 117.4081 | 0.49219 |  | 757 | 29.94 | 47.8439 | 2.2679 | 117.4081
758 | 78.64 | 47.9721 | 38.4489 | 80.8504 | 0.49353 |  | 758 | 27.66 | 47.9721 | 3 | 80.8504
759 | 65.52 | 55.1104 | 48.9233 | 53.4403 | 0.49541 |  | 759 | 27.5 | 55.1104 | 4 | 53.4403
760 | 64.55 | 71.8075 | 42.0748 | 63.8147 | 0.49474 |  | 760 | 27.5 | 71.8075 | 5 | 63.8147
761 | 63.91 | 93.1237 | 51.2819 | 117.3215 | 0.49617 |  | 761 | 24.85 | 93.1237 | 5.7321 | 117.3215
762 | 67.71 | 137.4958 | 54.2755 | 200.4149 | 0.49333 |  | 762 | 28 | 137.4958 | 6 | 200.4149
763 | 70.25 | 173.8474 | 37.7718 | 277.3486 | 0.4892 |  | 763 | 39.28 | 173.8474 | 5.7321 | 277.3486
764 | 69.9 | 140.7656 | 29.0436 | 256.6599 | 0.49043 |  | 764 | 39.98 | 140.7656 | 5 | 256.6599
765 | 62.99 | 114.3078 | 29.1626 | 261.0882 | 0.49144 |  | 765 | 34.94 | 114.3078 | 4 | 261.0882
766 | 56.05 | 106.8019 | 23.8339 | 219.9736 | 0.49285 |  | 766 | 21.37 | 106.8019 | 3 | 219.9736
767 | 54.01 | 76.3826 | 27.2169 | 252.0723 | 0.49706 |  | 767 | 20.23 | 76.3826 | 2.2679 | 252.0723
768 | 50.92 | 38.2487 | 24.0932 | 206.1651 | 0.50404 |  | 768 | 22.24 | 38.2487 | 2 | 206.1651
769 | 49.21 | 33.9211 | 37.6227 | 224.8104 | 0.51347 |  | 769 | 17.03 | 33.9211 | 2.2679 | 224.8104
770 | 47.07 | 32.4324 | 22.4747 | 258.3106 | 0.51257 |  | 770 | 17.36 | 32.4324 | 3 | 258.3106
771 | 45.7 | 30.9628 | 25.3056 | 242.4708 | 0.51389 |  | 771 | 16.5 | 30.9628 | 4 | 242.4708
772 | 43.14 | 29.548 | 30.016 | 280.1859 | 0.51282 |  | 772 | 11.34 | 29.548 | 5 | 280.1859
773 | 42.71 | 28.5553 | 25.4587 | 293.8171 | 0.50952 |  | 773 | 14.04 | 28.5553 | 5.7321 | 293.8171
774 | 42.6 | 28.5004 | 25.1725 | 339.5662 | 0.50556 |  | 774 | 9.52 | 28.5004 | 6 | 339.5662
775 | 43.47 | 42.7316 | 20.1159 | 335.1323 | 0.50505 |  | 775 | 22.72 | 42.7316 | 5.7321 | 335.1323
776 | 47.68 | 65.1785 | 49.0612 | 351.6128 | 0.50605 |  | 776 | 30.54 | 65.1785 | 5 | 351.6128
777 | 51.47 | 49.8895 | 39.0939 | 350.9123 | 0.51041 |  | 777 | 31.6 | 49.8895 | 4 | 350.9123
778 | 55.79 | 43.5625 | 241.0984 | 290.4524 | 0.51523 |  | 778 | 31.18 | 43.5625 | 3 | 290.4524
779 | 59.5 | 45.4093 | 38.4031 | 272.0806 | 0.51677 |  | 779 | 31.79 | 45.4093 | 2.2679 | 272.0806
780 | 59.15 | 48.3764 | 60.9302 | 236.0957 | 0.51975 |  | 780 | 31.99 | 48.3764 | 2 | 236.0957
781 | 56.08 | 50.2992 | 36.0732 | 266.7627 | 0.51934 |  | 781 | 31.92 | 50.2992 | 2.2679 | 266.7627
782 | 50.33 | 53.8378 | 43.6851 | 201.8147 | 0.52522 |  | 782 | 27.14 | 53.8378 | 3 | 201.8147
783 | 49.09 | 59.0812 | 25.37 | 229.8416 | 0.52987 |  | 783 | 26.17 | 59.0812 | 4 | 229.8416
784 | 48.6 | 74.7278 | 39.0545 | 227.6919 | 0.52621 |  | 784 | 25.46 | 74.7278 | 5 | 227.6919
785 | 49.39 | 91.3454 | 47.5025 | 201.6755 | 0.52899 |  | 785 | 26.58 | 91.3454 | 5.7321 | 201.6755
786 | 56.86 | 155.3609 | 45.0717 | 228.5614 | 0.52205 |  | 786 | 30.25 | 155.3609 | 6 | 228.5614
787 | 57.91 | 165.6289 | 244.1567 | 281.4488 | 0.51531 |  | 787 | 39.39 | 165.6289 | 5.7321 | 281.4488
788 | 54.59 | 137.2547 | 27.0043 | 256.2615 | 0.51626 |  | 788 | 38.52 | 137.2547 | 5 | 256.2615
789 | 50.43 | 115.7941 | 23.9091 | 248.4625 | 0.51407 |  | 789 | 29.96 | 115.7941 | 4 | 248.4625
790 | 48.48 | 106.5811 | 26.7609 | 286.4059 | 0.51185 |  | 790 | 24.94 | 106.5811 | 3 | 286.4059
791 | 48.49 | 76.5523 | 31.1597 | 248.8002 | 0.50926 |  | 791 | 29 | 76.5523 | 2.2679 | 248.8002
792 | 46.06 | 39.4099 | 23.9608 | 236.6862 | 0.50409 |  | 792 | 27 | 39.4099 | 2 | 236.6862
793 | 42.3 | 33.7075 | 27.5059 | 177.5299 | 0.50015 |  | 793 | 18.45 | 33.7075 | 2.2679 | 177.5299
794 | 41.29 | 32.2043 | 26.1358 | 165.5696 | 0.51004 |  | 794 | 16.24 | 32.2043 | 3 | 165.5696
795 | 40.48 | 30.7304 | 31.3816 | 168.5129 | 0.5132 |  | 795 | 19.1 | 30.7304 | 4 | 168.5129
796 | 39 | 29.3781 | 20.1976 | 221.693 | 0.50378 |  | 796 | 16.22 | 29.3781 | 5 | 221.693
797 | 38.9 | 28.4862 | 22.75 | 304.2168 | 0.51384 |  | 797 | 14.52 | 28.4862 | 5.7321 | 304.2168
798 | 38.47 | 28.3028 | 28.7945 | 314.8903 | 0.52458 |  | 798 | 17.55 | 28.3028 | 6 | 314.8903
799 | 39.88 | 42.8833 | 29.0732 | 333.4344 | 0.5282 |  | 799 | 21.41 | 42.8833 | 5.7321 | 333.4344
800 | 40.97 | 64.9888 | 41.6938 | 323.4608 | 0.53854 |  | 800 | 33.25 | 64.9888 | 5 | 323.4608
801 | 43.8 | 47.7568 | 35.5276 | 261.2054 | 0.53528 |  | 801 | 35 | 47.7568 | 4 | 261.2054
802 | 47.05 | 43.2149 | 43.0105 | 277.7854 | 0.52855 |  | 802 | 33.96 | 43.2149 | 3 | 277.7854
803 | 49.33 | 44.4226 | 36.8126 | 261.4276 | 0.52923 |  | 803 | 29.94 | 44.4226 | 2.2679 | 261.4276
804 | 51.11 | 46.4085 | 47.7247 | 263.7598 | 0.52787 |  | 804 | 28.55 | 46.4085 | 2 | 263.7598
805 | 50.35 | 50.6609 | 41.086 | 200.7882 | 0.51502 |  | 805 | 25.69 | 50.6609 | 2.2679 | 200.7882
806 | 47.09 | 51.1932 | 237.5692 | 166.1723 | 0.49964 |  | 806 | 25.97 | 51.1932 | 3 | 166.1723
807 | 45.14 | 58.783 | 46.9677 | 99.1859 | 0.51176 |  | 807 | 25.24 | 58.783 | 4 | 99.1859
808 | 44.4 | 75.243 | 30.4098 | 155.6107 | 0.51904 |  | 808 | 23.52 | 75.243 | 5 | 155.6107
809 | 45.79 | 90.4576 | 48.7209 | 219.0399 | 0.52384 |  | 809 | 26.4 | 90.4576 | 5.7321 | 219.0399
810 | 51.94 | 146.2079 | 48.0649 | 211.0482 | 0.52583 |  | 810 | 32.62 | 146.2079 | 6 | 211.0482
811 | 59.54 | 151.917 | 47.478 | 247.4565 | 0.521 |  | 811 | 36.69 | 151.917 | 5.7321 | 247.4565
812 | 60.67 | 139.8203 | 18.8247 | 258.5244 | 0.51602 |  | 812 | 36.19 | 139.8203 | 5 | 258.5244
813 | 57.4 | 111.9881 | 23.5602 | 223.0089 | 0.50644 |  | 813 | 30.13 | 111.9881 | 4 | 223.0089
814 | 51.94 | 104.1701 | 27.4282 | 213.0849 | 0.4986 |  | 814 | 23.75 | 104.1701 | 3 | 213.0849
815 | 46.25 | 76.9281 | 30.2065 | 205.5652 | 0.48729 |  | 815 | 25.42 | 76.9281 | 2.2679 | 205.5652
816 | 41.76 | 39.057 | 34.2735 | 239.5014 | 0.4801 |  | 816 | 29 | 39.057 | 2 | 239.5014
817 | 40 | 33.6057 | 21.6424 | 268.1719 | 0.47963 |  | 817 | 18.04 | 33.6057 | 2.2679 | 268.1719
818 | 40.11 | 32.1025 | 24.5274 | 209.7175 | 0.47555 |  | 818 | 17.78 | 32.1025 | 3 | 209.7175
819 | 39.42 | 30.4874 | 27.9379 | 199.3542 | 0.47464 |  | 819 | 16.52 | 30.4874 | 4 | 199.3542
820 | 39.21 | 29.2163 | 29.208 | 272.4854 | 0.47611 |  | 820 | 15.8 | 29.2163 | 5 | 272.4854
821 | 38.55 | 28.3474 | 25.0777 | 302.5275 | 0.47125 |  | 821 | 16.03 | 28.3474 | 5.7321 | 302.5275
822 | 40.63 | 27.8444 | 27.7651 | 313.3986 | 0.46871 |  | 822 | 17.01 | 27.8444 | 6 | 313.3986
823 | 47.16 | 27.7413 | 28.5627 | 350.475 | 0.46606 |  | 823 | 22.43 | 27.7413 | 5.7321 | 350.475
824 | 55.74 | 30.7066 | 47.16 | 368.1243 | 0.46541 |  | 824 | 31.96 | 30.7066 | 5 | 368.1243
825 | 55.34 | 51.6024 | 49.7525 | 359.8494 | 0.4621 |  | 825 | 31.73 | 51.6024 | 4 | 359.8494
826 | 59 | 68.8074 | 40.6511 | 248.3592 | 0.45996 |  | 826 | 29 | 68.8074 | 3 | 248.3592
827 | 53 | 74.1283 | 45.8572 | 188.8309 | 0.45681 |  | 827 | 29.19 | 74.1283 | 2.2679 | 188.8309
828 | 44.7 | 76.3601 | 44.4598 | 123.5262 | 0.45475 |  | 828 | 30.22 | 76.3601 | 2 | 123.5262
829 | 41.69 | 79.506 | 46.4712 | 84.2232 | 0.45606 |  | 829 | 27.97 | 79.506 | 2.2679 | 84.2232
830 | 40.8 | 74.4085 | 244.0736 | 69.6631 | 0.45915 |  | 830 | 26.87 | 74.4085 | 3 | 69.6631
831 | 45.4 | 68.842 | 36.6149 | 52.8993 | 0.45953 |  | 831 | 25.85 | 68.842 | 4 | 52.8993
832 | 45.49 | 74.4893 | 46.1141 | 65.1817 | 0.45822 |  | 832 | 27.94 | 74.4893 | 5 | 65.1817
833 | 46.59 | 79.917 | 51.9545 | 87.7508 | 0.45617 |  | 833 | 27.81 | 79.917 | 5.7321 | 87.7508
834 | 49.9 | 114.1464 | 51.2205 | 118.1621 | 0.45285 |  | 834 | 35 | 114.1464 | 6 | 118.1621
835 | 46.78 | 163.6831 | 34.7958 | 204.5807 | 0.45029 |  | 835 | 42.18 | 163.6831 | 5.7321 | 204.5807
836 | 42.08 | 149.0121 | 31.2255 | 261.5592 | 0.45295 |  | 836 | 39.01 | 149.0121 | 5 | 261.5592
837 | 40.59 | 115.8622 | 26.4321 | 276.3252 | 0.45953 |  | 837 | 32.04 | 115.8622 | 4 | 276.3252
838 | 39.9 | 101.4243 | 23.7593 | 303.5362 | 0.46808 |  | 838 | 26.96 | 101.4243 | 3 | 303.5362
839 | 39.7 | 88.6123 | 31.5968 | 221.1298 | 0.47893 |  | 839 | 27.83 | 88.6123 | 2.2679 | 221.1298
840 | 34.9 | 39.9319 | 30.4644 | 222.4718 | 0.47478 |  | 840 | 23.98 | 39.9319 | 2 | 222.4718
841 | 37.3 | 33.995 | 22.7136 | 181.2146 | 0.4766 |  | 841 | 24.61 | 33.995 | 2.2679 | 181.2146
842 | 37.4 | 32.4471 | 31.2066 | 200.6016 | 0.4869 |  | 842 | 23 | 32.4471 | 3 | 200.6016
843 | 38.42 | 30.8762 | 18.8395 | 251.1102 | 0.49657 |  | 843 | 22.22 | 30.8762 | 4 | 251.1102
844 | 39.9 | 29.4406 | 30.6296 | 277.8638 | 0.51158 |  | 844 | 20.1 | 29.4406 | 5 | 277.8638
845 | 39.9 | 28.5532 | 27.7787 | 324.464 | 0.51178 |  | 845 | 21.18 | 28.5532 | 5.7321 | 324.464
846 | 42.99 | 27.9607 | 27.9395 | 371.6937 | 0.50886 |  | 846 | 21.18 | 27.9607 | 6 | 371.6937
847 | 54.13 | 27.6413 | 29.4204 | 383.3228 | 0.50212 |  | 847 | 26.01 | 27.6413 | 5.7321 | 383.3228
848 | 62.22 | 30.8302 | 37.5687 | 454.4946 | 0.50168 |  | 848 | 33.98 | 30.8302 | 5 | 454.4946
849 | 70.3 | 50.5193 | 48.1803 | 473.0529 | 0.50557 |  | 849 | 37.7 | 50.5193 | 4 | 473.0529
850 | 75.19 | 66.6259 | 454.9894 | 360.0148 | 0.5058 |  | 850 | 35.79 | 66.6259 | 3 | 360.0148
851 | 69.96 | 71.4956 | 42.5037 | 242.9397 | 0.51533 |  | 851 | 36.5 | 71.4956 | 2.2679 | 242.9397
852 | 62.85 | 73.3579 | 32.4019 | 126.2345 | 0.51999 |  | 852 | 35.94 | 73.3579 | 2 | 126.2345
853 | 58.93 | 79.3952 | 41.071 | 130.0634 | 0.51601 |  | 853 | 34.36 | 79.3952 | 2.2679 | 130.0634
854 | 57.96 | 77.0146 | 35.6377 | 80.3013 | 0.52083 |  | 854 | 31.95 | 77.0146 | 3 | 80.3013
855 | 57.96 | 77.0988 | 42.9479 | 71.0534 | 0.52171 |  | 855 | 27.74 | 77.0988 | 4 | 71.0534
856 | 58.04 | 70.8204 | 29.9353 | 60.3307 | 0.52171 |  | 856 | 25.33 | 70.8204 | 5 | 60.3307
857 | 60.35 | 77.6154 | 50.8124 | 176.4669 | 0.51997 |  | 857 | 24.78 | 77.6154 | 5.7321 | 176.4669
858 | 63.06 | 118.5811 | 30.8318 | 334.5755 | 0.51274 |  | 858 | 29.96 | 118.5811 | 6 | 334.5755
859 | 65.79 | 147.1429 | 46.5226 | 298.3283 | 0.50473 |  | 859 | 33.09 | 147.1429 | 5.7321 | 298.3283
860 | 62.63 | 150.5256 | 28.1558 | 370.7431 | 0.49755 |  | 860 | 28.92 | 150.5256 | 5 | 370.7431
861 | 61.77 | 115.2433 | 27.7353 | 308.0149 | 0.49319 |  | 861 | 27.92 | 115.2433 | 4 | 308.0149
862 | 52.93 | 101.1418 | 23.2862 | 372.7074 | 0.49175 |  | 862 | 24.96 | 101.1418 | 3 | 372.7074
863 | 46.03 | 85.7606 | 33.0772 | 341.3863 | 0.4865 |  | 863 | 24.55 | 85.7606 | 2.2679 | 341.3863
864 | 42.6 | 40.4827 | 35.2004 | 331.0823 | 0.48119 |  | 864 | 22.71 | 40.4827 | 2 | 331.0823
865 | 42.8 | 35.4348 | 23.5877 | 397.1381 | 0.4811 |  | 865 | 19.08 | 35.4348 | 2.2679 | 397.1381
866 | 41.63 | 33.551 | 241.5089 | 364.6354 | 0.47822 |  | 866 | 16.73 | 33.551 | 3 | 364.6354
867 | 40.5 | 31.8593 | 29.5932 | 360.5876 | 0.47464 |  | 867 | 16.54 | 31.8593 | 4 | 360.5876
868 | 40.4 | 30.32 | 30.1307 | 427.7069 | 0.47311 |  | 868 | 15.4 | 30.32 | 5 | 427.7069
869 | 41.38 | 29.1549 | 24.4375 | 363.0228 | 0.47228 |  | 869 | 14.94 | 29.1549 | 5.7321 | 363.0228
870 | 42.31 | 28.7048 | 31.9131 | 404.3848 | 0.47647 |  | 870 | 15.01 | 28.7048 | 6 | 404.3848
871 | 50.66 | 43.8896 | 24.5555 | 445.3091 | 0.47648 |  | 871 | 15.59 | 43.8896 | 5.7321 | 445.3091
872 | 53.3 | 68.7227 | 39.646 | 429.2641 | 0.47666 |  | 872 | 19.88 | 68.7227 | 5 | 429.2641
873 | 55.93 | 47.8279 | 47.9521 | 434.7481 | 0.47771 |  | 873 | 22.62 | 47.8279 | 4 | 434.7481
874 | 53.45 | 42.2602 | 40.9357 | 386.0184 | 0.47942 |  | 874 | 23 | 42.2602 | 3 | 386.0184
875 | 55.37 | 46.0547 | 27.0199 | 296.8278 | 0.48184 |  | 875 | 24.96 | 46.0547 | 2.2679 | 296.8278
876 | 55.09 | 46.4774 | 44.072 | 282.2282 | 0.48518 |  | 876 | 22.44 | 46.4774 | 2 | 282.2282
877 | 54.94 | 49.0078 | 42.7712 | 232.1337 | 0.48916 |  | 877 | 21.2 | 49.0078 | 2.2679 | 232.1337
878 | 54.55 | 52.4026 | 45.4015 | 184.5878 | 0.49798 |  | 878 | 19.9 | 52.4026 | 3 | 184.5878
879 | 52.93 | 57.7925 | 42.1481 | 197.8481 | 0.50536 |  | 879 | 15.88 | 57.7925 | 4 | 197.8481
880 | 54.3 | 72.301 | 42.7899 | 159.8361 | 0.50876 |  | 880 | 16.05 | 72.301 | 5 | 159.8361
881 | 56.73 | 95.7629 | 38.3339 | 216.7309 | 0.50987 |  | 881 | 17.01 | 95.7629 | 5.7321 | 216.7309
882 | 60.27 | 143.35 | 248.9582 | 325.5687 | 0.50603 |  | 882 | 19.97 | 143.35 | 6 | 325.5687
883 | 62.4 | 161.0982 | 42.6784 | 348.4383 | 0.50417 |  | 883 | 23.15 | 161.0982 | 5.7321 | 348.4383
884 | 58.94 | 157.3962 | 31.2446 | 379.5166 | 0.5052 |  | 884 | 24.96 | 157.3962 | 5 | 379.5166
885 | 54.37 | 122.1954 | 31.8933 | 403.7132 | 0.50733 |  | 885 | 19.96 | 122.1954 | 4 | 403.7132
886 | 50.49 | 107.0487 | 24.6425 | 385.7854 | 0.50697 |  | 886 | 18.31 | 107.0487 | 3 | 385.7854
887 | 49.5 | 77.4261 | 26.0042 | 332.2224 | 0.51017 |  | 887 | 18.6 | 77.4261 | 2.2679 | 332.2224
888 | 46.18 | 40.7591 | 23.2878 | 398.2238 | 0.50617 |  | 888 | 18.62 | 40.7591 | 2 | 398.2238
889 | 46.25 | 35.5557 | 24.6623 | 308.5286 | 0.50368 |  | 889 | 14.95 | 35.5557 | 2.2679 | 308.5286
890 | 45.21 | 33.7792 | 37.2879 | 404.2988 | 0.49681 |  | 890 | 14.31 | 33.7792 | 3 | 404.2988
891 | 41.24 | 32.0492 | 19.6873 | 310.8197 | 0.4884 |  | 891 | 14.05 | 32.0492 | 4 | 310.8197
892 | 38.05 | 30.3199 | 37.0377 | 391.6038 | 0.47523 |  | 892 | 12.86 | 30.3199 | 5 | 391.6038
893 | 37 | 29.2331 | 26.3852 | 480.4456 | 0.46027 |  | 893 | 12.51 | 29.2331 | 5.7321 | 480.4456
894 | 39.04 | 28.7471 | 30.3763 | 405.8834 | 0.45276 |  | 894 | 12.84 | 28.7471 | 6 | 405.8834
895 | 48.06 | 43.2943 | 27.107 | 469.1617 | 0.4545 |  | 895 | 13.17 | 43.2943 | 5.7321 | 469.1617
896 | 50.77 | 67.2764 | 248.2516 | 430.7814 | 0.45829 |  | 896 | 14.96 | 67.2764 | 5 | 430.7814
897 | 54.79 | 47.1207 | 35.2214 | 455.4809 | 0.45875 |  | 897 | 15.09 | 47.1207 | 4 | 455.4809
898 | 53.7 | 41.9731 | 34.9352 | 388.4921 | 0.45795 |  | 898 | 19.99 | 41.9731 | 3 | 388.4921
899 | 53.17 | 43.9327 | 51.2028 | 274.311 | 0.45599 |  | 899 | 25.4 | 43.9327 | 2.2679 | 274.311
900 | 50 | 46.7121 | 41.4413 | 199.5202 | 0.45572 |  | 900 | 22.44 | 46.7121 | 2 | 199.5202
901 | 49.45 | 50.6418 | 35.068 | 190.1824 | 0.46009 |  | 901 | 24.96 | 50.6418 | 2.2679 | 190.1824
902 | 46.09 | 49.8843 | 51.0973 | 134.2179 | 0.46877 |  | 902 | 19.99 | 49.8843 | 3 | 134.2179
903 | 42.58 | 56.054 | 33.6938 | 147.1919 | 0.46793 |  | 903 | 15.09 | 56.054 | 4 | 147.1919
904 | 43.32 | 72.0311 | 36.0503 | 128.9669 | 0.47035 |  | 904 | 15.13 | 72.0311 | 5 | 128.9669
905 | 46.28 | 92.4632 | 41.4148 | 212.3572 | 0.4732 |  | 905 | 14.23 | 92.4632 | 5.7321 | 212.3572
906 | 51.65 | 145.8773 | 44.5421 | 306.4124 | 0.46658 |  | 906 | 16.64 | 145.8773 | 6 | 306.4124
907 | 49.76 | 163.4269 | 62.044 | 308.9687 | 0.4647 |  | 907 | 29.96 | 163.4269 | 5.7321 | 308.9687
908 | 45.4 | 141.6879 | 33.2646 | 300.4619 | 0.46888 |  | 908 | 24.96 | 141.6879 | 5 | 300.4619
909 | 43.19 | 116.6873 | 31.5205 | 293.4353 | 0.47241 |  | 909 | 19.96 | 116.6873 | 4 | 293.4353
910 | 45.7 | 106.0817 | 222.9601 | 252.4098 | 0.47439 |  | 910 | 18.64 | 106.0817 | 3 | 252.4098
911 | 43.55 | 76.4335 | 35.5537 | 252.505 | 0.4798 |  | 911 | 16.72 | 76.4335 | 2.2679 | 252.505
912 | 42 | 40.6028 | 23.3612 | 227.3579 | 0.48882 |  | 912 | 14.59 | 40.6028 | 2 | 227.3579
913 | 46.85 | 34.3947 | 229.1615 | 246.5608 | 0.49102 |  | 913 | 10.02 | 34.3947 | 2.2679 | 246.5608
914 | 45 | 32.6854 | 40.0163 | 252.489 | 0.48341 |  | 914 | 8.31 | 32.6854 | 3 | 252.489
915 | 46 | 31.0357 | 26.3415 | 267.5306 | 0.47601 |  | 915 | 11.89 | 31.0357 | 4 | 267.5306
916 | 45 | 29.683 | 29.5425 | 236.1701 | 0.47121 |  | 916 | 9.97 | 29.683 | 5 | 236.1701
917 | 37.4 | 28.6546 | 17.8858 | 279.3125 | 0.47511 |  | 917 | 11.39 | 28.6546 | 5.7321 | 279.3125
918 | 39.49 | 28.539 | 30.3243 | 338.1483 | 0.4728 |  | 918 | 9.67 | 28.539 | 6 | 338.1483
919 | 46.5 | 43.497 | 19.8122 | 346.1635 | 0.46381 |  | 919 | 21.15 | 43.497 | 5.7321 | 346.1635
920 | 55.87 | 67.1031 | 42.4511 | 328.2086 | 0.45943 |  | 920 | 27 | 67.1031 | 5 | 328.2086
921 | 57.83 | 47.6269 | 54.071 | 386.547 | 0.4569 |  | 921 | 34.83 | 47.6269 | 4 | 386.547
922 | 58.31 | 42.2501 | 44.275 | 322.0552 | 0.45545 |  | 922 | 32 | 42.2501 | 3 | 322.0552
923 | 59.04 | 44.9581 | 52.8155 | 241.3497 | 0.45344 |  | 923 | 32.44 | 44.9581 | 2.2679 | 241.3497
924 | 57.56 | 45.872 | 35.6903 | 230.4913 | 0.45197 |  | 924 | 30.99 | 45.872 | 2 | 230.4913
925 | 54.13 | 48.7208 | 45.01 | 195.8712 | 0.44975 |  | 925 | 29.94 | 48.7208 | 2.2679 | 195.8712
926 | 51.48 | 50.5256 | 234.227 | 169.7144 | 0.4491 |  | 926 | 27.35 | 50.5256 | 3 | 169.7144
927 | 48.31 | 56.5555 | 39.258 | 97.5444 | 0.44664 |  | 927 | 27 | 56.5555 | 4 | 97.5444
928 | 45.45 | 72.3313 | 38.5521 | 88.1961 | 0.44591 |  | 928 | 24.96 | 72.3313 | 5 | 88.1961
929 | 45.8 | 96.2962 | 39.6061 | 106.9569 | 0.44393 |  | 929 | 24 | 96.2962 | 5.7321 | 106.9569
930 | 50 | 148.5065 | 43.7313 | 207.8822 | 0.44008 |  | 930 | 28.65 | 148.5065 | 6 | 207.8822
931 | 52.34 | 165.4588 | 37.5176 | 306.0792 | 0.43633 |  | 931 | 37.25 | 165.4588 | 5.7321 | 306.0792
932 | 47.59 | 140.1778 | 28.6655 | 302.4302 | 0.43969 |  | 932 | 35.3 | 140.1778 | 5 | 302.4302
933 | 47.4 | 119.3559 | 25.8979 | 346.1826 | 0.44143 |  | 933 | 24.94 | 119.3559 | 4 | 346.1826
934 | 46.66 | 107.5054 | 31.4318 | 285.5689 | 0.43863 |  | 934 | 24.94 | 107.5054 | 3 | 285.5689
935 | 46.43 | 75.7666 | 27.4449 | 230.6743 | 0.43788 |  | 935 | 25.28 | 75.7666 | 2.2679 | 230.6743
936 | 46.49 | 39.8112 | 26.3503 | 238.1529 | 0.44566 |  | 936 | 22.84 | 39.8112 | 2 | 238.1529
937 | 46.2 | 35.6803 | 23.6011 | 258.9979 | 0.45336 |  | 937 | 14.96 | 35.6803 | 2.2679 | 258.9979
938 | 40 | 33.8901 | 25.2462 | 252.1678 | 0.45554 |  | 938 | 14.73 | 33.8901 | 3 | 252.1678
939 | 39.87 | 32.0541 | 34.6299 | 192.2591 | 0.44535 |  | 939 | 16.86 | 32.0541 | 4 | 192.2591
940 | 37.1 | 30.3098 | 28.945 | 222.3385 | 0.42716 |  | 940 | 10.05 | 30.3098 | 5 | 222.3385
941 | 33.18 | 29.2157 | 27.2492 | 339.154 | 0.41241 |  | 941 | 9.96 | 29.2157 | 5.7321 | 339.154
942 | 30.13 | 28.8742 | 23.6823 | 349.0817 | 0.41154 |  | 942 | 14.02 | 28.8742 | 6 | 349.0817
943 | 38 | 44.1546 | 224.6306 | 358.3861 | 0.43064 |  | 943 | 22.13 | 44.1546 | 5.7321 | 358.3861
944 | 41.12 | 65.0133 | 49.5732 | 317.6972 | 0.44047 |  | 944 | 29.94 | 65.0133 | 5 | 317.6972
945 | 43.82 | 47.1707 | 50.3067 | 277.6499 | 0.45044 |  | 945 | 34.39 | 47.1707 | 4 | 277.6499
946 | 48.54 | 42.8268 | 50.8606 | 312.4608 | 0.45239 |  | 946 | 27.44 | 42.8268 | 3 | 312.4608
947 | 49.9 | 45.126 | 36.3732 | 289.3846 | 0.45352 |  | 947 | 27.97 | 45.126 | 2.2679 | 289.3846
948 | 47.09 | 47.4572 | 31.0576 | 276.8121 | 0.4634 |  | 948 | 30 | 47.4572 | 2 | 276.8121
949 | 46.82 | 51.8268 | 45.1264 | 231.1777 | 0.45978 |  | 949 | 27.03 | 51.8268 | 2.2679 | 231.1777
950 | 43.6 | 52.2873 | 46.1026 | 233.532 | 0.45378 |  | 950 | 28.69 | 52.2873 | 3 | 233.532
951 | 38.9 | 59.9989 | 42.3906 | 177.2309 | 0.45472 |  | 951 | 27.44 | 59.9989 | 4 | 177.2309
952 | 42.4 | 77.9689 | 47.518 | 173.1068 | 0.45551 |  | 952 | 26.97 | 77.9689 | 5 | 173.1068
953 | 43.35 | 96.0679 | 39.5822 | 229.0005 | 0.45562 |  | 953 | 27.24 | 96.0679 | 5.7321 | 229.0005
954 | 54.37 | 142.082 | 55.5223 | 285.3048 | 0.44712 |  | 954 | 31.01 | 142.082 | 6 | 285.3048
955 | 50.98 | 174.4962 | 41.6583 | 280.6232 | 0.44389 |  | 955 | 39.98 | 174.4962 | 5.7321 | 280.6232
956 | 50.01 | 148.2943 | 30.995 | 240.0148 | 0.44319 |  | 956 | 34.06 | 148.2943 | 5 | 240.0148
957 | 52.01 | 117.1033 | 29.7065 | 261.9625 | 0.44479 |  | 957 | 29.1 | 117.1033 | 4 | 261.9625
958 | 43.6 | 109.2385 | 23.928 | 232.8747 | 0.44804 |  | 958 | 24.45 | 109.2385 | 3 | 232.8747
959 | 46.3 | 79.8622 | 24.9093 | 239.022 | 0.44984 |  | 959 | 24.74 | 79.8622 | 2.2679 | 239.022
960 | 46.18 | 41.4317 | 26.9518 | 214.7649 | 0.44888 |  | 960 | 19.88 | 41.4317 | 2 | 214.7649
961 | 45.55 | 33.0423 | 29.4341 | 249.9016 | 0.45625 |  | 961 | 17.75 | 33.0423 | 2.2679 | 249.9016
962 | 44.6 | 31.6198 | 35.1751 | 241.1615 | 0.46589 |  | 962 | 16.56 | 31.6198 | 3 | 241.1615
963 | 44.6 | 30.1787 | 28.5457 | 219.3499 | 0.47766 |  | 963 | 17 | 30.1787 | 4 | 219.3499
964 | 40 | 28.9545 | 24.1631 | 281.1197 | 0.48609 |  | 964 | 16.55 | 28.9545 | 5 | 281.1197
965 | 37.2 | 28.2144 | 24.3309 | 334.1906 | 0.50272 |  | 965 | 16.69 | 28.2144 | 5.7321 | 334.1906
966 | 37.1 | 28.0007 | 232.5897 | 313.1457 | 0.50585 |  | 966 | 16.2 | 28.0007 | 6 | 313.1457
967 | 50 | 43.3522 | 27.8458 | 352.0619 | 0.50334 |  | 967 | 22.8 | 43.3522 | 5.7321 | 352.0619
968 | 45.21 | 64.6327 | 43.8683 | 287.1138 | 0.5118 |  | 968 | 30.59 | 64.6327 | 5 | 287.1138
969 | 45 | 46.531 | 37.3215 | 316.8893 | 0.51057 |  | 969 | 32.05 | 46.531 | 4 | 316.8893
970 | 48.85 | 41.5289 | 31.0052 | 278.672 | 0.50959 |  | 970 | 35 | 41.5289 | 3 | 278.672
971 | 49.29 | 43.2064 | 40.8518 | 250.8099 | 0.51761 |  | 971 | 37.44 | 43.2064 | 2.2679 | 250.8099
972 | 50 | 44.9112 | 50.4274 | 269.9473 | 0.51065 |  | 972 | 35.5 | 44.9112 | 2 | 269.9473
973 | 54.9 | 48.883 | 49.6145 | 231.0745 | 0.51365 |  | 973 | 30.45 | 48.883 | 2.2679 | 231.0745
974 | 44.6 | 49.1386 | 45.5072 | 230.9279 | 0.52059 |  | 974 | 27.74 | 49.1386 | 3 | 230.9279
975 | 45.4 | 54.6218 | 246.1374 | 255.9085 | 0.5173 |  | 975 | 27.44 | 54.6218 | 4 | 255.9085
976 | 44.6 | 69.5673 | 34.0574 | 276.5601 | 0.51152 |  | 976 | 27.77 | 69.5673 | 5 | 276.5601
977 | 46.67 | 89.7248 | 38.4819 | 239.7605 | 0.50463 |  | 977 | 28.68 | 89.7248 | 5.7321 | 239.7605
978 | 51.05 | 130.6478 | 46.4548 | 312.9407 | 0.47968 |  | 978 | 32.1 | 130.6478 | 6 | 312.9407
979 | 51.37 | 151.0522 | 53.5073 | 340.7142 | 0.46651 |  | 979 | 36.59 | 151.0522 | 5.7321 | 340.7142
980 | 51.12 | 149.2075 | 32.3672 | 345.0603 | 0.45806 |  | 980 | 29.44 | 149.2075 | 5 | 345.0603
981 | 49.73 | 117.5614 | 25.0118 | 326.2476 | 0.44973 |  | 981 | 24.08 | 117.5614 | 4 | 326.2476
982 | 45.74 | 100.9939 | 28.3948 | 306.1156 | 0.44359 |  | 982 | 21.81 | 100.9939 | 3 | 306.1156
983 | 44.3 | 75.3191 | 28.7864 | 266.9998 | 0.44962 |  | 983 | 22.3 | 75.3191 | 2.2679 | 266.9998
984 | 44.6 | 38.2948 | 33.1314 | 195.2055 | 0.44471 |  | 984 | 28.3 | 38.2948 | 2 | 195.2055
985 | 42.59 | 33.6565 | 30.5124 | 229.2288 | 0.45486 |  | 985 | 23.82 | 33.6565 | 2.2679 | 229.2288
986 | 41.4 | 32.0802 | 23.8835 | 252.039 | 0.45975 |  | 986 | 21.48 | 32.0802 | 3 | 252.039
987 | 39.8 | 30.6554 | 26.5428 | 219.5767 | 0.46334 |  | 987 | 19.1 | 30.6554 | 4 | 219.5767
988 | 39.8 | 29.362 | 28.4619 | 267.9544 | 0.46405 |  | 988 | 17.75 | 29.362 | 5 | 267.9544
989 | 41.6 | 28.4446 | 28.7163 | 266.0813 | 0.46957 |  | 989 | 18.6 | 28.4446 | 5.7321 | 266.0813
990 | 45.03 | 27.9465 | 34.3446 | 337.3607 | 0.46859 |  | 990 | 20 | 27.9465 | 6 | 337.3607
991 | 57.63 | 27.7432 | 27.7669 | 426.4373 | 0.4647 |  | 991 | 21.3 | 27.7432 | 5.7321 | 426.4373
992 | 70.59 | 30.5463 | 38.0501 | 323.4527 | 0.46165 |  | 992 | 31.76 | 30.5463 | 5 | 323.4527
993 | 65 | 50.3965 | 43.9983 | 310.5217 | 0.46478 |  | 993 | 28.55 | 50.3965 | 4 | 310.5217
994 | 71.21 | 66.9822 | 39.764 | 307.6541 | 0.46877 |  | 994 | 26.78 | 66.9822 | 3 | 307.6541
995 | 71.21 | 75.3586 | 39.4625 | 286.2523 | 0.47114 |  | 995 | 24.97 | 75.3586 | 2.2679 | 286.2523
996 | 58.43 | 77.0538 | 39.1737 | 238.7687 | 0.46945 |  | 996 | 32 | 77.0538 | 2 | 238.7687
997 | 49.9 | 79.0474 | 243.3209 | 288.4348 | 0.4635 |  | 997 | 28 | 79.0474 | 2.2679 | 288.4348
998 | 41.7 | 76.27 | 45.9509 | 282.4333 | 0.46286 |  | 998 | 25.12 | 76.27 | 3 | 282.4333
999 | 49.81 | 71.5464 | 43.7861 | 268.094 | 0.46792 |  | 999 | 22.44 | 71.5464 | 4 | 268.094
1000 | 47 | 73.5431 | 45.9544 | 270.295 | 0.46725 |  | 1000 | 30 | 73.5431 | 5 | 270.295
1001 | 57.83 | 77.2134 | 27.7805 | 317.9865 | 0.46785 |  | 1001 | 31.62 | 77.2134 | 5.7321 | 317.9865
1002 | 74 | 131.2921 | 51.6142 | 265.3668 | 0.47407 |  | 1002 | 36 | 131.2921 | 6 | 265.3668
1003 | 85.23 | 166.3471 | 45.2656 | 344.5241 | 0.48147 |  | 1003 | 41.02 | 166.3471 | 5.7321 | 344.5241
1004 | 94.31 | 153.7715 | 32.769 | 324.3469 | 0.48376 |  | 1004 | 41.51 | 153.7715 | 5 | 324.3469
1005 | 79.9 | 115.2624 | 31.5303 | 338.8698 | 0.48183 |  | 1005 | 34.07 | 115.2624 | 4 | 338.8698
1006 | 60.26 | 100.7418 | 30.6981 | 333.7566 | 0.48122 |  | 1006 | 29.96 | 100.7418 | 3 | 333.7566
1007 | 45 | 86.8787 | 33.9295 | 290.4452 | 0.47924 |  | 1007 | 28.92 | 86.8787 | 2.2679 | 290.4452
1008 | 39.8 | 40.309 | 29.3875 | 245.2762 | 0.48376 |  | 1008 | 26.11 | 40.309 | 2 | 245.2762
1009 | 40.3 | 35.6675 | 23.8371 | 336.4239 | 0.48489 |  | 1009 | 22.81 | 35.6675 | 2.2679 | 336.4239
1010 | 37 | 33.847 | 24.6604 | 255.8029 | 0.48739 |  | 1010 | 21.59 | 33.847 | 3 | 255.8029
1011 | 37.32 | 31.9508 | 28.5887 | 282.5808 | 0.48797 |  | 1011 | 21.3 | 31.9508 | 4 | 282.5808
1012 | 37.4 | 30.2708 | 28.3262 | 321.5167 | 0.4873 |  | 1012 | 19.86 | 30.2708 | 5 | 321.5167
1013 | 37.3 | 29.1844 | 27.6011 | 347.7601 | 0.48833 |  | 1013 | 20.69 | 29.1844 | 5.7321 | 347.7601
1014 | 40.02 | 28.4864 | 24.82 | 439.1103 | 0.49777 |  | 1014 | 21.64 | 28.4864 | 6 | 439.1103
1015 | 46.5 | 28.1903 | 28.984 | 398.3018 | 0.50411 |  | 1015 | 27.18 | 28.1903 | 5.7321 | 398.3018
1016 | 61.22 | 31.1753 | 32.7683 | 426.6823 | 0.5012 |  | 1016 | 36.43 | 31.1753 | 5 | 426.6823
1017 | 64.8 | 49.8265 | 32.9742 | 322.3948 | 0.50197 |  | 1017 | 37.3 | 49.8265 | 4 | 322.3948
1018 | 64.74 | 68.3016 | 227.1155 | 355.0072 | 0.49916 |  | 1018 | 34.97 | 68.3016 | 3 | 355.0072
1019 | 60.28 | 76.1269 | 48.7079 | 350.1595 | 0.49803 |  | 1019 | 34.7 | 76.1269 | 2.2679 | 350.1595
1020 | 60.49 | 76.5008 | 50.4051 | 330.1846 | 0.50108 |  | 1020 | 33.48 | 76.5008 | 2 | 330.1846
1021 | 53.82 | 80.549 | 41.9084 | 321.9458 | 0.50329 |  | 1021 | 30 | 80.549 | 2.2679 | 321.9458
1022 | 49.98 | 80.7767 | 34.4938 | 240.605 | 0.50043 |  | 1022 | 26.93 | 80.7767 | 3 | 240.605
1023 | 49.98 | 77.9746 | 35.4983 | 180.7204 | 0.49002 |  | 1023 | 25.62 | 77.9746 | 4 | 180.7204
1024 | 50.17 | 77.8803 | 42.7753 | 180.5856 | 0.48435 |  | 1024 | 25 | 77.8803 | 5 | 180.5856
1025 | 52.84 | 82.1511 | 42.8639 | 198.207 | 0.47804 |  | 1025 | 27.18 | 82.1511 | 5.7321 | 198.207
1026 | 56.92 | 121.4842 | 41.2231 | 249.7316 | 0.46968 |  | 1026 | 34.56 | 121.4842 | 6 | 249.7316
1027 | 60.47 | 147.1199 | 32.2266 | 341.7113 | 0.4595 |  | 1027 | 40.36 | 147.1199 | 5.7321 | 341.7113
1028 | 51.27 | 155.9677 | 23.4302 | 349.9737 | 0.45543 |  | 1028 | 35.56 | 155.9677 | 5 | 349.9737
1029 | 45.96 | 119.698 | 26.2641 | 297.3556 | 0.4496 |  | 1029 | 29.96 | 119.698 | 4 | 297.3556
1030 | 41.6 | 103.4156 | 32.2023 | 311.5846 | 0.4453 |  | 1030 | 26.45 | 103.4156 | 3 | 311.5846
1031 | 44.9 | 89.2099 | 25.4473 | 297.2984 | 0.44869 |  | 1031 | 27.18 | 89.2099 | 2.2679 | 297.2984
1032 | 40.2 | 42.3154 | 26.6711 | 295.5096 | 0.45197 |  | 1032 | 25.49 | 42.3154 | 2 | 295.5096
1033 | 39.9 | 33.3232 | 29.407 | 286.0372 | 0.44971 |  | 1033 | 22.23 | 33.3232 | 2.2679 | 286.0372
1034 | 37.6 | 31.7242 | 27.5506 | 329.8384 | 0.45362 |  | 1034 | 21.1 | 31.7242 | 3 | 329.8384
1035 | 36.3 | 30.2373 | 17.0821 | 373.9008 | 0.45597 |  | 1035 | 20.21 | 30.2373 | 4 | 373.9008
1036 | 36 | 29.0516 | 34.6764 | 301.8405 | 0.45364 |  | 1036 | 19.94 | 29.0516 | 5 | 301.8405
1037 | 37.58 | 28.3222 | 231.695 | 350.7 | 0.461 |  | 1037 | 19.9 | 28.3222 | 5.7321 | 350.7
1038 | 37.18 | 28.1537 | 236.3312 | 440.9992 | 0.473 |  | 1038 | 19.98 | 28.1537 | 6 | 440.9992
1039 | 45.62 | 44.6174 | 33.7219 | 455.552 | 0.48914 |  | 1039 | 19.9 | 44.6174 | 5.7321 | 455.552
1040 | 52.9 | 66.8162 | 49.4646 | 429.7 | 0.4903 |  | 1040 | 21.48 | 66.8162 | 5 | 429.7
1041 | 64.85 | 46.7246 | 46.8986 | 518.8467 | 0.49134 |  | 1041 | 28.38 | 46.7246 | 4 | 518.8467
1042 | 62.97 | 42.9182 | 42.0669 | 382.9258 | 0.48386 |  | 1042 | 30.36 | 42.9182 | 3 | 382.9258
1043 | 50 | 47.3857 | 44.9306 | 259.145 | 0.47705 |  | 1043 | 30.09 | 47.3857 | 2.2679 | 259.145
1044 | 48.63 | 49.5948 | 36.5325 | 341.4838 | 0.47491 |  | 1044 | 29.84 | 49.5948 | 2 | 341.4838
1045 | 48.49 | 50.9082 | 37.8937 | 257.0319 | 0.47599 |  | 1045 | 26.75 | 50.9082 | 2.2679 | 257.0319
1046 | 47.6 | 51.2095 | 48.6118 | 236.3947 | 0.47804 |  | 1046 | 23.93 | 51.2095 | 3 | 236.3947
1047 | 46.3 | 58.6905 | 52.9352 | 161.9298 | 0.48155 |  | 1047 | 21.37 | 58.6905 | 4 | 161.9298
1048 | 46.82 | 74.001 | 41.5837 | 127.5665 | 0.48522 |  | 1048 | 21.15 | 74.001 | 5 | 127.5665
1049 | 49.71 | 92.5847 | 56.8597 | 179.9351 | 0.48442 |  | 1049 | 20.96 | 92.5847 | 5.7321 | 179.9351
1050 | 53.94 | 137.6062 | 39.355 | 323.8775 | 0.48549 |  | 1050 | 24.69 | 137.6062 | 6 | 323.8775
1051 | 56.55 | 168.175 | 49.5728 | 376.6754 | 0.4823 |  | 1051 | 32.07 | 168.175 | 5.7321 | 376.6754
1052 | 54.34 | 150.7788 | 30.7738 | 366.8989 | 0.48224 |  | 1052 | 32.44 | 150.7788 | 5 | 366.8989
1053 | 50.13 | 118.6696 | 28.5097 | 442.4983 | 0.48012 |  | 1053 | 29 | 118.6696 | 4 | 442.4983
1054 | 46.76 | 107.3504 | 27.2214 | 331.9502 | 0.48234 |  | 1054 | 24.94 | 107.3504 | 3 | 331.9502
1055 | 44.5 | 74.7352 | 25.1594 | 343.4611 | 0.48303 |  | 1055 | 29.94 | 74.7352 | 2.2679 | 343.4611
1056 | 42.85 | 39.3377 | 30.7699 | 345.7443 | 0.4874 |  | 1056 | 29.94 | 39.3377 | 2 | 345.7443
1057 | 38.6 | 32.5154 | 21.3458 | 432.2782 | 0.50101 |  | 1057 | 13.06 | 32.5154 | 2.2679 | 432.2782
1058 | 39.15 | 31.3118 | 225.6436 | 310.6328 | 0.5096 |  | 1058 | 16.24 | 31.3118 | 3 | 310.6328
1059 | 38.6 | 30.0223 | 24.7531 | 314.5709 | 0.51762 |  | 1059 | 10.2 | 30.0223 | 4 | 314.5709
1060 | 39 | 28.9038 | 22.8626 | 375.7753 | 0.51062 |  | 1060 | 13.57 | 28.9038 | 5 | 375.7753
1061 | 38.47 | 28.1171 | 34.7696 | 451.7535 | 0.51779 |  | 1061 | 16.08 | 28.1171 | 5.7321 | 451.7535
1062 | 43.04 | 28.0139 | 20.9508 | 478.1783 | 0.52179 |  | 1062 | 16.3 | 28.0139 | 6 | 478.1783
1063 | 47.9 | 42.9561 | 31.1328 | 470.892 | 0.51156 |  | 1063 | 16.39 | 42.9561 | 5.7321 | 470.892
1064 | 60.73 | 66.1025 | 45.0834 | 564.1404 | 0.50909 |  | 1064 | 16.37 | 66.1025 | 5 | 564.1404
1065 | 63.67 | 44.3695 | 43.5904 | 500.8239 | 0.50372 |  | 1065 | 15.64 | 44.3695 | 4 | 500.8239
1066 | 65.25 | 41.9164 | 43.8907 | 339.7865 | 0.5011 |  | 1066 | 19.1 | 41.9164 | 3 | 339.7865
1067 | 58 | 44.684 | 22.3231 | 301.9455 | 0.50197 |  | 1067 | 18.28 | 44.684 | 2.2679 | 301.9455
1068 | 46.12 | 46.89 | 47.3425 | 304.0472 | 0.49969 |  | 1068 | 18.43 | 46.89 | 2 | 304.0472
1069 | 44 | 50.0744 | 45.5004 | 180.4963 | 0.50081 |  | 1069 | 19.94 | 50.0744 | 2.2679 | 180.4963
1070 | 44.65 | 49.3965 | 37.169 | 139.216 | 0.50417 |  | 1070 | 18.99 | 49.3965 | 3 | 139.216
1071 | 44.62 | 55.9347 | 45.7035 | 120.0364 | 0.50881 |  | 1071 | 17.39 | 55.9347 | 4 | 120.0364
1072 | 47.12 | 69.9369 | 54.903 | 156.252 | 0.51325 |  | 1072 | 17.7 | 69.9369 | 5 | 156.252
1073 | 52.39 | 93.7926 | 41.5162 | 233.0469 | 0.51576 |  | 1073 | 18.2 | 93.7926 | 5.7321 | 233.0469
1074 | 55.63 | 152.4161 | 38.3835 | 328.2428 | 0.51308 |  | 1074 | 22.48 | 152.4161 | 6 | 328.2428
1075 | 60.2 | 170.8857 | 48.16 | 351.7017 | 0.50803 |  | 1075 | 29.94 | 170.8857 | 5.7321 | 351.7017
1076 | 61.93 | 129.6241 | 34.4913 | 432.8459 | 0.50531 |  | 1076 | 30.38 | 129.6241 | 5 | 432.8459
1077 | 54.97 | 116.8307 | 26.8361 | 356.2505 | 0.50241 |  | 1077 | 29.1 | 116.8307 | 4 | 356.2505
1078 | 49.69 | 107.3607 | 26.6508 | 367.6389 | 0.49741 |  | 1078 | 20.21 | 107.3607 | 3 | 367.6389
1079 | 47.39 | 77.0886 | 29.3156 | 303.8224 | 0.50129 |  | 1079 | 20.33 | 77.0886 | 2.2679 | 303.8224
1080 | 41.51 | 37.9069 | 24.7294 | 363.2759 | 0.50628 |  | 1080 | 18.1 | 37.9069 | 2 | 363.2759
1081 | 42.3 | 35.0838 | 232.5214 | 289.0438 | 0.51158 |  | 1081 | 16.57 | 35.0838 | 2.2679 | 289.0438
1082 | 42.19 | 33.2829 | 32.6275 | 327.8939 | 0.51645 |  | 1082 | 16 | 33.2829 | 3 | 327.8939
1083 | 41.72 | 31.5704 | 29.7883 | 294.1121 | 0.51461 |  | 1083 | 15.46 | 31.5704 | 4 | 294.1121
1084 | 40.19 | 29.9372 | 24.6405 | 354.0157 | 0.5163 |  | 1084 | 13.14 | 29.9372 | 5 | 354.0157
1085 | 41.1 | 28.9241 | 28.1922 | 395.6565 | 0.51663 |  | 1085 | 12.68 | 28.9241 | 5.7321 | 395.6565
1086 | 43.67 | 28.7842 | 22.7569 | 428.168 | 0.51028 |  | 1086 | 14.65 | 28.7842 | 6 | 428.168
1087 | 52.98 | 43.6415 | 36.4643 | 535.7246 | 0.50472 |  | 1087 | 21.38 | 43.6415 | 5.7321 | 535.7246
1088 | 59.98 | 66.7635 | 40.4196 | 518.1886 | 0.50214 |  | 1088 | 33.29 | 66.7635 | 5 | 518.1886
1089 | 61.73 | 45.224 | 37.2901 | 512.086 | 0.50193 |  | 1089 | 30.11 | 45.224 | 4 | 512.086
1090 | 57.4 | 41.1944 | 43.8243 | 379.1726 | 0.49648 |  | 1090 | 32.71 | 41.1944 | 3 | 379.1726
1091 | 50.25 | 42.427 | 47.7576 | 306.5963 | 0.49353 |  | 1091 | 30.91 | 42.427 | 2.2679 | 306.5963
1092 | 40.84 | 46.6053 | 54.3189 | 288.8156 | 0.49244 |  | 1092 | 29.93 | 46.6053 | 2 | 288.8156
1093 | 41.05 | 48.0014 | 38.784 | 190.6467 | 0.49349 |  | 1093 | 27.22 | 48.0014 | 2.2679 | 190.6467
1094 | 41 | 49.5491 | 40.0597 | 111.2597 | 0.49309 |  | 1094 | 25.39 | 49.5491 | 3 | 111.2597
1095 | 42.52 | 56.7411 | 53.9211 | 86.3427 | 0.49324 |  | 1095 | 24.81 | 56.7411 | 4 | 86.3427
1096 | 44.41 | 72.4268 | 47.3188 | 147.3318 | 0.49995 |  | 1096 | 24.4 | 72.4268 | 5 | 147.3318
1097 | 48.18 | 93.8441 | 50.9669 | 189.6695 | 0.50334 |  | 1097 | 24.93 | 93.8441 | 5.7321 | 189.6695
1098 | 53.61 | 150.3822 | 234.3623 | 261.1396 | 0.49418 |  | 1098 | 28.45 | 150.3822 | 6 | 261.1396
1099 | 56.54 | 160.9761 | 26.3929 | 309.698 | 0.48791 |  | 1099 | 35.71 | 160.9761 | 5.7321 | 309.698
1100 | 55.49 | 135.3907 | 27.0777 | 366.3573 | 0.4787 |  | 1100 | 34.23 | 135.3907 | 5 | 366.3573
1101 | 49.9 | 121.7619 | 27.4702 | 366.4924 | 0.4688 |  | 1101 | 31.74 | 121.7619 | 4 | 366.4924
1102 | 41.15 | 109.9868 | 26.8576 | 372.7332 | 0.46511 |  | 1102 | 25 | 109.9868 | 3 | 372.7332
1103 | 45.86 | 80.1609 | 22.0869 | 348.593 | 0.46022 |  | 1103 | 25.87 | 80.1609 | 2.2679 | 348.593
1104 | 41.93 | 40.496 | 226.2586 | 387.8285 | 0.44605 |  | 1104 | 23.48 | 40.496 | 2 | 387.8285
1105 | 41.17 | 33.5187 | 36.4563 | 297.1322 | 0.43904 |  | 1105 | 25.99 | 33.5187 | 2.2679 | 297.1322
1106 | 39.79 | 32.0876 | 25.5304 | 329.6519 | 0.423 |  | 1106 | 23.65 | 32.0876 | 3 | 329.6519
1107 | 36 | 30.6051 | 32.9379 | 328.0184 | 0.41953 |  | 1107 | 22.91 | 30.6051 | 4 | 328.0184
1108 | 36.29 | 29.3148 | 26.9056 | 324.9191 | 0.42304 |  | 1108 | 22.04 | 29.3148 | 5 | 324.9191
1109 | 36.52 | 28.3438 | 24.1278 | 362.0683 | 0.42632 |  | 1109 | 21.83 | 28.3438 | 5.7321 | 362.0683
1110 | 40 | 28.0691 | 31.6212 | 486.6355 | 0.42626 |  | 1110 | 22.74 | 28.0691 | 6 | 486.6355
1111 | 43.1 | 43.1529 | 32.2698 | 519.9999 | 0.41457 |  | 1111 | 29.39 | 43.1529 | 5.7321 | 519.9999
1112 | 45 | 63.6149 | 39.131 | 529.0812 | 0.41564 |  | 1112 | 40.43 | 63.6149 | 5 | 529.0812
1113 | 50.34 | 44.8897 | 49.2088 | 387.3354 | 0.42154 |  | 1113 | 42.46 | 44.8897 | 4 | 387.3354
1114 | 55.07 | 41.5981 | 35.4681 | 360.0786 | 0.43142 |  | 1114 | 42.42 | 41.5981 | 3 | 360.0786
1115 | 57.73 | 45.2645 | 67.5506 | 342.3358 | 0.43861 |  | 1115 | 37.91 | 45.2645 | 2.2679 | 342.3358
1116 | 38.8 | 45.3193 | 47.064 | 346.4619 | 0.44225 |  | 1116 | 35.72 | 45.3193 | 2 | 346.4619
1117 | 35.62 | 48.7473 | 32.9211 | 348.7847 | 0.44434 |  | 1117 | 33.21 | 48.7473 | 2.2679 | 348.7847
1118 | 36 | 50.3779 | 43.4233 | 310.1628 | 0.43972 |  | 1118 | 32.77 | 50.3779 | 3 | 310.1628
1119 | 37.21 | 55.8027 | 34.3999 | 303.0932 | 0.45225 |  | 1119 | 31.7 | 55.8027 | 4 | 303.0932
1120 | 39.61 | 73.0024 | 43.5748 | 259.1719 | 0.47015 |  | 1120 | 32.09 | 73.0024 | 5 | 259.1719
1121 | 42.11 | 90.0269 | 43.6336 | 348.3573 | 0.48109 |  | 1121 | 34.88 | 90.0269 | 5.7321 | 348.3573
1122 | 46.83 | 146.8473 | 49.7645 | 338.0607 | 0.47909 |  | 1122 | 39.81 | 146.8473 | 6 | 338.0607
1123 | 53.13 | 157.7448 | 39.933 | 354.9691 | 0.47466 |  | 1123 | 53.46 | 157.7448 | 5.7321 | 354.9691
1124 | 75.92 | 134.3922 | 225.2738 | 434.2532 | 0.47124 |  | 1124 | 49.94 | 134.3922 | 5 | 434.2532
1125 | 46.47 | 116.4205 | 27.0908 | 352.3282 | 0.4694 |  | 1125 | 35.75 | 116.4205 | 4 | 352.3282
1126 | 40.67 | 106.6242 | 32.1955 | 389.9862 | 0.46739 |  | 1126 | 27 | 106.6242 | 3 | 389.9862
1127 | 42.33 | 74.3982 | 22.8427 | 305.0803 | 0.46865 |  | 1127 | 24.98 | 74.3982 | 2.2679 | 305.0803
1128 | 40.7 | 39.0193 | 26.425 | 333.0736 | 0.47532 |  | 1128 | 21.9 | 39.0193 | 2 | 333.0736
1129 | 39 | 32.929 | 29.4357 | 315.5441 | 0.48115 |  | 1129 | 21.1 | 32.929 | 2.2679 | 315.5441
1130 | 39.97 | 31.6249 | 23.2053 | 360.7569 | 0.48903 |  | 1130 | 20.4 | 31.6249 | 3 | 360.7569
1131 | 37.24 | 30.3141 | 31.0175 | 303.7837 | 0.48601 |  | 1131 | 21.1 | 30.3141 | 4 | 303.7837
1132 | 36.27 | 29.0983 | 27.141 | 418.104 | 0.48774 |  | 1132 | 19.4 | 29.0983 | 5 | 418.104
1133 | 36.13 | 28.1943 | 26.1936 | 458.6191 | 0.49379 |  | 1133 | 19.99 | 28.1943 | 5.7321 | 458.6191
1134 | 36.74 | 28.1464 | 28.4477 | 526.4722 | 0.49235 |  | 1134 | 20 | 28.1464 | 6 | 526.4722
1135 | 36.52 | 43.8774 | 21.9522 | 453.5608 | 0.48575 |  | 1135 | 22.75 | 43.8774 | 5.7321 | 453.5608
1136 | 38.82 | 64.1215 | 44.1421 | 412.9137 | 0.47669 |  | 1136 | 30.97 | 64.1215 | 5 | 412.9137
1137 | 40 | 44.0641 | 37.7402 | 396.1888 | 0.4657 |  | 1137 | 40 | 44.0641 | 4 | 396.1888
1138 | 38.88 | 41.505 | 44.1891 | 420.1608 | 0.47314 |  | 1138 | 34.19 | 41.505 | 3 | 420.1608
1139 | 36.91 | 42.3399 | 31.5079 | 445.4084 | 0.46752 |  | 1139 | 31.88 | 42.3399 | 2.2679 | 445.4084
1140 | 36.5 | 44.1152 | 57.305 | 406.2708 | 0.4602 |  | 1140 | 31.4 | 44.1152 | 2 | 406.2708
1141 | 37.41 | 46.6635 | 38.8158 | 414.9921 | 0.45597 |  | 1141 | 29.69 | 46.6635 | 2.2679 | 414.9921
1142 | 35.09 | 48.3314 | 47.2483 | 310.4534 | 0.4513 |  | 1142 | 30.6 | 48.3314 | 3 | 310.4534
1143 | 35.12 | 56.7766 | 49.2801 | 357.972 | 0.44828 |  | 1143 | 31.26 | 56.7766 | 4 | 357.972
1144 | 36.27 | 71.8864 | 40.9252 | 397.2657 | 0.46351 |  | 1144 | 32.93 | 71.8864 | 5 | 397.2657
1145 | 39.36 | 90.3493 | 230.6516 | 413.1123 | 0.47816 |  | 1145 | 33.61 | 90.3493 | 5.7321 | 413.1123
1146 | 44.03 | 142.2537 | 29.5804 | 441.7409 | 0.46782 |  | 1146 | 39.26 | 142.2537 | 6 | 441.7409
1147 | 49.6 | 151.7321 | 48.6306 | 468.5446 | 0.46362 |  | 1147 | 41 | 151.7321 | 5.7321 | 468.5446
1148 | 50.07 | 135.8472 | 24.325 | 411.0109 | 0.46196 |  | 1148 | 41.73 | 135.8472 | 5 | 411.0109
1149 | 46.15 | 113.9946 | 31.7448 | 410.7771 | 0.46259 |  | 1149 | 34.7 | 113.9946 | 4 | 410.7771
1150 | 40 | 105.3656 | 30.443 | 423.3468 | 0.46787 |  | 1150 | 29 | 105.3656 | 3 | 423.3468
1151 | 42.83 | 74.8168 | 36.0715 | 370.3887 | 0.47391 |  | 1151 | 25.83 | 74.8168 | 2.2679 | 370.3887
1152 | 38.75 | 37.7479 | 30.4415 | 417.9062 | 0.47907 |  | 1152 | 23.98 | 37.7479 | 2 | 417.9062
1153 | 39.41 | 36.1455 | 25.9321 | 385.1324 | 0.48167 |  | 1153 | 21.32 | 36.1455 | 2.2679 | 385.1324
1154 | 38.78 | 34.1256 | 36.6097 | 406.2435 | 0.48883 |  | 1154 | 20.82 | 34.1256 | 3 | 406.2435
1155 | 38.78 | 32.0829 | 21.7514 | 428.8382 | 0.50289 |  | 1155 | 19.39 | 32.0829 | 4 | 428.8382
1156 | 38.2 | 30.451 | 30.231 | 355.6787 | 0.51191 |  | 1156 | 19.96 | 30.451 | 5 | 355.6787
1157 | 38.8 | 29.4474 | 27.5763 | 400.1475 | 0.50884 |  | 1157 | 19.89 | 29.4474 | 5.7321 | 400.1475
1158 | 40 | 28.7139 | 34.6538 | 529.4078 | 0.50503 |  | 1158 | 20.45 | 28.7139 | 6 | 529.4078
1159 | 51.72 | 28.2559 | 32.5374 | 497.3969 | 0.50101 |  | 1159 | 23.95 | 28.2559 | 5.7321 | 497.3969
1160 | 57.37 | 31.211 | 240.2765 | 520.0052 | 0.50022 |  | 1160 | 36.36 | 31.211 | 5 | 520.0052
1161 | 56.01 | 48.9147 | 26.2217 | 503.8606 | 0.49828 |  | 1161 | 40.89 | 48.9147 | 4 | 503.8606
1162 | 52.61 | 67.3434 | 37.5956 | 431.6566 | 0.50593 |  | 1162 | 37.26 | 67.3434 | 3 | 431.6566
1163 | 48.43 | 74.569 | 51.9836 | 391.462 | 0.50527 |  | 1163 | 32.71 | 74.569 | 2.2679 | 391.462
1164 | 44.96 | 79.6065 | 46.4926 | 437.4068 | 0.50628 |  | 1164 | 29.18 | 79.6065 | 2 | 437.4068
1165 | 43.26 | 78.5738 | 36.62 | 383.1834 | 0.51109 |  | 1165 | 26.75 | 78.5738 | 2.2679 | 383.1834
1166 | 43.07 | 79.3037 | 51.4722 | 419.6209 | 0.51098 |  | 1166 | 27.06 | 79.3037 | 3 | 419.6209
1167 | 44.73 | 76.5362 | 32.7394 | 351.2662 | 0.51563 |  | 1167 | 27.53 | 76.5362 | 4 | 351.2662
1168 | 47.35 | 81.5543 | 246.4878 | 437.7254 | 0.51829 |  | 1168 | 30.44 | 81.5543 | 5 | 437.7254
1169 | 50.9 | 86.7794 | 35.7134 | 408.4276 | 0.51636 |  | 1169 | 33.34 | 86.7794 | 5.7321 | 408.4276
1170 | 52.94 | 128.9821 | 34.4785 | 523.4675 | 0.51264 |  | 1170 | 39.17 | 128.9821 | 6 | 523.4675
1171 | 56.94 | 168.1317 | 36.8884 | 553.3852 | 0.50686 |  | 1171 | 46.89 | 168.1317 | 5.7321 | 553.3852
1172 | 55.76 | 153.0643 | 32.293 | 421.4171 | 0.50843 |  | 1172 | 40.7 | 153.0643 | 5 | 421.4171
1173 | 51.91 | 119.0545 | 32.4077 | 489.8071 | 0.51282 |  | 1173 | 34.33 | 119.0545 | 4 | 489.8071
1174 | 43.98 | 105.9067 | 28.7458 | 387.1392 | 0.51075 |  | 1174 | 27.82 | 105.9067 | 3 | 387.1392
1175 | 40 | 92.2313 | 34.4025 | 353.0216 | 0.50791 |  | 1175 | 24.68 | 92.2313 | 2.2679 | 353.0216
1176 | 38.5 | 43.4766 | 25.8467 | 376.1969 | 0.48856 |  | 1176 | 22.26 | 43.4766 | 2 | 376.1969
1177 | 36.1 | 35.5077 | 27.3773 | 395.3849 | 0.47634 |  | 1177 | 22.2 | 35.5077 | 2.2679 | 395.3849
1178 | 35.43 | 33.6478 | 32.2122 | 329.5387 | 0.45942 |  | 1178 | 21.77 | 33.6478 | 3 | 329.5387
1179 | 35.42 | 31.966 | 23.1628 | 333.7245 | 0.44574 |  | 1179 | 21.89 | 31.966 | 4 | 333.7245
1180 | 36 | 30.3684 | 19.3406 | 368.4974 | 0.44415 |  | 1180 | 22.19 | 30.3684 | 5 | 368.4974
1181 | 36.08 | 29.1169 | 27.5506 | 390.5054 | 0.44738 |  | 1181 | 22.37 | 29.1169 | 5.7321 | 390.5054
1182 | 38.1 | 28.2486 | 62.2706 | 439.6566 | 0.45632 |  | 1182 | 19.63 | 28.2486 | 6 | 439.6566
1183 | 45.36 | 27.7623 | 102.6407 | 425.2769 | 0.47179 |  | 1183 | 28 | 27.7623 | 5.7321 | 425.2769
1184 | 48.72 | 30.139 | 60.577 | 483.4956 | 0.48458 |  | 1184 | 36.82 | 30.139 | 5 | 483.4956
1185 | 47.17 | 48.4564 | 58.7983 | 411.0424 | 0.48867 |  | 1185 | 40 | 48.4564 | 4 | 411.0424
1186 | 61.66 | 65.8068 | 51.2601 | 368.7452 | 0.48352 |  | 1186 | 37.55 | 65.8068 | 3 | 368.7452
1187 | 57.4 | 72.7653 | 48.852 | 395.4856 | 0.47672 |  | 1187 | 37.31 | 72.7653 | 2.2679 | 395.4856
1188 | 42.05 | 73.0011 | 17.4057 | 341.8162 | 0.47625 |  | 1188 | 38.89 | 73.0011 | 2 | 341.8162
1189 | 38.6 | 77.3727 | 245.9554 | 351.2197 | 0.46795 |  | 1189 | 31.86 | 77.3727 | 2.2679 | 351.2197
1190 | 38.6 | 76.4707 | 31.2054 | 343.761 | 0.46393 |  | 1190 | 28.46 | 76.4707 | 3 | 343.761
1191 | 38.6 | 74.8173 | 49.9978 | 287.553 | 0.47143 |  | 1191 | 26.2 | 74.8173 | 4 | 287.553
1192 | 42.4 | 74.5031 | 52.2237 | 340.7862 | 0.47989 |  | 1192 | 25.49 | 74.5031 | 5 | 340.7862
1193 | 43.9 | 76.464 | 39.6635 | 313.6 | 0.4902 |  | 1193 | 25 | 76.464 | 5.7321 | 313.6
1194 | 50.92 | 107.2073 | 34.3569 | 384.195 | 0.49097 |  | 1194 | 30.04 | 107.2073 | 6 | 384.195
1195 | 54.09 | 144.3536 | 44.8131 | 458.4069 | 0.49505 |  | 1195 | 30.4 | 144.3536 | 5.7321 | 458.4069
1196 | 52.42 | 157.0032 | 27.5067 | 545.1657 | 0.49393 |  | 1196 | 25.84 | 157.0032 | 5 | 545.1657
1197 | 44.9 | 116.5448 | 22.2128 | 419.3343 | 0.49169 |  | 1197 | 24.45 | 116.5448 | 4 | 419.3343
1198 | 41.63 | 102.2525 | 32.6506 | 478.8348 | 0.49853 |  | 1198 | 25.22 | 102.2525 | 3 | 478.8348
1199 | 41.98 | 87.1795 | 28.0464 | 428.2154 | 0.50352 |  | 1199 | 23.38 | 87.1795 | 2.2679 | 428.2154
1200 | 35.69 | 42.0295 | 28.0002 | 433.9621 | 0.48861 |  | 1200 | 18.9 | 42.0295 | 2 | 433.9621
1201 | 36 | 35.1751 | 31.9262 | 415.2018 | 0.49324 |  | 1201 | 18.3 | 35.1751 | 2.2679 | 415.2018
1202 | 35.4 | 33.5016 | 27.9796 | 402.9627 | 0.48731 |  | 1202 | 17.37 | 33.5016 | 3 | 402.9627
1203 | 32.95 | 31.8302 | 36.7374 | 519.9773 | 0.48875 |  | 1203 | 16.01 | 31.8302 | 4 | 519.9773
1204 | 35.5 | 30.1187 | 32.8994 | 594.3112 | 0.49069 |  | 1204 | 16.04 | 30.1187 | 5 | 594.3112
1205 | 36.06 | 29.0448 | 224.9573 | 563.0514 | 0.49302 |  | 1205 | 16.24 | 29.0448 | 5.7321 | 563.0514
1206 | 38.06 | 28.5968 | 61.9691 | 633.8976 | 0.49988 |  | 1206 | 19.96 | 28.5968 | 6 | 633.8976
1207 | 49.05 | 43.5947 | 107.3517 | 530.1352 | 0.49426 |  | 1207 | 16.89 | 43.5947 | 5.7321 | 530.1352
1208 | 54.54 | 65.7509 | 106.5449 | 643.6643 | 0.49688 |  | 1208 | 15.57 | 65.7509 | 5 | 643.6643
1209 | 54.58 | 44.6814 | 99.5544 | 525.1729 | 0.49934 |  | 1209 | 26.39 | 44.6814 | 4 | 525.1729
1210 | 53.08 | 41.287 | 65.5031 | 376.2187 | 0.49576 |  | 1210 | 35 | 41.287 | 3 | 376.2187
1211 | 52.09 | 44.5786 | 100.3389 | 348.7116 | 0.491 |  | 1211 | 34.01 | 44.5786 | 2.2679 | 348.7116
1212 | 49.01 | 46.5276 | 53.3184 | 334.8965 | 0.48678 |  | 1212 | 29.94 | 46.5276 | 2 | 334.8965
1213 | 43.26 | 49.3115 | 54.2194 | 291.3819 | 0.48622 |  | 1213 | 31 | 49.3115 | 2.2679 | 291.3819
1214 | 45.05 | 51.8923 | 48.978 | 207.1282 | 0.48251 |  | 1214 | 24.94 | 51.8923 | 3 | 207.1282
1215 | 45.58 | 59.56 | 49.7731 | 178.8414 | 0.48325 |  | 1215 | 23.47 | 59.56 | 4 | 178.8414
1216 | 46.01 | 75.3996 | 36.5299 | 218.2339 | 0.48252 |  | 1216 | 24 | 75.3996 | 5 | 218.2339
1217 | 49.79 | 97.3382 | 53.0981 | 217.023 | 0.48545 |  | 1217 | 22.44 | 97.3382 | 5.7321 | 217.023
1218 | 51.96 | 144.7699 | 45.0473 | 288.2605 | 0.48397 |  | 1218 | 25 | 144.7699 | 6 | 288.2605
1219 | 54.25 | 166.3319 | 58.6069 | 342.5237 | 0.4825 |  | 1219 | 26.32 | 166.3319 | 5.7321 | 342.5237
1220 | 54.05 | 153.3034 | 68.4782 | 376.8405 | 0.48216 |  | 1220 | 26.96 | 153.3034 | 5 | 376.8405
1221 | 49.97 | 122.7515 | 70.5068 | 494.8858 | 0.48149 |  | 1221 | 24.23 | 122.7515 | 4 | 494.8858
1222 | 40.59 | 107.9035 | 281.2849 | 436.728 | 0.47304 |  | 1222 | 23.94 | 107.9035 | 3 | 436.728
1223 | 39.07 | 77.3666 | 41.7079 | 376.5972 | 0.46103 |  | 1223 | 24.23 | 77.3666 | 2.2679 | 376.5972
1224 | 35.6 | 40.7231 | 259.3546 | 359.1413 | 0.45239 |  | 1224 | 24.23 | 40.7231 | 2 | 359.1413
1225 | 37.13 | 36.1781 | 57.0601 | 470.5481 | 0.45956 |  | 1225 | 15.89 | 36.1781 | 2.2679 | 470.5481
1226 | 36 | 34.2308 | 27.8851 | 359.2229 | 0.45707 |  | 1226 | 14.45 | 34.2308 | 3 | 359.2229
1227 | 35.49 | 32.2056 | 23.0899 | 419.7396 | 0.457 |  | 1227 | 15 | 32.2056 | 4 | 419.7396
1228 | 35.36 | 30.5452 | 31.7035 | 497.7844 | 0.45774 |  | 1228 | 15.4 | 30.5452 | 5 | 497.7844
1229 | 36.08 | 29.3193 | 25.3711 | 577.4724 | 0.45861 |  | 1229 | 15.35 | 29.3193 | 5.7321 | 577.4724
1230 | 37.9 | 28.7792 | 35.1376 | 629.2965 | 0.46468 |  | 1230 | 15.43 | 28.7792 | 6 | 629.2965
1231 | 39.9 | 44.7974 | 41.8434 | 552.9048 | 0.47958 |  | 1231 | 15.85 | 44.7974 | 5.7321 | 552.9048
1232 | 43 | 64.4238 | 101.2642 | 644.0543 | 0.49214 |  | 1232 | 16.12 | 64.4238 | 5 | 644.0543
1233 | 50.5 | 45.2612 | 119.0344 | 642.1496 | 0.49589 |  | 1233 | 16.43 | 45.2612 | 4 | 642.1496
1234 | 61.8 | 43.1431 | 52.7971 | 397.6941 | 0.49812 |  | 1234 | 17.19 | 43.1431 | 3 | 397.6941
1235 | 39.9 | 45.7136 | 54.3644 | 404.1538 | 0.50072 |  | 1235 | 17.37 | 45.7136 | 2.2679 | 404.1538
1236 | 38.2 | 48.3793 | 113.3193 | 315.2183 | 0.49813 |  | 1236 | 17.21 | 48.3793 | 2 | 315.2183
1237 | 36.7 | 49.8527 | 84.1738 | 255.9828 | 0.49485 |  | 1237 | 17.08 | 49.8527 | 2.2679 | 255.9828
1238 | 37.45 | 52.1099 | 105.0904 | 149.7234 | 0.50083 |  | 1238 | 16.49 | 52.1099 | 3 | 149.7234
1239 | 39.23 | 59.8408 | 110.3602 | 72.0753 | 0.50167 |  | 1239 | 16.29 | 59.8408 | 4 | 72.0753
1240 | 42.94 | 75.1494 | 86.2064 | 58.9059 | 0.50268 |  | 1240 | 16.18 | 75.1494 | 5 | 58.9059
1241 | 46.3 | 94.5583 | 237.1138 | 114.8531 | 0.51193 |  | 1241 | 15.34 | 94.5583 | 5.7321 | 114.8531
1242 | 50.61 | 147.2596 | 45.916 | 184.2067 | 0.51184 |  | 1242 | 16.06 | 147.2596 | 6 | 184.2067
1243 | 53.1 | 157.0812 | 41.7146 | 267.2027 | 0.51467 |  | 1243 | 19.94 | 157.0812 | 5.7321 | 267.2027
1244 | 52.98 | 130.189 | 31.1198 | 408.6404 | 0.51611 |  | 1244 | 22 | 130.189 | 5 | 408.6404
1245 | 51.39 | 115.6305 | 33.4178 | 340.3304 | 0.51901 |  | 1245 | 19.08 | 115.6305 | 4 | 340.3304
1246 | 46.13 | 109.1811 | 29.2893 | 408.093 | 0.52485 |  | 1246 | 17.37 | 109.1811 | 3 | 408.093
1247 | 45.08 | 79.6774 | 25.94 | 329.1126 | 0.52176 |  | 1247 | 17.51 | 79.6774 | 2.2679 | 329.1126
1248 | 42.69 | 41.9689 | 26.4008 | 417.8624 | 0.5205 |  | 1248 | 18.36 | 41.9689 | 2 | 417.8624
1249 | 41.58 | 34.4313 | 25.5502 | 335.4105 | 0.52674 |  | 1249 | 7.72 | 34.4313 | 2.2679 | 335.4105
1250 | 40.32 | 32.8094 | 25.5442 | 421.216 | 0.52836 |  | 1250 | 8.35 | 32.8094 | 3 | 421.216
1251 | 39.84 | 31.2335 | 31.083 | 351.1219 | 0.52985 |  | 1251 | 12.54 | 31.2335 | 4 | 351.1219
1252 | 39.59 | 29.746 | 31.1269 | 441.7741 | 0.53095 |  | 1252 | 15.23 | 29.746 | 5 | 441.7741
1253 | 39.35 | 28.7219 | 24.4974 | 494.7873 | 0.53187 |  | 1253 | 15.78 | 28.7219 | 5.7321 | 494.7873
1254 | 42 | 28.3881 | 22.6206 | 577.4544 | 0.52793 |  | 1254 | 10.25 | 28.3881 | 6 | 577.4544
1255 | 50.31 | 43.3338 | 33.8785 | 548.6511 | 0.52775 |  | 1255 | 18.05 | 43.3338 | 5.7321 | 548.6511
1256 | 54.93 | 64.0847 | 41.3453 | 588.8243 | 0.53222 |  | 1256 | 26.38 | 64.0847 | 5 | 588.8243
1257 | 57.85 | 42.8214 | 66.6415 | 573.7427 | 0.53287 |  | 1257 | 27.92 | 42.8214 | 4 | 573.7427
1258 | 55.62 | 39.981 | 326.9558 | 416.6927 | 0.53245 |  | 1258 | 32.97 | 39.981 | 3 | 416.6927
1259 | 54.14 | 42.4733 | 113.7466 | 389.8563 | 0.53168 |  | 1259 | 39.94 | 42.4733 | 2.2679 | 389.8563
1260 | 53.06 | 44.4376 | 106.235 | 271.8301 | 0.52984 |  | 1260 | 33.31 | 44.4376 | 2 | 271.8301
1261 | 51.45 | 45.9321 | 133.121 | 190.922 | 0.52609 |  | 1261 | 27.44 | 45.9321 | 2.2679 | 190.922
1262 | 48.99 | 47.4825 | 121.1665 | 192.7734 | 0.52466 |  | 1262 | 24.52 | 47.4825 | 3 | 192.7734
1263 | 45.88 | 54.9615 | 58.4722 | 119.7724 | 0.52956 |  | 1263 | 23.98 | 54.9615 | 4 | 119.7724
1264 | 45.38 | 70.5141 | 46.5037 | 171.9344 | 0.52976 |  | 1264 | 23.91 | 70.5141 | 5 | 171.9344
1265 | 49.23 | 95.4938 | 45.5327 | 217.2552 | 0.53245 |  | 1265 | 23.92 | 95.4938 | 5.7321 | 217.2552
1266 | 52.33 | 136.962 | 43.2745 | 280.301 | 0.5281 |  | 1266 | 27.93 | 136.962 | 6 | 280.301
1267 | 53.48 | 165.4786 | 41.3517 | 358.27 | 0.52357 |  | 1267 | 40.13 | 165.4786 | 5.7321 | 358.27
1268 | 49.58 | 137.7129 | 15.3494 | 399.3174 | 0.52352 |  | 1268 | 39.45 | 137.7129 | 5 | 399.3174
1269 | 44.3 | 111.6873 | 34.1867 | 389.2763 | 0.52464 |  | 1269 | 29.37 | 111.6873 | 4 | 389.2763
1270 | 43.02 | 108.3777 | 25.8198 | 370.8279 | 0.52011 |  | 1270 | 24.69 | 108.3777 | 3 | 370.8279
1271 | 43.41 | 75.0363 | 34.4782 | 287.0003 | 0.50427 |  | 1271 | 25.08 | 75.0363 | 2.2679 | 287.0003
1272 | 39.6 | 39.4731 | 21.5272 | 270.1352 | 0.49527 |  | 1272 | 24.94 | 39.4731 | 2 | 270.1352
1273 | 38.04 | 36.0967 | 29.3284 | 264.0713 | 0.4939 |  | 1273 | 27.45 | 36.0967 | 2.2679 | 264.0713
1274 | 36.54 | 34.1233 | 28.63 | 251.6305 | 0.50664 |  | 1274 | 22.36 | 34.1233 | 3 | 251.6305
1275 | 36.06 | 32.1943 | 226.2449 | 269.1988 | 0.50412 |  | 1275 | 21.12 | 32.1943 | 4 | 269.1988
1276 | 36.01 | 30.572 | 34.7195 | 319.223 | 0.50271 |  | 1276 | 17.47 | 30.572 | 5 | 319.223
1277 | 35.61 | 29.4103 | 22.126 | 405.828 | 0.50719 |  | 1277 | 17.83 | 29.4103 | 5.7321 | 405.828
1278 | 36.03 | 29.1445 | 29.3256 | 348.0483 | 0.51556 |  | 1278 | 20.96 | 29.1445 | 6 | 348.0483
1279 | 37.3 | 44.6382 | 34.9674 | 390.359 | 0.52325 |  | 1279 | 27.32 | 44.6382 | 5.7321 | 390.359
1280 | 41.11 | 65.2404 | 48.1763 | 368.7649 | 0.52262 |  | 1280 | 31.52 | 65.2404 | 5 | 368.7649
1281 | 43.57 | 44.6532 | 33.5846 | 426.406 | 0.51526 |  | 1281 | 33.31 | 44.6532 | 4 | 426.406
1282 | 51.16 | 42.8291 | 52.4977 | 380.0628 | 0.51418 |  | 1282 | 32.63 | 42.8291 | 3 | 380.0628
1283 | 40.94 | 45.2603 | 39.3677 | 273.9795 | 0.5126 |  | 1283 | 31.08 | 45.2603 | 2.2679 | 273.9795
1284 | 38.02 | 48.349 | 238.3449 | 251.137 | 0.51129 |  | 1284 | 31.54 | 48.349 | 2 | 251.137
1285 | 35.66 | 51.2086 | 30.4606 | 209.5404 | 0.51165 |  | 1285 | 29.39 | 51.2086 | 2.2679 | 209.5404
1286 | 35.32 | 53.1758 | 48.0361 | 195.2424 | 0.50945 |  | 1286 | 27.27 | 53.1758 | 3 | 195.2424
1287 | 35.62 | 61.2355 | 42.3136 | 151.2265 | 0.51627 |  | 1287 | 26.14 | 61.2355 | 4 | 151.2265
1288 | 35.5 | 76.3934 | 41.2712 | 188.3894 | 0.52373 |  | 1288 | 26.3 | 76.3934 | 5 | 188.3894
1289 | 45.47 | 94.5914 | 31.2217 | 195.5992 | 0.53406 |  | 1289 | 26.47 | 94.5914 | 5.7321 | 195.5992
1290 | 47.49 | 147.3053 | 50.7787 | 258.4979 | 0.52799 |  | 1290 | 30.08 | 147.3053 | 6 | 258.4979
1291 | 52.2 | 162.7655 | 37.9285 | 274.4063 | 0.50833 |  | 1291 | 36.75 | 162.7655 | 5.7321 | 274.4063
1292 | 50.97 | 137.3546 | 28.901 | 279.3625 | 0.49886 |  | 1292 | 29.94 | 137.3546 | 5 | 279.3625
1293 | 46.99 | 119.7154 | 230.8973 | 276.0512 | 0.50423 |  | 1293 | 26.25 | 119.7154 | 4 | 276.0512
1294 | 40.35 | 112.1293 | 24.3479 | 283.1744 | 0.50753 |  | 1294 | 23.28 | 112.1293 | 3 | 283.1744
1295 | 41.59 | 80.268 | 27.179 | 223.8015 | 0.50096 |  | 1295 | 23.06 | 80.268 | 2.2679 | 223.8015
1296 | 39 | 42.9058 | 29.7341 | 205.7035 | 0.50216 |  | 1296 | 24.94 | 42.9058 | 2 | 205.7035
1297 | 37.82 | 35.9979 | 25.7631 | 231.0806 | 0.51594 |  | 1297 | 23.99 | 35.9979 | 2.2679 | 231.0806
1298 | 37.48 | 34.1012 | 36.7342 | 181.7313 | 0.52203 |  | 1298 | 22.8 | 34.1012 | 3 | 181.7313
1299 | 37.48 | 32.2045 | 26.1432 | 204.7232 | 0.53681 |  | 1299 | 22.17 | 32.2045 | 4 | 204.7232
1300 | 36.21 | 30.4806 | 31.5286 | 229.0608 | 0.54199 |  | 1300 | 20.8 | 30.4806 | 5 | 229.0608
1301 | 36.21 | 29.4056 | 22.7249 | 272.2438 | 0.54187 |  | 1301 | 19.26 | 29.4056 | 5.7321 | 272.2438
1302 | 37.04 | 28.9785 | 28.5585 | 340.3748 | 0.54459 |  | 1302 | 20.76 | 28.9785 | 6 | 340.3748
1303 | 37.3 | 43.9489 | 18.6602 | 361.4887 | 0.54642 |  | 1303 | 24.39 | 43.9489 | 5.7321 | 361.4887
1304 | 37.98 | 65.1268 | 30.6706 | 309.9649 | 0.55205 |  | 1304 | 33.69 | 65.1268 | 5 | 309.9649
1305 | 39.11 | 44.2708 | 37.9893 | 287.2777 | 0.55505 |  | 1305 | 36.73 | 44.2708 | 4 | 287.2777
1306 | 39.79 | 43.1698 | 43.9613 | 293.3308 | 0.55257 |  | 1306 | 44.23 | 43.1698 | 3 | 293.3308
1307 | 37.65 | 47.4483 | 44.933 | 236.889 | 0.53754 |  | 1307 | 34.94 | 47.4483 | 2.2679 | 236.889
1308 | 37.06 | 48.0294 | 48.2779 | 161.718 | 0.52509 |  | 1308 | 29.1 | 48.0294 | 2 | 161.718
1309 | 37.14 | 51.0033 | 39.9926 | 76.3601 | 0.51612 |  | 1309 | 23.8 | 51.0033 | 2.2679 | 76.3601
1310 | 35 | 53.1007 | 46.5387 | 59.4367 | 0.51667 |  | 1310 | 24.96 | 53.1007 | 3 | 59.4367
1311 | 34.54 | 59.4795 | 41.4245 | 62.337 | 0.51093 |  | 1311 | 25 | 59.4795 | 4 | 62.337
1312 | 35.25 | 73.0706 | 33.9934 | 65.4924 | 0.52328 |  | 1312 | 24 | 73.0706 | 5 | 65.4924
1313 | 38.57 | 93.0348 | 254.8892 | 61.8882 | 0.52906 |  | 1313 | 25.43 | 93.0348 | 5.7321 | 61.8882
1314 | 45.75 | 130.4373 | 54.3854 | 96.373 | 0.52716 |  | 1314 | 32.04 | 130.4373 | 6 | 96.373
1315 | 51.68 | 149.7423 | 38.2547 | 105.3645 | 0.5195 |  | 1315 | 36.13 | 149.7423 | 5.7321 | 105.3645
1316 | 51.47 | 141.4216 | 33.2418 | 104.1476 | 0.51682 |  | 1316 | 37.31 | 141.4216 | 5 | 104.1476
1317 | 50 | 116.0334 | 27.6025 | 158.9055 | 0.52015 |  | 1317 | 31.33 | 116.0334 | 4 | 158.9055
1318 | 44.46 | 107.2007 | 26.8306 | 163.0304 | 0.52589 |  | 1318 | 24.88 | 107.2007 | 3 | 163.0304
1319 | 47.65 | 77.716 | 29.9744 | 163.0289 | 0.5244 |  | 1319 | 23.03 | 77.716 | 2.2679 | 163.0289
1320 | 44.1 | 41.4272 | 25.6796 | 174.8026 | 0.5254 |  | 1320 | 20.74 | 41.4272 | 2 | 174.8026
1321 | 38.7 | 32.8908 | 25.1535 | 180.7342 | 0.52927 |  | 1321 | 24.04 | 32.8908 | 2.2679 | 180.7342
1322 | 37.02 | 31.4836 | 28.1988 | 130.8269 | 0.52524 |  | 1322 | 22.58 | 31.4836 | 3 | 130.8269
1323 | 37 | 30.094 | 23.7947 | 203.1138 | 0.52171 |  | 1323 | 21.26 | 30.094 | 4 | 203.1138
1324 | 36.37 | 28.8487 | 20.2424 | 250.5668 | 0.52082 |  | 1324 | 20.09 | 28.8487 | 5 | 250.5668
1325 | 36.06 | 28.0675 | 32.6515 | 221.1562 | 0.52743 |  | 1325 | 19.94 | 28.0675 | 5.7321 | 221.1562
1326 | 40.07 | 27.7067 | 25.8483 | 281.6428 | 0.52871 |  | 1326 | 21.7 | 27.7067 | 6 | 281.6428
1327 | 50.02 | 27.6597 | 27.2882 | 339.3483 | 0.52427 |  | 1327 | 27.19 | 27.6597 | 5.7321 | 339.3483
1328 | 56.88 | 31.0822 | 42.7214 | 350.8937 | 0.52204 |  | 1328 | 36.04 | 31.0822 | 5 | 350.8937
1329 | 55.59 | 49.5771 | 46.1006 | 266.6969 | 0.52397 |  | 1329 | 38.29 | 49.5771 | 4 | 266.6969
1330 | 50.72 | 68.9868 | 53.4257 | 237.8305 | 0.52256 |  | 1330 | 34.44 | 68.9868 | 3 | 237.8305
1331 | 40.03 | 77.1247 | 23.2805 | 169.5882 | 0.51766 |  | 1331 | 32.12 | 77.1247 | 2.2679 | 169.5882
1332 | 38.97 | 77.3961 | 234.3032 | 112.5944 | 0.5142 |  | 1332 | 30.44 | 77.3961 | 2 | 112.5944
1333 | 37.4 | 85.3348 | 45.7535 | 65.7632 | 0.51289 |  | 1333 | 26.55 | 85.3348 | 2.2679 | 65.7632
1334 | 38.98 | 78.1004 | 31.8517 | 72.0653 | 0.51899 |  | 1334 | 26.01 | 78.1004 | 3 | 72.0653
1335 | 37.88 | 71.3782 | 46.2365 | 50.3144 | 0.52204 |  | 1335 | 25 | 71.3782 | 4 | 50.3144
1336 | 42 | 74.8636 | 41.7134 | 58.9059 | 0.52537 |  | 1336 | 24.78 | 74.8636 | 5 | 58.9059
1337 | 44.4 | 79.7696 | 32.8088 | 81.7592 | 0.52878 |  | 1337 | 25.39 | 79.7696 | 5.7321 | 81.7592
1338 | 53.24 | 118.8433 | 42.2842 | 75.6345 | 0.52822 |  | 1338 | 31.16 | 118.8433 | 6 | 75.6345
1339 | 56.92 | 155.1439 | 48.1761 | 122.9783 | 0.52662 |  | 1339 | 39.91 | 155.1439 | 5.7321 | 122.9783
1340 | 54.4 | 144.7839 | 28.9345 | 105.4847 | 0.5243 |  | 1340 | 36.51 | 144.7839 | 5 | 105.4847
1341 | 50.61 | 115.2624 | 25.6343 | 106.3907 | 0.5256 |  | 1341 | 30.31 | 115.2624 | 4 | 106.3907
1342 | 43.09 | 101.2261 | 31.3575 | 61.6591 | 0.52628 |  | 1342 | 25.2 | 101.2261 | 3 | 61.6591
1343 | 42.4 | 88.358 | 24.5776 | 41.8167 | 0.5216 |  | 1343 | 25.1 | 88.358 | 2.2679 | 41.8167
1344 | 40.4 | 39.2699 | 26.0664 | 119.4613 | 0.52037 |  | 1344 | 24.63 | 39.2699 | 2 | 119.4613
1345 | 37.1 | 35.4725 | 32.2527 | 181.4459 | 0.52505 |  | 1345 | 25.44 | 35.4725 | 2.2679 | 181.4459
1346 | 37 | 33.7724 | 229.5003 | 141.9258 | 0.52604 |  | 1346 | 23 | 33.7724 | 3 | 141.9258
1347 | 36.84 | 32.0014 | 238.28 | 242.1324 | 0.52542 |  | 1347 | 21.11 | 32.0014 | 4 | 242.1324
1348 | 35.88 | 30.3729 | 26.1604 | 259.4865 | 0.52614 |  | 1348 | 20 | 30.3729 | 5 | 259.4865
1349 | 36.77 | 29.1206 | 27.8738 | 322.1319 | 0.52647 |  | 1349 | 21.02 | 29.1206 | 5.7321 | 322.1319
1350 | 39.41 | 28.2951 | 23.5772 | 327.581 | 0.52085 |  | 1350 | 22.07 | 28.2951 | 6 | 327.581
1351 | 48.74 | 27.7915 | 33.1877 | 332.5163 | 0.52084 |  | 1351 | 27.35 | 27.7915 | 5.7321 | 332.5163
1352 | 53.04 | 30.1963 | 31.868 | 357.4536 | 0.52806 |  | 1352 | 32.93 | 30.1963 | 5 | 357.4536
1353 | 51.88 | 47.5859 | 24.141 | 314.0369 | 0.52889 |  | 1353 | 36.08 | 47.5859 | 4 | 314.0369
1354 | 49.92 | 67.2946 | 43.3 | 258.6622 | 0.526 |  | 1354 | 33.48 | 67.2946 | 3 | 258.6622
1355 | 42 | 72.9985 | 31.8794 | 206.4543 | 0.52069 |  | 1355 | 32.6 | 72.9985 | 2.2679 | 206.4543
1356 | 39.08 | 74.3915 | 37.0738 | 113.463 | 0.51756 |  | 1356 | 29.5 | 74.3915 | 2 | 113.463
1357 | 39.28 | 81.1709 | 43.9036 | 92.2555 | 0.51133 |  | 1357 | 27.57 | 81.1709 | 2.2679 | 92.2555
1358 | 39 | 79.3472 | 31.9359 | 55.5246 | 0.51344 |  | 1358 | 25.06 | 79.3472 | 3 | 55.5246
1359 | 37.91 | 73.8996 | 47.3822 | 54.6426 | 0.51651 |  | 1359 | 24 | 73.8996 | 4 | 54.6426
1360 | 41.45 | 71.9393 | 37.6085 | 63.504 | 0.52008 |  | 1360 | 25.11 | 71.9393 | 5 | 63.504
1361 | 45.14 | 75.2328 | 255.094 | 72.5063 | 0.52474 |  | 1361 | 26.94 | 75.2328 | 5.7321 | 72.5063
1362 | 55.24 | 103.7144 | 40.461 | 109.1352 | 0.52342 |  | 1362 | 33.98 | 103.7144 | 6 | 109.1352
1363 | 62.98 | 144.5629 | 39.1968 | 123.0844 | 0.51955 |  | 1363 | 39.94 | 144.5629 | 5.7321 | 123.0844
1364 | 54.94 | 153.6482 | 23.6679 | 119.8738 | 0.5175 |  | 1364 | 37.55 | 153.6482 | 5 | 119.8738
1365 | 51.19 | 115.9481 | 29.8453 | 82.8963 | 0.51705 |  | 1365 | 31.18 | 115.9481 | 4 | 82.8963
1366 | 47.57 | 102.5163 | 32.0434 | 121.4475 | 0.51681 |  | 1366 | 26.35 | 102.5163 | 3 | 121.4475
1367 | 46.8 | 90.6872 | 23.1248 | 143.569 | 0.50426 |  | 1367 | 26.86 | 90.6872 | 2.2679 | 143.569
1368 | 41.41 | 42.4431 | 28.0898 | 142.4953 | 0.49535 |  | 1368 | 25 | 42.4431 | 2 | 142.4953
1369 | 40.98 | 35.4503 | 31.9329 | 161.1288 | 0.48956 |  | 1369 | 26.94 | 35.4503 | 2.2679 | 161.1288
1370 | 39.42 | 33.6635 | 31.8125 | 152.7295 | 0.48855 |  | 1370 | 23.02 | 33.6635 | 3 | 152.7295
1371 | 38.58 | 31.8729 | 28.4381 | 190.2958 | 0.48714 |  | 1371 | 21.77 | 31.8729 | 4 | 190.2958
1372 | 37.99 | 30.3032 | 26.8738 | 219.0603 | 0.48164 |  | 1372 | 19.76 | 30.3032 | 5 | 219.0603
1373 | 38.59 | 29.2056 | 30.6236 | 270.5151 | 0.48092 |  | 1373 | 19.83 | 29.2056 | 5.7321 | 270.5151
1374 | 41.48 | 28.4723 | 27.1077 | 323.5603 | 0.48435 |  | 1374 | 20.16 | 28.4723 | 6 | 323.5603
1375 | 50.75 | 45.0176 | 219.9795 | 354.1503 | 0.49086 |  | 1375 | 21.18 | 45.0176 | 5.7321 | 354.1503
1376 | 59.84 | 63.8233 | 38.4709 | 333.5105 | 0.50041 |  | 1376 | 22.76 | 63.8233 | 5 | 333.5105
1377 | 54.19 | 43.193 | 36.623 | 227.8542 | 0.50401 |  | 1377 | 25.71 | 43.193 | 4 | 227.8542
1378 | 49.95 | 41.1758 | 47.2718 | 203.4251 | 0.50171 |  | 1378 | 26.79 | 41.1758 | 3 | 203.4251
1379 | 44.57 | 44.1463 | 45.644 | 143.8247 | 0.49733 |  | 1379 | 24.96 | 44.1463 | 2.2679 | 143.8247
1380 | 40.79 | 45.8155 | 51.2707 | 82.5807 | 0.49489 |  | 1380 | 23.3 | 45.8155 | 2 | 82.5807
1381 | 39.63 | 49.1128 | 42.8951 | 86.1778 | 0.49172 |  | 1381 | 22.03 | 49.1128 | 2.2679 | 86.1778
1382 | 39.58 | 50.3412 | 39.8213 | 66.9178 | 0.49628 |  | 1382 | 19.94 | 50.3412 | 3 | 66.9178
1383 | 40.06 | 56.8273 | 36.9745 | 64.0803 | 0.49492 |  | 1383 | 19.68 | 56.8273 | 4 | 64.0803
1384 | 40.62 | 73.4996 | 54.2859 | 63.6905 | 0.50128 |  | 1384 | 19.93 | 73.4996 | 5 | 63.6905
1385 | 43.92 | 93.2476 | 36.0543 | 73.7956 | 0.50458 |  | 1385 | 20.21 | 93.2476 | 5.7321 | 73.7956
1386 | 53.16 | 138.4032 | 44.398 | 76.1037 | 0.4989 |  | 1386 | 24.97 | 138.4032 | 6 | 76.1037
1387 | 54.48 | 151.418 | 32.9151 | 102.0752 | 0.49446 |  | 1387 | 32.04 | 151.418 | 5.7321 | 102.0752
1388 | 51.82 | 149.2928 | 230.2701 | 96.0683 | 0.4893 |  | 1388 | 31.91 | 149.2928 | 5 | 96.0683
1389 | 46.69 | 122.0556 | 22.7522 | 121.5438 | 0.48177 |  | 1389 | 25.72 | 122.0556 | 4 | 121.5438
1390 | 41.58 | 110.3423 | 29.6175 | 139.3568 | 0.4812 |  | 1390 | 21.74 | 110.3423 | 3 | 139.3568
1391 | 41.39 | 80.2874 | 20.0647 | 189.4609 | 0.47228 |  | 1391 | 23.1 | 80.2874 | 2.2679 | 189.4609
1392 | 37.4 | 41.6167 | 33.8752 | 165.2396 | 0.46521 |  | 1392 | 23.4 | 41.6167 | 2 | 165.2396
1393 | 37.5 | 35.483 | 28.7071 | 169.1638 | 0.46927 |  | 1393 | 19.9 | 35.483 | 2.2679 | 169.1638
1394 | 37.98 | 33.6517 | 30.796 | 169.4468 | 0.48188 |  | 1394 | 18.39 | 33.6517 | 3 | 169.4468
1395 | 37.5 | 31.8821 | 35.1562 | 250.3787 | 0.48258 |  | 1395 | 18.01 | 31.8821 | 4 | 250.3787
1396 | 38.6 | 30.2586 | 28.5349 | 249.001 | 0.47524 |  | 1396 | 17.62 | 30.2586 | 5 | 249.001
1397 | 36.4 | 29.0639 | 33.4113 | 328.6766 | 0.47173 |  | 1397 | 17.31 | 29.0639 | 5.7321 | 328.6766
1398 | 34.9 | 28.6545 | 29.1302 | 400.1065 | 0.47826 |  | 1398 | 17.46 | 28.6545 | 6 | 400.1065
1399 | 42.45 | 43.9146 | 25.2602 | 423.0477 | 0.4952 |  | 1399 | 17.51 | 43.9146 | 5.7321 | 423.0477
1400 | 49.59 | 63.7082 | 243.733 | 403.2555 | 0.51312 |  | 1400 | 17.58 | 63.7082 | 5 | 403.2555
1401 | 56.49 | 43.6484 | 44.7512 | 359.561 | 0.51542 |  | 1401 | 17.9 | 43.6484 | 4 | 359.561
1402 | 57.3 | 42.4454 | 62.7315 | 258.9336 | 0.51138 |  | 1402 | 19.02 | 42.4454 | 3 | 258.9336
1403 | 42.66 | 45.3305 | 41.9151 | 177.1785 | 0.49734 |  | 1403 | 19.01 | 45.3305 | 2.2679 | 177.1785
1404 | 38.89 | 46.3197 | 45.1593 | 100.2226 | 0.47457 |  | 1404 | 19.02 | 46.3197 | 2 | 100.2226
1405 | 38 | 48.6501 | 51.8574 | 86.8791 | 0.46768 |  | 1405 | 17.12 | 48.6501 | 2.2679 | 86.8791
1406 | 37.08 | 50.6651 | 41.1282 | 74.0557 | 0.46061 |  | 1406 | 17.61 | 50.6651 | 3 | 74.0557
1407 | 38.05 | 57.8289 | 35.5145 | 59.5117 | 0.46151 |  | 1407 | 17.46 | 57.8289 | 4 | 59.5117
1408 | 44.68 | 73.9397 | 246.8711 | 57.9117 | 0.46323 |  | 1408 | 14.98 | 73.9397 | 5 | 57.9117
1409 | 47.45 | 90.6039 | 40.8765 | 89.116 | 0.468 |  | 1409 | 13.26 | 90.6039 | 5.7321 | 89.116
1410 | 53.67 | 128.9779 | 38.8053 | 82.954 | 0.47488 |  | 1410 | 19.11 | 128.9779 | 6 | 82.954
1411 | 53.76 | 163.0843 | 35.9454 | 99.5286 | 0.47469 |  | 1411 | 24.6 | 163.0843 | 5.7321 | 99.5286
1412 | 50.97 | 137.2187 | 225.9732 | 113.5257 | 0.47892 |  | 1412 | 26.98 | 137.2187 | 5 | 113.5257
1413 | 49.2 | 114.5306 | 27.7613 | 75.506 | 0.48686 |  | 1413 | 21.81 | 114.5306 | 4 | 75.506
1414 | 44.2 | 108.6898 | 30.7411 | 137.4225 | 0.4903 |  | 1414 | 20.3 | 108.6898 | 3 | 137.4225
1415 | 43.21 | 77.6315 | 32.5301 | 168.4621 | 0.4894 |  | 1415 | 20.44 | 77.6315 | 2.2679 | 168.4621
1416 | 41.44 | 40.8008 | 30.4671 | 191.635 | 0.49145 |  | 1416 | 20.19 | 40.8008 | 2 | 191.635
1417 | 39.4 | 32.7614 | 28.6062 | 296.5346 | 0.48736 |  | 1417 | 22.75 | 32.7614 | 2.2679 | 296.5346
1418 | 37.7 | 31.3802 | 39.244 | 311.489 | 0.48658 |  | 1418 | 18.81 | 31.3802 | 3 | 311.489
1419 | 37.23 | 29.9808 | 33.092 | 275.7318 | 0.47997 |  | 1419 | 17.6 | 29.9808 | 4 | 275.7318
1420 | 37.72 | 28.8181 | 27.2554 | 319.3435 | 0.47877 |  | 1420 | 17.43 | 28.8181 | 5 | 319.3435
1421 | 40.06 | 28.1049 | 31.9511 | 347.0658 | 0.47421 |  | 1421 | 17.01 | 28.1049 | 5.7321 | 347.0658
1422 | 41.96 | 28.1003 | 30.7816 | 415.776 | 0.46488 |  | 1422 | 19.97 | 28.1003 | 6 | 415.776
1423 | 46.75 | 43.6844 | 23.793 | 433.6469 | 0.46153 |  | 1423 | 28.23 | 43.6844 | 5.7321 | 433.6469
1424 | 47.98 | 63.9167 | 229.6018 | 454.2921 | 0.47463 |  | 1424 | 35.7 | 63.9167 | 5 | 454.2921
1425 | 50.62 | 44.3882 | 43.2744 | 360.3168 | 0.48284 |  | 1425 | 34.05 | 44.3882 | 4 | 360.3168
1426 | 51.08 | 42.3722 | 51.0547 | 365.6628 | 0.48573 |  | 1426 | 28.91 | 42.3722 | 3 | 365.6628
1427 | 52.21 | 43.828 | 40.3414 | 359.3839 | 0.4873 |  | 1427 | 26 | 43.828 | 2.2679 | 359.3839
1428 | 52.03 | 45.2185 | 48.4341 | 353.1991 | 0.48665 |  | 1428 | 24.74 | 45.2185 | 2 | 353.1991
1429 | 48.56 | 49.7858 | 52.3009 | 351.7058 | 0.48801 |  | 1429 | 23.71 | 49.7858 | 2.2679 | 351.7058
1430 | 47.4 | 51.05 | 48.2735 | 304.4628 | 0.49477 |  | 1430 | 22.64 | 51.05 | 3 | 304.4628
1431 | 46.91 | 57.3887 | 50.6356 | 337.4882 | 0.49968 |  | 1431 | 22.16 | 57.3887 | 4 | 337.4882
1432 | 47.31 | 74.4868 | 46.4818 | 346.6281 | 0.49906 |  | 1432 | 22.34 | 74.4868 | 5 | 346.6281
1433 | 50.04 | 93.1248 | 54.5943 | 305.9659 | 0.50032 |  | 1433 | 22.72 | 93.1248 | 5.7321 | 305.9659
1434 | 53.59 | 136.3032 | 32.1278 | 410.7405 | 0.50061 |  | 1434 | 26.58 | 136.3032 | 6 | 410.7405
1435 | 55 | 158.2745 | 39.5041 | 341.5402 | 0.49943 |  | 1435 | 34.03 | 158.2745 | 5.7321 | 341.5402
1436 | 52.49 | 150.7162 | 23.1742 | 419.5922 | 0.50156 |  | 1436 | 32.12 | 150.7162 | 5 | 419.5922
1437 | 48.66 | 113.6521 | 31.8165 | 388.5646 | 0.5005 |  | 1437 | 27.88 | 113.6521 | 4 | 388.5646
1438 | 46.53 | 105.4067 | 232.3626 | 384.4366 | 0.49846 |  | 1438 | 24 | 105.4067 | 3 | 384.4366
1439 | 45.65 | 75.203 | 37.1524 | 352.3723 | 0.49058 |  | 1439 | 24 | 75.203 | 2.2679 | 352.3723
1440 | 44.41 | 38.7235 | 24.8183 | 352.7259 | 0.48115 |  | 1440 | 23.32 | 38.7235 | 2 | 352.7259
1441 | 44.19 | 33.4137 | 26.907 | 280.8158 | 0.48824 |  | 1441 | 22.76 | 33.4137 | 2.2679 | 280.8158
1442 | 43.28 | 31.9891 | 30.2771 | 344.5312 | 0.50086 |  | 1442 | 22.11 | 31.9891 | 3 | 344.5312
1443 | 41.09 | 30.5978 | 32.0587 | 306.8385 | 0.50192 |  | 1443 | 20.4 | 30.5978 | 4 | 306.8385
1444 | 39.49 | 29.2596 | 35.3944 | 340.6153 | 0.50019 |  | 1444 | 19.74 | 29.2596 | 5 | 340.6153
1445 | 40.63 | 28.4144 | 30.6516 | 325.1921 | 0.4985 |  | 1445 | 19.96 | 28.4144 | 5.7321 | 325.1921
1446 | 39.97 | 28.44 | 36.7951 | 379.7994 | 0.49609 |  | 1446 | 20.45 | 28.44 | 6 | 379.7994
1447 | 41.42 | 42.792 | 35.8599 | 423.891 | 0.49616 |  | 1447 | 27.14 | 42.792 | 5.7321 | 423.891
1448 | 43.92 | 61.1265 | 38.138 | 358.6049 | 0.49933 |  | 1448 | 32.93 | 61.1265 | 5 | 358.6049
1449 | 47.89 | 43.4101 | 33.5468 | 439.435 | 0.49545 |  | 1449 | 38.66 | 43.4101 | 4 | 439.435
1450 | 48.6 | 42.7195 | 47.6502 | 311.6559 | 0.49187 |  | 1450 | 36.6 | 42.7195 | 3 | 311.6559
1451 | 47.9 | 44.6379 | 255.8809 | 338.1938 | 0.48329 |  | 1451 | 35.6 | 44.6379 | 2.2679 | 338.1938
1452 | 45.84 | 47.3019 | 39.2557 | 304.3932 | 0.46987 |  | 1452 | 31.68 | 47.3019 | 2 | 304.3932
1453 | 43.9 | 50.2915 | 46.0372 | 315.9575 | 0.46021 |  | 1453 | 30 | 50.2915 | 2.2679 | 315.9575
1454 | 40.21 | 49.9999 | 58.6992 | 256.7587 | 0.459 |  | 1454 | 29.34 | 49.9999 | 3 | 256.7587
1455 | 40.68 | 57.9319 | 52.6907 | 281.8504 | 0.46178 |  | 1455 | 26.62 | 57.9319 | 4 | 281.8504
1456 | 41.04 | 70.7009 | 46.9533 | 304.6723 | 0.45884 |  | 1456 | 26.47 | 70.7009 | 5 | 304.6723
1457 | 41.91 | 90.6288 | 32.1282 | 272.2275 | 0.45368 |  | 1457 | 24.5 | 90.6288 | 5.7321 | 272.2275
1458 | 45.1 | 146.8707 | 37.0082 | 294.5277 | 0.44589 |  | 1458 | 26.95 | 146.8707 | 6 | 294.5277
1459 | 46.49 | 142.5299 | 33.2466 | 333.2269 | 0.43952 |  | 1459 | 27.52 | 142.5299 | 5.7321 | 333.2269
1460 | 46.8 | 138.5006 | 34.0591 | 389.2689 | 0.42227 |  | 1460 | 26.5 | 138.5006 | 5 | 389.2689
1461 | 40.46 | 117.0198 | 31.9849 | 368.9042 | 0.39976 |  | 1461 | 25.07 | 117.0198 | 4 | 368.9042
1462 | 39.9 | 106.9192 | 34.2913 | 435.8177 | 0.38142 |  | 1462 | 20.76 | 106.9192 | 3 | 435.8177
1463 | 39.9 | 77.0555 | 29.0835 | 356.2699 | 0.37299 |  | 1463 | 19.37 | 77.0555 | 2.2679 | 356.2699
1464 | 38.57 | 39.2502 | 35.0135 | 319.7434 | 0.35999 |  | 1464 | 17.73 | 39.2502 | 2 | 319.7434
1465 | 39.9 | 33.7881 | 31.5357 | 409.9382 | 0.3503 |  | 1465 | 15 | 33.7881 | 2.2679 | 409.9382
1466 | 40.19 | 32.2687 | 230.642 | 337.6053 | 0.34577 |  | 1466 | 19.03 | 32.2687 | 3 | 337.6053
1467 | 36.9 | 30.6328 | 33.6174 | 314.1266 | 0.33777 |  | 1467 | 17.56 | 30.6328 | 4 | 314.1266
1468 | 37.26 | 29.418 | 26.5491 | 392.1023 | 0.3317 |  | 1468 | 17.6 | 29.418 | 5 | 392.1023
1469 | 36.7 | 28.4968 | 36.3983 | 443.0671 | 0.32866 |  | 1469 | 16.82 | 28.4968 | 5.7321 | 443.0671
1470 | 35.71 | 28.2843 | 25.333 | 539.4218 | 0.33247 |  | 1470 | 15.95 | 28.2843 | 6 | 539.4218
1471 | 38.83 | 41.6583 | 33.1298 | 555.2749 | 0.34726 |  | 1471 | 21.45 | 41.6583 | 5.7321 | 555.2749
1472 | 41.37 | 60.3892 | 49.5516 | 475.3641 | 0.36034 |  | 1472 | 36.56 | 60.3892 | 5 | 475.3641
1473 | 38 | 44.1877 | 37.7809 | 459.7326 | 0.37332 |  | 1473 | 30.8 | 44.1877 | 4 | 459.7326
1474 | 45.12 | 42.9116 | 39.7608 | 375.4265 | 0.38654 |  | 1474 | 34.86 | 42.9116 | 3 | 375.4265
1475 | 52.02 | 46.6101 | 243.649 | 469.2998 | 0.39649 |  | 1475 | 27.44 | 46.6101 | 2.2679 | 469.2998
1476 | 58.44 | 46.8269 | 51.1117 | 475.1197 | 0.40295 |  | 1476 | 28 | 46.8269 | 2 | 475.1197
1477 | 51.16 | 49.6618 | 47.9744 | 424.5118 | 0.39952 |  | 1477 | 27.43 | 49.6618 | 2.2679 | 424.5118
1478 | 43.33 | 52.7118 | 47.129 | 344.5742 | 0.38988 |  | 1478 | 26 | 52.7118 | 3 | 344.5742
1479 | 39.75 | 60.2198 | 44.534 | 383.5685 | 0.37764 |  | 1479 | 25.92 | 60.2198 | 4 | 383.5685
1480 | 38.3 | 76.1827 | 29.2902 | 389.7222 | 0.37175 |  | 1480 | 28.06 | 76.1827 | 5 | 389.7222
1481 | 33.8 | 93.8502 | 45.1879 | 460.4613 | 0.3705 |  | 1481 | 28.56 | 93.8502 | 5.7321 | 460.4613
1482 | 40 | 140.0367 | 53.6667 | 353.7565 | 0.37083 |  | 1482 | 31.99 | 140.0367 | 6 | 353.7565
1483 | 39 | 160.5897 | 247.7969 | 496.0398 | 0.37436 |  | 1483 | 40 | 160.5897 | 5.7321 | 496.0398
1484 | 41.8 | 133.636 | 22.5984 | 467.58 | 0.37858 |  | 1484 | 38.45 | 133.636 | 5 | 467.58
1485 | 44.09 | 114.2453 | 36.8827 | 379.1144 | 0.37699 |  | 1485 | 31 | 114.2453 | 4 | 379.1144
1486 | 40.88 | 104.9834 | 33.4707 | 483.4715 | 0.37347 |  | 1486 | 27.49 | 104.9834 | 3 | 483.4715
1487 | 41.9 | 74.4581 | 31.5959 | 416.183 | 0.36569 |  | 1487 | 26.2 | 74.4581 | 2.2679 | 416.183
1488 | 42.84 | 38.7955 | 35.662 | 307.8258 | 0.35865 |  | 1488 | 22.44 | 38.7955 | 2 | 307.8258
1489 | 40.25 | 35.9383 | 36.4641 | 444.2721 | 0.34749 |  | 1489 | 20.75 | 35.9383 | 2.2679 | 444.2721
1490 | 40.31 | 34.06 | 23.5752 | 410.6728 | 0.33914 |  | 1490 | 19.73 | 34.06 | 3 | 410.6728
1491 | 39.8 | 32.3459 | 30.2902 | 354.2457 | 0.35088 |  | 1491 | 18.64 | 32.3459 | 4 | 354.2457
1492 | 39.97 | 30.6107 | 35.8145 | 397.3904 | 0.34849 |  | 1492 | 17.93 | 30.6107 | 5 | 397.3904
1493 | 36.2 | 29.3213 | 37.0185 | 463.4351 | 0.34436 |  | 1493 | 18.26 | 29.3213 | 5.7321 | 463.4351
1494 | 39.76 | 28.4907 | 30.2612 | 459.6983 | 0.35338 |  | 1494 | 19.38 | 28.4907 | 6 | 459.6983
1495 | 40.1 | 28.0747 | 29.1414 | 432.8424 | 0.38181 |  | 1495 | 24.58 | 28.0747 | 5.7321 | 432.8424
1496 | 41.57 | 31.0969 | 47.6429 | 484.6643 | 0.39233 |  | 1496 | 30.96 | 31.0969 | 5 | 484.6643
1497 | 45.48 | 49.254 | 46.3601 | 480.8758 | 0.40125 |  | 1497 | 31.04 | 49.254 | 4 | 480.8758
1498 | 54.43 | 68.3392 | 39.3985 | 411.6702 | 0.41432 |  | 1498 | 31.25 | 68.3392 | 3 | 411.6702
1499 | 58.5 | 74.5663 | 43.5696 | 404.9688 | 0.41242 |  | 1499 | 31.16 | 74.5663 | 2.2679 | 404.9688
1500 | 44.53 | 74.7741 | 43.6353 | 357.2636 | 0.4045 |  | 1500 | 31.94 | 74.7741 | 2 | 357.2636
1501 | 41.58 | 80.5629 | 45.2178 | 336.551 | 0.39869 |  | 1501 | 30.28 | 80.5629 | 2.2679 | 336.551
1502 | 42.59 | 77.7859 | 54.3604 | 317.8042 | 0.39686 |  | 1502 | 30.53 | 77.7859 | 3 | 317.8042
1503 | 44.25 | 68.9536 | 37.8748 | 286.4632 | 0.38433 |  | 1503 | 30.06 | 68.9536 | 4 | 286.4632
1504 | 44.9 | 73.3937 | 43.0465 | 242.0875 | 0.39017 |  | 1504 | 30.97 | 73.3937 | 5 | 242.0875
1505 | 47.64 | 79.7575 | 44.581 | 282.9628 | 0.39711 |  | 1505 | 30.96 | 79.7575 | 5.7321 | 282.9628
1506 | 44.65 | 119.156 | 51.2811 | 294.4888 | 0.39962 |  | 1506 | 32.85 | 119.156 | 6 | 294.4888
1507 | 44.52 | 150.6553 | 44.8298 | 375.3135 | 0.39421 |  | 1507 | 42.71 | 150.6553 | 5.7321 | 375.3135
1508 | 44.44 | 148.896 | 25.469 | 416.2448 | 0.39405 |  | 1508 | 42.92 | 148.896 | 5 | 416.2448
1509 | 44.1 | 119.8942 | 34.1754 | 393.3646 | 0.39529 |  | 1509 | 34.86 | 119.8942 | 4 | 393.3646
1510 | 44.25 | 106.7197 | 37.3744 | 365.7079 | 0.38485 |  | 1510 | 29.95 | 106.7197 | 3 | 365.7079
1511 | 40.86 | 89.7382 | 29.762 | 410.8161 | 0.37392 |  | 1511 | 27 | 89.7382 | 2.2679 | 410.8161
1512 | 40.29 | 42.978 | 32.5639 | 291.3512 | 0.3673 |  | 1512 | 24 | 42.978 | 2 | 291.3512
1513 | 36.5 | 32.6553 | 22.2649 | 316.7761 | 0.36363 |  | 1513 | 22.95 | 32.6553 | 2.2679 | 316.7761
1514 | 35.7 | 31.3059 | 235.1355 | 292.5972 | 0.36103 |  | 1514 | 20.78 | 31.3059 | 3 | 292.5972
1515 | 37.1 | 29.9451 | 35.6054 | 276.4993 | 0.36315 |  | 1515 | 20.03 | 29.9451 | 4 | 276.4993
1516 | 35.7 | 28.6962 | 27.0673 | 328.9456 | 0.36337 |  | 1516 | 19.19 | 28.6962 | 5 | 328.9456
1517 | 37 | 28.0826 | 34.4067 | 345.1018 | 0.36772 |  | 1517 | 18.99 | 28.0826 | 5.7321 | 345.1018
1518 | 40 | 27.6995 | 27.0999 | 452.5031 | 0.38289 |  | 1518 | 20.18 | 27.6995 | 6 | 452.5031
1519 | 40.97 | 27.5 | 30.0618 | 506.1204 | 0.39668 |  | 1519 | 26.92 | 27.5 | 5.7321 | 506.1204
1520 | 45.71 | 30.1578 | 56.9653 | 511.4214 | 0.41633 |  | 1520 | 31.73 | 30.1578 | 5 | 511.4214
1521 | 61.5 | 48.3258 | 47.9629 | 388.38 | 0.42535 |  | 1521 | 33.97 | 48.3258 | 4 | 388.38
1522 | 63.41 | 69.4886 | 44.9127 | 300.0333 | 0.42712 |  | 1522 | 31.06 | 69.4886 | 3 | 300.0333
1523 | 49.9 | 75.1565 | 33.9334 | 275.0848 | 0.42201 |  | 1523 | 28.82 | 75.1565 | 2.2679 | 275.0848
1524 | 45.86 | 79.2716 | 52.1703 | 319.3373 | 0.42087 |  | 1524 | 27.44 | 79.2716 | 2 | 319.3373
1525 | 42.59 | 84.5754 | 32.3641 | 271.2661 | 0.41627 |  | 1525 | 25.37 | 84.5754 | 2.2679 | 271.2661
1526 | 42.39 | 80.8707 | 53.3295 | 277.4379 | 0.4126 |  | 1526 | 24.55 | 80.8707 | 3 | 277.4379
1527 | 42.37 | 80.0597 | 46.4153 | 264.0426 | 0.41543 |  | 1527 | 25.64 | 80.0597 | 4 | 264.0426
1528 | 44.09 | 78.7419 | 45.0649 | 237.546 | 0.42306 |  | 1528 | 27.44 | 78.7419 | 5 | 237.546
1529 | 46.39 | 79.9723 | 47.6501 | 329.9683 | 0.42996 |  | 1529 | 29.94 | 79.9723 | 5.7321 | 329.9683
1530 | 49.27 | 109.8956 | 37.4655 | 379.7803 | 0.44326 |  | 1530 | 32.44 | 109.8956 | 6 | 379.7803
1531 | 56.45 | 147.9054 | 45.3056 | 409.2008 | 0.44405 |  | 1531 | 33.99 | 147.9054 | 5.7321 | 409.2008
1532 | 55.23 | 152.2495 | 32.4877 | 325.8074 | 0.44336 |  | 1532 | 33.7 | 152.2495 | 5 | 325.8074
1533 | 51.1 | 117.4009 | 27.2338 | 370.0533 | 0.44449 |  | 1533 | 31.22 | 117.4009 | 4 | 370.0533
1534 | 48.09 | 100.8021 | 31.8474 | 326.6938 | 0.44064 |  | 1534 | 26.73 | 100.8021 | 3 | 326.6938
1535 | 46.09 | 86.6727 | 26.6374 | 419.8978 | 0.43673 |  | 1535 | 24.83 | 86.6727 | 2.2679 | 419.8978
1536 | 41.54 | 39.2559 | 39.1157 | 361.0793 | 0.42072 |  | 1536 | 23.29 | 39.2559 | 2 | 361.0793
1537 | 36.08 | 35.7153 | 36.2639 | 396.6854 | 0.40908 |  | 1537 | 42.19 | 35.7153 | 2.2679 | 396.6854
1538 | 36 | 33.635 | 30.9167 | 401.1205 | 0.40037 |  | 1538 | 29 | 33.635 | 3 | 401.1205
1539 | 34.98 | 31.7237 | 26.7791 | 320.8447 | 0.38763 |  | 1539 | 20.29 | 31.7237 | 4 | 320.8447
1540 | 36 | 30.1441 | 31.4124 | 327.7057 | 0.38959 |  | 1540 | 18.96 | 30.1441 | 5 | 327.7057
1541 | 34 | 29.0836 | 23.3627 | 438.9525 | 0.38112 |  | 1541 | 18.88 | 29.0836 | 5.7321 | 438.9525
1542 | 35 | 28.6541 | 229.5452 | 566.4963 | 0.38913 |  | 1542 | 19.01 | 28.6541 | 6 | 566.4963
1543 | 43.2 | 45.1161 | 228.413 | 532.6539 | 0.41348 |  | 1543 | 19.16 | 45.1161 | 5.7321 | 532.6539
1544 | 49.64 | 59.9082 | 56.0616 | 549.6696 | 0.42204 |  | 1544 | 20.75 | 59.9082 | 5 | 549.6696
1545 | 49.37 | 44.5502 | 63.4485 | 495.9705 | 0.42063 |  | 1545 | 24.55 | 44.5502 | 4 | 495.9705
1546 | 54.26 | 43.2445 | 78.7215 | 350.4741 | 0.41795 |  | 1546 | 27.44 | 43.2445 | 3 | 350.4741
1547 | 57.98 | 45.352 | 56.0951 | 321.2425 | 0.4218 |  | 1547 | 37.21 | 45.352 | 2.2679 | 321.2425
1548 | 57.25 | 46.7055 | 51.0268 | 260.8971 | 0.42119 |  | 1548 | 26.8 | 46.7055 | 2 | 260.8971
1549 | 47.85 | 50.6256 | 44.2024 | 258.0139 | 0.42324 |  | 1549 | 24.96 | 50.6256 | 2.2679 | 258.0139
1550 | 47.59 | 51.9644 | 49.1345 | 184.2107 | 0.42962 |  | 1550 | 25.12 | 51.9644 | 3 | 184.2107
1551 | 47.14 | 60.0766 | 35.1411 | 205.364 | 0.4315 |  | 1551 | 21.89 | 60.0766 | 4 | 205.364
1552 | 46.53 | 77.5656 | 47.685 | 189.4373 | 0.43475 |  | 1552 | 20.57 | 77.5656 | 5 | 189.4373
1553 | 46.85 | 97.9268 | 38.8063 | 298.3777 | 0.43017 |  | 1553 | 21.25 | 97.9268 | 5.7321 | 298.3777
1554 | 47.24 | 142.283 | 27.5434 | 345.4934 | 0.42768 |  | 1554 | 25.92 | 142.283 | 6 | 345.4934
1555 | 47.4 | 149.9462 | 50.9555 | 405.6123 | 0.41818 |  | 1555 | 34.02 | 149.9462 | 5.7321 | 405.6123
1556 | 52.35 | 150.9261 | 27.4479 | 505.5304 | 0.416 |  | 1556 | 35 | 150.9261 | 5 | 505.5304
1557 | 50 | 121.8622 | 29.5776 | 378.9451 | 0.41518 |  | 1557 | 27.86 | 121.8622 | 4 | 378.9451
1558 | 42.6 | 108.2257 | 30.2139 | 374.8252 | 0.40943 |  | 1558 | 24.44 | 108.2257 | 3 | 374.8252
1559 | 41.1 | 78.1743 | 29.9906 | 465.6561 | 0.40111 |  | 1559 | 25.18 | 78.1743 | 2.2679 | 465.6561
1560 | 40.61 | 41.4643 | 27.7837 | 370.9799 | 0.39811 |  | 1560 | 25.12 | 41.4643 | 2 | 370.9799
1561 | 37 | 32.8334 | 37.0385 | 375.6173 | 0.40253 |  | 1561 | 20.69 | 32.8334 | 2.2679 | 375.6173
1562 | 39.53 | 31.5182 | 31.7854 | 354.0524 | 0.39791 |  | 1562 | 19.94 | 31.5182 | 3 | 354.0524
1563 | 37.26 | 30.1387 | 32.7945 | 397.7923 | 0.38832 |  | 1563 | 19.13 | 30.1387 | 4 | 397.7923
1564 | 37.4 | 28.88 | 28.146 | 459.6037 | 0.3953 |  | 1564 | 18.69 | 28.88 | 5 | 459.6037
1565 | 35.7 | 28.1655 | 28.7611 | 520.9749 | 0.40214 |  | 1565 | 18.58 | 28.1655 | 5.7321 | 520.9749
1566 | 35.09 | 28.0902 | 29.2497 | 460.6367 | 0.40436 |  | 1566 | 18.83 | 28.0902 | 6 | 460.6367
1567 | 39.06 | 43.5853 | 22.5559 | 559.4088 | 0.41675 |  | 1567 | 18.65 | 43.5853 | 5.7321 | 559.4088
1568 | 48.32 | 59.9489 | 48.2746 | 480.2609 | 0.41678 |  | 1568 | 18.78 | 59.9489 | 5 | 480.2609
1569 | 51 | 44.2051 | 45.3621 | 441.6535 | 0.41427 |  | 1569 | 19.28 | 44.2051 | 4 | 441.6535
1570 | 49.19 | 43.2447 | 247.1829 | 369.5915 | 0.41046 |  | 1570 | 19.99 | 43.2447 | 3 | 369.5915
1571 | 49.02 | 47.1272 | 39.6731 | 287.5968 | 0.4062 |  | 1571 | 20.26 | 47.1272 | 2.2679 | 287.5968
1572 | 45.2 | 46.9096 | 49.1693 | 209.5683 | 0.40256 |  | 1572 | 20.51 | 46.9096 | 2 | 209.5683
1573 | 39.9 | 51.1144 | 42.246 | 166.2958 | 0.39608 |  | 1573 | 20.06 | 51.1144 | 2.2679 | 166.2958
1574 | 42 | 52.8456 | 51.8545 | 154.2842 | 0.3892 |  | 1574 | 19.14 | 52.8456 | 3 | 154.2842
1575 | 38.03 | 57.9925 | 40.4271 | 159.3205 | 0.38249 |  | 1575 | 18.24 | 57.9925 | 4 | 159.3205
1576 | 39 | 74.677 | 46.4218 | 133.7987 | 0.39095 |  | 1576 | 18.23 | 74.677 | 5 | 133.7987
1577 | 41.57 | 97.0024 | 36.7641 | 199.075 | 0.39979 |  | 1577 | 18.73 | 97.0024 | 5.7321 | 199.075
1578 | 43.27 | 138.2063 | 35.9406 | 260.4624 | 0.40374 |  | 1578 | 20.57 | 138.2063 | 6 | 260.4624
1579 | 43.95 | 149.4799 | 49.8903 | 300.0386 | 0.40149 |  | 1579 | 28.93 | 149.4799 | 5.7321 | 300.0386
1580 | 46.49 | 143.6789 | 26.8571 | 375.4451 | 0.4035 |  | 1580 | 31.62 | 143.6789 | 5 | 375.4451
1581 | 42.3 | 116.9254 | 24.5774 | 344.5934 | 0.4 |  | 1581 | 29.17 | 116.9254 | 4 | 344.5934
1582 | 40 | 108.4411 | 33.095 | 418.9293 | 0.39825 |  | 1582 | 26.1 | 108.4411 | 3 | 418.9293
1583 | 41.23 | 76.8614 | 24.9176 | 423.0415 | 0.39109 |  | 1583 | 27.44 | 76.8614 | 2.2679 | 423.0415
1584 | 39.1 | 38.729 | 33.6072 | 412.0275 | 0.38575 |  | 1584 | 27.09 | 38.729 | 2 | 412.0275
1585 | 34 | 35.734 | 33.1101 | 354.124 | 0.37797 |  | 1585 | 25.45 | 35.734 | 2.2679 | 354.124
1586 | 40 | 33.8901 | 35.8479 | 365.6135 | 0.37974 |  | 1586 | 23.3 | 33.8901 | 3 | 365.6135
1587 | 35 | 32.0819 | 36.0878 | 454.2829 | 0.38976 |  | 1587 | 22.23 | 32.0819 | 4 | 454.2829
1588 | 38.7 | 30.5114 | 30.9532 | 524.8646 | 0.39349 |  | 1588 | 20.02 | 30.5114 | 5 | 524.8646
1589 | 40 | 29.352 | 34.6234 | 423.5007 | 0.39612 |  | 1589 | 20.44 | 29.352 | 5.7321 | 423.5007
1590 | 34.3 | 28.9364 | 29.7346 | 553.3302 | 0.40254 |  | 1590 | 21.87 | 28.9364 | 6 | 553.3302
1591 | 46.79 | 44.9135 | 24.7515 | 622.5707 | 0.41615 |  | 1591 | 32.7 | 44.9135 | 5.7321 | 622.5707
1592 | 45.08 | 60.447 | 40.5854 | 507.014 | 0.43198 |  | 1592 | 36.52 | 60.447 | 5 | 507.014
1593 | 69.23 | 42.1951 | 41.1165 | 434.117 | 0.43967 |  | 1593 | 39.43 | 42.1951 | 4 | 434.117
1594 | 59.2 | 41.4501 | 51.0804 | 319.4403 | 0.44078 |  | 1594 | 35.18 | 41.4501 | 3 | 319.4403
1595 | 48 | 44.8876 | 49.9506 | 285.9766 | 0.44831 |  | 1595 | 31.98 | 44.8876 | 2.2679 | 285.9766
1596 | 42.31 | 44.9465 | 51.363 | 172.6165 | 0.44704 |  | 1596 | 29.96 | 44.9465 | 2 | 172.6165
1597 | 41.49 | 47.5839 | 30.4656 | 120.2249 | 0.45683 |  | 1597 | 27.98 | 47.5839 | 2.2679 | 120.2249
1598 | 39.9 | 50.4439 | 40.9262 | 117.1757 | 0.46231 |  | 1598 | 27.44 | 50.4439 | 3 | 117.1757
1599 | 39.72 | 57.9928 | 41.0126 | 68.6799 | 0.44962 |  | 1599 | 27.72 | 57.9928 | 4 | 68.6799
1600 | 39.9 | 70.724 | 47.2654 | 117.4025 | 0.44988 |  | 1600 | 27.1 | 70.724 | 5 | 117.4025
1601 | 39.1 | 95.1193 | 35.2574 | 132.4553 | 0.44631 |  | 1601 | 30.07 | 95.1193 | 5.7321 | 132.4553
1602 | 43.07 | 128.3054 | 245.605 | 228.7167 | 0.4417 |  | 1602 | 34.11 | 128.3054 | 6 | 228.7167
1603 | 48.49 | 156.6072 | 39.9277 | 299.1008 | 0.43648 |  | 1603 | 48.29 | 156.6072 | 5.7321 | 299.1008
1604 | 50.44 | 150.768 | 26.4766 | 401.2191 | 0.43223 |  | 1604 | 46.65 | 150.768 | 5 | 401.2191
1605 | 44.04 | 116.0372 | 35.5327 | 328.7835 | 0.42061 |  | 1605 | 30.03 | 116.0372 | 4 | 328.7835
1606 | 40.57 | 107.3865 | 31.4867 | 457.2457 | 0.41221 |  | 1606 | 27.95 | 107.3865 | 3 | 457.2457
1607 | 39.24 | 79.2085 | 32.1143 | 457.8334 | 0.40324 |  | 1607 | 26.96 | 79.2085 | 2.2679 | 457.8334
1608 | 36.3 | 41.6214 | 21.2597 | 350.4452 | 0.39926 |  | 1608 | 24.5 | 41.6214 | 2 | 350.4452
1609 | 35 | 36.3417 | 28.4663 | 367.6508 | 0.39203 |  | 1609 | 22.39 | 36.3417 | 2.2679 | 367.6508
1610 | 34 | 34.3022 | 34.9075 | 388.9416 | 0.38263 |  | 1610 | 22.91 | 34.3022 | 3 | 388.9416
1611 | 35 | 32.41 | 228.4701 | 354.0406 | 0.3758 |  | 1611 | 22.81 | 32.41 | 4 | 354.0406
1612 | 32.4 | 30.6244 | 40.7128 | 520.0725 | 0.3704 |  | 1612 | 22 | 30.6244 | 5 | 520.0725
1613 | 22.64 | 29.4832 | 30.0395 | 563.9065 | 0.36806 |  | 1613 | 21.67 | 29.4832 | 5.7321 | 563.9065
1614 | 24.8 | 29.0066 | 30.7758 | 601.424 | 0.37351 |  | 1614 | 22.7 | 29.0066 | 6 | 601.424
1615 | 37 | 43.9195 | 36.511 | 628.2548 | 0.37698 |  | 1615 | 27.44 | 43.9195 | 5.7321 | 628.2548
1616 | 31.7 | 58.6492 | 46.9455 | 605.8726 | 0.38016 |  | 1616 | 37.73 | 58.6492 | 5 | 605.8726
1617 | 36.52 | 45.0377 | 51.2527 | 430.7795 | 0.3938 |  | 1617 | 39.08 | 45.0377 | 4 | 430.7795
1618 | 51.36 | 44.9274 | 50.2248 | 303.436 | 0.41825 |  | 1618 | 34.98 | 44.9274 | 3 | 303.436
1619 | 49.76 | 47.0761 | 31.1369 | 225.1038 | 0.41247 |  | 1619 | 29.96 | 47.0761 | 2.2679 | 225.1038
1620 | 42.2 | 49.8366 | 40.5859 | 190.3155 | 0.40634 |  | 1620 | 26.79 | 49.8366 | 2 | 190.3155
1621 | 39.5 | 56.6074 | 39.7755 | 70.4383 | 0.39663 |  | 1621 | 25.83 | 56.6074 | 2.2679 | 70.4383
1622 | 40.5 | 56.2376 | 39.2139 | 62.6625 | 0.40065 |  | 1622 | 26.09 | 56.2376 | 3 | 62.6625
1623 | 37 | 62.3998 | 48.9566 | 53.6808 | 0.40276 |  | 1623 | 25.78 | 62.3998 | 4 | 53.6808
1624 | 35.1 | 78.8694 | 33.8662 | 62.0128 | 0.39183 |  | 1624 | 26.05 | 78.8694 | 5 | 62.0128
1625 | 41.95 | 98.6411 | 28.7317 | 71.5962 | 0.39937 |  | 1625 | 27.92 | 98.6411 | 5.7321 | 71.5962
1626 | 42.33 | 144.4417 | 39.1039 | 82.954 | 0.40707 |  | 1626 | 33.1 | 144.4417 | 6 | 82.954
1627 | 39.4 | 163.8623 | 41.9399 | 104.8711 | 0.41269 |  | 1627 | 44.93 | 163.8623 | 5.7321 | 104.8711
1628 | 49.9 | 145.4608 | 27.7553 | 221.9249 | 0.42564 |  | 1628 | 37.44 | 145.4608 | 5 | 221.9249
1629 | 45 | 117.7738 | 35.3577 | 335.906 | 0.42798 |  | 1629 | 29.33 | 117.7738 | 4 | 335.906
1630 | 48 | 115.7974 | 29.7552 | 299.1553 | 0.42292 |  | 1630 | 25.07 | 115.7974 | 3 | 299.1553
1631 | 55 | 81.3992 | 26.9766 | 384.2384 | 0.41215 |  | 1631 | 27.8 | 81.3992 | 2.2679 | 384.2384
1632 | 60.9 | 42.6489 | 36.4314 | 306.6518 | 0.41269 |  | 1632 | 22.61 | 42.6489 | 2 | 306.6518
1633 | 63.05 | 36.0456 | 27.2436 | 437.8998 | 0.42695 |  | 1633 | 23.8 | 36.0456 | 2.2679 | 437.8998
1634 | 60.9 | 34.2179 | 32.0459 | 457.3263 | 0.45212 |  | 1634 | 22.03 | 34.2179 | 3 | 457.3263
1635 | 60.9 | 32.3398 | 27.9961 | 433.8927 | 0.46488 |  | 1635 | 20.94 | 32.3398 | 4 | 433.8927
1636 | 62.15 | 30.5643 | 40.4501 | 516.4995 | 0.47346 |  | 1636 | 20.08 | 30.5643 | 5 | 516.4995
1637 | 54.4 | 29.2485 | 35.8916 | 416.6298 | 0.48429 |  | 1637 | 20.01 | 29.2485 | 5.7321 | 416.6298
1638 | 44.94 | 29.0498 | 29.9987 | 522.5036 | 0.50096 |  | 1638 | 21.14 | 29.0498 | 6 | 522.5036
1639 | 41.88 | 42.867 | 30.6296 | 623.743 | 0.50665 |  | 1639 | 24.95 | 42.867 | 5.7321 | 623.743
1640 | 28.05 | 57.5952 | 41.4976 | 550.0883 | 0.51427 |  | 1640 | 31.92 | 57.5952 | 5 | 550.0883
1641 | 41.8 | 44.1714 | 49.8529 | 484.4069 | 0.51693 |  | 1641 | 30.53 | 44.1714 | 4 | 484.4069
1642 | 42.3 | 43.0291 | 45.0688 | 360.1749 | 0.51378 |  | 1642 | 26.09 | 43.0291 | 3 | 360.1749
1643 | 42.18 | 46.7651 | 49.7324 | 235.6137 | 0.50046 |  | 1643 | 23.83 | 46.7651 | 2.2679 | 235.6137
1644 | 42.26 | 47.1374 | 49.6807 | 154.2512 | 0.49529 |  | 1644 | 25 | 47.1374 | 2 | 154.2512
1645 | 47.7 | 51.2401 | 37.1697 | 119.895 | 0.49151 |  | 1645 | 24.15 | 51.2401 | 2.2679 | 119.895
1646 | 35 | 52.3892 | 33.8197 | 61.9075 | 0.48357 |  | 1646 | 24.94 | 52.3892 | 3 | 61.9075
1647 | 33.95 | 58.971 | 44.2521 | 49.2925 | 0.44529 |  | 1647 | 23.31 | 58.971 | 4 | 49.2925
1648 | 33.51 | 73.0174 | 49.9008 | 56.2962 | 0.41752 |  | 1648 | 23.18 | 73.0174 | 5 | 56.2962
1649 | 33.95 | 90.4021 | 50.9619 | 111.4858 | 0.39825 |  | 1649 | 24.83 | 90.4021 | 5.7321 | 111.4858
1650 | 37.36 | 140.6371 | 41.3734 | 192.6382 | 0.41673 |  | 1650 | 33 | 140.6371 | 6 | 192.6382
1651 | 41.4 | 153.1636 | 32.7823 | 341.6494 | 0.43857 |  | 1651 | 38.77 | 153.1636 | 5.7321 | 341.6494
1652 | 40.92 | 140.246 | 34.174 | 375.0547 | 0.43774 |  | 1652 | 37.99 | 140.246 | 5 | 375.0547
1653 | 36 | 116.5964 | 236.8405 | 351.3916 | 0.40718 |  | 1653 | 29.81 | 116.5964 | 4 | 351.3916
1654 | 37.4 | 107.012 | 29.2427 | 364.1395 | 0.39477 |  | 1654 | 25.8 | 107.012 | 3 | 364.1395
1655 | 39.62 | 79.1599 | 21.9321 | 371.0667 | 0.39472 |  | 1655 | 27.51 | 79.1599 | 2.2679 | 371.0667
1656 | 33.96 | 42.1321 | 39.499 | 346.2467 | 0.38666 |  | 1656 | 25.91 | 42.1321 | 2 | 346.2467
1657 | 34.3 | 35.4572 | 34.751 | 401.6176 | 0.3932 |  | 1657 | 21.91 | 35.4572 | 2.2679 | 401.6176
1658 | 39.9 | 33.6449 | 32.4425 | 437.9431 | 0.39228 |  | 1658 | 21.54 | 33.6449 | 3 | 437.9431
1659 | 41.38 | 31.7586 | 28.4048 | 480.9748 | 0.38911 |  | 1659 | 21.48 | 31.7586 | 4 | 480.9748
1660 | 35.4 | 30.2025 | 26.5259 | 439.779 | 0.37892 |  | 1660 | 21.03 | 30.2025 | 5 | 439.779
1661 | 33.96 | 29.1626 | 35.7827 | 552.4429 | 0.37855 |  | 1661 | 21.59 | 29.1626 | 5.7321 | 552.4429
1662 | 34.9 | 28.4183 | 41.9766 | 604.3764 | 0.39148 |  | 1662 | 22.3 | 28.4183 | 6 | 604.3764
1663 | 40.53 | 28.0251 | 27.6151 | 521.6259 | 0.40463 |  | 1663 | 28.48 | 28.0251 | 5.7321 | 521.6259
1664 | 47.96 | 30.2743 | 36.6502 | 589.3973 | 0.42697 |  | 1664 | 35.44 | 30.2743 | 5 | 589.3973
1665 | 48.06 | 48.2785 | 35.3225 | 445.0685 | 0.43398 |  | 1665 | 36.62 | 48.2785 | 4 | 445.0685
1666 | 46.84 | 68.2832 | 47.4126 | 375.6489 | 0.43187 |  | 1666 | 34.78 | 68.2832 | 3 | 375.6489
1667 | 45.31 | 73.9978 | 25.4146 | 367.7557 | 0.42956 |  | 1667 | 30.31 | 73.9978 | 2.2679 | 367.7557
1668 | 42.66 | 73.9974 | 35.024 | 325.4499 | 0.42017 |  | 1668 | 28.27 | 73.9974 | 2 | 325.4499
1669 | 39.95 | 77.7475 | 42.9188 | 197.438 | 0.41493 |  | 1669 | 26.35 | 77.7475 | 2.2679 | 197.438
1670 | 38.69 | 77.5395 | 41.1662 | 72.8139 | 0.41103 |  | 1670 | 25 | 77.5395 | 3 | 72.8139
1671 | 36.9 | 71.8762 | 36.5219 | 60.8546 | 0.41436 |  | 1671 | 25 | 71.8762 | 4 | 60.8546
1672 | 37.11 | 76.3271 | 44.3664 | 96.1184 | 0.41752 |  | 1672 | 24.89 | 76.3271 | 5 | 96.1184
1673 | 40.1 | 82.0597 | 53.8893 | 166.0071 | 0.42352 |  | 1673 | 25.03 | 82.0597 | 5.7321 | 166.0071
1674 | 46.28 | 121.4002 | 39.1573 | 242.593 | 0.43241 |  | 1674 | 29.95 | 121.4002 | 6 | 242.593
1675 | 50.29 | 150.541 | 54.2402 | 379.1617 | 0.44057 |  | 1675 | 35.49 | 150.541 | 5.7321 | 379.1617
1676 | 57.9 | 144.611 | 33.0628 | 397.7739 | 0.45785 |  | 1676 | 39.8 | 144.611 | 5 | 397.7739
1677 | 50.06 | 116.359 | 27.0138 | 450.4279 | 0.47134 |  | 1677 | 31.09 | 116.359 | 4 | 450.4279
1678 | 47.91 | 105.5716 | 38.4173 | 357.4058 | 0.48666 |  | 1678 | 27 | 105.5716 | 3 | 357.4058
1679 | 47.61 | 90.386 | 230.9903 | 339.1182 | 0.49595 |  | 1679 | 24.52 | 90.386 | 2.2679 | 339.1182
1680 | 44.01 | 42.2886 | 34.4672 | 360.6339 | 0.50027 |  | 1680 | 22.96 | 42.2886 | 2 | 360.6339
1681 | 40.98 | 34.8881 | 37.8145 | 365.6345 | 0.49499 |  | 1681 | 23.61 | 34.8881 | 2.2679 | 365.6345
1682 | 38.97 | 33.0885 | 29.8473 | 337.0699 | 0.47546 |  | 1682 | 22.46 | 33.0885 | 3 | 337.0699
1683 | 36.91 | 31.4008 | 28.2225 | 280.385 | 0.44029 |  | 1683 | 21.96 | 31.4008 | 4 | 280.385
1684 | 35 | 29.8961 | 30.3241 | 420.1362 | 0.40159 |  | 1684 | 21.44 | 29.8961 | 5 | 420.1362
1685 | 32.92 | 28.8119 | 36.6134 | 434.201 | 0.39573 |  | 1685 | 21.75 | 28.8119 | 5.7321 | 434.201
1686 | 36.3 | 28.1561 | 23.2582 | 479.1016 | 0.41182 |  | 1686 | 23.13 | 28.1561 | 6 | 479.1016
1687 | 46.83 | 27.8463 | 31.2376 | 435.6774 | 0.42406 |  | 1687 | 28.73 | 27.8463 | 5.7321 | 435.6774
1688 | 52.05 | 29.7639 | 48.2551 | 517.6478 | 0.42766 |  | 1688 | 34.91 | 29.7639 | 5 | 517.6478
1689 | 51.37 | 48.2687 | 42.4688 | 415.8794 | 0.42602 |  | 1689 | 38.34 | 48.2687 | 4 | 415.8794
1690 | 48.02 | 65.9976 | 50.5803 | 300.0538 | 0.41911 |  | 1690 | 36.69 | 65.9976 | 3 | 300.0538
1691 | 45.52 | 73.9337 | 42.4784 | 197.547 | 0.41846 |  | 1691 | 32.91 | 73.9337 | 2.2679 | 197.547
1692 | 44.34 | 75.1483 | 40.4167 | 127.2322 | 0.41936 |  | 1692 | 32.02 | 75.1483 | 2 | 127.2322
1693 | 43.82 | 83.1732 | 52.1221 | 69.3474 | 0.41975 |  | 1693 | 30.29 | 83.1732 | 2.2679 | 69.3474
1694 | 43.83 | 77.3832 | 49.6931 | 70.0749 | 0.41979 |  | 1694 | 27.03 | 77.3832 | 3 | 70.0749
1695 | 43.52 | 76.4483 | 41.3322 | 67.9275 | 0.41894 |  | 1695 | 25.01 | 76.4483 | 4 | 67.9275
1696 | 43.19 | 73.5971 | 47.027 | 59.2166 | 0.418 |  | 1696 | 24.92 | 73.5971 | 5 | 59.2166
1697 | 42.37 | 77.6653 | 32.322 | 78.2704 | 0.41572 |  | 1697 | 24.88 | 77.6653 | 5.7321 | 78.2704
1698 | 42 | 115.504 | 57.9718 | 105.757 | 0.41493 |  | 1698 | 27.9 | 115.504 | 6 | 105.757
1699 | 44.02 | 135.0131 | 44.5247 | 110.1393 | 0.41066 |  | 1699 | 32.55 | 135.0131 | 5.7321 | 110.1393
1700 | 50 | 158.3056 | 28.7272 | 104.0035 | 0.41389 |  | 1700 | 35.69 | 158.3056 | 5 | 104.0035
1701 | 47.73 | 117.4923 | 34.0732 | 125.9987 | 0.41313 |  | 1701 | 30.69 | 117.4923 | 4 | 125.9987
1702 | 39.9 | 103.0522 | 35.8907 | 183.0217 | 0.41153 |  | 1702 | 26.8 | 103.0522 | 3 | 183.0217
1703 | 39.6 | 89.7032 | 45.1241 | 254.3041 | 0.4121 |  | 1703 | 29.1 | 89.7032 | 2.2679 | 254.3041
1704 | 37.4 | 41.4157 | 31.2926 | 222.402 | 0.39077 |  | 1704 | 26.06 | 41.4157 | 2 | 222.402
1705 | 34.6 | 31.9639 | 27.6197 | 294.63 | 0.38488 |  | 1705 | 29.01 | 31.9639 | 2.2679 | 294.63
1706 | 36.4 | 30.8906 | 26.0867 | 280.2457 | 0.37565 |  | 1706 | 26.1 | 30.8906 | 3 | 280.2457
1707 | 35.6 | 29.7223 | 27.1478 | 262.9127 | 0.36685 |  | 1707 | 25.69 | 29.7223 | 4 | 262.9127
1708 | 37.4 | 28.6302 | 30.1167 | 269.1473 | 0.36717 |  | 1708 | 24.5 | 28.6302 | 5 | 269.1473
1709 | 34.8 | 27.8558 | 31.1995 | 391.5701 | 0.36457 |  | 1709 | 23.26 | 27.8558 | 5.7321 | 391.5701
1710 | 30 | 27.609 | 33.4659 | 347.3282 | 0.37313 |  | 1710 | 24.5 | 27.609 | 6 | 347.3282
1711 | 37.4 | 42.7391 | 30.7657 | 399.0504 | 0.39101 |  | 1711 | 25.45 | 42.7391 | 5.7321 | 399.0504
1712 | 44.16 | 55.7056 | 250.9535 | 445.3745 | 0.40969 |  | 1712 | 25.51 | 55.7056 | 5 | 445.3745
1713 | 55.33 | 42.8967 | 28.0395 | 382.6522 | 0.41457 |  | 1713 | 28.91 | 42.8967 | 4 | 382.6522
1714 | 50 | 41.1192 | 31.5817 | 332.1138 | 0.41596 |  | 1714 | 30.09 | 41.1192 | 3 | 332.1138
1715 | 45.27 | 46.2361 | 36.6513 | 215.5271 | 0.41598 |  | 1715 | 29.26 | 46.2361 | 2.2679 | 215.5271
1716 | 44.91 | 46.5783 | 35.3682 | 150.7132 | 0.41804 |  | 1716 | 28.44 | 46.5783 | 2 | 150.7132
1717 | 44.59 | 48.1396 | 50.0977 | 124.9533 | 0.41771 |  | 1717 | 27.6 | 48.1396 | 2.2679 | 124.9533
1718 | 44.38 | 47.9325 | 89.7848 | 114.5685 | 0.41343 |  | 1718 | 25.01 | 47.9325 | 3 | 114.5685
1719 | 41.53 | 51.9114 | 58.7852 | 162.5218 | 0.41305 |  | 1719 | 23.38 | 51.9114 | 4 | 162.5218
1720 | 41.53 | 67.9471 | 52.0456 | 183.2018 | 0.41187 |  | 1720 | 22.96 | 67.9471 | 5 | 183.2018
1721 | 41.75 | 86.1167 | 46.3781 | 258.6804 | 0.41363 |  | 1721 | 23.67 | 86.1167 | 5.7321 | 258.6804
1722 | 44.06 | 127.8267 | 53.9843 | 317.9575 | 0.41581 |  | 1722 | 27.07 | 127.8267 | 6 | 317.9575
1723 | 40.1 | 167.0039 | 40.5227 | 292.9479 | 0.41203 |  | 1723 | 34.09 | 167.0039 | 5.7321 | 292.9479
1724 | 48.36 | 143.1087 | 26.3758 | 368.3162 | 0.41409 |  | 1724 | 36.97 | 143.1087 | 5 | 368.3162
1725 | 41.39 | 119.1396 | 36.3956 | 380.2261 | 0.41804 |  | 1725 | 35 | 119.1396 | 4 | 380.2261
1726 | 41 | 100.73 | 36.4512 | 346.5897 | 0.41474 |  | 1726 | 30.17 | 100.73 | 3 | 346.5897
1727 | 40.56 | 72.6556 | 27.3874 | 299.5573 | 0.41014 |  | 1727 | 30.91 | 72.6556 | 2.2679 | 299.5573
1728 | 37.4 | 36.9647 | 32.8739 | 256.1421 | 0.40616 |  | 1728 | 30 | 36.9647 | 2 | 256.1421
1729 | 37.11 | 36.1033 | 23.7499 | 256.7007 | 0.40683 |  | 1729 | 26.51 | 36.1033 | 2.2679 | 256.7007
1730 | 36.1 | 34.1231 | 30.4381 | 270.371 | 0.39794 |  | 1730 | 22.84 | 34.1231 | 3 | 270.371
1731 | 38.3 | 32.2268 | 31.2 | 291.9546 | 0.39558 |  | 1731 | 21.67 | 32.2268 | 4 | 291.9546
1732 | 33 | 30.5705 | 31.4411 | 255.359 | 0.37986 |  | 1732 | 21.05 | 30.5705 | 5 | 255.359
1733 | 27.5 | 29.4207 | 32.5156 | 362.3258 | 0.36982 |  | 1733 | 21.12 | 29.4207 | 5.7321 | 362.3258
1734 | 27.59 | 28.9235 | 51.3089 | 404.5287 | 0.37509 |  | 1734 | 21.17 | 28.9235 | 6 | 404.5287
1735 | 37.69 | 43.5818 | 88.544 | 398.4913 | 0.39363 |  | 1735 | 21.11 | 43.5818 | 5.7321 | 398.4913
1736 | 46.01 | 57.0143 | 47.5974 | 369.7085 | 0.41201 |  | 1736 | 21.08 | 57.0143 | 5 | 369.7085
1737 | 46.52 | 43.9626 | 47.121 | 361.1918 | 0.41844 |  | 1737 | 21.31 | 43.9626 | 4 | 361.1918
1738 | 47.38 | 43.3808 | 35.514 | 299.4073 | 0.41993 |  | 1738 | 21.69 | 43.3808 | 3 | 299.4073
1739 | 45.71 | 44.8041 | 72.281 | 283.0794 | 0.42073 |  | 1739 | 21.73 | 44.8041 | 2.2679 | 283.0794
1740 | 45.06 | 48.636 | 125.6339 | 239.9258 | 0.41785 |  | 1740 | 21.69 | 48.636 | 2 | 239.9258
1741 | 44.87 | 53.1848 | 115.2543 | 198.5254 | 0.41459 |  | 1741 | 21.07 | 53.1848 | 2.2679 | 198.5254
1742 | 41.68 | 51.9079 | 311.1724 | 155.4183 | 0.4149 |  | 1742 | 19.4 | 51.9079 | 3 | 155.4183
1743 | 39 | 58.7871 | 59.7733 | 143.0869 | 0.41544 |  | 1743 | 19.7 | 58.7871 | 4 | 143.0869
1744 | 39.5 | 78.1984 | 41.536 | 229.6232 | 0.41028 |  | 1744 | 20.01 | 78.1984 | 5 | 229.6232
1745 | 41 | 92.2114 | 46.6149 | 267.9361 | 0.40987 |  | 1745 | 20.56 | 92.2114 | 5.7321 | 267.9361
1746 | 42.32 | 131.8788 | 243.2733 | 310.3195 | 0.4162 |  | 1746 | 20.19 | 131.8788 | 6 | 310.3195
1747 | 41.76 | 151.6655 | 47.0934 | 309.9234 | 0.41244 |  | 1747 | 26.08 | 151.6655 | 5.7321 | 309.9234
1748 | 49.09 | 151.9371 | 33.4122 | 368.4364 | 0.41904 |  | 1748 | 33.55 | 151.9371 | 5 | 368.4364
1749 | 46.75 | 119.0929 | 34.4947 | 322.5494 | 0.42434 |  | 1749 | 31.05 | 119.0929 | 4 | 322.5494
1750 | 38.4 | 109.7742 | 36.4885 | 309.1895 | 0.41692 |  | 1750 | 27.24 | 109.7742 | 3 | 309.1895
1751 | 40 | 80.8757 | 40.6367 | 317.4568 | 0.41829 |  | 1751 | 28.93 | 80.8757 | 2.2679 | 317.4568
1752 | 40 | 42.4866 | 30.2776 | 301.9815 | 0.41434 |  | 1752 | 26.63 | 42.4866 | 2 | 301.9815
1753 | 30.07 | 34.0271 | 28.8369 | 306.6169 | 0.41064 |  | 1753 | 22.44 | 34.0271 | 2.2679 | 306.6169
1754 | 39.11 | 32.4799 | 22.7174 | 329.6183 | 0.41308 |  | 1754 | 20.7 | 32.4799 | 3 | 329.6183
1755 | 37.8 | 30.9394 | 35.0865 | 346.3502 | 0.41099 |  | 1755 | 20.22 | 30.9394 | 4 | 346.3502
1756 | 35 | 29.563 | 21.3687 | 333.3871 | 0.41118 |  | 1756 | 19.99 | 29.563 | 5 | 333.3871
1757 | 36.1 | 28.6098 | 27.3437 | 418.9959 | 0.4092 |  | 1757 | 20.36 | 28.6098 | 5.7321 | 418.9959
1758 | 31.7 | 28.3056 | 31.607 | 352.4383 | 0.41154 |  | 1758 | 22 | 28.3056 | 6 | 352.4383
1759 | 36 | 42.3372 | 45.5664 | 376.1735 | 0.42235 |  | 1759 | 29.52 | 42.3372 | 5.7321 | 376.1735
1760 | 45 | 57.0911 | 118.9999 | 398.7553 | 0.44116 |  | 1760 | 35.43 | 57.0911 | 5 | 398.7553
1761 | 43.72 | 43.0041 | 94.4256 | 383.573 | 0.43866 |  | 1761 | 35.81 | 43.0041 | 4 | 383.573
1762 | 42.59 | 41.0661 | 62.6047 | 362.1879 | 0.43381 |  | 1762 | 31.75 | 41.0661 | 3 | 362.1879
1763 | 41.54 | 43.8049 | 101.7567 | 279.6231 | 0.4282 |  | 1763 | 28.82 | 43.8049 | 2.2679 | 279.6231
1764 | 40.97 | 44.8656 | 121.6368 | 305.0815 | 0.42826 |  | 1764 | 24.33 | 44.8656 | 2 | 305.0815
1765 | 39.91 | 46.0581 | 96.0117 | 234.7439 | 0.42398 |  | 1765 | 23.31 | 46.0581 | 2.2679 | 234.7439
1766 | 36.4 | 50.3074 | 44.2411 | 190.6368 | 0.42022 |  | 1766 | 22.84 | 50.3074 | 3 | 190.6368
1767 | 41.75 | 56.8577 | 29.8314 | 133.4774 | 0.42672 |  | 1767 | 22.55 | 56.8577 | 4 | 133.4774
1768 | 41.64 | 71.2509 | 50.2543 | 154.9667 | 0.43315 |  | 1768 | 23.04 | 71.2509 | 5 | 154.9667
1769 | 41.74 | 92.0433 | 49.1579 | 168.617 | 0.43272 |  | 1769 | 24.8 | 92.0433 | 5.7321 | 168.617
1770 | 42.5 | 134.652 | 31.3393 | 268.5267 | 0.43446 |  | 1770 | 29.94 | 134.652 | 6 | 268.5267
1771 | 40 | 154.4359 | 32.1315 | 316.5968 | 0.43346 |  | 1771 | 39.48 | 154.4359 | 5.7321 | 316.5968
1772 | 46.75 | 146.1505 | 30.8179 | 405.9514 | 0.43562 |  | 1772 | 47.92 | 146.1505 | 5 | 405.9514
1773 | 43.99 | 114.6375 | 29.5241 | 378.2243 | 0.43684 |  | 1773 | 34.32 | 114.6375 | 4 | 378.2243
1774 | 40.1 | 107.5582 | 17.2187 | 313.3412 | 0.43672 |  | 1774 | 29.48 | 107.5582 | 3 | 313.3412
1775 | 40.18 | 75.1542 | 27.2581 | 299.4134 | 0.43361 |  | 1775 | 26.37 | 75.1542 | 2.2679 | 299.4134
1776 | 39.88 | 39.3551 | 232.6561 | 397.4526 | 0.43958 |  | 1776 | 24.79 | 39.3551 | 2 | 397.4526
1777 | 39.98 | 33.6824 | 19.5913 | 319.9227 | 0.44494 |  | 1777 | 22.67 | 33.6824 | 2.2679 | 319.9227
1778 | 39.86 | 32.1685 | 36.3607 | 295.2512 | 0.4473 |  | 1778 | 21.34 | 32.1685 | 3 | 295.2512
1779 | 39.9 | 30.5448 | 34.9225 | 423.6603 | 0.45987 |  | 1779 | 21.17 | 30.5448 | 4 | 423.6603
1780 | 39.42 | 29.2922 | 33.5008 | 455.9011 | 0.47702 |  | 1780 | 20.74 | 29.2922 | 5 | 455.9011
1781 | 39.54 | 28.4587 | 30.964 | 487.389 | 0.48893 |  | 1781 | 20.91 | 28.4587 | 5.7321 | 487.389
1782 | 39.65 | 28.3686 | 63.6136 | 494.5776 | 0.47424 |  | 1782 | 23.8 | 28.3686 | 6 | 494.5776
1783 | 36.4 | 43.1865 | 139.6332 | 446.6306 | 0.4607 |  | 1783 | 29.3 | 43.1865 | 5.7321 | 446.6306
1784 | 32 | 57.2775 | 110.6568 | 520.154 | 0.4433 |  | 1784 | 35.75 | 57.2775 | 5 | 520.154
1785 | 35.4 | 44.4504 | 49.3994 | 401.0645 | 0.42932 |  | 1785 | 39.77 | 44.4504 | 4 | 401.0645
1786 | 37.43 | 43.8808 | 71.778 | 326.0008 | 0.4217 |  | 1786 | 39.3 | 43.8808 | 3 | 326.0008
1787 | 38.22 | 46.2364 | 83.1714 | 251.1279 | 0.4145 |  | 1787 | 36.09 | 46.2364 | 2.2679 | 251.1279
1788 | 37.4 | 48.8348 | 48.9312 | 181.4508 | 0.40315 |  | 1788 | 34.31 | 48.8348 | 2 | 181.4508
1789 | 34.9 | 52.0354 | 44.2842 | 162.5297 | 0.37935 |  | 1789 | 30.93 | 52.0354 | 2.2679 | 162.5297
1790 | 26.37 | 55.1878 | 42.6178 | 101.5922 | 0.36926 |  | 1790 | 27.44 | 55.1878 | 3 | 101.5922
1791 | 32.5 | 58.4532 | 46.9758 | 48.992 | 0.37741 |  | 1791 | 24.78 | 58.4532 | 4 | 48.992
1792 | 33.24 | 74.9619 | 43.2553 | 64.1317 | 0.38277 |  | 1792 | 23.71 | 74.9619 | 5 | 64.1317
1793 | 32.5 | 90.6263 | 38.043 | 84.2702 | 0.38847 |  | 1793 | 23.3 | 90.6263 | 5.7321 | 84.2702
1794 | 38 | 132.5546 | 33.365 | 188.7695 | 0.40429 |  | 1794 | 25.45 | 132.5546 | 6 | 188.7695
1795 | 39.9 | 150.7268 | 41.1476 | 250.0908 | 0.41236 |  | 1795 | 31.91 | 150.7268 | 5.7321 | 250.0908
1796 | 38.5 | 137.0467 | 218.5972 | 376.3981 | 0.42728 |  | 1796 | 34.58 | 137.0467 | 5 | 376.3981
1797 | 36.4 | 113.1225 | 38.0471 | 369.293 | 0.41506 |  | 1797 | 29.94 | 113.1225 | 4 | 369.293
1798 | 34.9 | 108.1338 | 38.8737 | 398.1909 | 0.4022 |  | 1798 | 25.09 | 108.1338 | 3 | 398.1909
1799 | 31.7 | 77.3605 | 28.3128 | 397.4289 | 0.39026 |  | 1799 | 25.5 | 77.3605 | 2.2679 | 397.4289
1800 | 35 | 39.4178 | 23.6714 | 371.8232 | 0.38836 |  | 1800 | 22.11 | 39.4178 | 2 | 371.8232
1801 | 35 | 33.1932 | 42.4537 | 421.6221 | 0.38578 |  | 1801 | 22.33 | 33.1932 | 2.2679 | 421.6221
1802 | 26.5 | 31.7483 | 39.9028 | 325.9402 | 0.37579 |  | 1802 | 22.11 | 31.7483 | 3 | 325.9402
1803 | 20.1 | 30.4531 | 28.977 | 467.1238 | 0.37383 |  | 1803 | 21.6 | 30.4531 | 4 | 467.1238
1804 | 0.1 | 29.124 | 36.7476 | 501.307 | 0.37608 |  | 1804 | 20.06 | 29.124 | 5 | 501.307
1805 | 9 | 28.2123 | 23.6316 | 445.118 | 0.39345 |  | 1805 | 20.49 | 28.2123 | 5.7321 | 445.118
1806 | 35 | 28.1241 | 22.2919 | 522.2663 | 0.43368 |  | 1806 | 22.11 | 28.1241 | 6 | 522.2663
1807 | 38.64 | 42.5289 | 24.0053 | 552.9398 | 0.44577 |  | 1807 | 27.17 | 42.5289 | 5.7321 | 552.9398
1808 | 36.2 | 56.4307 | 53.1179 | 534.5164 | 0.45602 |  | 1808 | 34.26 | 56.4307 | 5 | 534.5164
1809 | 36.1 | 44.0648 | 27.4312 | 359.3165 | 0.44927 |  | 1809 | 33.68 | 44.0648 | 4 | 359.3165
1810 | 39 | 43.5487 | 37.9729 | 301.1922 | 0.44131 |  | 1810 | 28.3 | 43.5487 | 3 | 301.1922
1811 | 37.8 | 47.1579 | 32.4809 | 183.285 | 0.43131 |  | 1811 | 26.27 | 47.1579 | 2.2679 | 183.285
1812 | 36.35 | 49.1837 | 39.9349 | 147.1755 | 0.4173 |  | 1812 | 24.43 | 49.1837 | 2 | 147.1755
1813 | 37.4 | 51.5386 | 37.8473 | 135.1224 | 0.40224 |  | 1813 | 22.96 | 51.5386 | 2.2679 | 135.1224
1814 | 36.9 | 51.3069 | 52.1944 | 56.005 | 0.38825 |  | 1814 | 22.81 | 51.3069 | 3 | 56.005
1815 | 34.5 | 58.9125 | 447.1197 | 60.1729 | 0.3746 |  | 1815 | 22.62 | 58.9125 | 4 | 60.1729
1816 | 35.1 | 75.1457 | 46.7489 | 67.2323 | 0.38699 |  | 1816 | 22.51 | 75.1457 | 5 | 67.2323
1817 | 35.2 | 93.9185 | 34.511 | 85.0205 | 0.40077 |  | 1817 | 23.94 | 93.9185 | 5.7321 | 85.0205
1818 | 39.81 | 140.193 | 54.2537 | 103.4635 | 0.42911 |  | 1818 | 29.92 | 140.193 | 6 | 103.4635
1819 | 37.54 | 152.568 | 30.5396 | 220.8986 | 0.44663 |  | 1819 | 35.6 | 152.568 | 5.7321 | 220.8986
1820 | 49.72 | 139.0353 | 36.8594 | 389.4293 | 0.45664 |  | 1820 | 39.94 | 139.0353 | 5 | 389.4293
1821 | 45 | 113.8669 | 29.7895 | 421.7037 | 0.45509 |  | 1821 | 32.66 | 113.8669 | 4 | 421.7037
1822 | 38.82 | 105.3135 | 31.2622 | 362.5712 | 0.45785 |  | 1822 | 28.14 | 105.3135 | 3 | 362.5712
1823 | 39.32 | 75.403 | 34.5177 | 440.3067 | 0.45684 |  | 1823 | 26.5 | 75.403 | 2.2679 | 440.3067
1824 | 39.5 | 38.3889 | 25.2956 | 428.9593 | 0.45033 |  | 1824 | 25.28 | 38.3889 | 2 | 428.9593
1825 | 33 | 34.3669 | 31.941 | 454.2551 | 0.45162 |  | 1825 | 23.08 | 34.3669 | 2.2679 | 454.2551
1826 | 34 | 32.84 | 32.8599 | 373.951 | 0.45902 |  | 1826 | 22.39 | 32.84 | 3 | 373.951
1827 | 35 | 31.1556 | 29.2657 | 328.0092 | 0.46494 |  | 1827 | 22.63 | 31.1556 | 4 | 328.0092
1828 | 37.7 | 29.6979 | 37.7729 | 439.6481 | 0.46855 |  | 1828 | 22.38 | 29.6979 | 5 | 439.6481
1829 | 37.95 | 28.6781 | 39.9101 | 464.1364 | 0.46941 |  | 1829 | 22.52 | 28.6781 | 5.7321 | 464.1364
1830 | 39.66 | 27.9037 | 35.3465 | 444.6652 | 0.4668 |  | 1830 | 23.99 | 27.9037 | 6 | 444.6652
1831 | 42.16 | 27.4907 | 39.1146 | 646.9137 | 0.46853 |  | 1831 | 33.9 | 27.4907 | 5.7321 | 646.9137
1832 | 48.29 | 29.72 | 49.8763 | 616.0812 | 0.47213 |  | 1832 | 38.16 | 29.72 | 5 | 616.0812
1833 | 56.8 | 48.7576 | 33.7681 | 398.2841 | 0.47146 |  | 1833 | 36 | 48.7576 | 4 | 398.2841
1834 | 46.34 | 67.4238 | 44.4691 | 352.5939 | 0.46221 |  | 1834 | 36 | 67.4238 | 3 | 352.5939
1835 | 42.6 | 75.0956 | 246.305 | 264.427 | 0.45983 |  | 1835 | 36 | 75.0956 | 2.2679 | 264.427
1836 | 40.1 | 74.6846 | 59.3942 | 140.8233 | 0.45932 |  | 1836 | 29.23 | 74.6846 | 2 | 140.8233
1837 | 35 | 81.4866 | 43.5998 | 105.7226 | 0.45466 |  | 1837 | 23.72 | 81.4866 | 2.2679 | 105.7226
1838 | 36.2 | 76.5982 | 42.0825 | 100.8667 | 0.44806 |  | 1838 | 23.7 | 76.5982 | 3 | 100.8667
1839 | 36.2 | 74.1984 | 34.5899 | 59.692 | 0.44805 |  | 1839 | 22.89 | 74.1984 | 4 | 59.692
1840 | 37.77 | 75.836 | 50.7764 | 65.2439 | 0.45608 |  | 1840 | 23.43 | 75.836 | 5 | 65.2439
1841 | 38 | 78.66 | 47.4389 | 92.8621 | 0.47355 |  | 1841 | 25.85 | 78.66 | 5.7321 | 92.8621
1842 | 47.4 | 117.3208 | 56.2656 | 173.9243 | 0.48138 |  | 1842 | 31.92 | 117.3208 | 6 | 173.9243
1843 | 46.12 | 140.4692 | 46.9691 | 252.0142 | 0.48323 |  | 1843 | 38.81 | 140.4692 | 5.7321 | 252.0142
1844 | 53 | 150.5419 | 35.1815 | 369.1395 | 0.48919 |  | 1844 | 46.69 | 150.5419 | 5 | 369.1395
1845 | 46 | 111.205 | 21.857 | 381.0395 | 0.49365 |  | 1845 | 37.76 | 111.205 | 4 | 381.0395
1846 | 44.39 | 102.7448 | 32.7919 | 373.4695 | 0.49968 |  | 1846 | 30.98 | 102.7448 | 3 | 373.4695
1847 | 41.7 | 88.6053 | 32.9264 | 315.7014 | 0.50608 |  | 1847 | 27.89 | 88.6053 | 2.2679 | 315.7014
1848 | 40.74 | 40.6609 | 31.8867 | 415.5142 | 0.51085 |  | 1848 | 24.94 | 40.6609 | 2 | 415.5142
1849 | 39.08 | 35.2134 | 35.2066 | 338.2155 | 0.51896 |  | 1849 | 24.94 | 35.2134 | 2.2679 | 338.2155
1850 | 38.49 | 33.2955 | 25.743 | 351.1518 | 0.51882 |  | 1850 | 23.24 | 33.2955 | 3 | 351.1518
1851 | 37.45 | 31.6142 | 34.0696 | 361.6144 | 0.51591 |  | 1851 | 21.82 | 31.6142 | 4 | 361.6144
1852 | 36.47 | 30.0256 | 231.7525 | 386.7893 | 0.51062 |  | 1852 | 21.97 | 30.0256 | 5 | 386.7893
1853 | 36.42 | 29.0407 | 38.2959 | 503.8418 | 0.51309 |  | 1853 | 22.01 | 29.0407 | 5.7321 | 503.8418
1854 | 40.29 | 28.4101 | 21.5926 | 460.9523 | 0.51399 |  | 1854 | 23.24 | 28.4101 | 6 | 460.9523
1855 | 46.96 | 28.0963 | 25.6548 | 539.9739 | 0.51376 |  | 1855 | 27.44 | 28.0963 | 5.7321 | 539.9739
1856 | 51.27 | 30.8662 | 49.2117 | 522.2174 | 0.51498 |  | 1856 | 33.96 | 30.8662 | 5 | 522.2174
1857 | 54.38 | 50.5569 | 44.534 | 444.9538 | 0.5147 |  | 1857 | 32.64 | 50.5569 | 4 | 444.9538
1858 | 49.69 | 70.3166 | 65.6063 | 332.8933 | 0.51352 |  | 1858 | 29.01 | 70.3166 | 3 | 332.8933
1859 | 46.31 | 79.417 | 51.6483 | 249.143 | 0.50843 |  | 1859 | 25.06 | 79.417 | 2.2679 | 249.143
1860 | 44.55 | 80.1952 | 61.8134 | 225.7419 | 0.50481 |  | 1860 | 35.5 | 80.1952 | 2 | 225.7419
1861 | 43.31 | 82.8209 | 47.2021 | 277.2171 | 0.50285 |  | 1861 | 35.5 | 82.8209 | 2.2679 | 277.2171
1862 | 42.89 | 83.2077 | 40.7458 | 149.4897 | 0.50536 |  | 1862 | 29.94 | 83.2077 | 3 | 149.4897
1863 | 42.48 | 76.8953 | 51.9982 | 178.2431 | 0.5071 |  | 1863 | 26.78 | 76.8953 | 4 | 178.2431
1864 | 43.74 | 79.6425 | 32.8289 | 208.8724 | 0.50763 |  | 1864 | 23.46 | 79.6425 | 5 | 208.8724
1865 | 44.61 | 78.7599 | 43.3892 | 262.814 | 0.50958 |  | 1865 | 24.42 | 78.7599 | 5.7321 | 262.814
1866 | 48.96 | 110.7679 | 34.7819 | 261.1869 | 0.51178 |  | 1866 | 27.82 | 110.7679 | 6 | 261.1869
1867 | 55.17 | 141.0867 | 44.9428 | 374.8449 | 0.5074 |  | 1867 | 33.99 | 141.0867 | 5.7321 | 374.8449
1868 | 60.73 | 163.7474 | 34.8618 | 295.176 | 0.50484 |  | 1868 | 39.3 | 163.7474 | 5 | 295.176
1869 | 52.55 | 120.4095 | 21.6637 | 364.249 | 0.50505 |  | 1869 | 33.91 | 120.4095 | 4 | 364.249
1870 | 46.46 | 102.3824 | 31.4166 | 355.5071 | 0.50256 |  | 1870 | 27.09 | 102.3824 | 3 | 355.5071
1871 | 44.72 | 88.2684 | 38.5289 | 309.3458 | 0.50241 |  | 1871 | 26.92 | 88.2684 | 2.2679 | 309.3458
1872 | 41.08 | 41.7647 | 230.8286 | 218.8249 | 0.4962 |  | 1872 | 25.15 | 41.7647 | 2 | 218.8249
1873 | 38.28 | 33.3077 | 27.1802 | 281.3939 | 0.49048 |  | 1873 | 24.67 | 33.3077 | 2.2679 | 281.3939
1874 | 36.3 | 31.8331 | 32.3422 | 253.7021 | 0.47563 |  | 1874 | 22.69 | 31.8331 | 3 | 253.7021
1875 | 35.05 | 30.4058 | 32.4888 | 202.0501 | 0.4609 |  | 1875 | 22.58 | 30.4058 | 4 | 202.0501
1876 | 34.33 | 29.188 | 30.6076 | 255.4061 | 0.45659 |  | 1876 | 22.89 | 29.188 | 5 | 255.4061
1877 | 34.69 | 28.403 | 33.2415 | 254.5076 | 0.4601 |  | 1877 | 22.85 | 28.403 | 5.7321 | 254.5076
1878 | 37.2 | 28.1673 | 53.0787 | 374.3149 | 0.47101 |  | 1878 | 22.57 | 28.1673 | 6 | 374.3149
1879 | 41.23 | 43.7063 | 120.6565 | 385.7861 | 0.4846 |  | 1879 | 23.17 | 43.7063 | 5.7321 | 385.7861
1880 | 45.56 | 55.4713 | 117.7526 | 359.9128 | 0.49084 |  | 1880 | 29.09 | 55.4713 | 5 | 359.9128
1881 | 52.94 | 44.7481 | 123.0306 | 290.99 | 0.49563 |  | 1881 | 29.38 | 44.7481 | 4 | 290.99
1882 | 46.36 | 42.9207 | 77.5184 | 234.8617 | 0.49856 |  | 1882 | 28.58 | 42.9207 | 3 | 234.8617
1883 | 43.89 | 44.7851 | 47.8353 | 236.0635 | 0.49705 |  | 1883 | 26.96 | 44.7851 | 2.2679 | 236.0635
1884 | 39.86 | 47.7833 | 239.7158 | 185.6284 | 0.4964 |  | 1884 | 25.22 | 47.7833 | 2 | 185.6284
1885 | 37.59 | 49.7786 | 49.9015 | 141.7722 | 0.49718 |  | 1885 | 30.97 | 49.7786 | 2.2679 | 141.7722
1886 | 37.47 | 55.0104 | 55.0077 | 55.7991 | 0.49457 |  | 1886 | 26 | 55.0104 | 3 | 55.7991
1887 | 38.16 | 58.0943 | 32.6199 | 66.9056 | 0.49027 |  | 1887 | 21.34 | 58.0943 | 4 | 66.9056
1888 | 40.36 | 73.2949 | 39.0837 | 53.8728 | 0.4946 |  | 1888 | 20.93 | 73.2949 | 5 | 53.8728
1889 | 42.1 | 90.4003 | 39.5392 | 64.9978 | 0.50275 |  | 1889 | 21.3 | 90.4003 | 5.7321 | 64.9978
1890 | 45.49 | 132.3245 | 46.4998 | 106.6954 | 0.50107 |  | 1890 | 24 | 132.3245 | 6 | 106.6954
1891 | 51 | 154.1788 | 46.7282 | 94.1171 | 0.49651 |  | 1891 | 31.21 | 154.1788 | 5.7321 | 94.1171
1892 | 55.55 | 142.9319 | 29.8667 | 133.6698 | 0.49404 |  | 1892 | 35.42 | 142.9319 | 5 | 133.6698
1893 | 48.74 | 122.3675 | 22.2939 | 224.3809 | 0.49002 |  | 1893 | 27.08 | 122.3675 | 4 | 224.3809
1894 | 44.24 | 104.9216 | 34.0707 | 245.8315 | 0.49093 |  | 1894 | 23 | 104.9216 | 3 | 245.8315
1895 | 42.74 | 74.6688 | 225.7745 | 202.4455 | 0.49337 |  | 1895 | 26.98 | 74.6688 | 2.2679 | 202.4455
1896 | 38.65 | 38.6729 | 31.2788 | 184.9914 | 0.49022 |  | 1896 | 21.97 | 38.6729 | 2 | 184.9914
1897 | 35.47 | 35.6749 | 23.9903 | 183.2915 | 0.48178 |  | 1897 | 29 | 35.6749 | 2.2679 | 183.2915
1898 | 34.7 | 33.9218 | 28.8543 | 180.7395 | 0.47088 |  | 1898 | 24.08 | 33.9218 | 3 | 180.7395
1899 | 33.51 | 32.0531 | 27.5433 | 165.963 | 0.45728 |  | 1899 | 20.82 | 32.0531 | 4 | 165.963
1900 | 33.04 | 30.4445 | 31.6933 | 222.1823 | 0.45558 |  | 1900 | 20.4 | 30.4445 | 5 | 222.1823
1901 | 33.1 | 29.2749 | 29.2861 | 274.9361 | 0.46247 |  | 1901 | 20 | 29.2749 | 5.7321 | 274.9361
1902 | 35.93 | 28.7961 | 35.2188 | 310.8393 | 0.47452 |  | 1902 | 20.29 | 28.7961 | 6 | 310.8393
1903 | 44 | 42.9774 | 32.6395 | 347.4912 | 0.4861 |  | 1903 | 20.4 | 42.9774 | 5.7321 | 347.4912
1904 | 43.31 | 54.4917 | 42.8204 | 354.1472 | 0.48965 |  | 1904 | 20.34 | 54.4917 | 5 | 354.1472
1905 | 45.26 | 42.6271 | 38.4578 | 235.8316 | 0.49156 |  | 1905 | 20.58 | 42.6271 | 4 | 235.8316
1906 | 45.55 | 40.8217 | 43.2399 | 171.301 | 0.49057 |  | 1906 | 20.97 | 40.8217 | 3 | 171.301
1907 | 38.5 | 42.8668 | 29.9838 | 84.695 | 0.48728 |  | 1907 | 24.94 | 42.8668 | 2.2679 | 84.695
1908 | 35.89 | 43.5803 | 43.7262 | 64.8002 | 0.47654 |  | 1908 | 24.87 | 43.5803 | 2 | 64.8002
1909 | 35.43 | 48.3319 | 38.3952 | 80.8794 | 0.47212 |  | 1909 | 26 | 48.3319 | 2.2679 | 80.8794
1910 | 34.5 | 49.4626 | 42.927 | 82.223 | 0.46556 |  | 1910 | 27.44 | 49.4626 | 3 | 82.223
1911 | 34.9 | 57.7491 | 40.6619 | 71.6545 | 0.46846 |  | 1911 | 24.94 | 57.7491 | 4 | 71.6545
1912 | 36.81 | 71.7164 | 47.2999 | 71.7061 | 0.48613 |  | 1912 | 23.1 | 71.7164 | 5 | 71.7061
1913 | 39.27 | 96.7599 | 52.8673 | 87.2958 | 0.50376 |  | 1913 | 20.71 | 96.7599 | 5.7321 | 87.2958
1914 | 43.4 | 136.015 | 47.7718 | 81.5464 | 0.51173 |  | 1914 | 21.25 | 136.015 | 6 | 81.5464
1915 | 46.7 | 150.8167 | 46.0152 | 111.6354 | 0.51224 |  | 1915 | 26 | 150.8167 | 5.7321 | 111.6354
1916 | 55 | 131.8634 | 25.9611 | 189.2048 | 0.51195 |  | 1916 | 42.53 | 131.8634 | 5 | 189.2048
1917 | 47.53 | 118.4528 | 29.9907 | 202.6979 | 0.51289 |  | 1917 | 41.33 | 118.4528 | 4 | 202.6979
1918 | 43.92 | 110.4498 | 29.4502 | 189.4607 | 0.51504 |  | 1918 | 32.4 | 110.4498 | 3 | 189.4607
1919 | 41.94 | 78.954 | 25.5132 | 180.1615 | 0.51784 |  | 1919 | 31.48 | 78.954 | 2.2679 | 180.1615
1920 | 39.09 | 41.1854 | 28.4148 | 189.9334 | 0.52035 |  | 1920 | 32.44 | 41.1854 | 2 | 189.9334
1921 | 39 | 34.004 | 228.7024 | 218.4131 | 0.51497 |  | 1921 | 27.6 | 34.004 | 2.2679 | 218.4131
1922 | 35.95 | 32.5317 | 32.5664 | 184.2614 | 0.51252 |  | 1922 | 25.99 | 32.5317 | 3 | 184.2614
1923 | 36.69 | 31.0697 | 29.0187 | 194.6027 | 0.50716 |  | 1923 | 24.98 | 31.0697 | 4 | 194.6027
1924 | 36.39 | 29.6019 | 30.9514 | 177.6248 | 0.50887 |  | 1924 | 21 | 29.6019 | 5 | 177.6248
1925 | 36.28 | 28.5639 | 34.1517 | 236.8062 | 0.51597 |  | 1925 | 21.62 | 28.5639 | 5.7321 | 236.8062
1926 | 39.95 | 28.3161 | 32.7748 | 272.795 | 0.51968 |  | 1926 | 23.84 | 28.3161 | 6 | 272.795
1927 | 46.01 | 42.4766 | 41.3413 | 276.2043 | 0.51847 |  | 1927 | 32.01 | 42.4766 | 5.7321 | 276.2043
1928 | 50.98 | 54.3503 | 98.3187 | 320.8704 | 0.51669 |  | 1928 | 31.72 | 54.3503 | 5 | 320.8704
1929 | 49.2 | 42.2219 | 137.8162 | 286.7938 | 0.5146 |  | 1929 | 31.55 | 42.2219 | 4 | 286.7938
1930 | 44.97 | 39.9266 | 139.6796 | 200.0964 | 0.51526 |  | 1930 | 31 | 39.9266 | 3 | 200.0964
1931 | 40.41 | 41.7934 | 142.4212 | 219.9457 | 0.51096 |  | 1931 | 29.94 | 41.7934 | 2.2679 | 219.9457
1932 | 36.57 | 42.3774 | 109.3313 | 168.3541 | 0.50168 |  | 1932 | 30 | 42.3774 | 2 | 168.3541
1933 | 35 | 47.7239 | 114.3694 | 154.1491 | 0.48493 |  | 1933 | 26.45 | 47.7239 | 2.2679 | 154.1491
1934 | 34.3 | 48.7834 | 52.4704 | 106.3045 | 0.47705 |  | 1934 | 26.1 | 48.7834 | 3 | 106.3045
1935 | 34.46 | 55.1118 | 33.9329 | 49.9538 | 0.4804 |  | 1935 | 24.33 | 55.1118 | 4 | 49.9538
1936 | 35 | 70.6578 | 55.2407 | 68.6373 | 0.48882 |  | 1936 | 24.51 | 70.6578 | 5 | 68.6373
1937 | 37.78 | 88.0591 | 48.0737 | 111.3384 | 0.49951 |  | 1937 | 24.07 | 88.0591 | 5.7321 | 111.3384
1938 | 43.61 | 129.5444 | 38.0818 | 158.7319 | 0.50521 |  | 1938 | 27.63 | 129.5444 | 6 | 158.7319
1939 | 46.91 | 149.2408 | 48.9171 | 195.3847 | 0.50434 |  | 1939 | 31 | 149.2408 | 5.7321 | 195.3847
1940 | 50.17 | 141.295 | 33.0719 | 261.5703 | 0.50103 |  | 1940 | 35.37 | 141.295 | 5 | 261.5703
1941 | 46 | 115.8454 | 26.854 | 245.7258 | 0.50025 |  | 1941 | 31.63 | 115.8454 | 4 | 245.7258
1942 | 40.61 | 106.9826 | 26.4825 | 187.0104 | 0.50238 |  | 1942 | 26.23 | 106.9826 | 3 | 187.0104
1943 | 39.9 | 75.9254 | 29.0185 | 202.4031 | 0.50527 |  | 1943 | 26.16 | 75.9254 | 2.2679 | 202.4031
1944 | 37.12 | 39.407 | 32.975 | 192.1478 | 0.50431 |  | 1944 | 22.12 | 39.407 | 2 | 192.1478
1945 | 35.53 | 33.9209 | 27.6152 | 215.256 | 0.50735 |  | 1945 | 22.74 | 33.9209 | 2.2679 | 215.256
1946 | 34.94 | 32.3694 | 25.1603 | 217.9768 | 0.51006 |  | 1946 | 21.81 | 32.3694 | 3 | 217.9768
1947 | 34.9 | 30.7927 | 42.635 | 226.6993 | 0.50451 |  | 1947 | 21.71 | 30.7927 | 4 | 226.6993
1948 | 33.1 | 29.3644 | 28.7569 | 261.0362 | 0.50042 |  | 1948 | 21.84 | 29.3644 | 5 | 261.0362
1949 | 33.05 | 28.4526 | 32.1692 | 278.8272 | 0.49821 |  | 1949 | 21.96 | 28.4526 | 5.7321 | 278.8272
1950 | 34.6 | 28.3832 | 27.1946 | 313.812 | 0.5129 |  | 1950 | 22.74 | 28.3832 | 6 | 313.812
1951 | 36.64 | 42.2997 | 226.8986 | 340.0133 | 0.52998 |  | 1951 | 25.89 | 42.2997 | 5.7321 | 340.0133
1952 | 38.86 | 54.2061 | 246.6106 | 310.8443 | 0.53556 |  | 1952 | 30.42 | 54.2061 | 5 | 310.8443
1953 | 38.43 | 43.4651 | 30.4658 | 305.7666 | 0.53277 |  | 1953 | 32.14 | 43.4651 | 4 | 305.7666
1954 | 40.36 | 43.0543 | 41.178 | 225.1441 | 0.52603 |  | 1954 | 32.01 | 43.0543 | 3 | 225.1441
1955 | 37.34 | 45.6178 | 42.1579 | 207.9949 | 0.51736 |  | 1955 | 29.63 | 45.6178 | 2.2679 | 207.9949
1956 | 36.62 | 47.3451 | 48.0239 | 184.5796 | 0.51226 |  | 1956 | 30.5 | 47.3451 | 2 | 184.5796
1957 | 36 | 50.186 | 34.4791 | 230.398 | 0.5042 |  | 1957 | 29.27 | 50.186 | 2.2679 | 230.398
1958 | 31.1 | 51.5459 | 41.2522 | 223.6779 | 0.48709 |  | 1958 | 29.25 | 51.5459 | 3 | 223.6779
1959 | 30.1 | 57.861 | 37.1101 | 174.8994 | 0.47284 |  | 1959 | 29.12 | 57.861 | 4 | 174.8994
1960 | 31.1 | 71.907 | 43.3719 | 191.1351 | 0.47627 |  | 1960 | 29.29 | 71.907 | 5 | 191.1351
1961 | 32.58 | 92.4484 | 49.43 | 152.4345 | 0.49049 |  | 1961 | 30.08 | 92.4484 | 5.7321 | 152.4345
1962 | 38.71 | 138.8087 | 47.6573 | 210.3402 | 0.5119 |  | 1962 | 34.01 | 138.8087 | 6 | 210.3402
1963 | 41.27 | 142.0175 | 56.662 | 262.9292 | 0.52439 |  | 1963 | 36.73 | 142.0175 | 5.7321 | 262.9292
1964 | 44.99 | 143.452 | 24.4756 | 244.8701 | 0.52702 |  | 1964 | 40.64 | 143.452 | 5 | 244.8701
1965 | 42.25 | 114.9535 | 34.0936 | 230.2416 | 0.53015 |  | 1965 | 38.1 | 114.9535 | 4 | 230.2416
1966 | 39.1 | 107.2105 | 31.4487 | 259.8048 | 0.5341 |  | 1966 | 33.05 | 107.2105 | 3 | 259.8048
1967 | 40.35 | 75.5 | 34.5531 | 239.7536 | 0.53761 |  | 1967 | 30.27 | 75.5 | 2.2679 | 239.7536
1968 | 37.93 | 39.7574 | 22.5081 | 240.7241 | 0.54193 |  | 1968 | 25.41 | 39.7574 | 2 | 240.7241
1969 | 39.15 | 34.5826 | 31.22 | 228.9595 | 0.54668 |  | 1969 | 22.69 | 34.5826 | 2.2679 | 228.9595
1970 | 36.05 | 32.8754 | 25.2947 | 198.3302 | 0.54477 |  | 1970 | 22.45 | 32.8754 | 3 | 198.3302
1971 | 34.45 | 31.2031 | 33.8394 | 269.6077 | 0.54115 |  | 1971 | 20.93 | 31.2031 | 4 | 269.6077
1972 | 33.61 | 29.7905 | 30.5588 | 310.3832 | 0.5245 |  | 1972 | 21.33 | 29.7905 | 5 | 310.3832
1973 | 33.85 | 28.8207 | 28.2815 | 312.1502 | 0.52372 |  | 1973 | 21.51 | 28.8207 | 5.7321 | 312.1502
1974 | 34.2 | 28.557 | 30.3601 | 325.8181 | 0.52946 |  | 1974 | 21.93 | 28.557 | 6 | 325.8181
1975 | 34.32 | 42.4265 | 34.7608 | 327.4047 | 0.53713 |  | 1975 | 26.26 | 42.4265 | 5.7321 | 327.4047
1976 | 34.98 | 54.2772 | 42.7847 | 335.7523 | 0.5445 |  | 1976 | 33.06 | 54.2772 | 5 | 335.7523
1977 | 36.6 | 43.3957 | 52.2002 | 275.7358 | 0.53821 |  | 1977 | 35.37 | 43.3957 | 4 | 275.7358
1978 | 35.81 | 43.3466 | 45.3539 | 218.2719 | 0.5247 |  | 1978 | 33.95 | 43.3466 | 3 | 218.2719
1979 | 33.78 | 44.2472 | 43.3408 | 108.1167 | 0.50255 |  | 1979 | 32.44 | 44.2472 | 2.2679 | 108.1167
1980 | 32.01 | 47.6893 | 48.0608 | 69.7787 | 0.48119 |  | 1980 | 31.05 | 47.6893 | 2 | 69.7787
1981 | 31.1 | 49.6052 | 34.8256 | 90.4633 | 0.46788 |  | 1981 | 29.8 | 49.6052 | 2.2679 | 90.4633
1982 | 25.08 | 52.8191 | 34.1483 | 61.1525 | 0.4648 |  | 1982 | 25 | 52.8191 | 3 | 61.1525
1983 | 24.13 | 59.5781 | 44.6147 | 59.0308 | 0.45936 |  | 1983 | 24.03 | 59.5781 | 4 | 59.0308
1984 | 23.79 | 73.6711 | 52.4606 | 74.2538 | 0.455 |  | 1984 | 24.13 | 73.6711 | 5 | 74.2538
1985 | 25.1 | 91.8777 | 48.9917 | 68.8658 | 0.45126 |  | 1985 | 24.18 | 91.8777 | 5.7321 | 68.8658
1986 | 36.6 | 133.1604 | 45.312 | 126.1704 | 0.4588 |  | 1986 | 28 | 133.1604 | 6 | 126.1704
1987 | 39.37 | 141.0672 | 44.6673 | 156.7712 | 0.48578 |  | 1987 | 32.44 | 141.0672 | 5.7321 | 156.7712
1988 | 42.93 | 152.5579 | 25.6898 | 212.097 | 0.49253 |  | 1988 | 37.16 | 152.5579 | 5 | 212.097
1989 | 40.55 | 114.1303 | 33.5434 | 216.5729 | 0.48959 |  | 1989 | 35.25 | 114.1303 | 4 | 216.5729
1990 | 37.6 | 105.6905 | 34.2507 | 164.3604 | 0.47167 |  | 1990 | 31.6 | 105.6905 | 3 | 164.3604
1991 | 40 | 78.7171 | 31.3138 | 145.7473 | 0.45777 |  | 1991 | 25.9 | 78.7171 | 2.2679 | 145.7473
1992 | 38.2 | 40.2258 | 38.0566 | 163.5993 | 0.43378 |  | 1992 | 24.87 | 40.2258 | 2 | 163.5993
1993 | 24.34 | 32.021 | 32.4601 | 147.2031 | 0.41165 |  | 1993 | 22.72 | 32.021 | 2.2679 | 147.2031
1994 | 22.5 | 30.8008 | 234.781 | 167.5759 | 0.38866 |  | 1994 | 21.91 | 30.8008 | 3 | 167.5759
1995 | 25 | 29.691 | 30.1585 | 190.211 | 0.37979 |  | 1995 | 21.37 | 29.691 | 4 | 190.211
1996 | 22.4 | 28.7529 | 32.8412 | 201.056 | 0.37916 |  | 1996 | 21.38 | 28.7529 | 5 | 201.056
1997 | 27.6 | 27.8748 | 40.1665 | 200.4168 | 0.37289 |  | 1997 | 21.75 | 27.8748 | 5.7321 | 200.4168
1998 | 28 | 27.4477 | 20.3379 | 285.9244 | 0.38721 |  | 1998 | 22.99 | 27.4477 | 6 | 285.9244
1999 | 34.45 | 27.0897 | 27.5042 | 303.4373 | 0.40513 |  | 1999 | 31.49 | 27.0897 | 5.7321 | 303.4373
2000 | 42 | 29.4362 | 32.5867 | 282.4052 | 0.4256 |  | 2000 | 35 | 29.4362 | 5 | 282.4052
2001 | 41.18 | 47.7341 | 28.3694 | 271.3251 | 0.43006 |  | 2001 | 34.94 | 47.7341 | 4 | 271.3251
2002 | 39.69 | 66.6563 | 41.2693 | 219.1772 | 0.42502 |  | 2002 | 32.4 | 66.6563 | 3 | 219.1772
2003 | 34.61 | 73.7909 | 55.05 | 178.1469 | 0.40971 |  | 2003 | 31.69 | 73.7909 | 2.2679 | 178.1469
2004 | 34 | 73.0745 | 39.8061 | 173.6962 | 0.40003 |  | 2004 | 31 | 73.0745 | 2 | 173.6962
2005 | 33.06 | 76.6093 | 44.3968 | 163.4651 | 0.38689 |  | 2005 | 28.62 | 76.6093 | 2.2679 | 163.4651
2006 | 32.4 | 71.9817 | 44.9774 | 144.1439 | 0.38545 |  | 2006 | 27.27 | 71.9817 | 3 | 144.1439
2007 | 31.2 | 65.6003 | 51.9839 | 95.3515 | 0.38227 |  | 2007 | 26.5 | 65.6003 | 4 | 95.3515
2008 | 31.52 | 71.1749 | 50.5294 | 119.9904 | 0.38571 |  | 2008 | 25.35 | 71.1749 | 5 | 119.9904
2009 | 32.4 | 75.5915 | 56.0319 | 161.769 | 0.40572 |  | 2009 | 26.6 | 75.5915 | 5.7321 | 161.769
2010 | 36.68 | 114.3265 | 49.452 | 188.1912 | 0.4252 |  | 2010 | 30 | 114.3265 | 6 | 188.1912
2011 | 41.2 | 136.678 | 45.5382 | 249.5711 | 0.43681 |  | 2011 | 32.47 | 136.678 | 5.7321 | 249.5711
2012 | 48.5 | 138.7244 | 33.0368 | 247.2184 | 0.44126 |  | 2012 | 35.18 | 138.7244 | 5 | 247.2184
2013 | 43.22 | 114.9958 | 32.8028 | 271.5668 | 0.44977 |  | 2013 | 33.97 | 114.9958 | 4 | 271.5668
2014 | 39.81 | 100.5461 | 21.5492 | 262.5048 | 0.46098 |  | 2014 | 27.64 | 100.5461 | 3 | 262.5048
2015 | 39.99 | 85.7669 | 32.8884 | 217.3397 | 0.48374 |  | 2015 | 26.63 | 85.7669 | 2.2679 | 217.3397
2016 | 37.56 | 38.2253 | 33.2787 | 248.9104 | 0.49739 |  | 2016 | 23.98 | 38.2253 | 2 | 248.9104
2017 | 33.25 | 32.8552 | 31.4783 | 250.6243 | 0.48865 |  | 2017 | 23.92 | 32.8552 | 2.2679 | 250.6243
2018 | 31.3 | 31.5626 | 33.4113 | 242.5271 | 0.46987 |  | 2018 | 20.95 | 31.5626 | 3 | 242.5271
2019 | 31.2 | 30.0705 | 226.1812 | 214.1497 | 0.45981 |  | 2019 | 20.92 | 30.0705 | 4 | 214.1497
2020 | 31.3 | 28.8106 | 32.3386 | 249.3163 | 0.45733 |  | 2020 | 20 | 28.8106 | 5 | 249.3163
2021 | 31.3 | 28.2117 | 30.1305 | 287.8178 | 0.45337 |  | 2021 | 20.01 | 28.2117 | 5.7321 | 287.8178
2022 | 32.5 | 27.7448 | 32.3429 | 378.7088 | 0.4641 |  | 2022 | 20.3 | 27.7448 | 6 | 378.7088
2023 | 39 | 27.6162 | 35.7432 | 363.7922 | 0.47025 |  | 2023 | 23.31 | 27.6162 | 5.7321 | 363.7922
2024 | 42.8 | 29.8701 | 253.7034 | 382.0513 | 0.4809 |  | 2024 | 29.64 | 29.8701 | 5 | 382.0513
2025 | 42.75 | 49.3691 | 44.5429 | 289.0492 | 0.48417 |  | 2025 | 27.44 | 49.3691 | 4 | 289.0492
2026 | 40 | 68.9983 | 44.0188 | 296.9379 | 0.48396 |  | 2026 | 27.44 | 68.9983 | 3 | 296.9379
2027 | 42 | 75.0957 | 44.865 | 313.975 | 0.48126 |  | 2027 | 27.26 | 75.0957 | 2.2679 | 313.975
2028 | 39.05 | 74.8982 | 53.3303 | 318.7572 | 0.47458 |  | 2028 | 28.91 | 74.8982 | 2 | 318.7572
2029 | 38.78 | 83.9793 | 51.7373 | 300.71 | 0.48181 |  | 2029 | 27.87 | 83.9793 | 2.2679 | 300.71
2030 | 37.4 | 83.7598 | 37.0778 | 279.4153 | 0.47706 |  | 2030 | 27.06 | 83.7598 | 3 | 279.4153
2031 | 36.1 | 76.0581 | 36.0817 | 257.8626 | 0.47371 |  | 2031 | 26.01 | 76.0581 | 4 | 257.8626
2032 | 33.9 | 75.3794 | 39.5472 | 232.1948 | 0.47534 |  | 2032 | 24.44 | 75.3794 | 5 | 232.1948
2033 | 34 | 73.4543 | 32.9316 | 330.0646 | 0.47672 |  | 2033 | 23.5 | 73.4543 | 5.7321 | 330.0646
2034 | 39.76 | 109.1448 | 42.5849 | 267.9027 | 0.49772 |  | 2034 | 26.1 | 109.1448 | 6 | 267.9027
2035 | 43 | 128.9807 | 36.7782 | 323.9116 | 0.50031 |  | 2035 | 29.44 | 128.9807 | 5.7321 | 323.9116
2036 | 49.4 | 152.8133 | 27.2888 | 303.9021 | 0.50291 |  | 2036 | 33.08 | 152.8133 | 5 | 303.9021
2037 | 46.41 | 118.3741 | 34.2568 | 375.0482 | 0.5085 |  | 2037 | 32.95 | 118.3741 | 4 | 375.0482
2038 | 43.37 | 104.5742 | 29.0374 | 290.0832 | 0.51063 |  | 2038 | 31.48 | 104.5742 | 3 | 290.0832
2039 | 42.28 | 86.8715 | 30.5627 | 285.2449 | 0.51276 |  | 2039 | 30.12 | 86.8715 | 2.2679 | 285.2449
2040 | 38.42 | 39.2087 | 30.3329 | 247.0375 | 0.51362 |  | 2040 | 30 | 39.2087 | 2 | 247.0375
2041 | 36.62 | 32.942 | 28.5312 | 244.4765 | 0.51383 |  | 2041 | 28.1 | 32.942 | 2.2679 | 244.4765
2042 | 34.81 | 31.5018 | 34.3863 | 238.7322 | 0.50716 |  | 2042 | 24.09 | 31.5018 | 3 | 238.7322
2043 | 34.27 | 30.2205 | 30.1765 | 242.9315 | 0.49826 |  | 2043 | 21.11 | 30.2205 | 4 | 242.9315
2044 | 33.37 | 29.0062 | 28.49 | 313.7005 | 0.49583 |  | 2044 | 20 | 29.0062 | 5 | 313.7005
2045 | 34.14 | 28.1164 | 33.2326 | 301.2184 | 0.50514 |  | 2045 | 20 | 28.1164 | 5.7321 | 301.2184
2046 | 36.82 | 27.8984 | 37.4154 | 401.8744 | 0.51583 |  | 2046 | 20.01 | 27.8984 | 6 | 401.8744
2047 | 42.01 | 41.8536 | 34.0432 | 418.7439 | 0.51796 |  | 2047 | 20.01 | 41.8536 | 5.7321 | 418.7439
2048 | 46 | 54.2813 | 38.0389 | 326.6003 | 0.50736 |  | 2048 | 21.69 | 54.2813 | 5 | 326.6003
2049 | 47.04 | 42.3271 | 38.2867 | 267.9848 | 0.50326 |  | 2049 | 22.49 | 42.3271 | 4 | 267.9848
2050 | 43.94 | 40.9676 | 45.0647 | 271.7412 | 0.49901 |  | 2050 | 24 | 40.9676 | 3 | 271.7412
2051 | 41.48 | 43.6183 | 43.7343 | 301.5612 | 0.49812 |  | 2051 | 21.6 | 43.6183 | 2.2679 | 301.5612
2052 | 40.61 | 44.759 | 46.5593 | 180.4774 | 0.49922 |  | 2052 | 19.97 | 44.759 | 2 | 180.4774
2053 | 40 | 47.6044 | 77.4823 | 122.7155 | 0.4985 |  | 2053 | 19.06 | 47.6044 | 2.2679 | 122.7155
2054 | 39.58 | 50.0919 | 56.5547 | 131.1143 | 0.49745 |  | 2054 | 18.07 | 50.0919 | 3 | 131.1143
2055 | 38.75 | 56.2003 | 101.0474 | 124.4285 | 0.50358 |  | 2055 | 16.28 | 56.2003 | 4 | 124.4285
2056 | 38.75 | 69.6122 | 88.2117 | 149.2309 | 0.498 |  | 2056 | 17.17 | 69.6122 | 5 | 149.2309
2057 | 39.18 | 93.8521 | 46.505 | 178.8802 | 0.49453 |  | 2057 | 17.3 | 93.8521 | 5.7321 | 178.8802
2058 | 41.49 | 130.866 | 48.4536 | 233.7553 | 0.49644 |  | 2058 | 19.39 | 130.866 | 6 | 233.7553
2059 | 44.17 | 149.1677 | 239.1611 | 258.1268 | 0.49787 |  | 2059 | 21.32 | 149.1677 | 5.7321 | 258.1268
2060 | 47.68 | 146.0331 | 23.4436 | 251.6273 | 0.49888 |  | 2060 | 22.12 | 146.0331 | 5 | 251.6273
2061 | 43.99 | 117.7999 | 29.8544 | 314.3608 | 0.50173 |  | 2061 | 20.75 | 117.7999 | 4 | 314.3608
2062 | 41.22 | 104.9209 | 28.4945 | 249.8088 | 0.50441 |  | 2062 | 19.18 | 104.9209 | 3 | 249.8088
2063 | 40.83 | 75.258 | 31.166 | 237.1874 | 0.50992 |  | 2063 | 18.5 | 75.258 | 2.2679 | 237.1874
2064 | 36.92 | 38.644 | 28.4689 | 219.7743 | 0.51069 |  | 2064 | 17.83 | 38.644 | 2 | 219.7743
2065 | 32.73 | 35.5489 | 28.5725 | 242.308 | 0.49987 |  | 2065 | 7.33 | 35.5489 | 2.2679 | 242.308
2066 | 33.67 | 33.8628 | 32.5545 | 221.3371 | 0.48651 |  | 2066 | 15 | 33.8628 | 3 | 221.3371
2067 | 33.38 | 32.0317 | 31.2581 | 192.8941 | 0.48113 |  | 2067 |  | 32.0317 | 4 | 192.8941
2068 | 33.29 | 30.3421 | 45.7117 | 291.8709 | 0.47875 |  | 2068 | 16.55 | 30.3421 | 5 | 291.8709
2069 | 33.12 | 29.1714 | 91.9545 | 322.8039 | 0.49518 |  | 2069 | 16.56 | 29.1714 | 5.7321 | 322.8039
2070 | 36.67 | 28.7321 | 128.7132 | 296.0746 | 0.50409 |  | 2070 | 15.8 | 28.7321 | 6 | 296.0746
2071 | 44.48 | 41.1184 | 110.4251 | 428.853 | 0.51563 |  | 2071 | 18.39 | 41.1184 | 5.7321 | 428.853
2072 | 49.06 | 54.1951 | 114.0528 | 443.9525 | 0.51496 |  | 2072 | 19.9 | 54.1951 | 5 | 443.9525
2073 | 48.53 | 43.2004 | 132.3298 | 354.3053 | 0.5132 |  | 2073 | 13.03 | 43.2004 | 4 | 354.3053
2074 | 46.78 | 42.1138 | 129.7277 | 234.0298 | 0.51105 |  | 2074 | 17.56 | 42.1138 | 3 | 234.0298
2075 | 44.12 | 44.5981 | 127.7049 | 206.3621 | 0.50941 |  | 2075 | 17.88 | 44.5981 | 2.2679 | 206.3621
2076 | 43.36 | 46.5053 | 132.1164 | 126.8576 | 0.50682 |  | 2076 | 17.93 | 46.5053 | 2 | 126.8576
2077 | 42.54 | 49.0102 | 109.9745 | 109.556 | 0.50794 |  | 2077 | 16.27 | 49.0102 | 2.2679 | 109.556
2078 | 42.39 | 51.4818 | 60.8747 | 56.6914 | 0.5066 |  | 2078 | 14.06 | 51.4818 | 3 | 56.6914
2079 | 41.74 | 60.1642 | 48.5717 | 68.9494 | 0.5068 |  | 2079 | 10.01 | 60.1642 | 4 | 68.9494
2080 | 41.94 | 74.7151 | 49.6871 | 74.8963 | 0.50775 |  | 2080 | 15 | 74.7151 | 5 | 74.8963
2081 | 42.53 | 95.1926 | 45.5737 | 177.4595 | 0.5092 |  | 2081 | 10.12 | 95.1926 | 5.7321 | 177.4595
2082 | 45.74 | 125.3642 | 42.5775 | 232.6021 | 0.50854 |  | 2082 | 19.7 | 125.3642 | 6 | 232.6021
2083 | 47.65 | 145.2315 | 44.1287 | 241.3728 | 0.50613 |  | 2083 | 16.98 | 145.2315 | 5.7321 | 241.3728
2084 | 52.66 | 142.0558 | 28.5645 | 305.8068 | 0.50732 |  | 2084 | 19.7 | 142.0558 | 5 | 305.8068
2085 | 46.36 | 117.1884 | 36.4933 | 312.1944 | 0.5096 |  | 2085 | 22.86 | 117.1884 | 4 | 312.1944
2086 | 43.3 | 110.2804 | 35.5242 | 280.1458 | 0.51132 |  | 2086 | 20.36 | 110.2804 | 3 | 280.1458
2087 | 42.38 | 79.1215 | 224.2516 | 249.5813 | 0.51284 |  | 2087 | 19.98 | 79.1215 | 2.2679 | 249.5813
2088 | 39.32 | 41.6031 | 35.9158 | 241.0901 | 0.51667 |  | 2088 | 18.5 | 41.6031 | 2 | 241.0901
2089 | 39.28 | 34.2388 | 28.1219 | 312.4242 | 0.5142 |  | 2089 | 12.88 | 34.2388 | 2.2679 | 312.4242
2090 | 34.1 | 32.4917 | 30.6469 | 248.0302 | 0.50066 |  | 2090 | 8.28 | 32.4917 | 3 | 248.0302
2091 | 34.44 | 30.7701 | 229.9675 | 272.1206 | 0.49425 |  | 2091 | 7.43 | 30.7701 | 4 | 272.1206
2092 | 34.47 | 29.4814 | 40.1253 | 360.2874 | 0.48823 |  | 2092 | 6.5 | 29.4814 | 5 | 360.2874
2093 | 34.99 | 28.6769 | 104.7776 | 351.1899 | 0.49285 |  | 2093 | 5.27 | 28.6769 | 5.7321 | 351.1899
2094 | 38.04 | 28.5548 | 113.3938 | 401.588 | 0.50096 |  | 2094 | 6.28 | 28.5548 | 6 | 401.588
2095 | 45.56 | 42.1655 | 110.0938 | 413.2639 | 0.50752 |  | 2095 | 5.86 | 42.1655 | 5.7321 | 413.2639
2096 | 48.33 | 57.0435 | 96.7082 | 369.197 | 0.50742 |  | 2096 | 5.96 | 57.0435 | 5 | 369.197
2097 | 47.62 | 44.2575 | 103.2581 | 368.831 | 0.50357 |  | 2097 | 3.99 | 44.2575 | 4 | 368.831
2098 | 43.07 | 43.0884 | 133.6476 | 306.0818 | 0.49362 |  | 2098 | 23.77 | 43.0884 | 3 | 306.0818
2099 | 38.2 | 45.4071 | 91.6027 | 357.9015 | 0.48392 |  | 2099 | 21.53 | 45.4071 | 2.2679 | 357.9015
2100 | 34.49 | 47.7485 | 92.905 | 306.7251 | 0.4743 |  | 2100 | 20.28 | 47.7485 | 2 | 306.7251
2101 | 33.43 | 51.8167 | 130.6387 | 277.8511 | 0.46392 |  | 2101 | 23.99 | 51.8167 | 2.2679 | 277.8511
2102 | 32.87 | 52.2101 | 82.2781 | 274.1852 | 0.45659 |  | 2102 | 21.06 | 52.2101 | 3 | 274.1852
2103 | 32.4 | 58.5851 | 41.1339 | 274.2115 | 0.45633 |  | 2103 | 19.6 | 58.5851 | 4 | 274.2115
2104 | 33.13 | 74.3814 | 48.0511 | 259.8266 | 0.45729 |  | 2104 | 18.13 | 74.3814 | 5 | 259.8266
2105 | 36.01 | 99.3712 | 71.5199 | 329.1705 | 0.47655 |  | 2105 | 18.15 | 99.3712 | 5.7321 | 329.1705
2106 | 43.27 | 132.8651 | 82.6024 | 262.9928 | 0.49037 |  | 2106 | 17.17 | 132.8651 | 6 | 262.9928
2107 | 48.51 | 149.3479 | 127.9896 | 305.7264 | 0.49372 |  | 2107 | 19.7 | 149.3479 | 5.7321 | 305.7264
2108 | 49.07 | 141.8662 | 121.511 | 370 | 0.49904 |  | 2108 | 19.7 | 141.8662 | 5 | 370
2109 | 47.62 | 118.6747 | 133.1046 | 352.1746 | 0.49759 |  | 2109 | 22.51 | 118.6747 | 4 | 352.1746
2110 | 43.04 | 105.4673 | 127.7264 | 357.0526 | 0.48212 |  | 2110 | 24.94 | 105.4673 | 3 | 357.0526
2111 | 42.75 | 78.1817 | 108.5048 | 287.9475 | 0.48368 |  | 2111 | 20.01 | 78.1817 | 2.2679 | 287.9475
2112 | 39.32 | 39.3819 | 47.2228 | 294.1992 | 0.48614 |  | 2112 | 17.37 | 39.3819 | 2 | 294.1992
2113 | 37.49 | 35.651 | 49.1592 | 317.701 | 0.47355 |  | 2113 | 17.19 | 35.651 | 2.2679 | 317.701
2114 | 36.68 | 33.8478 | 70.8274 | 300.6625 | 0.46336 |  | 2114 | 17.03 | 33.8478 | 3 | 300.6625
2115 | 34.36 | 32.1649 | 77.9073 | 330.5159 | 0.45098 |  | 2115 | 15.16 | 32.1649 | 4 | 330.5159
2116 | 34.61 | 30.4867 | 27.068 | 386.1397 | 0.45333 |  | 2116 | 15.28 | 30.4867 | 5 | 386.1397
2117 | 34.9 | 29.143 | 36.8691 | 413.6517 | 0.4643 |  | 2117 | 8.3 | 29.143 | 5.7321 | 413.6517
2118 | 35.02 | 28.7842 | 32.2428 | 430.5721 | 0.46585 |  | 2118 | 13.49 | 28.7842 | 6 | 430.5721
2119 | 33.51 | 43.1508 | 23.7445 | 459.3896 | 0.4767 |  | 2119 | 25.35 | 43.1508 | 5.7321 | 459.3896
2120 | 36.89 | 61.2728 | 51.8104 | 385.7406 | 0.47715 |  | 2120 | 31.68 | 61.2728 | 5 | 385.7406
2121 | 37.1 | 43.6517 | 104.5738 | 340.4025 | 0.46777 |  | 2121 | 32.44 | 43.6517 | 4 | 340.4025
2122 | 33.17 | 42.4956 | 131.67 | 248.5391 | 0.44962 |  | 2122 | 41.19 | 42.4956 | 3 | 248.5391
2123 | 31.63 | 45.2211 | 74.2685 | 232.8632 | 0.43388 |  | 2123 | 39.41 | 45.2211 | 2.2679 | 232.8632
2124 | 33.5 | 46.4564 | 48.5033 | 263.9682 | 0.43118 |  | 2124 | 36.1 | 46.4564 | 2 | 263.9682
2125 | 34.7 | 47.9118 | 43.3064 | 235.0892 | 0.42894 |  | 2125 | 33.64 | 47.9118 | 2.2679 | 235.0892
2126 | 32.4 | 50.8291 | 45.3589 | 241.915 | 0.42777 |  | 2126 | 34.12 | 50.8291 | 3 | 241.915
2127 | 34.4 | 55.5978 | 31.1513 | 271.0027 | 0.43106 |  | 2127 | 32.19 | 55.5978 | 4 | 271.0027
2128 | 30.85 | 70.5354 | 49.2308 | 309.024 | 0.43078 |  | 2128 | 20.68 | 70.5354 | 5 | 309.024
2129 | 34.4 | 91.9457 | 42.887 | 254.5521 | 0.4423 |  | 2129 | 21.44 | 91.9457 | 5.7321 | 254.5521
2130 | 40.29 | 124.9489 | 46.8483 | 349.0814 | 0.45724 |  | 2130 | 22.44 | 124.9489 | 6 | 349.0814
2131 | 46.81 | 141.8202 | 240.7608 | 368.0662 | 0.46994 |  | 2131 | 30.14 | 141.8202 | 5.7321 | 368.0662
2132 | 46.62 | 133.2454 | 29.4714 | 338.8394 | 0.47577 |  | 2132 | 35.79 | 133.2454 | 5 | 338.8394
2133 | 43.08 | 120.1119 | 30.3076 | 294.8791 | 0.47554 |  | 2133 | 39.54 | 120.1119 | 4 | 294.8791
2134 | 40.53 | 108.5186 | 27.1001 | 296.1419 | 0.48658 |  | 2134 | 32.64 | 108.5186 | 3 | 296.1419
2135 | 40.86 | 78.6228 | 34.632 | 303.0557 | 0.47765 |  | 2135 | 28.89 | 78.6228 | 2.2679 | 303.0557
2136 | 36.85 | 40.7835 | 25.8187 | 253.1105 | 0.4654 |  | 2136 | 24.04 | 40.7835 | 2 | 253.1105
2137 | 40.1 | 32.4733 | 29.3839 | 289.8243 | 0.4565 |  | 2137 | 24.9 | 32.4733 | 2.2679 | 289.8243
2138 | 37.33 | 31.2374 | 27.2693 | 282.5176 | 0.46537 |  | 2138 | 22 | 31.2374 | 3 | 282.5176
2139 | 40.03 | 29.9004 | 23.1126 | 277.7441 | 0.44848 |  | 2139 | 20.87 | 29.9004 | 4 | 277.7441
2140 | 37.38 | 28.7376 | 34.5605 | 349.1409 | 0.42191 |  | 2140 | 19.92 | 28.7376 | 5 | 349.1409
2141 | 33.67 | 28.0605 | 38.4306 | 327.7447 | 0.42106 |  | 2141 | 20.18 | 28.0605 | 5.7321 | 327.7447
2142 | 32 | 28.0638 | 30.5288 | 413.8173 | 0.4196 |  | 2142 | 21.65 | 28.0638 | 6 | 413.8173
2143 | 33.98 | 42.9824 | 23.2885 | 369.1188 | 0.41154 |  | 2143 | 29.6 | 42.9824 | 5.7321 | 369.1188
2144 | 33.07 | 59.3809 | 38.6542 | 419.4626 | 0.40833 |  | 2144 | 30.17 | 59.3809 | 5 | 419.4626
2145 | 36.28 | 44.3619 | 40.0581 | 386.3836 | 0.40099 |  | 2145 | 27.39 | 44.3619 | 4 | 386.3836
2146 | 37.42 | 43.2481 | 44.9755 | 320.3932 | 0.39364 |  | 2146 | 32.73 | 43.2481 | 3 | 320.3932
2147 | 37.38 | 45.5896 | 46.5826 | 263.8867 | 0.3831 |  | 2147 | 26.53 | 45.5896 | 2.2679 | 263.8867
2148 | 25.15 | 48.9143 | 34.5203 | 236.5833 | 0.38399 |  | 2148 | 28.75 | 48.9143 | 2 | 236.5833
2149 | 30.8 | 51.5213 | 49.3426 | 210.8193 | 0.38447 |  | 2149 | 24.37 | 51.5213 | 2.2679 | 210.8193
2150 | 24.9 | 53.7815 | 59.3306 | 157.001 | 0.38155 |  | 2150 | 23.23 | 53.7815 | 3 | 157.001
2151 | 10.1 | 58.77 | 40.3649 | 175.1979 | 0.39669 |  | 2151 | 23 | 58.77 | 4 | 175.1979
2152 | 20.06 | 74.4192 | 46.7864 | 215.6475 | 0.3878 |  | 2152 | 22.73 | 74.4192 | 5 | 215.6475
2153 | 26.73 | 87.0518 | 34.6281 | 295.4202 | 0.39179 |  | 2153 | 25.64 | 87.0518 | 5.7321 | 295.4202
2154 | 33.97 | 126.0487 | 46.1327 | 326.2944 | 0.3867 |  | 2154 | 29.04 | 126.0487 | 6 | 326.2944
2155 | 38.69 | 132.512 | 241.7813 | 327.6389 | 0.40568 |  | 2155 | 31.9 | 132.512 | 5.7321 | 327.6389
2156 | 41.8 | 116.5637 | 28.7473 | 347.1666 | 0.41726 |  | 2156 | 37.42 | 116.5637 | 5 | 347.1666
2157 | 39.08 | 111.5684 | 26.5596 | 275.7633 | 0.41945 |  | 2157 | 37 | 111.5684 | 4 | 275.7633
2158 | 40.3 | 102.0739 | 30.6268 | 318.0493 | 0.40406 |  | 2158 | 34.81 | 102.0739 | 3 | 318.0493
2159 | 37.51 | 73.824 | 38.9492 | 301.2109 | 0.38575 |  | 2159 | 30.54 | 73.824 | 2.2679 | 301.2109
2160 | 31.06 | 37.2792 | 27.9538 | 283.9422 | 0.38105 |  | 2160 | 27.51 | 37.2792 | 2 | 283.9422
2161 | 29.96 | 32.3886 | 32.2826 | 266.2838 | 0.37386 |  | 2161 | 23.34 | 32.3886 | 2.2679 | 266.2838
2162 | 31.07 | 31.0289 | 28.1898 | 256.3256 | 0.37964 |  | 2162 | 22.27 | 31.0289 | 3 | 256.3256
2163 | 30.63 | 29.8212 | 24.0793 | 291.6609 | 0.38238 |  | 2163 | 21.5 | 29.8212 | 4 | 291.6609
2164 | 30.5 | 28.6713 | 21.2136 | 276.3822 | 0.38632 |  | 2164 | 21.11 | 28.6713 | 5 | 276.3822
2165 | 36.57 | 28.0383 | 28.362 | 301.5674 | 0.40592 |  | 2165 | 21.29 | 28.0383 | 5.7321 | 301.5674
2166 | 45.93 | 27.5814 | 23.776 | 406.872 | 0.43689 |  | 2166 | 22.86 | 27.5814 | 6 | 406.872
2167 | 55.56 | 27.3039 | 34.0159 | 383.1236 | 0.44782 |  | 2167 | 29.08 | 27.3039 | 5.7321 | 383.1236
2168 | 53.56 | 29.625 | 33.1535 | 342.5685 | 0.45801 |  | 2168 | 36.09 | 29.625 | 5 | 342.5685
2169 | 45.95 | 48.0095 | 52.5802 | 329.4464 | 0.46126 |  | 2169 | 40.96 | 48.0095 | 4 | 329.4464
2170 | 42.2 | 67.7097 | 25.6467 | 278.6507 | 0.46193 |  | 2170 | 36.46 | 67.7097 | 3 | 278.6507
2171 | 39.11 | 73.8965 | 42.7183 | 276.0365 | 0.45945 |  | 2171 | 34.64 | 73.8965 | 2.2679 | 276.0365
2172 | 34.3 | 76.7758 | 42.5212 | 212.4594 | 0.46303 |  | 2172 | 33.95 | 76.7758 | 2 | 212.4594
2173 | 32.29 | 76.3765 | 38.5622 | 236.091 | 0.45329 |  | 2173 | 30.03 | 76.3765 | 2.2679 | 236.091
2174 | 31.1 | 74.0638 | 37.7082 | 274.0512 | 0.4486 |  | 2174 | 30.03 | 74.0638 | 3 | 274.0512
2175 | 31.55 | 68.606 | 50.7431 | 234.1536 | 0.45081 |  | 2175 | 27.92 | 68.606 | 4 | 234.1536
2176 | 31.8 | 71.3635 | 35.9436 | 238.7292 | 0.46525 |  | 2176 | 25.12 | 71.3635 | 5 | 238.7292
2177 | 35.74 | 74.2771 | 53.2993 | 319.4487 | 0.48036 |  | 2177 | 24.73 | 74.2771 | 5.7321 | 319.4487
2178 | 43.94 | 106.8086 | 253.3833 | 385.1701 | 0.49058 |  | 2178 | 24.93 | 106.8086 | 6 | 385.1701
2179 | 45.1 | 137.2187 | 35.6051 | 357.7891 | 0.49678 |  | 2179 | 27.44 | 137.2187 | 5.7321 | 357.7891
2180 | 45.06 | 133.2233 | 35.8393 | 351.4523 | 0.49829 |  | 2180 | 31.07 | 133.2233 | 5 | 351.4523
2181 | 39.41 | 108.5691 | 29.5165 | 335.3093 | 0.49174 |  | 2181 | 31.99 | 108.5691 | 4 | 335.3093
2182 | 35.8 | 98.105 | 27.2136 | 342.375 | 0.48904 |  | 2182 | 25.65 | 98.105 | 3 | 342.375
2183 | 36.81 | 84.9128 | 21.835 | 315.988 | 0.48405 |  | 2183 | 25.4 | 84.9128 | 2.2679 | 315.988
2184 | 34.23 | 38.4147 | 30.8103 | 239.9092 | 0.47018 |  | 2184 | 23.22 | 38.4147 | 2 | 239.9092
2185 | 34 | 33.1913 | 26.4346 | 302.159 | 0.45502 |  | 2185 | 21.6 | 33.1913 | 2.2679 | 302.159
2186 | 35 | 31.7435 | 32.9183 | 284.0099 | 0.43368 |  | 2186 | 20.98 | 31.7435 | 3 | 284.0099
2187 | 30.9 | 30.3476 | 18.5639 | 334.7404 | 0.42806 |  | 2187 | 21.19 | 30.3476 | 4 | 334.7404
2188 | 30.9 | 29.0915 | 30.0732 | 321.7451 | 0.42131 |  | 2188 | 20.64 | 29.0915 | 5 | 321.7451
2189 | 31.04 | 28.215 | 26.4375 | 410.2211 | 0.44359 |  | 2189 | 21.13 | 28.215 | 5.7321 | 410.2211
2190 | 40.29 | 27.7407 | 24.7729 | 439.5848 | 0.45283 |  | 2190 | 21.78 | 27.7407 | 6 | 439.5848
2191 | 43.78 | 27.7521 | 22.0975 | 358.0836 | 0.46349 |  | 2191 | 29.73 | 27.7521 | 5.7321 | 358.0836
2192 | 45.58 | 30.4422 | 35.7067 | 381.0114 | 0.46724 |  | 2192 | 36.5 | 30.4422 | 5 | 381.0114
2193 | 49.11 | 50.0949 | 37.2552 | 411.4893 | 0.46868 |  | 2193 | 40.44 | 50.0949 | 4 | 411.4893
2194 | 50 | 69.304 | 47.3055 | 359.6775 | 0.46784 |  | 2194 | 38.1 | 69.304 | 3 | 359.6775
2195 | 39.97 | 79.9283 | 48.3753 | 289.2551 | 0.46498 |  | 2195 | 34.88 | 79.9283 | 2.2679 | 289.2551
2196 | 48.7 | 77.0262 | 35.2005 | 305.0614 | 0.45653 |  | 2196 | 31.3 | 77.0262 | 2 | 305.0614
2197 | 42.88 | 83.281 | 50.1484 | 262.3308 | 0.45315 |  | 2197 | 26.83 | 83.281 | 2.2679 | 262.3308
2198 | 39.02 | 82.2369 | 39.1395 | 221.2201 | 0.4481 |  | 2198 | 24.32 | 82.2369 | 3 | 221.2201
2199 | 37.66 | 79.5654 | 41.7908 | 250.7 | 0.44482 |  | 2199 | 24.07 | 79.5654 | 4 | 250.7
2200 | 35 | 81.0459 | 40.5847 | 223.9085 | 0.4586 |  | 2200 | 23 | 81.0459 | 5 | 223.9085
2201 | 35.08 | 79.5831 | 51.8021 | 285.5989 | 0.47234 |  | 2201 | 22.98 | 79.5831 | 5.7321 | 285.5989
2202 | 40.73 | 110.9747 | 29.2107 | 346.2511 | 0.48555 |  | 2202 | 24.95 | 110.9747 | 6 | 346.2511
2203 | 43.15 | 124.6842 | 39.8188 | 331.8694 | 0.4787 |  | 2203 | 31.99 | 124.6842 | 5.7321 | 331.8694
2204 | 42.74 | 139.2531 | 27.7327 | 370.1572 | 0.48963 |  | 2204 | 31.27 | 139.2531 | 5 | 370.1572
2205 | 38.2 | 117.8392 | 31.6073 | 325.9006 | 0.48648 |  | 2205 | 32.44 | 117.8392 | 4 | 325.9006
2206 | 35.08 | 102.0044 | 27.6616 | 367.5616 | 0.48481 |  | 2206 | 29.94 | 102.0044 | 3 | 367.5616
2207 | 31.01 | 86.8091 | 27.3696 | 305.5346 | 0.48601 |  | 2207 | 26.14 | 86.8091 | 2.2679 | 305.5346
2208 | 31.9 | 39.7764 | 33.2374 | 315.9745 | 0.47857 |  | 2208 | 26.55 | 39.7764 | 2 | 315.9745
2209 | 31.5 | 33.7167 | 32.9861 | 298.0485 | 0.45573 |  | 2209 | 21.82 | 33.7167 | 2.2679 | 298.0485
2210 | 31.08 | 32.326 | 28.9539 | 228.6517 | 0.4524 |  | 2210 | 21.31 | 32.326 | 3 | 228.6517
2211 | 31.19 | 30.9046 | 46.6139 | 295.7614 | 0.45859 |  | 2211 | 21.28 | 30.9046 | 4 | 295.7614
2212 | 32.57 | 29.5152 | 95.8814 | 351.5987 | 0.47687 |  | 2212 | 19.84 | 29.5152 | 5 | 351.5987
2213 | 35 | 28.5534 | 123.5004 | 382.3841 | 0.49375 |  | 2213 | 19.91 | 28.5534 | 5.7321 | 382.3841
2214 | 42.98 | 27.9161 | 116.6134 | 326.9063 | 0.50426 |  | 2214 | 20.09 | 27.9161 | 6 | 326.9063
2215 | 48.25 | 43.1901 | 130.1734 | 439.4567 | 0.50461 |  | 2215 | 21.52 | 43.1901 | 5.7321 | 439.4567
2216 | 52.42 | 60.0377 | 116.442 | 415.2838 | 0.50143 |  | 2216 | 22.29 | 60.0377 | 5 | 415.2838
2217 | 54.72 | 43.9081 | 112.679 | 396.9577 | 0.49897 |  | 2217 | 35.28 | 43.9081 | 4 | 396.9577
2218 | 49.47 | 41.7263 | 126.9689 | 333.9225 | 0.4974 |  | 2218 | 28.72 | 41.7263 | 3 | 333.9225
2219 | 47.87 | 42.5403 | 115.9563 | 292.8813 | 0.49257 |  | 2219 | 29 | 42.5403 | 2.2679 | 292.8813
2220 | 44.89 | 45.1047 | 123.7106 | 346.0344 | 0.48569 |  | 2220 | 23.03 | 45.1047 | 2 | 346.0344
2221 | 43.11 | 48.7064 | 72.7491 | 326.8187 | 0.48253 |  | 2221 | 20.42 | 48.7064 | 2.2679 | 326.8187
2222 | 41.77 | 52.1209 | 30.478 | 357.6583 | 0.48318 |  | 2222 | 21 | 52.1209 | 3 | 357.6583
2223 | 41.48 | 55.9152 | 232.8692 | 270.8457 | 0.48226 |  | 2223 | 20 | 55.9152 | 4 | 270.8457
2224 | 41.73 | 70.5659 | 50.9246 | 345.2788 | 0.48883 |  | 2224 | 19.7 | 70.5659 | 5 | 345.2788
2225 | 42.68 | 90.1841 | 37.2336 | 330.122 | 0.49595 |  | 2225 | 18.79 | 90.1841 | 5.7321 | 330.122
2226 | 45.44 | 134.5668 | 41.1381 | 395.5388 | 0.4983 |  | 2226 | 20.12 | 134.5668 | 6 | 395.5388
2227 | 51.32 | 145.4922 | 35.4527 | 357.5917 | 0.49686 |  | 2227 | 23.41 | 145.4922 | 5.7321 | 357.5917
2228 | 52.34 | 133.0512 | 34.5234 | 350.4615 | 0.49806 |  | 2228 | 28.2 | 133.0512 | 5 | 350.4615
2229 | 44.08 | 116.6982 | 32.6866 | 351.2264 | 0.49943 |  | 2229 | 30.43 | 116.6982 | 4 | 351.2264
2230 | 39.1 | 105.9856 | 30.9781 | 289.451 | 0.50016 |  | 2230 | 30.1 | 105.9856 | 3 | 289.451
2231 | 36.58 | 77.3051 | 32.3478 | 234.464 | 0.50084 |  | 2231 | 26.79 | 77.3051 | 2.2679 | 234.464
2232 | 35.6 | 39.173 | 29.6562 | 226.2212 | 0.49937 |  | 2232 | 23.14 | 39.173 | 2 | 226.2212
2233 | 35.02 | 32.9272 | 36.6968 | 282.4109 | 0.49252 |  | 2233 | 19.59 | 32.9272 | 2.2679 | 282.4109
2234 | 33 | 31.4982 | 33.0205 | 210.6974 | 0.48433 |  | 2234 | 18.07 | 31.4982 | 3 | 210.6974
2235 | 32.59 | 30.0646 | 33.309 | 271.309 | 0.48107 |  | 2235 | 17.5 | 30.0646 | 4 | 271.309
2236 | 34.13 | 28.9034 | 20.1257 | 258.6122 | 0.49162 |  | 2236 | 15.7 | 28.9034 | 5 | 258.6122
2237 | 36.86 | 28.1483 | 30.8564 | 299.6196 | 0.50557 |  | 2237 | 17.5 | 28.1483 | 5.7321 | 299.6196
2238 | 44.67 | 28.1246 | 47.7076 | 391.5852 | 0.50525 |  | 2238 | 17.81 | 28.1246 | 6 | 391.5852
2239 | 53.64 | 43.6059 | 247.8476 | 464.3691 | 0.50477 |  | 2239 | 13.32 | 43.6059 | 5.7321 | 464.3691
2240 | 59.86 | 59.5264 | 55.5066 | 389.5496 | 0.5116 |  | 2240 | 14.6 | 59.5264 | 5 | 389.5496
2241 | 47.5 | 44.055 | 48.1782 | 342.7552 | 0.51255 |  | 2241 | 17.48 | 44.055 | 4 | 342.7552
2242 | 55.76 | 42.6382 | 71.2078 | 348.7323 | 0.50984 |  | 2242 | 18.78 | 42.6382 | 3 | 348.7323
2243 | 50.15 | 46.9509 | 121.7947 | 274.5815 | 0.50698 |  | 2243 | 17.36 | 46.9509 | 2.2679 | 274.5815
2244 | 45 | 46.3056 | 93.3893 | 303.5745 | 0.50385 |  | 2244 | 17.98 | 46.3056 | 2 | 303.5745
2245 | 41.32 | 50.5346 | 45.2389 | 232.5361 | 0.5046 |  | 2245 | 17.99 | 50.5346 | 2.2679 | 232.5361
2246 | 38.59 | 50.8685 | 37.9067 | 269.2447 | 0.50569 |  | 2246 | 16.74 | 50.8685 | 3 | 269.2447
2247 | 38.3 | 56.8425 | 36.1322 | 282.8093 | 0.50538 |  | 2247 | 17.92 | 56.8425 | 4 | 282.8093
2248 | 38.1 | 74.1893 | 42.6163 | 280.0659 | 0.49816 |  | 2248 | 18.83 | 74.1893 | 5 | 280.0659
2249 | 40.08 | 94.0255 | 52.5267 | 272.3876 | 0.49867 |  | 2249 | 21.55 | 94.0255 | 5.7321 | 272.3876
2250 | 45.23 | 127.8254 | 54.3084 | 349.1336 | 0.49983 |  | 2250 | 23.28 | 127.8254 | 6 | 349.1336
2251 | 50.5 | 141.9182 | 45.9725 | 345.3884 | 0.50152 |  | 2251 | 29.76 | 141.9182 | 5.7321 | 345.3884
2252 | 48.93 | 112.5213 | 29.5584 | 359.6301 | 0.49909 |  | 2252 | 28.3 | 112.5213 | 5 | 359.6301
2253 | 43.81 | 109.8507 | 28.6757 | 325.5105 | 0.49837 |  | 2253 | 29.94 | 109.8507 | 4 | 325.5105
2254 | 38.47 | 105.2326 | 34.0943 | 309.6858 | 0.49803 |  | 2254 | 25.01 | 105.2326 | 3 | 309.6858
2255 | 36.8 | 74.194 | 20.8262 | 323.7235 | 0.49887 |  | 2255 | 24.32 | 74.194 | 2.2679 | 323.7235
2256 | 35.36 | 38.1977 | 28.4394 | 236.0228 | 0.50113 |  | 2256 | 20.9 | 38.1977 | 2 | 236.0228
2257 | 34.9 | 36.2653 | 28.9868 | 303.0125 | 0.49519 |  | 2257 | 21 | 36.2653 | 2.2679 | 303.0125
2258 | 34.49 | 34.2464 | 22.4855 | 217.2287 | 0.48783 |  | 2258 | 19.59 | 34.2464 | 3 | 217.2287
2259 | 33.76 | 32.2758 | 31.7433 | 287.2384 | 0.49199 |  | 2259 | 19.15 | 32.2758 | 4 | 287.2384
2260 | 36.17 | 30.472 | 36.3142 | 314.3009 | 0.50537 |  | 2260 | 18.75 | 30.472 | 5 | 314.3009
2261 | 38.53 | 29.3306 | 60.568 | 388.2746 | 0.50751 |  | 2261 | 18.72 | 29.3306 | 5.7321 | 388.2746
2262 | 44.84 | 29.0805 | 111.2129 | 434.4441 | 0.50758 |  | 2262 | 20.39 | 29.0805 | 6 | 434.4441
2263 | 52.04 | 43.7341 | 57.2827 | 480.1893 | 0.5041 |  | 2263 | 29.1 | 43.7341 | 5.7321 | 480.1893
2264 | 58.67 | 58.8063 | 91.4128 | 327.8014 | 0.50394 |  | 2264 | 34.19 | 58.8063 | 5 | 327.8014
2265 | 53.64 | 43.726 | 104.3029 | 245.4822 | 0.498 |  | 2265 | 35.42 | 43.726 | 4 | 245.4822
2266 | 46.58 | 41.9911 | 83.962 | 218.0676 | 0.49378 |  | 2266 | 32.44 | 41.9911 | 3 | 218.0676
2267 | 42.65 | 46.4684 | 47.0464 | 89.5068 | 0.48861 |  | 2267 | 29.62 | 46.4684 | 2.2679 | 89.5068
2268 | 39.9 | 47.3716 | 44.8454 | 91.3524 | 0.48741 |  | 2268 | 25.1 | 47.3716 | 2 | 91.3524
2269 | 39.72 | 48.4855 | 34.6798 | 67.5553 | 0.48856 |  | 2269 | 23.37 | 48.4855 | 2.2679 | 67.5553
2270 | 38.54 | 50.3245 | 42.8916 | 73.1634 | 0.4881 |  | 2270 | 23.83 | 50.3245 | 3 | 73.1634
2271 | 38.34 | 58.4757 | 43.6349 | 62.5775 | 0.48495 |  | 2271 | 23.21 | 58.4757 | 4 | 62.5775
2272 | 38.64 | 73.0539 | 39.8137 | 55.2398 | 0.48563 |  | 2272 | 23.68 | 73.0539 | 5 | 55.2398
2273 | 40.96 | 95.9249 | 39.7734 | 83.8828 | 0.48616 |  | 2273 | 27.44 | 95.9249 | 5.7321 | 83.8828
2274 | 44.35 | 131.0126 | 40.2237 | 91.3057 | 0.48613 |  | 2274 | 29.25 | 131.0126 | 6 | 91.3057
2275 | 47.23 | 142.7497 | 39.8185 | 139.6733 | 0.4867 |  | 2275 | 32.96 | 142.7497 | 5.7321 | 139.6733
2276 | 46.94 | 132.9097 | 32.7615 | 243.5394 | 0.48844 |  | 2276 | 35.05 | 132.9097 | 5 | 243.5394
2277 | 41.99 | 115.4793 | 230.1012 | 265.3651 | 0.49268 |  | 2277 | 36.1 | 115.4793 | 4 | 265.3651
2278 | 41.33 | 109.5934 | 23.5815 | 282.9854 | 0.5004 |  | 2278 | 35.6 | 109.5934 | 3 | 282.9854
2279 | 40.33 | 77.6438 | 31.6688 | 268.7944 | 0.50697 |  | 2279 | 30.3 | 77.6438 | 2.2679 | 268.7944
2280 | 41.65 | 41.7807 | 24.7377 | 333.4816 | 0.51835 |  | 2280 | 25.96 | 41.7807 | 2 | 333.4816
2281 | 39.86 | 36.2433 | 23.1437 | 259.003 | 0.52729 |  | 2281 | 21.39 | 36.2433 | 2.2679 | 259.003
2282 | 38.31 | 34.2709 | 24.685 | 278.3174 | 0.52736 |  | 2282 | 20.8 | 34.2709 | 3 | 278.3174
2283 | 36.1 | 32.3253 | 24.9693 | 267.5048 | 0.52559 |  | 2283 | 20.76 | 32.3253 | 4 | 267.5048
2284 | 36.13 | 30.668 | 25.5009 | 361.3051 | 0.52945 |  | 2284 | 20.31 | 30.668 | 5 | 361.3051
2285 | 37.27 | 29.4882 | 43.0031 | 319.9553 | 0.53097 |  | 2285 | 20.34 | 29.4882 | 5.7321 | 319.9553
2286 | 39.2 | 29.2167 | 90.0744 | 363.8564 | 0.52775 |  | 2286 | 21.79 | 29.2167 | 6 | 363.8564
2287 | 42.03 | 44.125 | 97.5382 | 350.9957 | 0.52437 |  | 2287 | 27.84 | 44.125 | 5.7321 | 350.9957
2288 | 44.06 | 57.9193 | 49.4252 | 382.705 | 0.5138 |  | 2288 | 32.76 | 57.9193 | 5 | 382.705
2289 | 46.51 | 44.6179 | 49.1478 | 335.4399 | 0.50928 |  | 2289 | 35.18 | 44.6179 | 4 | 335.4399
2290 | 42.72 | 43.971 | 241.6535 | 281.2251 | 0.50848 |  | 2290 | 34.92 | 43.971 | 3 | 281.2251
2291 | 40.91 | 46.7056 | 42.2617 | 255.1716 | 0.51132 |  | 2291 | 34.1 | 46.7056 | 2.2679 | 255.1716
2292 | 37.87 | 48.281 | 47.076 | 196.8314 | 0.51209 |  | 2292 | 32.93 | 48.281 | 2 | 196.8314
2293 | 37.89 | 54.2122 | 35.4137 | 156.6028 | 0.50683 |  | 2293 | 29.52 | 54.2122 | 2.2679 | 156.6028
2294 | 34.6 | 54.2882 | 46.5585 | 89.3053 | 0.50266 |  | 2294 | 26.58 | 54.2882 | 3 | 89.3053
2295 | 36.2 | 60.1633 | 38.9944 | 64.0202 | 0.49502 |  | 2295 | 24.74 | 60.1633 | 4 | 64.0202
2296 | 37.38 | 75.3573 | 48.735 | 60.7079 | 0.49399 |  | 2296 | 24.19 | 75.3573 | 5 | 60.7079
2297 | 38.6 | 94.7967 | 40.7964 | 72.4305 | 0.49989 |  | 2297 | 23.96 | 94.7967 | 5.7321 | 72.4305
2298 | 41.62 | 125.754 | 39.9117 | 135.2427 | 0.50664 |  | 2298 | 27.05 | 125.754 | 6 | 135.2427
2299 | 42.91 | 140.1262 | 43.5411 | 203.917 | 0.51037 |  | 2299 | 29.79 | 140.1262 | 5.7321 | 203.917
2300 | 65 | 134.3266 | 30.3588 | 288.9368 | 0.51374 |  | 2300 | 30.66 | 134.3266 | 5 | 288.9368
2301 | 47.4 | 118.6432 | 26.706 | 332.5472 | 0.5117 |  | 2301 | 30.04 | 118.6432 | 4 | 332.5472
2302 | 48 | 112.4281 | 54.4894 | 339.0303 | 0.51546 |  | 2302 | 28 | 112.4281 | 3 | 339.0303
2303 | 45.53 | 81.3013 | 131.0121 | 366.4643 | 0.51333 |  | 2303 | 25.32 | 81.3013 | 2.2679 | 366.4643
2304 | 41.78 | 42.3758 | 110.4621 | 328.9834 | 0.51788 |  | 2304 | 21.97 | 42.3758 | 2 | 328.9834
2305 | 38.63 | 33.9577 | 83.4088 | 384.9485 | 0.52865 |  | 2305 | 20 | 33.9577 | 2.2679 | 384.9485
2306 | 37.4 | 32.4884 | 47.8682 | 332.1074 | 0.53672 |  | 2306 | 19.2 | 32.4884 | 3 | 332.1074
2307 | 35.5 | 31.0261 | 27.0205 | 356.6574 | 0.52034 |  | 2307 | 19.06 | 31.0261 | 4 | 356.6574
2308 | 35.64 | 29.6882 | 33.4085 | 286.7599 | 0.50798 |  | 2308 | 18.95 | 29.6882 | 5 | 286.7599
2309 | 36.17 | 28.6051 | 27.5147 | 389.7427 | 0.52606 |  | 2309 | 19.02 | 28.6051 | 5.7321 | 389.7427
2310 | 36.69 | 28.5174 | 28.4989 | 405.4274 | 0.5457 |  | 2310 | 20 | 28.5174 | 6 | 405.4274
2311 | 39.43 | 42.715 | 25.4537 | 426.1426 | 0.54348 |  | 2311 | 24.33 | 42.715 | 5.7321 | 426.1426
2312 | 40.51 | 55.9073 | 35.6411 | 382.2423 | 0.54143 |  | 2312 | 32.97 | 55.9073 | 5 | 382.2423
2313 | 40.66 | 43.8898 | 72.9708 | 295.5952 | 0.5307 |  | 2313 | 34.28 | 43.8898 | 4 | 295.5952
2314 | 36.63 | 43.4287 | 131.2678 | 252.0498 | 0.51649 |  | 2314 | 28.46 | 43.4287 | 3 | 252.0498
2315 | 34.99 | 46.902 | 124.5748 | 277.3483 | 0.49761 |  | 2315 | 23.43 | 46.902 | 2.2679 | 277.3483
2316 | 34.68 | 47.5398 | 90.6592 | 245.9263 | 0.46524 |  | 2316 | 22.67 | 47.5398 | 2 | 245.9263
2317 | 31.5 | 50.1664 | 108.6676 | 189.2599 | 0.44964 |  | 2317 | 22.94 | 50.1664 | 2.2679 | 189.2599
2318 | 28.03 | 52.9406 | 64.3315 | 115.8004 | 0.44558 |  | 2318 | 21.4 | 52.9406 | 3 | 115.8004
2319 | 28.92 | 57.1438 | 84.1036 | 115.4444 | 0.45108 |  | 2319 | 22.74 | 57.1438 | 4 | 115.4444
2320 | 31.4 | 72.7827 | 46.5807 | 95.3906 | 0.45799 |  | 2320 | 20.88 | 72.7827 | 5 | 95.3906
2321 | 34.87 | 95.1259 | 45.4417 | 105.8796 | 0.48566 |  | 2321 | 21.37 | 95.1259 | 5.7321 | 105.8796
2322 | 42.9 | 123.5575 | 45.7615 | 167.5909 | 0.50956 |  | 2322 | 21.7 | 123.5575 | 6 | 167.5909
2323 | 46.65 | 140.9079 | 39.3742 | 225.5198 | 0.51916 |  | 2323 | 23.1 | 140.9079 | 5.7321 | 225.5198
2324 | 49.65 | 124.1867 | 25.5003 | 257.2319 | 0.52362 |  | 2324 | 26.71 | 124.1867 | 5 | 257.2319
2325 | 46.27 | 108.1145 | 29.4128 | 332.3177 | 0.51149 |  | 2325 | 28.26 | 108.1145 | 4 | 332.3177
2326 | 45.55 | 102.1238 | 28.8686 | 292.748 | 0.50603 |  | 2326 | 23.23 | 102.1238 | 3 | 292.748
2327 | 44.01 | 75.7928 | 32.1671 | 285.3424 | 0.50332 |  | 2327 | 21.06 | 75.7928 | 2.2679 | 285.3424
2328 | 38.84 | 39.6691 | 40.8928 | 322.4345 | 0.51348 |  | 2328 | 19.01 | 39.6691 | 2 | 322.4345
2329 | 37.7 | 34.1616 | 24.8095 | 317.4673 | 0.52126 |  | 2329 | 16.42 | 34.1616 | 2.2679 | 317.4673
2330 | 36.73 | 32.5989 | 41.294 | 278.7849 | 0.52651 |  | 2330 | 16 | 32.5989 | 3 | 278.7849
2331 | 36.3 | 30.9398 | 29.9235 | 391.8301 | 0.53917 |  | 2331 | 15.43 | 30.9398 | 4 | 391.8301
2332 | 37.2 | 29.5111 | 30.6357 | 365.9214 | 0.53925 |  | 2332 | 14.92 | 29.5111 | 5 | 365.9214
2333 | 41.6 | 28.5952 | 35.7296 | 455.759 | 0.52843 |  | 2333 | 13.49 | 28.5952 | 5.7321 | 455.759
2334 | 54.96 | 27.9681 | 21.7726 | 486.7797 | 0.51166 |  | 2334 | 17.37 | 27.9681 | 6 | 486.7797
2335 | 59.47 | 27.8366 | 21.8193 | 478.9336 | 0.50188 |  | 2335 | 22.62 | 27.8366 | 5.7321 | 478.9336
2336 | 60 | 30.1541 | 50.1134 | 394.3366 | 0.49764 |  | 2336 | 28.4 | 30.1541 | 5 | 394.3366
2337 | 58.62 | 48.7889 | 37.0913 | 305.3031 | 0.49612 |  | 2337 | 31.31 | 48.7889 | 4 | 305.3031
2338 | 49.1 | 69.0118 | 31.3352 | 282.9734 | 0.48515 |  | 2338 | 27.29 | 69.0118 | 3 | 282.9734
2339 | 44.4 | 75.4538 | 33.9102 | 199.9407 | 0.48126 |  | 2339 | 23.23 | 75.4538 | 2.2679 | 199.9407
2340 | 41 | 75.8499 | 36.4707 | 147.2122 | 0.47683 |  | 2340 | 22.17 | 75.8499 | 2 | 147.2122
2341 | 40.51 | 81.0652 | 36.7607 | 101.9387 | 0.47348 |  | 2341 | 29.3 | 81.0652 | 2.2679 | 101.9387
2342 | 39.25 | 79.459 | 54.8145 | 73.1515 | 0.47062 |  | 2342 | 26.67 | 79.459 | 3 | 73.1515
2343 | 40.17 | 76.0797 | 244.0418 | 68.6743 | 0.46888 |  | 2343 | 22.57 | 76.0797 | 4 | 68.6743
2344 | 39.73 | 78.7207 | 52.2409 | 53.6747 | 0.46646 |  | 2344 | 21.86 | 78.7207 | 5 | 53.6747
2345 | 42.84 | 80.9435 | 35.2419 | 85.7031 | 0.46307 |  | 2345 | 21.94 | 80.9435 | 5.7321 | 85.7031
2346 | 45.05 | 113.5032 | 43.3045 | 107.7847 | 0.4637 |  | 2346 | 22.73 | 113.5032 | 6 | 107.7847
2347 | 48.46 | 139.4811 | 26.9121 | 162.6619 | 0.46708 |  | 2347 | 28.59 | 139.4811 | 5.7321 | 162.6619
2348 | 46.58 | 126.5376 | 20.0163 | 191.033 | 0.46684 |  | 2348 | 31.11 | 126.5376 | 5 | 191.033
2349 | 43.78 | 110.4248 | 24.8923 | 196.9442 | 0.4668 |  | 2349 | 32.68 | 110.4248 | 4 | 196.9442
2350 | 42.37 | 102.2021 | 21.5522 | 171.0835 | 0.46529 |  | 2350 | 29.41 | 102.2021 | 3 | 171.0835
2351 | 37.44 | 88.2628 | 24.9351 | 171.3622 | 0.46555 |  | 2351 | 28.27 | 88.2628 | 2.2679 | 171.3622
2352 | 34.75 | 40.8877 | 30.6189 | 179.6837 | 0.4595 |  | 2352 | 23.54 | 40.8877 | 2 | 179.6837
2353 | 34.69 | 36.0766 | 26.6618 | 181.7148 | 0.44891 |  | 2353 | 23.39 | 36.0766 | 2.2679 | 181.7148
2354 | 35.6 | 34.1021 | 33.368 | 183.8469 | 0.43156 |  | 2354 | 21.69 | 34.1021 | 3 | 183.8469
2355 | 34.96 | 32.2228 | 30.4894 | 193.7259 | 0.42481 |  | 2355 | 21.18 | 32.2228 | 4 | 193.7259
2356 | 35.12 | 30.5028 | 31.2634 | 245.3353 | 0.43856 |  | 2356 | 20.52 | 30.5028 | 5 | 245.3353
2357 | 37.47 | 29.276 | 31.2964 | 329.2853 | 0.45149 |  | 2357 | 21.04 | 29.276 | 5.7321 | 329.2853
2358 | 47.2 | 28.5321 | 225.7896 | 364.1092 | 0.46056 |  | 2358 | 21.72 | 28.5321 | 6 | 364.1092
2359 | 52.08 | 28.1155 | 32.0331 | 391.8238 | 0.46311 |  | 2359 | 29.12 | 28.1155 | 5.7321 | 391.8238
2360 | 55.32 | 30.0592 | 55.3564 | 375.1597 | 0.45862 |  | 2360 | 35 | 30.0592 | 5 | 375.1597
2361 | 49.47 | 49.5336 | 63.7434 | 231.8228 | 0.43894 |  | 2361 | 38.2 | 49.5336 | 4 | 231.8228
2362 | 47.11 | 67.9783 | 55.5224 | 151.6484 | 0.43224 |  | 2362 | 37.55 | 67.9783 | 3 | 151.6484
2363 | 44.79 | 73.5253 | 37.6789 | 77.5493 | 0.43704 |  | 2363 | 34.22 | 73.5253 | 2.2679 | 77.5493
2364 | 41.77 | 77.7877 | 39.8337 | 64.0099 | 0.4334 |  | 2364 | 32.96 | 77.7877 | 2 | 64.0099
2365 | 40.94 | 81.3639 | 44.431 | 69.5812 | 0.4325 |  | 2365 | 29.74 | 81.3639 | 2.2679 | 69.5812
2366 | 39.59 | 80.1928 | 44.5212 | 55.0441 | 0.42869 |  | 2366 | 27.9 | 80.1928 | 3 | 55.0441
2367 | 37.38 | 74.9079 | 31.113 | 55.6044 | 0.42898 |  | 2367 | 26.36 | 74.9079 | 4 | 55.6044
2368 | 37.39 | 77.8895 | 50.5501 | 60.1486 | 0.43221 |  | 2368 | 24.66 | 77.8895 | 5 | 60.1486
2369 | 40.71 | 81.1851 | 52.232 | 88.5093 | 0.4334 |  | 2369 | 23.95 | 81.1851 | 5.7321 | 88.5093
2370 | 44.09 | 111.2113 | 77.9983 | 78.4497 | 0.43912 |  | 2370 | 27.03 | 111.2113 | 6 | 78.4497
2371 | 47.01 | 131.5634 | 74.0535 | 96.2393 | 0.43975 |  | 2371 | 29.58 | 131.5634 | 5.7321 | 96.2393
2372 | 45.94 | 150.0589 | 70.8004 | 101.6759 | 0.43951 |  | 2372 | 32.22 | 150.0589 | 5 | 101.6759
2373 | 42.76 | 119.1412 | 111.9604 | 98.8309 | 0.43578 |  | 2373 | 31.96 | 119.1412 | 4 | 98.8309
2374 | 42.01 | 105.8479 | 80.8167 | 74.7617 | 0.43654 |  | 2374 | 30.66 | 105.8479 | 3 | 74.7617
2375 | 39.07 | 91.2739 | 28.8989 | 50.0967 | 0.4401 |  | 2375 | 30.68 | 91.2739 | 2.2679 | 50.0967
2376 | 36.5 | 43.0794 | 36.5467 | 101.3466 | 0.44721 |  | 2376 | 29 | 43.0794 | 2 | 101.3466
2377 | 37.18 | 32.8553 | 22.9338 | 144.5441 | 0.451 |  | 2377 | 28.45 | 32.8553 | 2.2679 | 144.5441
2378 | 36.54 | 31.5115 | 34.6197 | 159.1846 | 0.45003 |  | 2378 | 24.18 | 31.5115 | 3 | 159.1846
2379 | 35.78 | 30.0896 | 31.9934 | 226.3084 | 0.43985 |  | 2379 | 23.28 | 30.0896 | 4 | 226.3084
2380 | 36.63 | 28.8295 | 33.8615 | 294.9475 | 0.45802 |  | 2380 | 21.84 | 28.8295 | 5 | 294.9475
2381 | 38.55 | 28.2208 | 28.1053 | 336.2837 | 0.47037 |  | 2381 | 21.46 | 28.2208 | 5.7321 | 336.2837
2382 | 46.99 | 28.0394 | 34.4314 | 347.1143 | 0.45685 |  | 2382 | 21.72 | 28.0394 | 6 | 347.1143
2383 | 54.43 | 43.5149 | 43.6092 | 407.5048 | 0.45294 |  | 2383 | 22.42 | 43.5149 | 5.7321 | 407.5048
2384 | 58.02 | 56.2308 | 82.0077 | 323.2345 | 0.44381 |  | 2384 | 23.42 | 56.2308 | 5 | 323.2345
2385 | 50.59 | 43.9761 | 68.6855 | 193.1479 | 0.43083 |  | 2385 | 27.21 | 43.9761 | 4 | 193.1479
2386 | 44.68 | 41.1068 | 54.6015 | 120.6102 | 0.42723 |  | 2386 | 25.12 | 41.1068 | 3 | 120.6102
2387 | 41.34 | 44.1161 | 102.4862 | 76.7219 | 0.4308 |  | 2387 | 24.49 | 44.1161 | 2.2679 | 76.7219
2388 | 36.5 | 46.0457 | 61.3371 | 88.3495 | 0.43238 |  | 2388 | 22.98 | 46.0457 | 2 | 88.3495
2389 | 37.41 | 46.5243 | 50.7133 | 75.6588 | 0.43789 |  | 2389 | 22.55 | 46.5243 | 2.2679 | 75.6588
2390 | 38.14 | 48.1089 | 51.7079 | 63.2802 | 0.43874 |  | 2390 | 21.5 | 48.1089 | 3 | 63.2802
2391 | 37.6 | 53.7901 | 52.7399 | 60.0527 | 0.44226 |  | 2391 | 19.94 | 53.7901 | 4 | 60.0527
2392 | 38.12 | 69.2611 | 46.8004 | 50.2689 | 0.43605 |  | 2392 | 20.35 | 69.2611 | 5 | 50.2689
2393 | 42.6 | 90.724 | 42.991 | 70.0035 | 0.43742 |  | 2393 | 20.3 | 90.724 | 5.7321 | 70.0035
2394 | 46.5 | 130.4955 | 49.1318 | 99.0005 | 0.44214 |  | 2394 | 22.27 | 130.4955 | 6 | 99.0005
2395 | 47.2 | 140.3245 | 47.9858 | 108.6538 | 0.44535 |  | 2395 | 26.91 | 140.3245 | 5.7321 | 108.6538
2396 | 46.97 | 124.4952 | 35.0971 | 119.3448 | 0.45548 |  | 2396 | 29.62 | 124.4952 | 5 | 119.3448
2397 | 44.56 | 111.5168 | 30.3096 | 74.4919 | 0.45863 |  | 2397 | 31.81 | 111.5168 | 4 | 74.4919
2398 | 42.6 | 103.2543 | 37.6852 | 73.6406 | 0.46223 |  | 2398 | 29.56 | 103.2543 | 3 | 73.6406
2399 | 39.23 | 74.6002 | 29.4385 | 55.5289 | 0.46335 |  | 2399 | 27.44 | 74.6002 | 2.2679 | 55.5289
2400 | 37.5 | 37.8848 | 23.708 | 25.32 | 0.45267 |  | 2400 | 24 | 37.8848 | 2 | 25.32
2401 | 37.07 | 34.4499 | 25.6287 | 35.5271 | 0.43991 |  | 2401 | 21.69 | 34.4499 | 2.2679 | 35.5271
2402 | 37.07 | 32.6727 | 23.7159 | 130.9067 | 0.43058 |  | 2402 | 20.84 | 32.6727 | 3 | 130.9067
2403 | 36.52 | 31.0302 | 25.3371 | 201.8351 | 0.43356 |  | 2403 | 20.38 | 31.0302 | 4 | 201.8351
2404 | 37.1 | 29.6859 | 31.0478 | 232.6697 | 0.44871 |  | 2404 | 18.96 | 29.6859 | 5 | 232.6697
2405 | 38.87 | 28.6762 | 71.1884 | 364.8745 | 0.46935 |  | 2405 | 19.02 | 28.6762 | 5.7321 | 364.8745
2406 | 47.91 | 28.485 | 87.2451 | 356.5405 | 0.48404 |  | 2406 | 18.88 | 28.485 | 6 | 356.5405
2407 | 56.4 | 42.9409 | 32.3268 | 416.8971 | 0.48876 |  | 2407 | 19.15 | 42.9409 | 5.7321 | 416.8971
2408 | 59.24 | 55.5051 | 57.8075 | 322.6337 | 0.49288 |  | 2408 | 19.19 | 55.5051 | 5 | 322.6337
2409 | 51.7 | 43.3803 | 38.887 | 256.1176 | 0.48485 |  | 2409 | 20.22 | 43.3803 | 4 | 256.1176
2410 | 48.55 | 42.1822 | 45.1295 | 133.754 | 0.4779 |  | 2410 | 20.97 | 42.1822 | 3 | 133.754
2411 | 45.98 | 44.8949 | 109.8033 | 88.7567 | 0.47634 |  | 2411 | 21.75 | 44.8949 | 2.2679 | 88.7567
2412 | 43.95 | 46.4084 | 97.4037 | 94.5924 | 0.48316 |  | 2412 | 21.75 | 46.4084 | 2 | 94.5924
2413 | 39.86 | 49.4456 | 54.9958 | 80.8794 | 0.4845 |  | 2413 | 19.94 | 49.4456 | 2.2679 | 80.8794
2414 | 38.9 | 50.804 | 49.9718 | 60.878 | 0.47901 |  | 2414 | 19.94 | 50.804 | 3 | 60.878
2415 | 39.28 | 57.6356 | 37.466 | 53.8611 | 0.47813 |  | 2415 | 19.39 | 57.6356 | 4 | 53.8611
2416 | 39 | 71.7628 | 38.856 | 53.1272 | 0.4755 |  | 2416 | 20.61 | 71.7628 | 5 | 53.1272
2417 | 43.92 | 92.1413 | 36.2409 | 71.1411 | 0.47299 |  | 2417 | 22.44 | 92.1413 | 5.7321 | 71.1411
2418 | 47.69 | 143.8443 | 39.7466 | 81.171 | 0.46889 |  | 2418 | 32.13 | 143.8443 | 6 | 81.171
2419 | 54.02 | 144.9916 | 43.168 | 120.1134 | 0.46806 |  | 2419 | 27.84 | 144.9916 | 5.7321 | 120.1134
2420 | 52.99 | 118.6519 | 24.0548 | 87.9216 | 0.46737 |  | 2420 | 23.2 | 118.6519 | 5 | 87.9216
2421 | 49.02 | 108.9675 | 24.5732 | 108.5111 | 0.47027 |  | 2421 | 34.94 | 108.9675 | 4 | 108.5111
2422 | 47.2 | 109.7227 | 30.5812 | 76.0229 | 0.47747 |  | 2422 | 23 | 109.7227 | 3 | 76.0229
2423 | 44.05 | 77.7235 | 25.1417 | 55.1574 | 0.48571 |  | 2423 | 21.84 | 77.7235 | 2.2679 | 55.1574
2424 | 39.59 | 39.069 | 29.0126 | 67.317 | 0.49147 |  | 2424 | 19.57 | 39.069 | 2 | 67.317
2425 | 39.01 | 32.754 | 237.7834 | 140.6676 | 0.48948 |  | 2425 | 19.38 | 32.754 | 2.2679 | 140.6676
2426 | 37.95 | 31.4627 | 30.311 | 190.2681 | 0.48533 |  | 2426 | 13.7 | 31.4627 | 3 | 190.2681
2427 | 37.22 | 30.166 | 223.4418 | 242.2359 | 0.48079 |  | 2427 | 12.81 | 30.166 | 4 | 242.2359
2428 | 37.5 | 28.9726 | 36.9463 | 244.9987 | 0.47724 |  | 2428 | 10.66 | 28.9726 | 5 | 244.9987
2429 | 41.05 | 28.1298 | 46.7813 | 292.2588 | 0.48148 |  | 2429 | 12.92 | 28.1298 | 5.7321 | 292.2588
2430 | 49.62 | 28.0265 | 99.3384 | 321.2035 | 0.47992 |  | 2430 | 18.18 | 28.0265 | 6 | 321.2035
2431 | 58.98 | 42.5517 | 98.0879 | 352.2236 | 0.47504 |  | 2431 | 25.49 | 42.5517 | 5.7321 | 352.2236
2432 | 60.08 | 57.1879 | 89.6524 | 299.5377 | 0.47309 |  | 2432 | 32 | 57.1879 | 5 | 299.5377
2433 | 51.55 | 43.7566 | 37.1638 | 237.2034 | 0.4666 |  | 2433 | 34.61 | 43.7566 | 4 | 237.2034
2434 | 48.97 | 41.6463 | 59.4843 | 225.1398 | 0.46073 |  | 2434 | 28.98 | 41.6463 | 3 | 225.1398
2435 | 46.99 | 44.3632 | 106.9633 | 172.8343 | 0.4611 |  | 2435 | 25.63 | 44.3632 | 2.2679 | 172.8343
2436 | 45.1 | 44.883 | 124.534 | 182.5343 | 0.46484 |  | 2436 | 24.71 | 44.883 | 2 | 182.5343
2437 | 44.11 | 49.2488 | 83.0109 | 171.6012 | 0.46172 |  | 2437 | 23.26 | 49.2488 | 2.2679 | 171.6012
2438 | 42.11 | 49.1333 | 55.6157 | 160.2103 | 0.45926 |  | 2438 | 22.87 | 49.1333 | 3 | 160.2103
2439 | 40.67 | 56.0714 | 34.0527 | 181.2835 | 0.45778 |  | 2439 | 22.12 | 56.0714 | 4 | 181.2835
2440 | 38.57 | 72.5276 | 43.1372 | 146.3791 | 0.45516 |  | 2440 | 21.83 | 72.5276 | 5 | 146.3791
2441 | 41.73 | 93.5446 | 45.6278 | 205.2448 | 0.45476 |  | 2441 | 22.11 | 93.5446 | 5.7321 | 205.2448
2442 | 46.43 | 134.0676 | 45.6317 | 189.2173 | 0.4574 |  | 2442 | 23.68 | 134.0676 | 6 | 189.2173
2443 | 48.43 | 148.5675 | 38.3372 | 226.8196 | 0.4585 |  | 2443 | 28.47 | 148.5675 | 5.7321 | 226.8196
2444 | 48.08 | 114.2836 | 31.047 | 219.4912 | 0.45499 |  | 2444 | 31.27 | 114.2836 | 5 | 219.4912
2445 | 45.36 | 109.5454 | 19.8084 | 228.1273 | 0.45576 |  | 2445 | 32.44 | 109.5454 | 4 | 228.1273
2446 | 45.27 | 107.3146 | 25.8036 | 207.6204 | 0.45417 |  | 2446 | 31.49 | 107.3146 | 3 | 207.6204
2447 | 43.27 | 74.7596 | 28.5413 | 165.9057 | 0.46504 |  | 2447 | 27.86 | 74.7596 | 2.2679 | 165.9057
2448 | 44.78 | 38.446 | 34.3987 | 177.7054 | 0.47443 |  | 2448 | 27.44 | 38.446 | 2 | 177.7054
2449 | 43.47 | 33.4327 | 29.4832 | 150.9885 | 0.4847 |  | 2449 | 22.9 | 33.4327 | 2.2679 | 150.9885
2450 | 42.36 | 31.9294 | 36.2673 | 151.7445 | 0.49642 |  | 2450 | 22.2 | 31.9294 | 3 | 151.7445
2451 | 40.11 | 30.5171 | 23.5957 | 176.5951 | 0.50176 |  | 2451 | 21.69 | 30.5171 | 4 | 176.5951
2452 | 39.45 | 29.2107 | 21.7174 | 208.2034 | 0.50923 |  | 2452 | 21.05 | 29.2107 | 5 | 208.2034
2453 | 40.93 | 28.4623 | 38.6022 | 270.1848 | 0.50874 |  | 2453 | 21.32 | 28.4623 | 5.7321 | 270.1848
2454 | 43.78 | 28.3366 | 34.6248 | 322.0986 | 0.51131 |  | 2454 | 22.15 | 28.3366 | 6 | 322.0986
2455 | 45.1 | 42.5508 | 82.4578 | 343.9192 | 0.50541 |  | 2455 | 28.98 | 42.5508 | 5.7321 | 343.9192
2456 | 47.28 | 55.572 | 79.1585 | 250.9342 | 0.48911 |  | 2456 | 36 | 55.572 | 5 | 250.9342
2457 | 46.96 | 44.5186 | 46.8254 | 242.2563 | 0.47293 |  | 2457 | 38.94 | 44.5186 | 4 | 242.2563
2458 | 42.45 | 44.3668 | 54.5313 | 158.7355 | 0.46007 |  | 2458 | 37.6 | 44.3668 | 3 | 158.7355
2459 | 39.85 | 47.1124 | 49.0517 | 117.2806 | 0.44576 |  | 2459 | 34.25 | 47.1124 | 2.2679 | 117.2806
2460 | 38.57 | 49.4595 | 57.755 | 87.7591 | 0.42509 |  | 2460 | 34 | 49.4595 | 2 | 87.7591
2461 | 38.02 | 52.5131 | 40.7614 | 69.8149 | 0.40589 |  | 2461 | 27.97 | 52.5131 | 2.2679 | 69.8149
2462 | 37.11 | 55.5874 | 53.0703 | 75.2224 | 0.39516 |  | 2462 | 26.41 | 55.5874 | 3 | 75.2224
2463 | 36.42 | 62.1111 | 56.93 | 53.1397 | 0.39186 |  | 2463 | 24.94 | 62.1111 | 4 | 53.1397
2464 | 35.65 | 76.1507 | 54.1174 | 66.5488 | 0.38908 |  | 2464 | 30.01 | 76.1507 | 5 | 66.5488
2465 | 37.83 | 97.6547 | 44.0496 | 78.3462 | 0.40451 |  | 2465 | 32.44 | 97.6547 | 5.7321 | 78.3462
2466 | 43.03 | 132.9083 | 48.7104 | 75.4468 | 0.43317 |  | 2466 | 26.97 | 132.9083 | 6 | 75.4468
2467 | 46.09 | 158.9838 | 39.3939 | 90.1912 | 0.45769 |  | 2467 | 31 | 158.9838 | 5.7321 | 90.1912
2468 | 46.28 | 123.7858 | 29.1357 | 95.0103 | 0.4617 |  | 2468 | 34.07 | 123.7858 | 5 | 95.0103
2469 | 45.57 | 111.9781 | 31.2682 | 113.6489 | 0.46126 |  | 2469 | 34.36 | 111.9781 | 4 | 113.6489
2470 | 45.04 | 110.6273 | 29.6909 | 179.8472 | 0.45955 |  | 2470 | 32.24 | 110.6273 | 3 | 179.8472
2471 | 44.64 | 79.6964 | 27.4234 | 198.2674 | 0.46656 |  | 2471 | 30 | 79.6964 | 2.2679 | 198.2674
2472 | 39.6 | 39.1235 | 28.8353 | 209.5325 | 0.46872 |  | 2472 | 24.61 | 39.1235 | 2 | 209.5325
2473 | 40 | 33.0974 | 29.1477 | 191.8847 | 0.4602 |  | 2473 | 22.93 | 33.0974 | 2.2679 | 191.8847
2474 | 39.7 | 31.4909 | 30.5527 | 184.4744 | 0.46673 |  | 2474 | 21.68 | 31.4909 | 3 | 184.4744
2475 | 36.61 | 30.0848 | 35.0441 | 196.463 | 0.4661 |  | 2475 | 21.68 | 30.0848 | 4 | 196.463
2476 | 37.23 | 28.8671 | 23.0923 | 218.4321 | 0.47173 |  | 2476 | 21.41 | 28.8671 | 5 | 218.4321
2477 | 39.7 | 28.1974 | 32.8738 | 298.4824 | 0.4788 |  | 2477 | 21.71 | 28.1974 | 5.7321 | 298.4824
2478 | 37.36 | 28.0743 | 29.8721 | 283.206 | 0.46514 |  | 2478 | 22.77 | 28.0743 | 6 | 283.206
2479 | 38.18 | 41.7622 | 33.2339 | 357.3548 | 0.46021 |  | 2479 | 30.49 | 41.7622 | 5.7321 | 357.3548
2480 | 40.36 | 54.3708 | 41.1658 | 291.0036 | 0.46354 |  | 2480 | 34.99 | 54.3708 | 5 | 291.0036
2481 | 39.76 | 44.4133 | 50.5666 | 299.648 | 0.46268 |  | 2481 | 39.41 | 44.4133 | 4 | 299.648
2482 | 37.1 | 43.4897 | 45.8236 | 241.6871 | 0.46103 |  | 2482 | 35.06 | 43.4897 | 3 | 241.6871
2483 | 39.6 | 46.037 | 57.7658 | 216.4181 | 0.44871 |  | 2483 | 33.23 | 46.037 | 2.2679 | 216.4181
2484 | 35 | 47.7125 | 45.164 | 119.0923 | 0.45296 |  | 2484 | 31.94 | 47.7125 | 2 | 119.0923
2485 | 39.1 | 51.7903 | 40.409 | 76.438 | 0.43902 |  | 2485 | 28.9 | 51.7903 | 2.2679 | 76.438
2486 | 35 | 52.135 | 36.1296 | 63.7606 | 0.43678 |  | 2486 | 27.01 | 52.135 | 3 | 63.7606
2487 | 40.23 | 60.0183 | 48.3022 | 60.1128 | 0.42711 |  | 2487 | 25.96 | 60.0183 | 4 | 60.1128
2488 | 39.7 | 75.6457 | 45.0692 | 71.5819 | 0.43991 |  | 2488 | 26 | 75.6457 | 5 | 71.5819
2489 | 35.5 | 94.5413 | 48.3344 | 68.9417 | 0.44774 |  | 2489 | 26.03 | 94.5413 | 5.7321 | 68.9417
2490 | 41.87 | 122.2296 | 21.8228 | 109.7921 | 0.46073 |  | 2490 | 27.91 | 122.2296 | 6 | 109.7921
2491 | 44.7 | 145.3089 | 37.1682 | 125.4188 | 0.47475 |  | 2491 | 31.27 | 145.3089 | 5.7321 | 125.4188
2492 | 46.74 | 127.4994 | 25.8092 | 95.2219 | 0.47143 |  | 2492 | 33 | 127.4994 | 5 | 95.2219
2493 | 43.28 | 107.9273 | 224.5988 | 75.5982 | 0.46909 |  | 2493 | 33.37 | 107.9273 | 4 | 75.5982
2494 | 46.18 | 103.9714 | 29.9883 | 80.2662 | 0.47189 |  | 2494 | 31.31 | 103.9714 | 3 | 80.2662
2495 | 45.1 | 74.4477 | 23.9003 | 118.389 | 0.48062 |  | 2495 | 28 | 74.4477 | 2.2679 | 118.389
2496 | 45.64 | 38.3484 | 39.3494 | 135.4924 | 0.49354 |  | 2496 | 26 | 38.3484 | 2 | 135.4924
2497 | 41.61 | 33.9082 | 30.1971 | 189.4141 | 0.50159 |  | 2497 | 23.36 | 33.9082 | 2.2679 | 189.4141
2498 | 40.72 | 32.5077 | 25.9938 | 198.6934 | 0.5068 |  | 2498 | 21.93 | 32.5077 | 3 | 198.6934
2499 | 38.9 | 31.0142 | 30.267 | 219.0989 | 0.50333 |  | 2499 | 21.18 | 31.0142 | 4 | 219.0989
2500 | 37.99 | 29.6204 | 28.3972 | 213.5328 | 0.48977 |  | 2500 | 20.94 | 29.6204 | 5 | 213.5328
2501 | 42.6 | 28.5331 | 30.3701 | 281.4644 | 0.48156 |  | 2501 | 21.06 | 28.5331 | 5.7321 | 281.4644
2502 | 50.23 | 27.815 | 38.3005 | 315.3012 | 0.47178 |  | 2502 | 21.74 | 27.815 | 6 | 315.3012
2503 | 58.76 | 27.3846 | 48.6458 | 341.1993 | 0.46345 |  | 2503 | 27 | 27.3846 | 5.7321 | 341.1993
2504 | 61.86 | 29.68 | 53.3945 | 315.3849 | 0.46184 |  | 2504 | 32.03 | 29.68 | 5 | 315.3849
2505 | 54.84 | 48.0091 | 33.3378 | 249.9455 | 0.45764 |  | 2505 | 37.28 | 48.0091 | 4 | 249.9455
2506 | 46 | 67.0369 | 48.1086 | 197.6293 | 0.45162 |  | 2506 | 34.59 | 67.0369 | 3 | 197.6293
2507 | 41.25 | 72.7258 | 48.8877 | 81.8367 | 0.4512 |  | 2507 | 30.91 | 72.7258 | 2.2679 | 81.8367
2508 | 35.9 | 72.9768 | 246.6632 | 65.5904 | 0.4403 |  | 2508 | 28.08 | 72.9768 | 2 | 65.5904
2509 | 36.5 | 77.6177 | 29.8429 | 80.9573 | 0.41829 |  | 2509 | 26.4 | 77.6177 | 2.2679 | 80.9573
2510 | 39 | 73.2704 | 54.1599 | 68.2904 | 0.40022 |  | 2510 | 25.05 | 73.2704 | 3 | 68.2904
2511 | 37.26 | 70.5341 | 41.3008 | 59.3314 | 0.38715 |  | 2511 | 23.83 | 70.5341 | 4 | 59.3314
2512 | 36.66 | 72.768 | 41.9413 | 72.5139 | 0.39779 |  | 2512 | 23.44 | 72.768 | 5 | 72.5139
2513 | 40.96 | 76.2167 | 35.1935 | 87.4475 | 0.41382 |  | 2513 | 23.22 | 76.2167 | 5.7321 | 87.4475
2514 | 47.01 | 116.8101 | 39.1245 | 101.2527 | 0.42827 |  | 2514 | 24.2 | 116.8101 | 6 | 101.2527
2515 | 49.27 | 145.3101 | 47.6156 | 85.4163 | 0.43287 |  | 2515 | 27.25 | 145.3101 | 5.7321 | 85.4163
2516 | 48.56 | 126.786 | 31.5275 | 113.8431 | 0.42851 |  | 2516 | 31.72 | 126.786 | 5 | 113.8431
2517 | 45.7 | 105.2169 | 22.653 | 85.0941 | 0.42395 |  | 2517 | 31.78 | 105.2169 | 4 | 85.0941
2518 | 42.43 | 98.7315 | 30.235 | 82.7493 | 0.42049 |  | 2518 | 31.53 | 98.7315 | 3 | 82.7493
2519 | 36.6 | 86.9677 | 27.1721 | 43.6895 | 0.40782 |  | 2519 | 28.33 | 86.9677 | 2.2679 | 43.6895
2520 | 36.8 | 40.6461 | 34.8835 | 31.0867 | 0.39554 |  | 2520 | 24.94 | 40.6461 | 2 | 31.0867
2521 | 35.81 | 35.3165 | 24.8109 | 29.601 | 0.37768 |  | 2521 | 22.1 | 35.3165 | 2.2679 | 29.601
2522 | 36.66 | 33.6157 | 33.2945 | 7.6246 | 0.37954 |  | 2522 | 21.31 | 33.6157 | 3 | 7.6246
2523 | 36.03 | 31.8594 | 76.8946 | 20.1843 | 0.38124 |  | 2523 | 20.45 | 31.8594 | 4 | 20.1843
2524 | 35.06 | 30.2013 | 116.3982 | 42.6264 | 0.39529 |  | 2524 | 20.14 | 30.2013 | 5 | 42.6264
2525 | 37.42 | 29.0721 | 94.3791 | 130.2046 | 0.41862 |  | 2525 | 20.34 | 29.0721 | 5.7321 | 130.2046
2526 | 46.22 | 28.249 | 95.381 | 239.8139 | 0.43688 |  | 2526 | 21.08 | 28.249 | 6 | 239.8139
2527 | 52.06 | 27.6252 | 96.1956 | 224.8526 | 0.4401 |  | 2527 | 25 | 27.6252 | 5.7321 | 224.8526
2528 | 52.16 | 29.8548 | 105.7974 | 247.6066 | 0.44028 |  | 2528 | 31.69 | 29.8548 | 5 | 247.6066
2529 | 46.62 | 49.066 | 117.395 | 116.2038 | 0.43695 |  | 2529 | 34.7 | 49.066 | 4 | 116.2038
2530 | 40.72 | 66.8485 | 94.9888 | 83.3477 | 0.42525 |  | 2530 | 36.79 | 66.8485 | 3 | 83.3477
2531 | 36.4 | 73.3801 | 81.1987 | 83.7923 | 0.40921 |  | 2531 | 30.98 | 73.3801 | 2.2679 | 83.7923
2532 | 35.4 | 73.1502 | 131.3214 | 89.851 | 0.39479 |  | 2532 | 30 | 73.1502 | 2 | 89.851
2533 | 35.79 | 79.2095 | 147.9199 | 79.7106 | 0.38831 |  | 2533 | 28 | 79.2095 | 2.2679 | 79.7106
2534 | 35.6 | 77.8822 | 107.8365 | 64.241 | 0.39918 |  | 2534 | 29.94 | 77.8822 | 3 | 64.241
2535 | 36.87 | 76.5548 | 34.4729 | 52.8993 | 0.41799 |  | 2535 | 24.04 | 76.5548 | 4 | 52.8993
2536 | 39.28 | 75.5147 | 47.5199 | 51.2009 | 0.4368 |  | 2536 | 22.61 | 75.5147 | 5 | 51.2009
2537 | 44.5 | 78.6878 | 56.7185 | 70.9894 | 0.44926 |  | 2537 | 22.46 | 78.6878 | 5.7321 | 70.9894
2538 | 49.74 | 111.9242 | 37.2309 | 111.2935 | 0.45536 |  | 2538 | 22.87 | 111.9242 | 6 | 111.2935
2539 | 52.95 | 129.7364 | 49.7598 | 112.2615 | 0.45529 |  | 2539 | 23.77 | 129.7364 | 5.7321 | 112.2615
2540 | 50.32 | 138.6742 | 27.588 | 123.5769 | 0.45346 |  | 2540 | 26.34 | 138.6742 | 5 | 123.5769
2541 | 47.94 | 114.7209 | 28.3881 | 75.967 | 0.45205 |  | 2541 | 33.14 | 114.7209 | 4 | 75.967
2542 | 43.9 | 104.7211 | 35.7501 | 65.0223 | 0.45095 |  | 2542 | 29 | 104.7211 | 3 | 65.0223
2543 | 38.8 | 91.4811 | 24.4065 | 54.3217 | 0.44877 |  | 2543 | 25 | 91.4811 | 2.2679 | 54.3217
2544 | 33.5 | 41.8549 | 23.8449 | 28.8336 | 0.442 |  | 2544 | 24.69 | 41.8549 | 2 | 28.8336
2545 | 33.7 | 34.6583 | 30.7341 | 33.4398 | 0.44344 |  | 2545 | 21.3 | 34.6583 | 2.2679 | 33.4398
2546 | 35.02 | 33.0135 | 29.3453 | 6.3038 | 0.43557 |  | 2546 | 19.7 | 33.0135 | 3 | 6.3038
2547 | 35.02 | 31.319 | 33.1973 | 21.0097 | 0.43122 |  | 2547 | 19.24 | 31.319 | 4 | 21.0097
2548 | 35.36 | 29.9052 | 41.7012 | 53.6131 | 0.44368 |  | 2548 | 18.28 | 29.9052 | 5 | 53.6131
2549 | 37.94 | 28.775 | 73.4936 | 76.5069 | 0.45947 |  | 2549 | 17.19 | 28.775 | 5.7321 | 76.5069
2550 | 46.82 | 28.2061 | 98.9362 | 133.1482 | 0.47634 |  | 2550 | 18.76 | 28.2061 | 6 | 133.1482
2551 | 50.43 | 41.7779 | 104.2478 | 151.4254 | 0.4798 |  | 2551 | 19.46 | 41.7779 | 5.7321 | 151.4254
2552 | 52.23 | 55.837 | 95.6681 | 154.7016 | 0.47804 |  | 2552 | 19.54 | 55.837 | 5 | 154.7016
2553 | 50.4 | 43.3716 | 92.899 | 110.8966 | 0.47448 |  | 2553 | 21.14 | 43.3716 | 4 | 110.8966
2554 | 48.01 | 41.1582 | 108.2684 | 79.9622 | 0.47483 |  | 2554 | 21.64 | 41.1582 | 3 | 79.9622
2555 | 46.05 | 43.3777 | 131.0829 | 78.6023 | 0.47548 |  | 2555 | 20.67 | 43.3777 | 2.2679 | 78.6023
2556 | 45.37 | 44.7721 | 134.0955 | 75.3895 | 0.46297 |  | 2556 | 20.56 | 44.7721 | 2 | 75.3895
2557 | 41.89 | 48.7787 | 147.7369 | 69.1916 | 0.45912 |  | 2557 | 20.23 | 48.7787 | 2.2679 | 69.1916
2558 | 36.12 | 49.7109 | 101.6878 | 72.6143 | 0.45093 |  | 2558 | 19.91 | 49.7109 | 3 | 72.6143
2559 | 35.05 | 53.9214 | 78.1193 | 51.3364 | 0.4483 |  | 2559 | 19.72 | 53.9214 | 4 | 51.3364
2560 | 35.49 | 70.6345 | 46.9968 | 57.601 | 0.45322 |  | 2560 | 19.51 | 70.6345 | 5 | 57.601
2561 | 38.73 | 93.8961 | 237.6966 | 84.4137 | 0.46409 |  | 2561 | 19.94 | 93.8961 | 5.7321 | 84.4137
2562 | 46.09 | 137.2407 | 49.8575 | 111.2935 | 0.46825 |  | 2562 | 20.12 | 137.2407 | 6 | 111.2935
2563 | 49.49 | 159.9808 | 47.3336 | 94.1171 | 0.47057 |  | 2563 | 21.52 | 159.9808 | 5.7321 | 94.1171
2564 | 48.09 | 125.4874 | 24.4986 | 84.6417 | 0.47422 |  | 2564 | 22.05 | 125.4874 | 5 | 84.6417
2565 | 44.83 | 112.9473 | 24.0518 | 96.987 | 0.47457 |  | 2565 | 23.7 | 112.9473 | 4 | 96.987
2566 | 41.03 | 108.7064 | 25.7981 | 75.8827 | 0.46809 |  | 2566 | 24.31 | 108.7064 | 3 | 75.8827
2567 | 37.29 | 76.7936 | 26.153 | 45.4538 | 0.45437 |  | 2567 | 23.94 | 76.7936 | 2.2679 | 45.4538
2568 | 37.93 | 39.9269 | 23.2091 | 22.6914 | 0.43825 |  | 2568 | 21.7 | 39.9269 | 2 | 22.6914
2569 | 37.3 | 34.7507 | 26.5265 | 28.3783 | 0.42547 |  | 2569 | 19.33 | 34.7507 | 2.2679 | 28.3783
2570 | 37.24 | 33.0589 | 32.6301 | 6.1507 | 0.42364 |  | 2570 | 17.74 | 33.0589 | 3 | 6.1507
2571 | 35.02 | 31.3879 | 41.3332 | 16.3518 | 0.43075 |  | 2571 | 15.85 | 31.3879 | 4 | 16.3518
2572 | 35.06 | 29.7994 | 35.22 | 48.4734 | 0.43561 |  | 2572 | 15.13 | 29.7994 | 5 | 48.4734
2573 | 38.07 | 28.9198 | 84.1796 | 75.7136 | 0.44003 |  | 2573 | 15.15 | 28.9198 | 5.7321 | 75.7136
2574 | 47.82 | 28.627 | 73.7574 | 127.7503 | 0.44837 |  | 2574 | 14.57 | 28.627 | 6 | 127.7503
2575 | 51.95 | 43.5412 | 84.5468 | 143.0537 | 0.45254 |  | 2575 | 14.88 | 43.5412 | 5.7321 | 143.0537
2576 | 58.61 | 55.2499 | 98.5812 | 114.7872 | 0.45235 |  | 2576 | 16.4 | 55.2499 | 5 | 114.7872
2577 | 49.93 | 43.9025 | 100.9695 | 99.6823 | 0.44989 |  | 2577 | 17.56 | 43.9025 | 4 | 99.6823
2578 | 44.57 | 42.7208 | 91.9812 | 87.4586 | 0.45012 |  | 2578 | 18.69 | 42.7208 | 3 | 87.4586
2579 | 40.39 | 45.3381 | 142.905 | 86.3497 | 0.44399 |  | 2579 | 18.69 | 45.3381 | 2.2679 | 86.3497
2580 | 37.79 | 48.5342 | 127.3182 | 93.4861 | 0.43063 |  | 2580 | 18.94 | 48.5342 | 2 | 93.4861
2581 | 37.4 | 51.4986 | 133.8038 | 68.6462 | 0.41406 |  | 2581 | 19.94 | 51.4986 | 2.2679 | 68.6462
2582 | 36 | 52.5093 | 128.4236 | 74.9479 | 0.40395 |  | 2582 | 19.91 | 52.5093 | 3 | 74.9479
2583 | 35 | 59.8436 | 70.0565 | 49.9538 | 0.40106 |  | 2583 | 19.55 | 59.8436 | 4 | 49.9538
2584 | 35 | 75.7518 | 45.0743 | 60.9564 | 0.39989 |  | 2584 | 18.41 | 75.7518 | 5 | 60.9564
2585 | 39.4 | 94.8494 | 44.8688 | 88.3576 | 0.40365 |  | 2585 | 17.58 | 94.8494 | 5.7321 | 88.3576
2586 | 45.09 | 129.1156 | 41.8293 | 98.8128 | 0.41394 |  | 2586 | 18.2 | 129.1156 | 6 | 98.8128
2587 | 49.31 | 150.4483 | 40.3717 | 94.3293 | 0.42434 |  | 2587 | 19.95 | 150.4483 | 5.7321 | 94.3293
2588 | 48.19 | 120.7562 | 25.5982 | 96.4915 | 0.42132 |  | 2588 | 21.19 | 120.7562 | 5 | 96.4915
2589 | 45.81 | 109.0372 | 227.202 | 97.0792 | 0.41889 |  | 2589 | 26.4 | 109.0372 | 4 | 97.0792
2590 | 43.19 | 107.9039 | 37.888 | 81.9085 | 0.4145 |  | 2590 | 29.65 | 107.9039 | 3 | 81.9085
2591 | 41.65 | 79.3841 | 25.6795 | 45.1288 | 0.40824 |  | 2591 | 30.16 | 79.3841 | 2.2679 | 45.1288
2592 | 40.29 | 41.0804 | 23.3622 | 23.657 | 0.3991 |  | 2592 | 27.25 | 41.0804 | 2 | 23.657
2593 | 40.28 | 35.3517 | 21.3957 | 32.473 | 0.38501 |  | 2593 | 30.15 | 35.3517 | 2.2679 | 32.473
2594 | 36.7 | 33.4948 | 28.451 | 5.2766 | 0.37669 |  | 2594 | 20.9 | 33.4948 | 3 | 5.2766
2595 | 34.1 | 31.7494 | 29.2376 | 16.1749 | 0.37163 |  | 2595 | 19.7 | 31.7494 | 4 | 16.1749
2596 | 32.07 | 30.353 | 23.5652 | 55.4992 | 0.3798 |  | 2596 | 18.9 | 30.353 | 5 | 55.4992
2597 | 34.9 | 29.1878 | 35.8353 | 72.8049 | 0.39027 |  | 2597 | 19 | 29.1878 | 5.7321 | 72.8049
2598 | 40.34 | 28.6568 | 62.4589 | 129.5496 | 0.4078 |  | 2598 | 20.6 | 28.6568 | 6 | 129.5496
2599 | 42.97 | 41.3027 | 111.6206 | 163.1752 | 0.43369 |  | 2599 | 30 | 41.3027 | 5.7321 | 163.1752
2600 | 49.36 | 55.2584 | 118.0028 | 137.4232 | 0.441 |  | 2600 | 37.06 | 55.2584 | 5 | 137.4232
2601 | 44.49 | 43.8495 | 82.5103 | 107.9892 | 0.4394 |  | 2601 | 38.99 | 43.8495 | 4 | 107.9892
2602 | 41.59 | 42.2097 | 30.8706 | 86.1689 | 0.43943 |  | 2602 | 32.99 | 42.2097 | 3 | 86.1689
2603 | 41.39 | 44.653 | 61.2979 | 81.3854 | 0.44006 |  | 2603 | 29 | 44.653 | 2.2679 | 81.3854
2604 | 42.3 | 47.3011 | 96.6345 | 86.3739 | 0.43003 |  | 2604 | 27.44 | 47.3011 | 2 | 86.3739
2605 | 41.51 | 48.3628 | 102.3534 | 85.5545 | 0.41812 |  | 2605 | 24.94 | 48.3628 | 2.2679 | 85.5545
2606 | 41.51 | 49.664 | 126.4814 | 60.3976 | 0.41655 |  | 2606 | 29 | 49.664 | 3 | 60.3976
2607 | 39.67 | 58.1567 | 59.6008 | 57.5881 | 0.411 |  | 2607 | 24.94 | 58.1567 | 4 | 57.5881
2608 | 30.1 | 74.9518 | 41.5799 | 65.4303 | 0.40485 |  | 2608 | 23.77 | 74.9518 | 5 | 65.4303
2609 | 42.83 | 93.0918 | 43.6729 | 69.4726 | 0.41864 |  | 2609 | 20.98 | 93.0918 | 5.7321 | 69.4726
2610 | 47.97 | 143.834 | 48.3077 | 92.8071 | 0.43405 |  | 2610 | 21.59 | 143.834 | 6 | 92.8071
2611 | 52.02 | 139.443 | 56.4081 | 116.1874 | 0.43793 |  | 2611 | 23.19 | 139.443 | 5.7321 | 116.1874
2612 | 43.2 | 119.4619 | 29.9284 | 98.925 | 0.44323 |  | 2612 | 25.62 | 119.4619 | 5 | 98.925
2613 | 45.54 | 110.1863 | 32.3459 | 75.1373 | 0.43583 |  | 2613 | 27.92 | 110.1863 | 4 | 75.1373
2614 | 44.08 | 108.7153 | 32.2542 | 70.3474 | 0.43398 |  | 2614 | 29.04 | 108.7153 | 3 | 70.3474
2615 | 42.37 | 77.7078 | 33.2158 | 39.1859 | 0.43202 |  | 2615 | 22.7 | 77.7078 | 2.2679 | 39.1859
2616 | 41.09 | 41.4043 | 26.4251 | 27.0366 | 0.43732 |  | 2616 | 21.99 | 41.4043 | 2 | 27.0366
2617 | 31.57 | 33.1852 | 20.4741 | 33.8663 | 0.42354 |  | 2617 | 19.83 | 33.1852 | 2.2679 | 33.8663
2618 | 30 | 31.7299 | 21.4293 | 5.1809 | 0.42091 |  | 2618 | 19.37 | 31.7299 | 3 | 5.1809
2619 | 32.5 | 30.2894 | 27.4835 | 16.4304 | 0.39913 |  | 2619 | 19.5 | 30.2894 | 4 | 16.4304
2620 | 32.5 | 29.025 | 17.8485 | 39.0899 | 0.39402 |  | 2620 | 19.16 | 29.025 | 5 | 39.0899
2621 | 34.33 | 28.2303 | 42.713 | 96.1625 | 0.40655 |  | 2621 | 18.44 | 28.2303 | 5.7321 | 96.1625
2622 | 39.92 | 28.1851 | 69.8571 | 105.3876 | 0.422 |  | 2622 | 19.8 | 28.1851 | 6 | 105.3876
2623 | 40.1 | 41.0013 | 66.8401 | 164.3502 | 0.43169 |  | 2623 | 26.93 | 41.0013 | 5.7321 | 164.3502
2624 | 41.3 | 52.6469 | 44.7823 | 141.8433 | 0.42859 |  | 2624 | 30.07 | 52.6469 | 5 | 141.8433
2625 | 37.7 | 43.6271 | 39.4739 | 94.179 | 0.41499 |  | 2625 | 31.26 | 43.6271 | 4 | 94.179
2626 | 31.03 | 42.5776 | 50.6529 | 75.5288 | 0.40522 |  | 2626 | 38 | 42.5776 | 3 | 75.5288
2627 | 28.38 | 44.2156 | 50.2611 | 84.4693 | 0.3898 |  | 2627 | 37.51 | 44.2156 | 2.2679 | 84.4693
2628 | 26.91 | 48.3879 | 38.442 | 89.851 | 0.37727 |  | 2628 | 33.05 | 48.3879 | 2 | 89.851
2629 | 22.8 | 51.1012 | 245.9601 | 87.892 | 0.37674 |  | 2629 | 26.73 | 51.1012 | 2.2679 | 87.892
2630 | 21.03 | 53.0258 | 44.0844 | 58.4072 | 0.38355 |  | 2630 | 26 | 53.0258 | 3 | 58.4072
2631 | 33.7 | 60.6357 | 46.8459 | 59.8724 | 0.39582 |  | 2631 | 24.94 | 60.6357 | 4 | 59.8724
2632 | 39.16 | 75.103 | 40.7497 | 63.1934 | 0.40454 |  | 2632 | 24.94 | 75.103 | 5 | 63.1934
2633 | 42.81 | 92.5758 | 31.9219 | 87.1441 | 0.4061 |  | 2633 | 22.74 | 92.5758 | 5.7321 | 87.1441
2634 | 43.79 | 136.4601 | 43.9623 | 92.2441 | 0.41067 |  | 2634 | 22.5 | 136.4601 | 6 | 92.2441
2635 | 49.49 | 146.2808 | 46.6616 | 101.4385 | 0.41637 |  | 2635 | 25.05 | 146.2808 | 5.7321 | 101.4385
2636 | 55.63 | 133.9488 | 24.796 | 96.809 | 0.41283 |  | 2636 | 24.95 | 133.9488 | 5 | 96.809
2637 | 43.41 | 105.7554 | 24.5879 | 92.0086 | 0.4084 |  | 2637 | 26.12 | 105.7554 | 4 | 92.0086
2638 | 42.5 | 107.599 | 27.4403 | 67.6148 | 0.4087 |  | 2638 | 25 | 107.599 | 3 | 67.6148
2639 | 41.37 | 75.5596 | 32.3417 | 37.2359 | 0.41144 |  | 2639 | 22.44 | 75.5596 | 2.2679 | 37.2359
2640 | 36.95 | 38.78 | 30.4274 | 31.2744 | 0.38858 |  | 2640 | 20.06 | 38.78 | 2 | 31.2744
2641 | 34.02 | 35.458 | 28.5102 | 32.672 | 0.37375 |  | 2641 | 20.71 | 35.458 | 2.2679 | 32.672
2642 | 33 | 33.7974 | 35.0055 | 7.6054 | 0.38374 |  | 2642 | 19.5 | 33.7974 | 3 | 7.6054
2643 | 35.7 | 31.9058 | 59.05 | 17.531 | 0.40211 |  | 2643 | 19.09 | 31.9058 | 4 | 17.531
2644 | 38.47 | 30.194 | 84.1503 | 51.8213 | 0.41235 |  | 2644 | 17.49 | 30.194 | 5 | 51.8213
2645 | 40.4 | 29.035 | 82.2169 | 89.64 | 0.42553 |  | 2645 | 18.63 | 29.035 | 5.7321 | 89.64
2646 | 35.7 | 28.7273 | 100.5643 | 128.1359 | 0.41943 |  | 2646 | 20 | 28.7273 | 6 | 128.1359
2647 | 36.96 | 41.3878 | 78.4627 | 167.5814 | 0.42067 |  | 2647 | 25.76 | 41.3878 | 5.7321 | 167.5814
2648 | 34 | 55.3424 | 83.5162 | 114.9212 | 0.41185 |  | 2648 | 30.55 | 55.3424 | 5 | 114.9212
2649 | 32.23 | 45.0148 | 83.1833 | 118.7881 | 0.40407 |  | 2649 | 31.91 | 45.0148 | 4 | 118.7881
2650 | 29.1 | 44.5579 | 89.2404 | 69.7251 | 0.40096 |  | 2650 | 28.53 | 44.5579 | 3 | 69.7251
2651 | 29.05 | 47.427 | 101.1983 | 74.0141 | 0.39923 |  | 2651 | 30.73 | 47.427 | 2.2679 | 74.0141
2652 | 27.47 | 47.8387 | 75.0701 | 84.3192 | 0.3945 |  | 2652 | 27.41 | 47.8387 | 2 | 84.3192
2653 | 10 | 53.2419 | 36.5895 | 91.4763 | 0.39437 |  | 2653 | 22.41 | 53.2419 | 2.2679 | 91.4763
2654 | 6.27 | 54.4229 | 58.4808 | 80.5758 | 0.40095 |  | 2654 | 22.27 | 54.4229 | 3 | 80.5758
2655 | 9.7 | 60.9703 | 33.9157 | 55.2437 | 0.39969 |  | 2655 | 22.1 | 60.9703 | 4 | 55.2437
2656 | 22.4 | 77.2639 | 34.1579 | 50.7038 | 0.40219 |  | 2656 | 21.57 | 77.2639 | 5 | 50.7038
2657 | 38.99 | 97.0856 | 32.8172 | 73.8715 | 0.41353 |  | 2657 | 21.59 | 97.0856 | 5.7321 | 73.8715
2658 | 45.27 | 130.7493 | 62.8554 | 77.5113 | 0.4322 |  | 2658 | 22.89 | 130.7493 | 6 | 77.5113
2659 | 49.8 | 151.0364 | 38.7269 | 127.0104 | 0.44312 |  | 2659 | 27.24 | 151.0364 | 5.7321 | 127.0104
2660 | 46.08 | 130.0005 | 29.4923 | 116.4881 | 0.43752 |  | 2660 | 31.09 | 130.0005 | 5 | 116.4881
2661 | 44.16 | 111.0467 | 27.2716 | 102.242 | 0.43031 |  | 2661 | 32.16 | 111.0467 | 4 | 102.242
2662 | 41.38 | 105.9147 | 27.0386 | 81.8385 | 0.42577 |  | 2662 | 30.66 | 105.9147 | 3 | 81.8385
2663 | 38.34 | 78.9514 | 25.7662 | 42.7609 | 0.41066 |  | 2663 | 28.52 | 78.9514 | 2.2679 | 42.7609
2664 | 27.79 | 41.0495 | 27.2754 | 21.6185 | 0.37596 |  | 2664 | 24.5 | 41.0495 | 2 | 21.6185
2665 | 19.18 | 34.2555 | 32.7591 | 24.5111 | 0.35075 |  | 2665 | 22.51 | 34.2555 | 2.2679 | 24.5111
2666 | 13 | 32.5673 | 24.8575 | 6.7823 | 0.34631 |  | 2666 | 20.5 | 32.5673 | 3 | 6.7823
2667 | 10.01 | 31.0329 | 21.7247 | 20.7149 | 0.3574 |  | 2667 | 19.93 | 31.0329 | 4 | 20.7149
2668 | 27.7 | 29.6451 | 33.118 | 51.114 | 0.36853 |  | 2668 | 19.58 | 29.6451 | 5 | 51.114
2669 | 23.36 | 28.6349 | 28.3461 | 86.555 | 0.36722 |  | 2669 | 19.84 | 28.6349 | 5.7321 | 86.555
2670 | 27 | 28.0461 | 24.5429 | 134.4335 | 0.36442 |  | 2670 | 21.11 | 28.0461 | 6 | 134.4335
2671 | 32 | 27.7431 | 29.8963 | 158.1816 | 0.36689 |  | 2671 | 29.1 | 27.7431 | 5.7321 | 158.1816
2672 | 24.9 | 29.809 | 49.0575 | 158.5859 | 0.36351 |  | 2672 | 34.58 | 29.809 | 5 | 158.5859
2673 | 27.7 | 48.1322 | 39.517 | 112.2464 | 0.37093 |  | 2673 | 35.38 | 48.1322 | 4 | 112.2464
2674 | 44.9 | 67.0842 | 32.0403 | 93.4236 | 0.38784 |  | 2674 | 32.92 | 67.0842 | 3 | 93.4236
2675 | 54.97 | 75.2513 | 54.3799 | 71.7575 | 0.38208 |  | 2675 | 29.44 | 75.2513 | 2.2679 | 71.7575
2676 | 41.51 | 75.8066 | 49.2301 | 94.5924 | 0.36648 |  | 2676 | 31.14 | 75.8066 | 2 | 94.5924
2677 | 38.09 | 78.5227 | 41.3523 | 63.1919 | 0.34707 |  | 2677 | 25 | 78.5227 | 2.2679 | 63.1919
2678 | 36.46 | 77.0248 | 63.5676 | 74.6047 | 0.33678 |  | 2678 | 23.43 | 77.0248 | 3 | 74.6047
2679 | 33.65 | 72.0206 | 51.1049 | 70.332 | 0.33791 |  | 2679 | 23.47 | 72.0206 | 4 | 70.332
2680 | 38 | 71.527 | 53.6804 | 54.867 | 0.34224 |  | 2680 | 23.93 | 71.527 | 5 | 54.867
2681 | 42.5 | 77.5245 | 36.7659 | 87.675 | 0.35415 |  | 2681 | 23.95 | 77.5245 | 5.7321 | 87.675
2682 | 46.44 | 126.3704 | 50.2826 | 79.1066 | 0.36706 |  | 2682 | 27.61 | 126.3704 | 6 | 79.1066
2683 | 50.33 | 131.9403 | 44.8628 | 118.0974 | 0.37228 |  | 2683 | 30.74 | 131.9403 | 5.7321 | 118.0974
2684 | 53 | 130.7494 | 25.6437 | 97.4438 | 0.36711 |  | 2684 | 32.33 | 130.7494 | 5 | 97.4438
2685 | 65.06 | 108.338 | 31.7519 | 106.7595 | 0.36397 |  | 2685 | 32.34 | 108.338 | 4 | 106.7595
2686 | 52.4 | 105.9081 | 32.5171 | 81.7684 | 0.35603 |  | 2686 | 32.02 | 105.9081 | 3 | 81.7684
2687 | 42.86 | 90.3085 | 29.2977 | 54.3681 | 0.34984 |  | 2687 | 29.19 | 90.3085 | 2.2679 | 54.3681
2688 | 39.7 | 41.1596 | 230.3591 | 26.822 | 0.33746 |  | 2688 | 25 | 41.1596 | 2 | 26.822
2689 | 37.9 | 34.3178 | 28.7379 | 31.1081 | 0.33154 |  | 2689 | 21.95 | 34.3178 | 2.2679 | 31.1081
2690 | 37.76 | 32.7742 | 26.5907 | 6.055 | 0.33789 |  | 2690 | 20.7 | 32.7742 | 3 | 6.055
2691 | 38.05 | 31.1617 | 23.5654 | 17.7865 | 0.34411 |  | 2691 | 19.59 | 31.1617 | 4 | 17.7865
2692 | 37.75 | 29.6979 | 65.8353 | 42.1077 | 0.34872 |  | 2692 | 19.32 | 29.6979 | 5 | 42.1077
2693 | 38.38 | 28.7775 | 125.7765 | 74.5678 | 0.35729 |  | 2693 | 19.85 | 28.7775 | 5.7321 | 74.5678
2694 | 38.5 | 27.9752 | 129.7718 | 138.8032 | 0.37305 |  | 2694 | 22.94 | 27.9752 | 6 | 138.8032
2695 | 46.68 | 27.4131 | 100.8098 | 164.3502 | 0.38172 |  | 2695 | 28 | 27.4131 | 5.7321 | 164.3502
2696 | 49 | 29.9683 | 127.7595 | 122.5558 | 0.38536 |  | 2696 | 33.14 | 29.9683 | 5 | 122.5558
2697 | 55 | 47.92 | 105.5896 | 111.6234 | 0.38814 |  | 2697 | 34.61 | 47.92 | 4 | 111.6234
2698 | 42.4 | 68.6271 | 287.0016 | 90.8441 | 0.38661 |  | 2698 | 32.44 | 68.6271 | 3 | 90.8441
2699 | 43.91 | 75.8032 | 68.6595 | 74.0141 | 0.37864 |  | 2699 | 32.44 | 75.8032 | 2.2679 | 74.0141
2700 | 39.9 | 77.1407 | 38.5056 | 81.7905 | 0.37235 |  | 2700 | 32.26 | 77.1407 | 2 | 81.7905
2701 | 39.16 | 77.0854 | 47.4918 | 85.8661 | 0.36986 |  | 2701 | 29.5 | 77.0854 | 2.2679 | 85.8661
2702 | 38.14 | 78.2808 | 41.5787 | 66.7119 | 0.36866 |  | 2702 | 29.14 | 78.2808 | 3 | 66.7119
2703 | 33.65 | 73.9788 | 44.7666 | 59.3314 | 0.36804 |  | 2703 | 28.02 | 73.9788 | 4 | 59.3314
2704 | 37.67 | 75.017 | 53.2316 | 80.7338 | 0.37223 |  | 2704 | 24.25 | 75.017 | 5 | 80.7338
2705 | 40.48 | 77.332 | 38.0528 | 103.56 | 0.39021 |  | 2705 | 24.49 | 77.332 | 5.7321 | 103.56
2706 | 44.87 | 108.9336 | 43.0221 | 123.9082 | 0.40616 |  | 2706 | 24.75 | 108.9336 | 6 | 123.9082
2707 | 46.96 | 131.5855 | 25.4277 | 150.2782 | 0.42444 |  | 2707 | 28.99 | 131.5855 | 5.7321 | 150.2782
2708 | 50.1 | 136.4818 | 27.8726 | 187.7066 | 0.42487 |  | 2708 | 30.93 | 136.4818 | 5 | 187.7066
2709 | 59.46 | 108.6587 | 25.9174 | 236.7261 | 0.42363 |  | 2709 | 30.94 | 108.6587 | 4 | 236.7261
2710 | 44.14 | 103.792 | 32.1845 | 194.2411 | 0.41885 |  | 2710 | 29.33 | 103.792 | 3 | 194.2411
2711 | 40.72 | 90.6898 | 33.6507 | 227.8 | 0.41171 |  | 2711 | 27.94 | 90.6898 | 2.2679 | 227.8
2712 | 38 | 40.6331 | 27.2574 | 189.3911 | 0.41755 |  | 2712 | 25.04 | 40.6331 | 2 | 189.3911
2713 | 34.14 | 33.4737 | 27.9183 | 230.5114 | 0.41049 |  | 2713 | 27.72 | 33.4737 | 2.2679 | 230.5114
2714 | 34.05 | 31.8957 | 27.4783 | 181.7303 | 0.39906 |  | 2714 | 22.45 | 31.8957 | 3 | 181.7303
2715 | 32.9 | 30.5048 | 35.312 | 217.8849 | 0.3974 |  | 2715 | 21.47 | 30.5048 | 4 | 217.8849
2716 | 32.6 | 29.3063 | 38.1336 | 241.2183 | 0.4009 |  | 2716 | 20.99 | 29.3063 | 5 | 241.2183
2717 | 32.25 | 28.4214 | 75.9118 | 253.09 | 0.40037 |  | 2717 | 20.99 | 28.4214 | 5.7321 | 253.09
2718 | 39.59 | 28.2847 | 69.45 | 280.1822 | 0.41555 |  | 2718 | 20.9 | 28.2847 | 6 | 280.1822
2719 | 43.18 | 41.4116 | 48.8707 | 319.927 | 0.42902 |  | 2719 | 21.05 | 41.4116 | 5.7321 | 319.927
2720 | 50.2 | 54.0744 | 29.3875 | 295.5534 | 0.43125 |  | 2720 | 21.48 | 54.0744 | 5 | 295.5534
2721 | 41.97 | 44.9636 | 57.3433 | 229.1312 | 0.43217 |  | 2721 | 23.62 | 44.9636 | 4 | 229.1312
2722 | 39.65 | 42.3195 | 94.4774 | 205.2763 | 0.4167 |  | 2722 | 27.29 | 42.3195 | 3 | 205.2763
2723 | 38.56 | 44.8967 | 114.4355 | 213.9333 | 0.40234 |  | 2723 | 26.91 | 44.8967 | 2.2679 | 213.9333
2724 | 32.8 | 47.5292 | 71.3031 | 277.4953 | 0.38524 |  | 2724 | 25.76 | 47.5292 | 2 | 277.4953
2725 | 32.52 | 49.2613 | 39.3689 | 274.0565 | 0.36581 |  | 2725 | 23.4 | 49.2613 | 2.2679 | 274.0565
2726 | 31.6 | 52.3841 | 54.4442 | 273.0162 | 0.35941 |  | 2726 | 21.36 | 52.3841 | 3 | 273.0162
2727 | 32 | 59.5602 | 41.5914 | 263.4278 | 0.36555 |  | 2727 | 20.42 | 59.5602 | 4 | 263.4278
2728 | 33.94 | 73.1306 | 41.0446 | 257.9299 | 0.39223 |  | 2728 | 19.6 | 73.1306 | 5 | 257.9299
2729 | 40.36 | 92.7898 | 47.21 | 207.5014 | 0.41444 |  | 2729 | 19.69 | 92.7898 | 5.7321 | 207.5014
2730 | 45.38 | 129.6185 | 41.2494 | 268.268 | 0.42377 |  | 2730 | 19.13 | 129.6185 | 6 | 268.268
2731 | 46.48 | 143.5618 | 54.135 | 312.2628 | 0.44219 |  | 2731 | 21.07 | 143.5618 | 5.7321 | 312.2628
2732 | 44.36 | 131.5129 | 27.6688 | 281.1112 | 0.4385 |  | 2732 | 22.46 | 131.5129 | 5 | 281.1112
2733 | 43.07 | 106.8925 | 30.4731 | 288.4508 | 0.41937 |  | 2733 | 25 | 106.8925 | 4 | 288.4508
2734 | 38.65 | 111.1962 | 33.34 | 299.3192 | 0.41845 |  | 2734 | 27.19 | 111.1962 | 3 | 299.3192
2735 | 36.95 | 75.7083 | 20.1008 | 272.4832 | 0.416 |  | 2735 | 25.05 | 75.7083 | 2.2679 | 272.4832
2736 | 38.9 | 38.7983 | 28.9348 | 229.8456 | 0.40568 |  | 2736 | 22.1 | 38.7983 | 2 | 229.8456
2737 | 35.46 | 35.1304 | 31.876 | 189.0672 | 0.39848 |  | 2737 | 18.21 | 35.1304 | 2.2679 | 189.0672
2738 | 33.43 | 33.526 | 29.4347 | 213.807 | 0.40961 |  | 2738 | 18.05 | 33.526 | 3 | 213.807
2739 | 34.52 | 31.7885 | 27.7845 | 233.8188 | 0.41159 |  | 2739 | 14.31 | 31.7885 | 4 | 233.8188
2740 | 29.49 | 30.2221 | 31.7987 | 202.2184 | 0.40542 |  | 2740 | 12.59 | 30.2221 | 5 | 202.2184
2741 | 35.99 | 29.0375 | 34.8994 | 290.7714 | 0.41118 |  | 2741 | 12.79 | 29.0375 | 5.7321 | 290.7714
2742 | 42.5 | 28.4711 | 38.3048 | 315.2137 | 0.4273 |  | 2742 | 13.62 | 28.4711 | 6 | 315.2137
2743 | 50.03 | 41.7107 | 64.9649 | 386.144 | 0.42438 |  | 2743 | 12.76 | 41.7107 | 5.7321 | 386.144
2744 | 47.88 | 55.1209 | 55.137 | 346.8628 | 0.42756 |  | 2744 | 12.2 | 55.1209 | 5 | 346.8628
2745 | 44.18 | 43.0367 | 53.4811 | 273.6816 | 0.42128 |  | 2745 | 13.75 | 43.0367 | 4 | 273.6816
2746 | 40.96 | 41.2045 | 44.5776 | 222.0068 | 0.41325 |  | 2746 | 17.44 | 41.2045 | 3 | 222.0068
2747 | 37.65 | 43.2416 | 41.9041 | 145.0944 | 0.39783 |  | 2747 | 20.01 | 43.2416 | 2.2679 | 145.0944
2748 | 36.9 | 43.8981 | 43.5129 | 95.9719 | 0.38914 |  | 2748 | 19.6 | 43.8981 | 2 | 95.9719
2749 | 35.1 | 48.066 | 37.6235 | 83.5257 | 0.40073 |  | 2749 | 19.94 | 48.066 | 2.2679 | 83.5257
2750 | 32.4 | 51.0296 | 40.4054 | 69.3886 | 0.40223 |  | 2750 | 14.94 | 51.0296 | 3 | 69.3886
2751 | 38.01 | 56.8969 | 46.8524 | 55.0032 | 0.40614 |  | 2751 | 10.01 | 56.8969 | 4 | 55.0032
2752 | 34.3 | 71.244 | 49.537 | 58.0039 | 0.40938 |  | 2752 | 9.5 | 71.244 | 5 | 58.0039
2753 | 40.52 | 92.2341 | 36.7648 | 139.2516 | 0.40853 |  | 2753 | 10 | 92.2341 | 5.7321 | 139.2516
2754 | 46.22 | 129.7519 | 53.3516 | 179.8459 | 0.41641 |  | 2754 | 17.11 | 129.7519 | 6 | 179.8459
2755 | 58.59 | 138.3367 | 54.4131 | 205.0059 | 0.42411 |  | 2755 | 20.01 | 138.3367 | 5.7321 | 205.0059
2756 | 59.9 | 129.704 | 27.9035 | 202.7482 | 0.43491 |  | 2756 | 21.96 | 129.704 | 5 | 202.7482
2757 | 48.53 | 105.738 | 38.4676 | 241.6589 | 0.45506 |  | 2757 | 24.12 | 105.738 | 4 | 241.6589
2758 | 42.21 | 107.768 | 30.9226 | 207.0507 | 0.46463 |  | 2758 | 27.44 | 107.768 | 3 | 207.0507
2759 | 39.04 | 78.4984 | 30.8572 | 212.0178 | 0.46376 |  | 2759 | 27.87 | 78.4984 | 2.2679 | 212.0178
2760 | 37 | 40.4795 | 28.9299 | 196.4609 | 0.4659 |  | 2760 | 24.04 | 40.4795 | 2 | 196.4609
2761 | 35 | 32.9631 | 30.7212 | 214.0095 | 0.45763 |  | 2761 | 22.56 | 32.9631 | 2.2679 | 214.0095
2762 | 33.41 | 31.4455 | 31.8203 | 159.1433 | 0.45012 |  | 2762 | 21.46 | 31.4455 | 3 | 159.1433
2763 | 34.29 | 30.0356 | 234.8485 | 178.4574 | 0.44745 |  | 2763 | 20.82 | 30.0356 | 4 | 178.4574
2764 | 35.59 | 28.7699 | 32.5077 | 249.8621 | 0.4508 |  | 2764 | 20.23 | 28.7699 | 5 | 249.8621
2765 | 38.92 | 28.1175 | 51.2439 | 273.6639 | 0.46789 |  | 2765 | 20.26 | 28.1175 | 5.7321 | 273.6639
2766 | 45.09 | 28.1683 | 284.8111 | 311.7134 | 0.47093 |  | 2766 | 21.1 | 28.1683 | 6 | 311.7134
2767 | 53.6 | 40.8645 | 40.1033 | 335.4054 | 0.46224 |  | 2767 | 29.02 | 40.8645 | 5.7321 | 335.4054
2768 | 56.38 | 55.3548 | 50.975 | 257.6831 | 0.45679 |  | 2768 | 32.97 | 55.3548 | 5 | 257.6831
2769 | 52.94 | 44.7945 | 36.4372 | 180.1319 | 0.45247 |  | 2769 | 34.48 | 44.7945 | 4 | 180.1319
2770 | 49.93 | 43.1308 | 39.1344 | 70.9342 | 0.44461 |  | 2770 | 36.8 | 43.1308 | 3 | 70.9342
2771 | 46.94 | 45.7683 | 45.1181 | 67.3949 | 0.44672 |  | 2771 | 32.44 | 45.7683 | 2.2679 | 67.3949
2772 | 43.96 | 47.9641 | 36.2219 | 80.5261 | 0.4456 |  | 2772 | 29.46 | 47.9641 | 2 | 80.5261
2773 | 42.16 | 50.9147 | 41.8394 | 88.905 | 0.44464 |  | 2773 | 33.04 | 50.9147 | 2.2679 | 88.905
2774 | 40.35 | 53.9118 | 45.3301 | 62.7997 | 0.4436 |  | 2774 | 29.51 | 53.9118 | 3 | 62.7997
2775 | 40.38 | 58.3695 | 50.7271 | 69.4904 | 0.43633 |  | 2775 | 25.2 | 58.3695 | 4 | 69.4904
2776 | 40.86 | 78.5297 | 41.39 | 73.8188 | 0.4307 |  | 2776 | 24.53 | 78.5297 | 5 | 73.8188
2777 | 44.42 | 94.3995 | 27.5622 | 65.3012 | 0.4258 |  | 2777 | 24.51 | 94.3995 | 5.7321 | 65.3012
2778 | 44.68 | 136.3602 | 49.6709 | 84.7369 | 0.4275 |  | 2778 | 25.95 | 136.3602 | 6 | 84.7369
2779 | 48.75 | 143.0883 | 49.957 | 119.1584 | 0.44401 |  | 2779 | 28.41 | 143.0883 | 5.7321 | 119.1584
2780 | 48.97 | 131.4684 | 31.513 | 88.8738 | 0.45352 |  | 2780 | 31.19 | 131.4684 | 5 | 88.8738
2781 | 46.04 | 105.4556 | 27.109 | 81.5908 | 0.46109 |  | 2781 | 31.46 | 105.4556 | 4 | 81.5908
2782 | 41.97 | 108.2752 | 29.5314 | 65.9332 | 0.45689 |  | 2782 | 30.15 | 108.2752 | 3 | 65.9332
2783 | 37.05 | 76.8554 | 28.9069 | 45.3145 | 0.44034 |  | 2783 | 28.14 | 76.8554 | 2.2679 | 45.3145
2784 | 32.02 | 38.722 | 28.3339 | 22.8792 | 0.41052 |  | 2784 | 24.94 | 38.722 | 2 | 22.8792
2785 | 30.1 | 34.3896 | 24.8894 | 29.6863 | 0.39174 |  | 2785 | 21.81 | 34.3896 | 2.2679 | 29.6863
2786 | 29.05 | 32.8105 | 28.1113 | 7.5863 | 0.36535 |  | 2786 | 20.9 | 32.8105 | 3 | 7.5863
2787 | 28.04 | 31.1889 | 26.0904 | 45.9096 | 0.36922 |  | 2787 | 20.96 | 31.1889 | 4 | 45.9096
2788 | 30.34 | 29.7448 | 22.664 | 141.7336 | 0.35505 |  | 2788 | 20.62 | 29.7448 | 5 | 141.7336
2789 | 29.63 | 28.7037 | 33.2894 | 246.563 | 0.35395 |  | 2789 | 21.07 | 28.7037 | 5.7321 | 246.563
2790 | 28.91 | 28.3336 | 20.0539 | 308.9002 | 0.3482 |  | 2790 | 22.73 | 28.3336 | 6 | 308.9002
2791 | 34.87 | 40.5646 | 32.9126 | 280.3113 | 0.34646 |  | 2791 | 29.91 | 40.5646 | 5.7321 | 280.3113
2792 | 40 | 54.9647 | 49.0166 | 237.6211 | 0.3417 |  | 2792 | 34.64 | 54.9647 | 5 | 237.6211
2793 | 40.5 | 43.7865 | 51.6873 | 134.3343 | 0.33439 |  | 2793 | 37.56 | 43.7865 | 4 | 134.3343
2794 | 34.9 | 42.7604 | 56.1362 | 81.4131 | 0.34066 |  | 2794 | 39.84 | 42.7604 | 3 | 81.4131
2795 | 36.37 | 44.9006 | 29.5491 | 74.6158 | 0.32964 |  | 2795 | 38.02 | 44.9006 | 2.2679 | 74.6158
2796 | 30.48 | 47.1143 | 49.7408 | 71.5173 | 0.31556 |  | 2796 | 35.98 | 47.1143 | 2 | 71.5173
2797 | 30 | 49.3505 | 42.6723 | 79.1652 | 0.30837 |  | 2797 | 27.47 | 49.3505 | 2.2679 | 79.1652
2798 | 29.9 | 52.8107 | 42.3841 | 71.9966 | 0.31086 |  | 2798 | 29.94 | 52.8107 | 3 | 71.9966
2799 | 30.47 | 57.8759 | 33.1655 | 55.7246 | 0.30827 |  | 2799 | 25.56 | 57.8759 | 4 | 55.7246
2800 | 34.64 | 73.3299 | 49.2043 | 55.1777 | 0.31618 |  | 2800 | 25.27 | 73.3299 | 5 | 55.1777
2801 | 37.68 | 95.0346 | 47.1686 | 86.0823 | 0.32511 |  | 2801 | 24.94 | 95.0346 | 5.7321 | 86.0823
2802 | 40.74 | 130.9601 | 43.9588 | 99.7512 | 0.34279 |  | 2802 | 25.29 | 130.9601 | 6 | 99.7512
2803 | 40.11 | 133.3338 | 49.1704 | 118.5218 | 0.3611 |  | 2803 | 28.92 | 133.3338 | 5.7321 | 118.5218
2804 | 38.58 | 127.6296 | 27.8229 | 105.6963 | 0.36193 |  | 2804 | 31.11 | 127.6296 | 5 | 105.6963
2805 | 38.1 | 102.8657 | 34.9627 | 106.3907 | 0.36561 |  | 2805 | 31.61 | 102.8657 | 4 | 106.3907
2806 | 36.36 | 105.0595 | 35.8089 | 63.3407 | 0.35993 |  | 2806 | 31.07 | 105.0595 | 3 | 63.3407
2807 | 31.57 | 75.4032 | 27.281 | 48.2395 | 0.34219 |  | 2807 | 27.99 | 75.4032 | 2.2679 | 48.2395
2808 | 37.3 | 40.0794 | 29.0352 | 31.2208 | 0.37411 |  | 2808 | 23.99 | 40.0794 | 2 | 31.2208
2809 | 36.66 | 34.5956 | 31.7842 | 25.7623 | 0.36844 |  | 2809 | 23.01 | 34.5956 | 2.2679 | 25.7623
2810 | 30 | 32.8099 | 31.8115 | 5.8508 | 0.36381 |  | 2810 | 22.42 | 32.8099 | 3 | 5.8508
2811 | 29 | 31.214 | 35.617 | 19.2999 | 0.37378 |  | 2811 | 22.53 | 31.214 | 4 | 19.2999
2812 | 32.7 | 29.6955 | 28.5386 | 42.0134 | 0.38018 |  | 2812 | 22.04 | 29.6955 | 5 | 42.0134
2813 | 34 | 28.7937 | 29.7924 | 74.7441 | 0.39348 |  | 2813 | 22.17 | 28.7937 | 5.7321 | 74.7441
2814 | 40.33 | 28.6463 | 26.8432 | 108.9862 | 0.39766 |  | 2814 | 23.77 | 28.6463 | 6 | 108.9862
2815 | 39.18 | 40.5335 | 34.6043 | 146.2849 | 0.40449 |  | 2815 | 25.48 | 40.5335 | 5.7321 | 146.2849
2816 | 32.05 | 54.2891 | 62.217 | 147.8706 | 0.40219 |  | 2816 | 28.5 | 54.2891 | 5 | 147.8706
2817 | 38.7 | 45.4592 | 55.4332 | 98.8516 | 0.41959 |  | 2817 | 30.27 | 45.4592 | 4 | 98.8516
2818 | 39.2 | 45.0943 | 57.9908 | 69.0802 | 0.42803 |  | 2818 | 28.85 | 45.0943 | 3 | 69.0802
2819 | 37.3 | 47.5021 | 51.4282 | 77.3236 | 0.42237 |  | 2819 | 25.65 | 47.5021 | 2.2679 | 77.3236
2820 | 37.3 | 52.6788 | 45.7814 | 88.5075 | 0.42706 |  | 2820 | 24.91 | 52.6788 | 2 | 88.5075
2821 | 39.7 | 53.2583 | 46.0492 | 87.0349 | 0.42954 |  | 2821 | 24.21 | 53.2583 | 2.2679 | 87.0349
2822 | 37.3 | 57.4831 | 44.4036 | 78.3796 | 0.42254 |  | 2822 | 24.94 | 57.4831 | 3 | 78.3796
2823 | 34.87 | 61.3374 | 49.2176 | 49.4729 | 0.41346 |  | 2823 | 24.34 | 61.3374 | 4 | 49.4729
2824 | 34.72 | 77.8743 | 44.712 | 67.2944 | 0.41298 |  | 2824 | 24.19 | 77.8743 | 5 | 67.2944
2825 | 37.47 | 97.0496 | 41.1546 | 89.5711 | 0.43683 |  | 2825 | 24.31 | 97.0496 | 5.7321 | 89.5711
2826 | 42.06 | 134.4138 | 36.2809 | 76.1037 | 0.44969 |  | 2826 | 24.72 | 134.4138 | 6 | 76.1037
2827 | 46.59 | 151.7673 | 37.3018 | 122.3417 | 0.45243 |  | 2827 | 28.95 | 151.7673 | 5.7321 | 122.3417
2828 | 50.2 | 121.2783 | 28.4767 | 126.0103 | 0.45651 |  | 2828 | 30.27 | 121.2783 | 5 | 126.0103
2829 | 46.07 | 103.1181 | 28.2576 | 107.036 | 0.46068 |  | 2829 | 33 | 103.1181 | 4 | 107.036
2830 | 47.76 | 106.6592 | 23.8476 | 58.5762 | 0.46538 |  | 2830 | 33.27 | 106.6592 | 3 | 58.5762
2831 | 44.56 | 76.1203 | 29.2909 | 41.2752 | 0.46896 |  | 2831 | 29.09 | 76.1203 | 2.2679 | 41.2752
2832 | 38.53 | 39.4005 | 29.1779 | 24.9444 | 0.4639 |  | 2832 | 27.34 | 39.4005 | 2 | 24.9444
2833 | 36.22 | 35.0966 | 225.6725 | 42.715 | 0.45418 |  | 2833 | 27.7 | 35.0966 | 2.2679 | 42.715
2834 | 35.57 | 33.3595 | 38.6293 | 64.7964 | 0.45948 |  | 2834 | 23.46 | 33.3595 | 3 | 64.7964
2835 | 35.01 | 31.6145 | 36.773 | 120.7454 | 0.46294 |  | 2835 | 24.55 | 31.6145 | 4 | 120.7454
2836 | 34.18 | 30.1057 | 35.116 | 148.438 | 0.47011 |  | 2836 | 23.28 | 30.1057 | 5 | 148.438
2837 | 36.57 | 29.0338 | 229.0689 | 210.8333 | 0.48108 |  | 2837 | 23.73 | 29.0338 | 5.7321 | 210.8333
2838 | 46.82 | 28.246 | 30.8317 | 234.4099 | 0.48834 |  | 2838 | 25.59 | 28.246 | 6 | 234.4099
2839 | 52.77 | 27.6334 | 19.5387 | 304.2532 | 0.47725 |  | 2839 | 31.26 | 27.6334 | 5.7321 | 304.2532
2840 | 56.71 | 30.2892 | 42.2189 | 213.7447 | 0.46768 |  | 2840 | 40.04 | 30.2892 | 5 | 213.7447
2841 | 51.3 | 48.2403 | 52.696 | 201.4202 | 0.46162 |  | 2841 | 45.92 | 48.2403 | 4 | 201.4202
2842 | 46.99 | 66.1132 | 44.0884 | 114.1172 | 0.46033 |  | 2842 | 38.37 | 66.1132 | 3 | 114.1172
2843 | 45.61 | 73.0157 | 47.5549 | 88.4558 | 0.461 |  | 2843 | 43.63 | 73.0157 | 2.2679 | 88.4558
2844 | 44.06 | 76.4704 | 32.1113 | 93.0119 | 0.46116 |  | 2844 | 33.78 | 76.4704 | 2 | 93.0119
2845 | 43 | 78.4012 | 42.7932 | 66.3865 | 0.46085 |  | 2845 | 37.72 | 78.4012 | 2.2679 | 66.3865
2846 | 40.67 | 74.2867 | 45.5208 | 73.7811 | 0.45906 |  | 2846 | 38.04 | 74.2867 | 3 | 73.7811
2847 | 39.41 | 74.0184 | 33.4888 | 55.3639 | 0.45122 |  | 2847 | 27.7 | 74.0184 | 4 | 55.3639
2848 | 39.49 | 76.2521 | 40.5246 | 56.5447 | 0.44323 |  | 2848 | 26.96 | 76.2521 | 5 | 56.5447
2849 | 42.91 | 81.4557 | 38.1068 | 87.9784 | 0.44259 |  | 2849 | 26.5 | 81.4557 | 5.7321 | 87.9784
2850 | 47.27 | 116.5791 | 58.467 | 104.6309 | 0.44762 |  | 2850 | 30 | 116.5791 | 6 | 104.6309
2851 | 47.26 | 149.7704 | 43.7442 | 120.3256 | 0.45064 |  | 2851 | 34.79 | 149.7704 | 5.7321 | 120.3256
2852 | 49.07 | 134.9584 | 34.8203 | 108.6588 | 0.45498 |  | 2852 | 38.43 | 134.9584 | 5 | 108.6588
2853 | 46.81 | 102.7818 | 33.822 | 101.0435 | 0.45743 |  | 2853 | 35.75 | 102.7818 | 4 | 101.0435
2854 | 44.86 | 104.6877 | 28.356 | 59.417 | 0.46097 |  | 2854 | 37.19 | 104.6877 | 3 | 59.417
2855 | 38.43 | 91.9279 | 28.7617 | 62.6314 | 0.45948 |  | 2855 | 34.92 | 91.9279 | 2.2679 | 62.6314
2856 | 34 | 42.585 | 24.5714 | 119.3479 | 0.45215 |  | 2856 | 30.3 | 42.585 | 2 | 119.3479
2857 | 36.07 | 33.4919 | 27.0398 | 127.8023 | 0.4423 |  | 2857 | 26.41 | 33.4919 | 2.2679 | 127.8023
2858 | 35 | 32.0187 | 39.3868 | 116.0862 | 0.43788 |  | 2858 | 25.01 | 32.0187 | 3 | 116.0862
2859 | 35.24 | 30.5279 | 33.3134 | 140.0232 | 0.44051 |  | 2859 | 23.99 | 30.5279 | 4 | 140.0232
2860 | 34.44 | 29.2556 | 31.9566 | 166.0347 | 0.44934 |  | 2860 | 22.46 | 29.2556 | 5 | 166.0347
2861 | 37.01 | 28.3606 | 49.3431 | 249.4435 | 0.45725 |  | 2861 | 22.35 | 28.3606 | 5.7321 | 249.4435
2862 | 45.62 | 27.8932 | 46.9345 | 265.0702 | 0.46453 |  | 2862 | 23.47 | 27.8932 | 6 | 265.0702
2863 | 52.14 | 27.761 | 107.1494 | 267.502 | 0.46448 |  | 2863 | 26.8 | 27.761 | 5.7321 | 267.502
2864 | 60 | 29.8518 | 84.9361 | 222.9815 | 0.46244 |  | 2864 | 30.68 | 29.8518 | 5 | 222.9815
2865 | 51.47 | 48.7948 | 41.8091 | 174.1937 | 0.46019 |  | 2865 | 28.51 | 48.7948 | 4 | 174.1937
2866 | 47.43 | 68.3702 | 46.0542 | 67.1457 | 0.46125 |  | 2866 | 38.01 | 68.3702 | 3 | 67.1457
2867 | 44.85 | 73.6271 | 52.9502 | 63.3332 | 0.45935 |  | 2867 | 37.1 | 73.6271 | 2.2679 | 63.3332
2868 | 40.85 | 75.492 | 68.5083 | 82.7387 | 0.45349 |  | 2868 | 35.88 | 75.492 | 2 | 82.7387
2869 | 36.49 | 80.6989 | 47.5412 | 83.0611 | 0.44531 |  | 2869 | 35.16 | 80.6989 | 2.2679 | 83.0611
2870 | 34.98 | 79.8457 | 38.3889 | 55.6618 | 0.43963 |  | 2870 | 35 | 79.8457 | 3 | 55.6618
2871 | 34.94 | 73.7799 | 29.7089 | 54.4021 | 0.43946 |  | 2871 | 30.96 | 73.7799 | 4 | 54.4021
2872 | 35.34 | 76.59 | 34.6184 | 51.8844 | 0.44744 |  | 2872 | 26.8 | 76.59 | 5 | 51.8844
2873 | 41.3 | 77.6309 | 56.5072 | 65.9079 | 0.45148 |  | 2873 | 25.38 | 77.6309 | 5.7321 | 65.9079
2874 | 47.09 | 121.0948 | 51.6042 | 75.4468 | 0.45283 |  | 2874 | 26.01 | 121.0948 | 6 | 75.4468
2875 | 54.4 | 128.1343 | 39.7925 | 97.1942 | 0.45643 |  | 2875 | 30.82 | 128.1343 | 5.7321 | 97.1942
2876 | 51.76 | 136.585 | 30.8053 | 111.9387 | 0.46147 |  | 2876 | 34.83 | 136.585 | 5 | 111.9387
2877 | 48.71 | 104.3339 | 36.3017 | 95.5119 | 0.46433 |  | 2877 | 35.18 | 104.3339 | 4 | 95.5119
2878 | 46.28 | 102.2875 | 25.1732 | 57.4551 | 0.46773 |  | 2878 | 33.23 | 102.2875 | 3 | 57.4551
2879 | 43.41 | 90.1842 | 35.3307 | 42.8074 | 0.47171 |  | 2879 | 30.99 | 90.1842 | 2.2679 | 42.8074
2880 | 38 | 40.3594 | 28.1138 | 22.3159 | 0.46913 |  | 2880 | 27.35 | 40.3594 | 2 | 22.3159
2881 | 35.2 | 34.1851 | 34.7291 | 28.5489 | 0.4659 |  | 2881 | 24.17 | 34.1851 | 2.2679 | 28.5489
2882 | 32.64 | 32.6929 | 32.3645 | 5.2447 | 0.47268 |  | 2882 | 24.25 | 32.6929 | 3 | 5.2447
2883 | 31.16 | 31.0815 | 37.4725 | 35.8774 | 0.47561 |  | 2883 | 24.54 | 31.0815 | 4 | 35.8774
2884 | 33.3 | 29.5963 | 35.5988 | 139.4313 | 0.4716 |  | 2884 | 25.04 | 29.5963 | 5 | 139.4313
2885 | 30.7 | 28.7382 | 59.6167 | 219.4685 | 0.47046 |  | 2885 | 24 | 28.7382 | 5.7321 | 219.4685
2886 | 30.98 | 28.2631 | 85.0423 | 298.6601 | 0.46867 |  | 2886 | 24 | 28.2631 | 6 | 298.6601
2887 | 34.98 | 40.5431 | 98.1944 | 297.478 | 0.47328 |  | 2887 | 24.22 | 40.5431 | 5.7321 | 297.478
2888 | 39.5 | 55.4194 | 50.4896 | 262.5175 | 0.47229 |  | 2888 | 25.45 | 55.4194 | 5 | 262.5175
2889 | 37.05 | 43.759 | 34.3162 | 211.6751 | 0.47576 |  | 2889 | 26.81 | 43.759 | 4 | 211.6751
2890 | 36.95 | 41.6883 | 58.5479 | 189.5816 | 0.47535 |  | 2890 | 28.69 | 41.6883 | 3 | 189.5816
2891 | 32.89 | 46.1916 | 79.0817 | 168.8596 | 0.47738 |  | 2891 | 28 | 46.1916 | 2.2679 | 168.8596
2892 | 43.31 | 45.275 | 57.2571 | 125.9759 | 0.47928 |  | 2892 | 25.96 | 45.275 | 2 | 125.9759
2893 | 53.27 | 48.8503 | 58.911 | 83.9961 | 0.47674 |  | 2893 | 23.18 | 48.8503 | 2.2679 | 83.9961
2894 | 48.27 | 49.7099 | 247.8403 | 54.9755 | 0.44752 |  | 2894 | 22.44 | 49.7099 | 3 | 54.9755
2895 | 42.16 | 56.4381 | 39.1638 | 62.0364 | 0.43825 |  | 2895 | 21.48 | 56.4381 | 4 | 62.0364
2896 | 37.66 | 68.6718 | 40.2442 | 55.8612 | 0.43338 |  | 2896 | 21.17 | 68.6718 | 5 | 55.8612
2897 | 35.1 | 95.1778 | 51.5317 | 64.0118 | 0.43274 |  | 2897 | 21.54 | 95.1778 | 5.7321 | 64.0118
2898 | 34.66 | 143.3078 | 36.9729 | 89.4289 | 0.43724 |  | 2898 | 22.34 | 143.3078 | 6 | 89.4289
2899 | 39.4 | 146.2021 | 58.3213 | 92.7377 | 0.44077 |  | 2899 | 25.02 | 146.2021 | 5.7321 | 92.7377
2900 | 39.9 | 122.2198 | 112.2404 | 115.2185 | 0.44571 |  | 2900 | 25.51 | 122.2198 | 5 | 115.2185
2901 | 55.5 | 107.1029 | 93.3463 | 112.5369 | 0.44778 |  | 2901 | 25.61 | 107.1029 | 4 | 112.5369
2902 | 52.01 | 104.6941 | 65.7723 | 136.0735 | 0.44832 |  | 2902 | 28.53 | 104.6941 | 3 | 136.0735
2903 | 41.59 | 77.8319 | 66.3046 | 162.4807 | 0.4475 |  | 2903 | 27.92 | 77.8319 | 2.2679 | 162.4807
2904 | 35.5 | 40.173 | 44.2076 | 153.1991 | 0.43824 |  | 2904 | 25.04 | 40.173 | 2 | 153.1991
2905 | 36.64 | 35.7408 | 52.7197 | 182.78 | 0.41642 |  | 2905 | 22.13 | 35.7408 | 2.2679 | 182.78
2906 | 35.81 | 33.838 | 45.656 | 133.293 | 0.41115 |  | 2906 | 19.81 | 33.838 | 3 | 133.293
2907 | 34.45 | 32.021 | 30.3282 | 151.1144 | 0.41295 |  | 2907 | 18.72 | 32.021 | 4 | 151.1144
2908 | 26.97 | 30.4733 | 28.0303 | 204.6511 | 0.41886 |  | 2908 | 17.03 | 30.4733 | 5 | 204.6511
2909 | 31.93 | 29.2175 | 40.3334 | 250.2612 | 0.42468 |  | 2909 | 17.17 | 29.2175 | 5.7321 | 250.2612
2910 | 41.75 | 28.7201 | 59.1732 | 260.7005 | 0.43905 |  | 2910 | 17.92 | 28.7201 | 6 | 260.7005
2911 | 45.52 | 40.3345 | 54.1651 | 272.9539 | 0.4405 |  | 2911 | 17.64 | 40.3345 | 5.7321 | 272.9539
2912 | 47.18 | 57.0035 | 83.4725 | 281.7105 | 0.44064 |  | 2912 | 19.99 | 57.0035 | 5 | 281.7105
2913 | 43.3 | 44.318 | 121.6567 | 195.406 | 0.43628 |  | 2913 | 20.33 | 44.318 | 4 | 195.406
2914 | 45.45 | 43.3038 | 109.4594 | 138.0709 | 0.43588 |  | 2914 | 18.86 | 43.3038 | 3 | 138.0709
2915 | 44 | 46.9178 | 45.3936 | 115.1649 | 0.43226 |  | 2915 | 20.54 | 46.9178 | 2.2679 | 115.1649
2916 | 41.74 | 48.7037 | 41.4695 | 108.8489 | 0.42888 |  | 2916 | 18.5 | 48.7037 | 2 | 108.8489
2917 | 41.67 | 51.3984 | 240.1729 | 70.1266 | 0.42139 |  | 2917 | 20 | 51.3984 | 2.2679 | 70.1266
2918 | 39.74 | 52.406 | 31.7276 | 71.4316 | 0.42078 |  | 2918 | 20 | 52.406 | 3 | 71.4316
2919 | 37 | 59.554 | 41.4522 | 67.5558 | 0.41228 |  | 2919 | 16.33 | 59.554 | 4 | 67.5558
2920 | 37.48 | 76.9089 | 33.9905 | 102.9095 | 0.40236 |  | 2920 | 13.54 | 76.9089 | 5 | 102.9095
2921 | 40.41 | 94.7622 | 32.9452 | 140.0349 | 0.40877 |  | 2921 | 16.33 | 94.7622 | 5.7321 | 140.0349
2922 | 45.98 | 130.237 | 47.7878 | 160.0617 | 0.40833 |  | 2922 | 16.14 | 130.237 | 6 | 160.0617
2923 | 47.18 | 149.156 | 33.0885 | 180.2057 | 0.41986 |  | 2923 | 21.35 | 149.156 | 5.7321 | 180.2057
2924 | 48.56 | 124.3208 | 37.4514 | 201.0564 | 0.42469 |  | 2924 | 23.57 | 124.3208 | 5 | 201.0564
2925 | 46.96 | 104.7758 | 55.4938 | 200.0407 | 0.42125 |  | 2925 | 25.08 | 104.7758 | 4 | 200.0407
2926 | 44.72 | 110.6423 | 94.2637 | 176.3387 | 0.42428 |  | 2926 | 25.74 | 110.6423 | 3 | 176.3387
2927 | 41.71 | 78.026 | 20.9654 | 131.6519 | 0.42359 |  | 2927 | 26.35 | 78.026 | 2.2679 | 131.6519
2928 | 33.29 | 41.1628 | 30.0745 | 110.6952 | 0.41295 |  | 2928 | 27 | 41.1628 | 2 | 110.6952
2929 | 34.9 | 32.7945 | 35.7548 | 104.2335 | 0.41165 |  | 2929 | 22.7 | 32.7945 | 2.2679 | 104.2335
2930 | 33.6 | 31.4531 | 57.1262 | 97.0045 | 0.41321 |  | 2930 | 20.23 | 31.4531 | 3 | 97.0045
2931 | 32.48 | 30.1695 | 39.8886 | 100.3163 | 0.40902 |  | 2931 | 20.03 | 30.1695 | 4 | 100.3163
2932 | 33.1 | 28.8944 | 33.9634 | 136.8246 | 0.4121 |  | 2932 | 19.94 | 28.8944 | 5 | 136.8246
2933 | 35.96 | 28.0964 | 32.6672 | 171.916 | 0.42356 |  | 2933 | 20.08 | 28.0964 | 5.7321 | 171.916
2934 | 41.95 | 28.1499 | 32.7868 | 225.294 | 0.43038 |  | 2934 | 23.47 | 28.1499 | 6 | 225.294
2935 | 46.99 | 39.1184 | 35.8228 | 230.9455 | 0.43601 |  | 2935 | 31.12 | 39.1184 | 5.7321 | 230.9455
2936 | 50.1 | 54.7733 | 43.992 | 213.4546 | 0.43045 |  | 2936 | 35.71 | 54.7733 | 5 | 213.4546
2937 | 47.94 | 43.1608 | 59.0232 | 176.1822 | 0.42921 |  | 2937 | 34.96 | 43.1608 | 4 | 176.1822
2938 | 46.9 | 41.084 | 53.9422 | 132.8808 | 0.42974 |  | 2938 | 32.39 | 41.084 | 3 | 132.8808
2939 | 46.47 | 43.335 | 50.5934 | 124.7183 | 0.42818 |  | 2939 | 33.11 | 43.335 | 2.2679 | 124.7183
2940 | 43.7 | 43.9857 | 34.8632 | 119.966 | 0.43205 |  | 2940 | 35.52 | 43.9857 | 2 | 119.966
2941 | 41.24 | 48.1727 | 35.9926 | 120.005 | 0.4261 |  | 2941 | 36.03 | 48.1727 | 2.2679 | 120.005
2942 | 39.05 | 51.9717 | 30.1847 | 88.6442 | 0.42375 |  | 2942 | 35.46 | 51.9717 | 3 | 88.6442
2943 | 35.61 | 55.9829 | 53.6088 | 86.7404 | 0.4206 |  | 2943 | 31.2 | 55.9829 | 4 | 86.7404
2944 | 35.47 | 70.3738 | 41.2553 | 67.4808 | 0.42321 |  | 2944 | 26.12 | 70.3738 | 5 | 67.4808
2945 | 38.89 | 90.7926 | 57.232 | 63.1776 | 0.41206 |  | 2945 | 26.94 | 90.7926 | 5.7321 | 63.1776
2946 | 42.01 | 141.6795 | 44.7911 | 92.901 | 0.41226 |  | 2946 | 29.06 | 141.6795 | 6 | 92.901
2947 | 43.96 | 141.6443 | 60.6375 | 111.0943 | 0.41302 |  | 2947 | 33 | 141.6443 | 5.7321 | 111.0943
2948 | 44.57 | 121.1107 | 100.3173 | 119.8738 | 0.41529 |  | 2948 | 35.79 | 121.1107 | 5 | 119.8738
2949 | 44.92 | 100.1798 | 112.7788 | 98.9231 | 0.41816 |  | 2949 | 35.76 | 100.1798 | 4 | 98.9231
2950 | 45.37 | 102.6821 | 141.8245 | 79.4562 | 0.42178 |  | 2950 | 34.08 | 102.6821 | 3 | 79.4562
2951 | 42.01 | 74.1722 | 311.7593 | 80.8687 | 0.41693 |  | 2951 | 31.93 | 74.1722 | 2.2679 | 80.8687
2952 | 39.72 | 38.2429 | 33.077 | 120.0168 | 0.41011 |  | 2952 | 27.05 | 38.2429 | 2 | 120.0168
2953 | 39.15 | 34.247 | 28.869 | 127.9108 | 0.38177 |  | 2953 | 23.91 | 34.247 | 2.2679 | 127.9108
2954 | 35.56 | 32.6423 | 23.6218 | 106.6713 | 0.35435 |  | 2954 | 21.81 | 32.6423 | 3 | 106.6713
2955 | 34.9 | 30.9273 | 39.5183 | 139.1048 | 0.34917 |  | 2955 | 21.84 | 30.9273 | 4 | 139.1048
2956 | 34.98 | 29.5806 | 22.3698 | 178.1385 | 0.34508 |  | 2956 | 21.37 | 29.5806 | 5 | 178.1385
2957 | 34.51 | 28.6358 | 47.1762 | 193.6982 | 0.34186 |  | 2957 | 21.85 | 28.6358 | 5.7321 | 193.6982
2958 | 35.59 | 28.3304 | 90.4549 | 268.8859 | 0.33954 |  | 2958 | 23.26 | 28.3304 | 6 | 268.8859
2959 | 40.87 | 40.0285 | 105.4279 | 273.4482 | 0.34044 |  | 2959 | 30.39 | 40.0285 | 5.7321 | 273.4482
2960 | 45 | 54.9214 | 91.2107 | 182.2647 | 0.3385 |  | 2960 | 33.9 | 54.9214 | 5 | 182.2647
2961 | 45.07 | 44.1932 | 94.7733 | 115.7239 | 0.33058 |  | 2961 | 36.48 | 44.1932 | 4 | 115.7239
2962 | 43.62 | 43.7667 | 75.1217 | 79.0389 | 0.33492 |  | 2962 | 35.95 | 43.7667 | 3 | 79.0389
2963 | 42.65 | 46.7766 | 97.8113 | 63.8597 | 0.33051 |  | 2963 | 35.58 | 46.7766 | 2.2679 | 63.8597
2964 | 40.56 | 47.9652 | 39.9538 | 79.8148 | 0.32783 |  | 2964 | 34.9 | 47.9652 | 2 | 79.8148
2965 | 36.98 | 51.2657 | 42.2441 | 69.2695 | 0.33375 |  | 2965 | 31.55 | 51.2657 | 2.2679 | 69.2695
2966 | 34.95 | 51.8868 | 58.7056 | 60.9466 | 0.32575 |  | 2966 | 29.91 | 51.8868 | 3 | 60.9466
2967 | 35.11 | 61.0336 | 54.5197 | 64.2606 | 0.32016 |  | 2967 | 30.34 | 61.0336 | 4 | 64.2606
2968 | 37.5 | 75.395 | 44.4811 | 59.1545 | 0.32669 |  | 2968 | 28.42 | 75.395 | 5 | 59.1545
2969 | 39.2 | 94.7922 | 50.9393 | 68.1074 | 0.3416 |  | 2969 | 28.5 | 94.7922 | 5.7321 | 68.1074
2970 | 41.03 | 138.3325 | 52.5841 | 91.4934 | 0.35302 |  | 2970 | 25.17 | 138.3325 | 6 | 91.4934
2971 | 44.53 | 144.231 | 43.8718 | 87.4324 | 0.37492 |  | 2971 | 28.51 | 144.231 | 5.7321 | 87.4324
2972 | 44.81 | 127.1898 | 31.1653 | 113.3141 | 0.38368 |  | 2972 | 31.69 | 127.1898 | 5 | 113.3141
2973 | 45.5 | 105.2086 | 23.1699 | 77.6265 | 0.39402 |  | 2973 | 32.1 | 105.2086 | 4 | 77.6265
2974 | 45.92 | 106.2241 | 30.0371 | 68.0352 | 0.38805 |  | 2974 | 32.8 | 106.2241 | 3 | 68.0352
2975 | 44.3 | 78.3887 | 29.6256 | 44.2931 | 0.38724 |  | 2975 | 32.51 | 78.3887 | 2.2679 | 44.2931
2976 | 35.19 | 40.1008 | 30.519 | 24.8908 | 0.34909 |  | 2976 | 29.94 | 40.1008 | 2 | 24.8908
2977 | 32.02 | 35.34 | 34.9608 | 32.9564 | 0.32804 |  | 2977 | 23.02 | 35.34 | 2.2679 | 32.9564
2978 | 30 | 33.5596 | 31.6446 | 5.4552 | 0.33033 |  | 2978 | 22.16 | 33.5596 | 3 | 5.4552
2979 | 32.1 | 31.8519 | 23.73 | 20.8328 | 0.34086 |  | 2979 | 21.95 | 31.8519 | 4 | 20.8328
2980 | 32.1 | 30.2466 | 27.9507 | 40.9289 | 0.33221 |  | 2980 | 21.69 | 30.2466 | 5 | 40.9289
2981 | 38.57 | 29.0885 | 36.7125 | 98.0134 | 0.33849 |  | 2981 | 22.14 | 29.0885 | 5.7321 | 98.0134
2982 | 35 | 28.6018 | 31.1482 | 166.4352 | 0.33221 |  | 2982 | 23.59 | 28.6018 | 6 | 166.4352
2983 | 35.66 | 40.6303 | 27.025 | 180.1691 | 0.34041 |  | 2983 | 31.47 | 40.6303 | 5.7321 | 180.1691
2984 | 33.93 | 54.229 | 46.2218 | 156.2124 | 0.33272 |  | 2984 | 35.05 | 54.229 | 5 | 156.2124
2985 | 36.86 | 43.7094 | 41.0139 | 174.7679 | 0.33496 |  | 2985 | 35.97 | 43.7094 | 4 | 174.7679
2986 | 38 | 42.8862 | 37.2341 | 75.6582 | 0.32568 |  | 2986 | 33.54 | 42.8862 | 3 | 75.6582
2987 | 34.9 | 44.3919 | 35.7948 | 66.9436 | 0.32332 |  | 2987 | 29.45 | 44.3919 | 2.2679 | 66.9436
2988 | 40.3 | 46.6453 | 44.8377 | 68.2772 | 0.32016 |  | 2988 | 28.04 | 46.6453 | 2 | 68.2772
2989 | 40.12 | 49.8954 | 43.231 | 82.204 | 0.31971 |  | 2989 | 27.15 | 49.8954 | 2.2679 | 82.204
2990 | 30 | 51.2923 | 43.005 | 72.0653 | 0.31426 |  | 2990 | 26 | 51.2923 | 3 | 72.0653
2991 | 29.9 | 59.1747 | 37.8524 | 53.1999 | 0.31611 |  | 2991 | 24.8 | 59.1747 | 4 | 53.1999
2992 | 35.3 | 73.3825 | 43.1661 | 68.2886 | 0.32777 |  | 2992 | 23.64 | 73.3825 | 5 | 68.2886
2993 | 40.03 | 92.134 | 38.3186 | 75.54 | 0.36186 |  | 2993 | 23.88 | 92.134 | 5.7321 | 75.54
2994 | 40 | 128.9539 | 44.3074 | 105.8508 | 0.37973 |  | 2994 | 25.1 | 128.9539 | 6 | 105.8508
2995 | 40.58 | 152.9072 | 45.9198 | 96.0271 | 0.38903 |  | 2995 | 28.96 | 152.9072 | 5.7321 | 96.0271
2996 | 45 | 117.3337 | 29.2695 | 93.1059 | 0.40131 |  | 2996 | 31.73 | 117.3337 | 5 | 93.1059
2997 | 59.75 | 100.9762 | 34.2272 | 86.5692 | 0.40625 |  | 2997 | 32 | 100.9762 | 4 | 86.5692
2998 | 62.62 | 104.0014 | 49.2563 | 68.7359 | 0.41538 |  | 2998 | 32.9 | 104.0014 | 3 | 68.7359
2999 | 52.02 | 78.1496 | 72.5819 | 45.9181 | 0.42092 |  | 2999 | 31.93 | 78.1496 | 2.2679 | 45.9181
3000 | 52.33 | 40.441 | 69.2488 | 23.1742 | 0.42333 |  | 3000 | 27.8 | 40.441 | 2 | 23.1742
3001 | 42.66 | 35.9085 | 23.9899 | 32.8426 | 0.42243 |  | 3001 | 23.69 | 35.9085 | 2.2679 | 32.8426
3002 | 39.9 | 34.0531 | 34.5008 | 5.5445 | 0.4242 |  | 3002 | 21.86 | 34.0531 | 3 | 5.5445
3003 | 39.56 | 32.2197 | 34.3204 | 17.2166 | 0.41887 |  | 3003 | 21.26 | 32.2197 | 4 | 17.2166
3004 | 36.19 | 30.5067 | 38.3073 | 42.9565 | 0.41742 |  | 3004 | 20.26 | 30.5067 | 5 | 42.9565
3005 | 36.35 | 29.3755 | 29.348 | 123.525 | 0.41561 |  | 3005 | 19.79 | 29.3755 | 5.7321 | 123.525
3006 | 45.85 | 28.58 | 27.1474 | 246.5896 | 0.41984 |  | 3006 | 19.79 | 28.58 | 6 | 246.5896
3007 | 51.63 | 28.0659 | 29.4211 | 252.687 | 0.41794 |  | 3007 | 19.95 | 28.0659 | 5.7321 | 252.687
3008 | 48.84 | 29.8037 | 40.9652 | 234.5718 | 0.42126 |  | 3008 | 20.07 | 29.8037 | 5 | 234.5718
3009 | 45.22 | 47.1121 | 51.2949 | 165.7366 | 0.42244 |  | 3009 | 20 | 47.1121 | 4 | 165.7366
3010 | 45.42 | 68.5166 | 42.3024 | 120.6624 | 0.4222 |  | 3010 | 19.57 | 68.5166 | 3 | 120.6624
3011 | 46.21 | 75.6142 | 32.2865 | 109.5496 | 0.42326 |  | 3011 | 19.01 | 75.6142 | 2.2679 | 109.5496
3012 | 45.87 | 76.6427 | 51.0258 | 95.7207 | 0.42479 |  | 3012 | 17.76 | 76.6427 | 2 | 95.7207
3013 | 44.19 | 82.9596 | 40.0968 | 69.737 | 0.41717 |  | 3013 | 17.58 | 82.9596 | 2.2679 | 69.737
3014 | 42.08 | 78.0534 | 55.0581 | 78.5168 | 0.41297 |  | 3014 | 19.5 | 78.0534 | 3 | 78.5168
3015 | 41.09 | 74.017 | 43.7795 | 66.7252 | 0.41951 |  | 3015 | 19.47 | 74.017 | 4 | 66.7252
3016 | 41.16 | 79.0819 | 43.505 | 66.3623 | 0.41643 |  | 3016 | 15.01 | 79.0819 | 5 | 66.3623
3017 | 43.87 | 83.7079 | 45.1122 | 69.0934 | 0.42054 |  | 3017 | 15.12 | 83.7079 | 5.7321 | 69.0934
3018 | 47.19 | 120.2647 | 43.561 | 95.7161 | 0.42075 |  | 3018 | 17.77 | 120.2647 | 6 | 95.7161
3019 | 54.4 | 144.619 | 42.5532 | 87.7507 | 0.42866 |  | 3019 | 20.67 | 144.619 | 5.7321 | 87.7507
3020 | 56.14 | 132.1567 | 20.6664 | 122.4131 | 0.43146 |  | 3020 | 24.2 | 132.1567 | 5 | 122.4131
3021 | 56.14 | 102.0552 | 32.2939 | 93.0227 | 0.43641 |  | 3021 | 24.08 | 102.0552 | 4 | 93.0227
3022 | 55 | 100.3263 | 35.2163 | 58.0857 | 0.44017 |  | 3022 | 24.87 | 100.3263 | 3 | 58.0857
3023 | 45.33 | 89.6691 | 28.7523 | 49.9574 | 0.44619 |  | 3023 | 25.79 | 89.6691 | 2.2679 | 49.9574
3024 | 42.32 | 42.481 | 22.7348 | 31.033 | 0.45301 |  | 3024 | 22.34 | 42.481 | 2 | 31.033
3025 | 40.98 | 36.024 | 33.8677 | 25.3926 | 0.45623 |  | 3025 | 20.73 | 36.024 | 2.2679 | 25.3926
3026 | 40.8 | 34.085 | 28.8998 | 7.1843 | 0.45705 |  | 3026 | 19.08 | 34.085 | 3 | 7.1843
3027 | 40.03 | 32.1798 | 28.916 | 20.5577 | 0.45793 |  | 3027 | 18.46 | 32.1798 | 4 | 20.5577
3028 | 40.03 | 30.5245 | 39.4906 | 45.7385 | 0.45779 |  | 3028 | 17.87 | 30.5245 | 5 | 45.7385
3029 | 42.71 | 29.3425 | 105.6811 | 100.7458 | 0.45651 |  | 3029 | 19.11 | 29.3425 | 5.7321 | 100.7458
3030 | 51.59 | 28.5727 | 91.9264 | 122.3524 | 0.4549 |  | 3030 | 20 | 28.5727 | 6 | 122.3524
3031 | 60.16 | 28.1064 | 239.8236 | 192.9072 | 0.45085 |  | 3031 | 24.44 | 28.1064 | 5.7321 | 192.9072
3032 | 63.9 | 30.7434 | 42.8161 | 159.702 | 0.44766 |  | 3032 | 30.33 | 30.7434 | 5 | 159.702
3033 | 57.53 | 49.7789 | 38.3199 | 119.4111 | 0.44451 |  | 3033 | 30.99 | 49.7789 | 4 | 119.4111
3034 | 58.87 | 68.848 | 62.9478 | 92.2144 | 0.4416 |  | 3034 | 29.98 | 68.848 | 3 | 92.2144
3035 | 56.4 | 74.8226 | 117.7546 | 66.718 | 0.44265 |  | 3035 | 24.28 | 74.8226 | 2.2679 | 66.718
3036 | 54.07 | 80.2702 | 101.4157 | 90.7993 | 0.44499 |  | 3036 | 23.62 | 80.2702 | 2 | 90.7993
3037 | 48.94 | 81.3121 | 49.0927 | 68.0228 | 0.44423 |  | 3037 | 24.94 | 81.3121 | 2.2679 | 68.0228
3038 | 48 | 81.2265 | 45.1959 | 78.5855 | 0.44357 |  | 3038 | 31 | 81.2265 | 3 | 78.5855
3039 | 46.77 | 78.5995 | 37.0808 | 51.0959 | 0.44093 |  | 3039 | 30 | 78.5995 | 4 | 51.0959
3040 | 47.1 | 75.9046 | 37.1706 | 60.5215 | 0.44183 |  | 3040 | 24.94 | 75.9046 | 5 | 60.5215
3041 | 48.94 | 78.5747 | 28.15 | 86.8407 | 0.4433 |  | 3041 | 24 | 78.5747 | 5.7321 | 86.8407
3042 | 59.22 | 120.3279 | 48.9978 | 80.608 | 0.44426 |  | 3042 | 24.15 | 120.3279 | 6 | 80.608
3043 | 65.68 | 135.0307 | 40.7898 | 105.5767 | 0.44326 |  | 3043 | 32.44 | 135.0307 | 5.7321 | 105.5767
3044 | 67.87 | 137.2098 | 25.1473 | 102.4165 | 0.44848 |  | 3044 | 30.94 | 137.2098 | 5 | 102.4165
3045 | 55 | 106.6368 | 26.441 | 82.4205 | 0.45085 |  | 3045 | 29.94 | 106.6368 | 4 | 82.4205
3046 | 50.98 | 104.8969 | 40.0005 | 76.3032 | 0.4493 |  | 3046 | 34.94 | 104.8969 | 3 | 76.3032
3047 | 45 | 91.7416 | 229.6874 | 52.186 | 0.44837 |  | 3047 | 43.19 | 91.7416 | 2.2679 | 52.186
3048 | 44.18 | 42.7427 | 26.2838 | 22.45 | 0.44374 |  | 3048 | 32.81 | 42.7427 | 2 | 22.45
3049 | 39.03 | 35.1901 | 33.5557 | 25.3357 | 0.43212 |  | 3049 | 20.47 | 35.1901 | 2.2679 | 25.3357
3050 | 35.96 | 33.4892 | 33.1054 | 5.2447 | 0.42187 |  | 3050 | 17.46 | 33.4892 | 3 | 5.2447
3051 | 35.79 | 31.7712 | 28.838 | 19.7519 | 0.4222 |  | 3051 | 14.95 | 31.7712 | 4 | 19.7519
3052 | 35.08 | 30.1696 | 33.983 | 39.5614 | 0.42322 |  | 3052 | 14.64 | 30.1696 | 5 | 39.5614
3053 | 36.37 | 28.9336 | 60.3636 | 73.4219 | 0.42684 |  | 3053 | 14.96 | 28.9336 | 5.7321 | 73.4219
3054 | 43.67 | 28.3122 | 84.5471 | 117.0831 | 0.42984 |  | 3054 | 15.2 | 28.3122 | 6 | 117.0831
3055 | 49.09 | 40.0174 | 55.2681 | 134.8289 | 0.42561 |  | 3055 | 16.27 | 40.0174 | 5.7321 | 134.8289
3056 | 48.92 | 55.2673 | 101.5939 | 139.7002 | 0.42071 |  | 3056 | 19.32 | 55.2673 | 5 | 139.7002
3057 | 46.2 | 44.4903 | 116.5149 | 100.9283 | 0.42081 |  | 3057 | 19.94 | 44.4903 | 4 | 100.9283
3058 | 44.66 | 42.9028 | 112.8441 | 79.0755 | 0.41946 |  | 3058 | 20 | 42.9028 | 3 | 79.0755
3059 | 43.5 | 45.7888 | 107.6088 | 74.6158 | 0.41404 |  | 3059 | 19.62 | 45.7888 | 2.2679 | 74.6158
3060 | 42.87 | 46.2818 | 109.4463 | 92.9329 | 0.40873 |  | 3060 | 20 | 46.2818 | 2 | 92.9329
3061 | 38.19 | 49.998 | 101.5161 | 76.5159 | 0.39611 |  | 3061 | 23.7 | 49.998 | 2.2679 | 76.5159
3062 | 35.78 | 50.5561 | 45.4511 | 73.7125 | 0.37934 |  | 3062 | 21.14 | 50.5561 | 3 | 73.7125
3063 | 34.9 | 57.5262 | 47.8587 | 49.2324 | 0.37208 |  | 3063 | 20 | 57.5262 | 4 | 49.2324
3064 | 34.38 | 72.7253 | 46.1266 | 63.504 | 0.37576 |  | 3064 | 19.5 | 72.7253 | 5 | 63.504
3065 | 35.45 | 97.0186 | 44.3667 | 62.3433 | 0.38259 |  | 3065 | 18.75 | 97.0186 | 5.7321 | 62.3433
3066 | 37.35 | 139.9348 | 42.1928 | 101.2527 | 0.39271 |  | 3066 | 19.89 | 139.9348 | 6 | 101.2527
3067 | 39.19 | 146.2746 | 56.5058 | 117.0363 | 0.40245 |  | 3067 | 20.58 | 146.2746 | 5.7321 | 117.0363
3068 | 39.61 | 127.4262 | 31.1073 | 110.9864 | 0.40989 |  | 3068 | 22.13 | 127.4262 | 5 | 110.9864
3069 | 38.01 | 101.6057 | 38.5394 | 74.6763 | 0.41107 |  | 3069 | 20.59 | 101.6057 | 4 | 74.6763
3070 | 45 | 106.4191 | 23.0926 | 77.3542 | 0.40609 |  | 3070 | 23.7 | 106.4191 | 3 | 77.3542
3071 | 40.19 | 76.0882 | 27.8588 | 37.7931 | 0.4105 |  | 3071 | 24.94 | 76.0882 | 2.2679 | 37.7931
3072 | 33.92 | 40.8175 | 27.4101 | 31.8109 | 0.39718 |  | 3072 | 21.1 | 40.8175 | 2 | 31.8109
3073 | 32.01 | 33.2997 | 34.387 | 33.2976 | 0.37903 |  | 3073 | 15.68 | 33.2997 | 2.2679 | 33.2976
3074 | 30.26 | 31.7972 | 35.4315 | 6.3421 | 0.36978 |  | 3074 | 14.45 | 31.7972 | 3 | 6.3421
3075 | 30.69 | 30.3203 | 29.9941 | 18.6906 | 0.3618 |  | 3075 | 11.9 | 30.3203 | 4 | 18.6906
3076 | 33.1 | 29.066 | 37.8367 | 44.4182 | 0.36614 |  | 3076 | 7.39 | 29.066 | 5 | 44.4182
3077 | 37.07 | 28.2789 | 41.951 | 86.8195 | 0.37735 |  | 3077 | 6.81 | 28.2789 | 5.7321 | 86.8195
3078 | 45.99 | 28.1256 | 64.0388 | 133.7908 | 0.40428 |  | 3078 | 3 | 28.1256 | 6 | 133.7908
3079 | 49.92 | 39.4496 | 28.7638 | 138.9413 | 0.41073 |  | 3079 | 2.91 | 39.4496 | 5.7321 | 138.9413
3080 | 54.66 | 55.2877 | 54.4324 | 153.8979 | 0.40888 |  | 3080 | 2.79 | 55.2877 | 5 | 153.8979
3081 | 52.19 | 43.4467 | 47.4684 | 98.8516 | 0.4081 |  | 3081 | 16.4 | 43.4467 | 4 | 98.8516
3082 | 49.95 | 42.0126 | 41.7464 | 80.7682 | 0.41589 |  | 3082 | 15.01 | 42.0126 | 3 | 80.7682
3083 | 49.93 | 46.5499 | 57.2135 | 63.8597 | 0.42102 |  | 3083 | 22.36 | 46.5499 | 2.2679 | 63.8597
3084 | 49.05 | 47.7109 | 51.9434 | 69.3046 | 0.41693 |  | 3084 | 20.38 | 47.7109 | 2 | 69.3046
3085 | 47.76 | 48.8853 | 48.8094 | 82.2819 | 0.41649 |  | 3085 | 20 | 48.8853 | 2.2679 | 82.2819
3086 | 45.76 | 51.5987 | 50.4418 | 71.5848 | 0.42041 |  | 3086 | 20.01 | 51.5987 | 3 | 71.5848
3087 | 45.33 | 56.0223 | 29.1015 | 53.7409 | 0.41803 |  | 3087 | 18.74 | 56.0223 | 4 | 53.7409
3088 | 45.54 | 71.8365 | 42.334 | 51.0766 | 0.41589 |  | 3088 | 18.21 | 71.8365 | 5 | 51.0766
3089 | 51.41 | 97.438 | 40.5246 | 73.8715 | 0.42008 |  | 3089 | 17.75 | 97.438 | 5.7321 | 73.8715
3090 | 51.05 | 132.1552 | 36.3756 | 105.757 | 0.42035 |  | 3090 | 18.3 | 132.1552 | 6 | 105.757
3091 | 56.98 | 146.3775 | 46.2132 | 114.9142 | 0.42601 |  | 3091 | 17.35 | 146.3775 | 5.7321 | 114.9142
3092 | 55 | 122.2534 | 23.6266 | 91.6246 | 0.42703 |  | 3092 | 19.99 | 122.2534 | 5 | 91.6246
3093 | 49.9 | 97.7098 | 26.3198 | 80.8532 | 0.42734 |  | 3093 | 20.04 | 97.7098 | 4 | 80.8532
3094 | 49.07 | 104.1153 | 34.5423 | 59.0666 | 0.43627 |  | 3094 | 20.68 | 104.1153 | 3 | 59.0666
3095 | 44 | 76.0036 | 35.2714 | 50.5146 | 0.44011 |  | 3095 | 20.12 | 76.0036 | 2.2679 | 50.5146
3096 | 40.1 | 38.8312 | 30.3634 | 32.1864 | 0.43496 |  | 3096 | 18.66 | 38.8312 | 2 | 32.1864
3097 | 38.83 | 34.7452 | 31.254 | 31.8474 | 0.4337 |  | 3097 | 16.27 | 34.7452 | 2.2679 | 31.8474
3098 | 37.54 | 32.9823 | 22.678 | 5.9784 | 0.43062 |  | 3098 | 12.68 | 32.9823 | 3 | 5.9784
3099 | 37.25 | 31.2159 | 29.542 | 18.5923 | 0.42916 |  | 3099 | 12.09 | 31.2159 | 4 | 18.5923
3100 | 37.17 | 29.7864 | 25.5182 | 42.7207 | 0.43148 |  | 3100 | 9.57 | 29.7864 | 5 | 42.7207
3101 | 39.02 | 28.9196 | 32.19 | 88.1416 | 0.43502 |  | 3101 | 11 | 28.9196 | 5.7321 | 88.1416
3102 | 47.63 | 28.6542 | 28.6023 | 113.3559 | 0.43168 |  | 3102 | 14.18 | 28.6542 | 6 | 113.3559
3103 | 54.58 | 40.2225 | 35.8033 | 150.2505 | 0.43107 |  | 3103 | 28.57 | 40.2225 | 5.7321 | 150.2505
3104 | 56.17 | 54.7269 | 37.8764 | 143.7184 | 0.43185 |  | 3104 | 32.95 | 54.7269 | 5 | 143.7184
3105 | 53.07 | 43.2806 | 45.0943 | 100.7207 | 0.43215 |  | 3105 | 34.69 | 43.2806 | 4 | 100.7207
3106 | 50.41 | 41.2754 | 45.3448 | 82.461 | 0.43284 |  | 3106 | 31.24 | 41.2754 | 3 | 82.461
3107 | 46.93 | 43.6775 | 59.5533 | 60.6253 | 0.433 |  | 3107 | 25.55 | 43.6775 | 2.2679 | 60.6253
3108 | 45.11 | 47.1763 | 48.3723 | 72.2285 | 0.43495 |  | 3108 | 23.45 | 47.1763 | 2 | 72.2285
3109 | 41.98 | 48.2504 | 55.8668 | 73.2434 | 0.43902 |  | 3109 | 23.12 | 48.2504 | 2.2679 | 73.2434
3110 | 40.94 | 50.3537 | 37.9081 | 72.6143 | 0.43786 |  | 3110 | 22.93 | 50.3537 | 3 | 72.6143
3111 | 38 | 56.1144 | 48.4091 | 68.0477 | 0.43886 |  | 3111 | 22.75 | 56.1144 | 4 | 68.0477
3112 | 37.38 | 74.7251 | 46.1277 | 62.7584 | 0.44105 |  | 3112 | 24.94 | 74.7251 | 5 | 62.7584
3113 | 42.7 | 93.571 | 44.38 | 71.5962 | 0.44132 |  | 3113 | 24.94 | 93.571 | 5.7321 | 71.5962
3114 | 48.9 | 125.0738 | 63.9841 | 81.171 | 0.44284 |  | 3114 | 29.35 | 125.0738 | 6 | 81.171
3115 | 50.48 | 151.5431 | 49.5699 | 106.1072 | 0.4458 |  | 3115 | 27.12 | 151.5431 | 5.7321 | 106.1072
3116 | 51.81 | 124.2943 | 33.7142 | 109.8226 | 0.44687 |  | 3116 | 31.46 | 124.2943 | 5 | 109.8226
3117 | 51.45 | 104.026 | 29.1689 | 107.5892 | 0.44787 |  | 3117 | 31.28 | 104.026 | 4 | 107.5892
3118 | 51.22 | 109.6435 | 37.6114 | 83.9405 | 0.44775 |  | 3118 | 30 | 109.6435 | 3 | 83.9405
3119 | 48.47 | 78.9047 | 22.2857 | 51.3967 | 0.44664 |  | 3119 | 25.28 | 78.9047 | 2.2679 | 51.3967
3120 | 44.06 | 40.6374 | 30.2751 | 30.2016 | 0.44312 |  | 3120 | 23.2 | 40.6374 | 2 | 30.2016
3121 | 40 | 33.9871 | 32.299 | 29.2029 | 0.43164 |  | 3121 | 22.55 | 33.9871 | 2.2679 | 29.2029
3122 | 37.94 | 32.4059 | 24.7165 | 7.4204 | 0.42927 |  | 3122 | 21.09 | 32.4059 | 3 | 7.4204
3123 | 40.08 | 31.0032 | 28.9627 | 16.0374 | 0.43969 |  | 3123 | 19.61 | 31.0032 | 4 | 16.0374
3124 | 36.96 | 29.5362 | 27.4901 | 49.7937 | 0.43732 |  | 3124 | 19.33 | 29.5362 | 5 | 49.7937
3125 | 36.62 | 28.5032 | 28.6333 | 70.954 | 0.43706 |  | 3125 | 19.87 | 28.5032 | 5.7321 | 70.954
3126 | 37.16 | 28.3345 | 24.4047 | 152.6835 | 0.43727 |  | 3126 | 21.56 | 28.3345 | 6 | 152.6835
3127 | 38.65 | 38.7744 | 33.8486 | 142.76 | 0.43812 |  | 3127 | 28.5 | 38.7744 | 5.7321 | 142.76
3128 | 41.55 | 54.0059 | 45.6095 | 113.1799 | 0.43234 |  | 3128 | 31.87 | 54.0059 | 5 | 113.1799
3129 | 42.4 | 43.4597 | 48.4276 | 84.107 | 0.42296 |  | 3129 | 36.66 | 43.4597 | 4 | 84.107
3130 | 46.58 | 42.7648 | 34.6197 | 92.6175 | 0.41806 |  | 3130 | 34.94 | 42.7648 | 3 | 92.6175
3131 | 45.23 | 44.7403 | 52.5037 | 72.6601 | 0.40884 |  | 3131 | 31.56 | 44.7403 | 2.2679 | 72.6601
3132 | 39.87 | 46.0871 | 50.4524 | 94.2763 | 0.39966 |  | 3132 | 29.27 | 46.0871 | 2 | 94.2763
3133 | 36.09 | 51.5007 | 41.4997 | 76.438 | 0.3777 |  | 3133 | 27.47 | 51.5007 | 2.2679 | 76.438
3134 | 33.19 | 51.685 | 37.5756 | 62.5252 | 0.36838 |  | 3134 | 27.17 | 51.685 | 3 | 62.5252
3135 | 31.79 | 59.2646 | 247.1778 | 69.1298 | 0.36512 |  | 3135 | 26.31 | 59.2646 | 4 | 69.1298
3136 | 31.7 | 73.8932 | 45.0508 | 51.4495 | 0.36101 |  | 3136 | 30.01 | 73.8932 | 5 | 51.4495
3137 | 34.46 | 94.7008 | 42.7086 | 89.8744 | 0.365 |  | 3137 | 29.94 | 94.7008 | 5.7321 | 89.8744
3138 | 37.36 | 128.9963 | 41.9515 | 83.8924 | 0.37977 |  | 3138 | 30.69 | 128.9963 | 6 | 83.8924
3139 | 39.9 | 148.2601 | 40.2993 | 121.2806 | 0.39866 |  | 3139 | 31.93 | 148.2601 | 5.7321 | 121.2806
3140 | 37.88 | 126.5614 | 36.0371 | 117.0172 | 0.41471 |  | 3140 | 32.5 | 126.5614 | 5 | 117.0172
3141 | 45.31 | 103.2499 | 28.4702 | 108.0502 | 0.43072 |  | 3141 | 32.25 | 103.2499 | 4 | 108.0502
3142 | 57.7 | 103.5714 | 19.6979 | 69.7168 | 0.44835 |  | 3142 | 31.99 | 103.5714 | 3 | 69.7168
3143 | 52.91 | 75.9418 | 35.1541 | 43.7824 | 0.4533 |  | 3143 | 30.27 | 75.9418 | 2.2679 | 43.7824
3144 | 43.76 | 38.6738 | 34.0425 | 31.5695 | 0.45499 |  | 3144 | 22.34 | 38.6738 | 2 | 31.5695
3145 | 40.8 | 34.2439 | 29.2721 | 32.0464 | 0.46635 |  | 3145 | 22.4 | 34.2439 | 2.2679 | 32.0464
3146 | 40.5 | 32.7378 | 236.1635 | 5.8508 | 0.46045 |  | 3146 | 20.54 | 32.7378 | 3 | 5.8508
3147 | 39.88 | 31.1054 | 34.8963 | 20.3612 | 0.44417 |  | 3147 | 19.92 | 31.1054 | 4 | 20.3612
3148 | 40.44 | 29.7327 | 34.6622 | 38.0997 | 0.42547 |  | 3148 | 19.11 | 29.7327 | 5 | 38.0997
3149 | 37.4 | 28.7667 | 41.4656 | 96.7794 | 0.41903 |  | 3149 | 19.87 | 28.7667 | 5.7321 | 96.7794
3150 | 28.1 | 28.3158 | 31.7986 | 151.7839 | 0.42233 |  | 3150 | 21.84 | 28.3158 | 6 | 151.7839
3151 | 40.39 | 39.6937 | 26.4196 | 137.9132 | 0.44246 |  | 3151 | 28.96 | 39.6937 | 5.7321 | 137.9132
3152 | 40.56 | 54.3164 | 49.7204 | 152.8264 | 0.44547 |  | 3152 | 35.27 | 54.3164 | 5 | 152.8264
3153 | 40.6 | 43.7299 | 43.6806 | 89.2987 | 0.44216 |  | 3153 | 39.6 | 43.7299 | 4 | 89.2987
3154 | 38.9 | 43.3479 | 41.8515 | 83.5089 | 0.43773 |  | 3154 | 34.94 | 43.3479 | 3 | 83.5089
3155 | 38.2 | 45.5314 | 54.0813 | 78.9032 | 0.43959 |  | 3155 | 35.25 | 45.5314 | 2.2679 | 78.9032
3156 | 39 | 47.8631 | 48.1586 | 65.5114 | 0.43878 |  | 3156 | 38.16 | 47.8631 | 2 | 65.5114
3157 | 37.4 | 50.6627 | 47.9748 | 64.2827 | 0.43108 |  | 3157 | 29.49 | 50.6627 | 2.2679 | 64.2827
3158 | 35 | 52.1011 | 28.1194 | 57.0345 | 0.41528 |  | 3158 | 32.44 | 52.1011 | 3 | 57.0345
3159 | 34.9 | 59.083 | 42.5324 | 68.9494 | 0.40058 |  | 3159 | 32.44 | 59.083 | 4 | 68.9494
3160 | 40.53 | 71.6129 | 66.9833 | 67.8536 | 0.39643 |  | 3160 | 34.94 | 71.6129 | 5 | 67.8536
3161 | 33.2 | 94.6242 | 39.6152 | 87.1441 | 0.38678 |  | 3161 | 34.94 | 94.6242 | 5.7321 | 87.1441
3162 | 40.88 | 129.7549 | 33.444 | 90.3673 | 0.39884 |  | 3162 | 32 | 129.7549 | 6 | 90.3673
3163 | 37.98 | 138.3735 | 45.6159 | 88.2812 | 0.43161 |  | 3163 | 28.55 | 138.3735 | 5.7321 | 88.2812
3164 | 40 | 122.9961 | 18.8309 | 99.983 | 0.46575 |  | 3164 | 31.32 | 122.9961 | 5 | 99.983
3165 | 40.87 | 96.6961 | 31.8212 | 77.8109 | 0.48744 |  | 3165 | 29.94 | 96.6961 | 4 | 77.8109
3166 | 44.1 | 102.9675 | 37.8884 | 59.9074 | 0.50102 |  | 3166 | 25.09 | 102.9675 | 3 | 59.9074
3167 | 44.09 | 76.2549 | 26.9283 | 49.5395 | 0.52051 |  | 3167 | 23.11 | 76.2549 | 2.2679 | 49.5395
3168 | 44.94 | 39.8674 | 31.9539 | 24.7299 | 0.52808 |  | 3168 | 30.99 | 39.8674 | 2 | 24.7299
3169 | 42.59 | 35.8258 | 26.09 | 23.9424 | 0.51727 |  | 3169 | 20.83 | 35.8258 | 2.2679 | 23.9424
3170 | 39.9 | 33.9819 | 33.0964 | 6.4059 | 0.5015 |  | 3170 | 18.62 | 33.9819 | 3 | 6.4059
3171 | 36.8 | 32.2124 | 32.3257 | 23.5844 | 0.47993 |  | 3171 | 17.85 | 32.2124 | 4 | 23.5844
3172 | 31 | 30.5179 | 26.3403 | 37.8168 | 0.47095 |  | 3172 | 18.37 | 30.5179 | 5 | 37.8168
3173 | 35.73 | 29.2841 | 23.4858 | 99.0711 | 0.49465 |  | 3173 | 19.3 | 29.2841 | 5.7321 | 99.0711
3174 | 46.16 | 28.4699 | 26.3001 | 125.1799 | 0.50361 |  | 3174 | 20.32 | 28.4699 | 6 | 125.1799
3175 | 53.01 | 27.9614 | 19.1906 | 123.0791 | 0.49924 |  | 3175 | 24.08 | 27.9614 | 5.7321 | 123.0791
3176 | 53.01 | 29.516 | 49.1833 | 135.2802 | 0.49292 |  | 3176 | 30.93 | 29.516 | 5 | 135.2802
3177 | 47.26 | 48.4469 | 52.3162 | 93.8675 | 0.48573 |  | 3177 | 34.05 | 48.4469 | 4 | 93.8675
3178 | 40 | 68.0612 | 44.7166 | 65.1305 | 0.47865 |  | 3178 | 40.32 | 68.0612 | 3 | 65.1305
3179 | 36.7 | 74.9621 | 44.9177 | 67.6958 | 0.46716 |  | 3179 | 35 | 74.9621 | 2.2679 | 67.6958
3180 | 34.7 | 73.4189 | 44.961 | 69.3046 | 0.44709 |  | 3180 | 37.51 | 73.4189 | 2 | 69.3046
3181 | 32.74 | 79.8418 | 36.818 | 66.6982 | 0.42919 |  | 3181 | 32.53 | 79.8418 | 2.2679 | 66.6982
3182 | 31.33 | 75.4035 | 47.0736 | 67.8786 | 0.42305 |  | 3182 | 36.58 | 75.4035 | 3 | 67.8786
3183 | 30.98 | 70.9413 | 37.4478 | 69.1298 | 0.41977 |  | 3183 | 32.95 | 70.9413 | 4 | 69.1298
3184 | 32.06 | 71.4184 | 34.2474 | 70.7741 | 0.42397 |  | 3184 | 28.09 | 71.4184 | 5 | 70.7741
3185 | 38.94 | 77.5231 | 45.5989 | 64.9978 | 0.4374 |  | 3185 | 32.13 | 77.5231 | 5.7321 | 64.9978
3186 | 43.6 | 123.345 | 40.4498 | 111.2935 | 0.45522 |  | 3186 | 32.44 | 123.345 | 6 | 111.2935
3187 | 48.95 | 146.0997 | 41.0042 | 124.676 | 0.4634 |  | 3187 | 37.44 | 146.0997 | 5.7321 | 124.676
3188 | 51.21 | 119.1433 | 37.5856 | 90.6724 | 0.46895 |  | 3188 | 37.44 | 119.1433 | 5 | 90.6724
3189 | 47.61 | 98.429 | 29.9874 | 96.8948 | 0.47697 |  | 3189 | 32.85 | 98.429 | 4 | 96.8948
3190 | 46.88 | 103.4902 | 39.0391 | 64.1115 | 0.47354 |  | 3190 | 32.03 | 103.4902 | 3 | 64.1115
3191 | 41.26 | 91.9418 | 29.3784 | 49.911 | 0.45377 |  | 3191 | 32.28 | 91.9418 | 2.2679 | 49.911
3192 | 38.34 | 42.8998 | 28.5255 | 22.2086 | 0.44646 |  | 3192 | 25.14 | 42.8998 | 2 | 22.2086
3193 | 35.83 | 35.6567 | 28.1665 | 29.7148 | 0.43838 |  | 3193 | 23.07 | 35.6567 | 2.2679 | 29.7148
3194 | 35.32 | 33.7714 | 36.3729 | 5.7806 | 0.43465 |  | 3194 | 21.41 | 33.7714 | 3 | 5.7806
3195 | 34.96 | 31.8067 | 32.7378 | 19.634 | 0.43431 |  | 3195 | 21.04 | 31.8067 | 4 | 19.634
3196 | 35.6 | 30.1332 | 59.9177 | 52.2456 | 0.44101 |  | 3196 | 20.55 | 30.1332 | 5 | 52.2456
3197 | 38.79 | 29.1359 | 128.6758 | 96.3387 | 0.46835 |  | 3197 | 21.13 | 29.1359 | 5.7321 | 96.3387
3198 | 48.22 | 28.4255 | 140.7127 | 113.2274 | 0.48495 |  | 3198 | 23 | 28.4255 | 6 | 113.2274
3199 | 54.61 | 28.114 | 117.5569 | 164.3502 | 0.48031 |  | 3199 | 28.07 | 28.114 | 5.7321 | 164.3502
3200 | 55.53 | 31.0695 | 146.6242 | 119.4752 | 0.47488 |  | 3200 | 36.14 | 31.0695 | 5 | 119.4752
3201 | 46.98 | 49.1941 | 150.224 | 94.6982 | 0.46658 |  | 3201 | 40.21 | 49.1941 | 4 | 94.6982
3202 | 40.71 | 69.5476 | 131.974 | 87.8617 | 0.4641 |  | 3202 | 38.23 | 69.5476 | 3 | 87.8617
3203 | 36.3 | 75.9452 | 136.7568 | 87.3276 | 0.45954 |  | 3203 | 35.37 | 75.9452 | 2.2679 | 87.3276
3204 | 34.26 | 77.689 | 106.3568 | 90.1671 | 0.44916 |  | 3204 | 35.45 | 77.689 | 2 | 90.1671
3205 | 34 | 82.562 | 33.9278 | 92.723 | 0.4343 |  | 3205 | 30.94 | 82.562 | 2.2679 | 92.723
3206 | 33.84 | 84.2716 | 46.6286 | 58.4072 | 0.42858 |  | 3206 | 27.99 | 84.2716 | 3 | 58.4072
3207 | 34.04 | 80.4258 | 44.7529 | 54.0414 | 0.43299 |  | 3207 | 25.28 | 80.4258 | 4 | 54.0414
3208 | 34.93 | 79.0013 | 53.5317 | 59.838 | 0.44128 |  | 3208 | 23.9 | 79.0013 | 5 | 59.838
3209 | 37.3 | 84.376 | 47.5055 | 81.7592 | 0.45077 |  | 3209 | 23.53 | 84.376 | 5.7321 | 81.7592
3210 | 43.95 | 111.3318 | 48.2181 | 112.138 | 0.46271 |  | 3210 | 24.01 | 111.3318 | 6 | 112.138
3211 | 47.91 | 133.1532 | 43.964 | 120.8562 | 0.46588 |  | 3211 | 26.37 | 133.1532 | 5.7321 | 120.8562
3212 | 48.29 | 141.4377 | 28.3414 | 90.5666 | 0.46827 |  | 3212 | 29 | 141.4377 | 5 | 90.5666
3213 | 48.22 | 104.1707 | 29.3919 | 109.5253 | 0.46847 |  | 3213 | 27.1 | 104.1707 | 4 | 109.5253
3214 | 45.19 | 104.3621 | 39.1619 | 78.265 | 0.47192 |  | 3214 | 25.03 | 104.3621 | 3 | 78.265
3215 | 40.36 | 91.476 | 31.5045 | 44.9895 | 0.47448 |  | 3215 | 26.96 | 91.476 | 2.2679 | 44.9895
3216 | 37.1 | 42.4966 | 32.6561 | 29.236 | 0.45763 |  | 3216 | 23.02 | 42.4966 | 2 | 29.236
3217 | 35.68 | 34.1587 | 31.8005 | 30.3403 | 0.45073 |  | 3217 | 13.76 | 34.1587 | 2.2679 | 30.3403
3218 | 35.57 | 32.4872 | 29.3276 | 5.1362 | 0.45505 |  | 3218 | 19.94 | 32.4872 | 3 | 5.1362
3219 | 35.44 | 30.9038 | 36.5272 | 22.2872 | 0.46092 |  | 3219 | 19.86 | 30.9038 | 4 | 22.2872
3220 | 34.38 | 29.5894 | 45.4041 | 54.0374 | 0.46778 |  | 3220 | 19.59 | 29.5894 | 5 | 54.0374
3221 | 36.21 | 28.6659 | 62.6768 | 102.0679 | 0.48052 |  | 3221 | 19.06 | 28.6659 | 5.7321 | 102.0679
3222 | 44.1 | 28.176 | 57.4704 | 127.3648 | 0.48964 |  | 3222 | 19.41 | 28.176 | 6 | 127.3648
3223 | 50.99 | 40.1134 | 29.6982 | 130.1289 | 0.485 |  | 3223 | 18.85 | 40.1134 | 5.7321 | 130.1289
3224 | 55.07 | 54.4045 | 46.9642 | 115.7248 | 0.48146 |  | 3224 | 20.13 | 54.4045 | 5 | 115.7248
3225 | 47.82 | 44.2703 | 55.0486 | 101.759 | 0.47575 |  | 3225 | 20.88 | 44.2703 | 4 | 101.759
3226 | 44.84 | 42.5854 | 37.2176 | 71.0148 | 0.47325 |  | 3226 | 22.44 | 42.5854 | 3 | 71.0148
3227 | 40.94 | 45.3156 | 41.7937 | 79.0536 | 0.4696 |  | 3227 | 25.31 | 45.3156 | 2.2679 | 79.0536
3228 | 38.77 | 47.484 | 31.8298 | 89.1397 | 0.45753 |  | 3228 | 28 | 47.484 | 2 | 89.1397
3229 | 35.67 | 51.1733 | 34.5191 | 69.0358 | 0.45253 |  | 3229 | 26 | 51.1733 | 2.2679 | 69.0358
3230 | 35.57 | 53.1719 | 45.2469 | 76.3206 | 0.46159 |  | 3230 | 22.44 | 53.1719 | 3 | 76.3206
3231 | 34.28 | 60.1635 | 52.0297 | 59.0308 | 0.45839 |  | 3231 | 20.97 | 60.1635 | 4 | 59.0308
3232 | 35.52 | 75.6102 | 40.8392 | 63.4419 | 0.46354 |  | 3232 | 20.71 | 75.6102 | 5 | 63.4419
3233 | 40 | 93.2695 | 49.3277 | 62.0399 | 0.47246 |  | 3233 | 20.7 | 93.2695 | 5.7321 | 62.0399
3234 | 44.11 | 127.9407 | 44.3988 | 111.2935 | 0.47918 |  | 3234 | 20.13 | 127.9407 | 6 | 111.2935
3235 | 45.8 | 141.8579 | 43.3462 | 97.0881 | 0.48063 |  | 3235 | 20 | 141.8579 | 5.7321 | 97.0881
3236 | 44.37 | 148.1341 | 33.8248 | 110.5632 | 0.48191 |  | 3236 | 20.71 | 148.1341 | 5 | 110.5632
3237 | 43.23 | 102.6445 | 23.1677 | 87.9521 | 0.48109 |  | 3237 | 20.42 | 102.6445 | 4 | 87.9521
3238 | 43.5 | 102.5255 | 29.8839 | 69.3665 | 0.47897 |  | 3238 | 19.3 | 102.5255 | 3 | 69.3665
3239 | 38.91 | 76.0359 | 230.6124 | 51.536 | 0.47362 |  | 3239 | 23.6 | 76.0359 | 2.2679 | 51.536
3240 | 34.5 | 40.1797 | 37.8818 | 31.7036 | 0.46817 |  | 3240 | 21.3 | 40.1797 | 2 | 31.7036
3241 | 34.5 | 36.2996 | 32.8581 | 30.6531 | 0.45487 |  | 3241 | 23.81 | 36.2996 | 2.2679 | 30.6531
3242 | 34.01 | 34.3204 | 26.7949 | 6.374 | 0.44888 |  | 3242 | 20.15 | 34.3204 | 3 | 6.374
3243 | 32.07 | 32.4079 | 30.9979 | 21.5404 | 0.45277 |  | 3243 | 19.62 | 32.4079 | 4 | 21.5404
3244 | 33.09 | 30.5299 | 28.6788 | 39.1842 | 0.46403 |  | 3244 | 19.35 | 30.5299 | 5 | 39.1842
3245 | 35.05 | 29.412 | 31.281 | 97.132 | 0.47433 |  | 3245 | 18.68 | 29.412 | 5.7321 | 97.132
3246 | 42.7 | 29.1993 | 42.6652 | 152.6835 | 0.48928 |  | 3246 | 18.64 | 29.1993 | 6 | 152.6835
3247 | 47.21 | 40.9212 | 61.8929 | 129.1008 | 0.48914 |  | 3247 | 18.49 | 40.9212 | 5.7321 | 129.1008
3248 | 49.3 | 53.7062 | 63.0743 | 145.8615 | 0.47912 |  | 3248 | 19.17 | 53.7062 | 5 | 145.8615
3249 | 45.06 | 44.6891 | 60.7076 | 121.6955 | 0.47469 |  | 3249 | 19.94 | 44.6891 | 4 | 121.6955
3250 | 44.23 | 44.4839 | 135.3766 | 66.4202 | 0.47065 |  | 3250 | 20.93 | 44.4839 | 3 | 66.4202
3251 | 43.93 | 48.8625 | 101.2465 | 62.4306 | 0.46306 |  | 3251 | 24.82 | 48.8625 | 2.2679 | 62.4306
3252 | 41.7 | 50.169 | 66.6185 | 87.5592 | 0.46298 |  | 3252 | 24.75 | 50.169 | 2 | 87.5592
3253 | 39.97 | 54.7274 | 44.3954 | 68.0228 | 0.46598 |  | 3253 | 30 | 54.7274 | 2.2679 | 68.0228
3254 | 38.87 | 54.2291 | 29.4771 | 55.3873 | 0.46112 |  | 3254 | 46.65 | 54.2291 | 3 | 55.3873
3255 | 37.97 | 62.336 | 52.1493 | 56.3257 | 0.45172 |  | 3255 | 35.42 | 62.336 | 4 | 56.3257
3256 | 35.9 | 78.1848 | 31.7932 | 50.766 | 0.44692 |  | 3256 | 30.01 | 78.1848 | 5 | 50.766
3257 | 39.05 | 98.6763 | 37.5659 | 86.0064 | 0.45233 |  | 3257 | 22.44 | 98.6763 | 5.7321 | 86.0064
3258 | 40.97 | 131.7691 | 45.0684 | 85.4877 | 0.45885 |  | 3258 | 22.44 | 131.7691 | 6 | 85.4877
3259 | 42.8 | 151.6255 | 47.0179 | 117.779 | 0.45857 |  | 3259 | 21.15 | 151.6255 | 5.7321 | 117.779
3260 | 41.58 | 133.1746 | 40.1616 | 108.9762 | 0.46244 |  | 3260 | 22.12 | 133.1746 | 5 | 108.9762
3261 | 41.38 | 102.4575 | 229.0694 | 89.0584 | 0.4654 |  | 3261 | 22.41 | 102.4575 | 4 | 89.0584
3262 | 40.83 | 105.1076 | 31.2023 | 82.4691 | 0.46845 |  | 3262 | 22.95 | 105.1076 | 3 | 82.4691
3263 | 36.79 | 80.8511 | 28.3914 | 51.9538 | 0.46008 |  | 3263 | 26 | 80.8511 | 2.2679 | 51.9538
3264 | 35.7 | 42.1967 | 58.7772 | 31.2208 | 0.45382 |  | 3264 | 30.04 | 42.1967 | 2 | 31.2208
3265 | 35.18 | 35.872 | 118.9531 | 32.7573 | 0.44891 |  | 3265 | 37 | 35.872 | 2.2679 | 32.7573
3266 | 34.25 | 34.0281 | 87.1981 | 6.7696 | 0.4471 |  | 3266 | 20.79 | 34.0281 | 3 | 6.7696
3267 | 33.79 | 32.0621 | 29.003 | 22.2872 | 0.44828 |  | 3267 | 19.29 | 32.0621 | 4 | 22.2872
3268 | 34 | 30.4695 | 36.5343 | 51.0197 | 0.45664 |  | 3268 | 19.14 | 30.4695 | 5 | 51.0197
3269 | 36.09 | 29.1843 | 42.9382 | 80.297 | 0.46916 |  | 3269 | 19.09 | 29.1843 | 5.7321 | 80.297
3270 | 41.13 | 28.9035 | 80.6629 | 138.4176 | 0.48318 |  | 3270 | 20.09 | 28.9035 | 6 | 138.4176
3271 | 46.71 | 39.3904 | 84.8779 | 175.3656 | 0.48095 |  | 3271 | 20.65 | 39.3904 | 5.7321 | 175.3656
3272 | 50.89 | 55.2191 | 87.0637 | 155.3713 | 0.48087 |  | 3272 | 21.33 | 55.2191 | 5 | 155.3713
3273 | 49.17 | 42.3754 | 97.4079 | 83.3801 | 0.48303 |  | 3273 | 22.54 | 42.3754 | 4 | 83.3801
3274 | 46.27 | 39.8556 | 42.8937 | 75.8512 | 0.48986 |  | 3274 | 23.66 | 39.8556 | 3 | 75.8512
3275 | 46.03 | 42.2475 | 40.2407 | 88.155 | 0.49183 |  | 3275 | 23.87 | 42.2475 | 2.2679 | 88.155
3276 | 44.86 | 43.3752 | 46.6707 | 91.1944 | 0.48847 |  | 3276 | 24.94 | 43.3752 | 2 | 91.1944
3277 | 41.6 | 46.4569 | 45.5196 | 79.5547 | 0.48278 |  | 3277 | 24.99 | 46.4569 | 2.2679 | 79.5547
3278 | 39.15 | 48.6398 | 39.8653 | 73.7811 | 0.48243 |  | 3278 | 24.27 | 48.6398 | 3 | 73.7811
3279 | 38.49 | 55.5778 | 48.4605 | 60.2932 | 0.48317 |  | 3279 | 20.98 | 55.5778 | 4 | 60.2932
3280 | 39.04 | 71.9725 | 49.2971 | 51.9466 | 0.47975 |  | 3280 | 21.3 | 71.9725 | 5 | 51.9466
3281 | 42.53 | 93.4308 | 43.3388 | 65.1495 | 0.4784 |  | 3281 | 21.43 | 93.4308 | 5.7321 | 65.1495
3282 | 48.36 | 134.5208 | 30.9929 | 77.7928 | 0.48076 |  | 3282 | 23.5 | 134.5208 | 6 | 77.7928
3283 | 52.61 | 156.5026 | 48.9254 | 122.9783 | 0.4835 |  | 3283 | 24 | 156.5026 | 5.7321 | 122.9783
3284 | 52.55 | 127.1281 | 32.7926 | 109.5052 | 0.48584 |  | 3284 | 27.16 | 127.1281 | 5 | 109.5052
3285 | 48.83 | 100.1759 | 53.2163 | 101.2279 | 0.4911 |  | 3285 | 28.37 | 100.1759 | 4 | 101.2279
3286 | 48.32 | 103.9766 | 99.1263 | 75.112 | 0.49024 |  | 3286 | 32.07 | 103.9766 | 3 | 75.112
3287 | 43.47 | 80.94 | 110.3036 | 49.8645 | 0.48672 |  | 3287 | 38.37 | 80.94 | 2.2679 | 49.8645
3288 | 37.37 | 41.7263 | 101.9978 | 31.2208 | 0.49007 |  | 3288 | 37.31 | 41.7263 | 2 | 31.2208
3289 | 34.39 | 33.3852 | 59.4274 | 26.0751 | 0.48703 |  | 3289 | 30 | 33.3852 | 2.2679 | 26.0751
3290 | 34.85 | 31.9954 | 34.9719 | 5.2638 | 0.47719 |  | 3290 | 24 | 31.9954 | 3 | 5.2638
3291 | 34.11 | 30.6658 | 27.702 | 23.152 | 0.46564 |  | 3291 | 22.82 | 30.6658 | 4 | 23.152
3292 | 34.76 | 29.4094 | 28.499 | 53.8017 | 0.45468 |  | 3292 | 21.6 | 29.4094 | 5 | 53.8017
3293 | 33.42 | 28.4682 | 41.6417 | 81.7954 | 0.4566 |  | 3293 | 21.73 | 28.4682 | 5.7321 | 81.7954
3294 | 33.92 | 28.0436 | 108.2222 | 154.0972 | #DIV/0! |  | 3294 | 22.91 | 28.0436 | 6 | 154.0972
3295 | 36.24 | 37.9016 | 95.2996 | 152.7473 | 0.4628 |  | 3295 | 29.95 | 37.9016 | 5.7321 | 152.7473
3296 | 38.99 | 53.2517 | 83.8941 | 111.8405 | #DIV/0! |  | 3296 | 36.36 | 53.2517 | 5 | 111.8405
3297 | 37.52 | 42.8167 | 94.2167 | 87.3259 | #DIV/0! |  | 3297 | 38 | 42.8167 | 4 | 87.3259
3298 | 35.12 | 41.933 | 92.5897 | 66.1784 | #DIV/0! |  | 3298 | 38.52 | 41.933 | 3 | 66.1784
3299 | 34.79 | 44.4035 | 52.6935 | 87.7037 | #DIV/0! |  | 3299 | 37.35 | 44.4035 | 2.2679 | 87.7037
3300 | 33.9 | 44.3177 | 47.7061 | 93.8022 | 0.44409 |  | 3300 | 33.05 | 44.3177 | 2 | 93.8022
3301 | 33.05 | 48.2703 | 47.4102 | 93.1126 | 0.43855 |  | 3301 | 31.93 | 48.2703 | 2.2679 | 93.1126
3302 | 32.36 | 49.6512 | 45.2859 | 60.5348 | 0.43476 |  | 3302 | 30.54 | 49.6512 | 3 | 60.5348
3303 | 33.25 | 55.77 | 29.3491 | 53.3802 | 0.44584 |  | 3303 | 32.91 | 55.77 | 4 | 53.3802
3304 | 34.1 | 69.6602 | 41.282 | 63.3798 | 0.44826 |  | 3304 | 32.62 | 69.6602 | 5 | 63.3798
3305 | 35.36 | 90.3362 | 41.4267 | 85.8547 | #DIV/0! |  | 3305 | 30.02 | 90.3362 | 5.7321 | 85.8547
3306 | 42.9 | 133.8674 | 41.2549 | 86.8014 | 0.45977 |  | 3306 | 30.16 | 133.8674 | 6 | 86.8014
3307 | 44.93 | 133.5879 | 51.5355 | 110.3515 | 0.48649 |  | 3307 | 34.64 | 133.5879 | 5.7321 | 110.3515
3308 | 45.17 | 115.8886 | 36.409 | 115.7475 | 0.49334 |  | 3308 | 34.92 | 115.8886 | 5 | 115.7475
3309 | 44.75 | 98.4252 | 31.4456 | 101.0435 | 0.47978 |  | 3309 | 36.76 | 98.4252 | 4 | 101.0435
3310 | 44.96 | 99.7625 | 29.7903 | 61.3088 | 0.48016 |  | 3310 | 37.44 | 99.7625 | 3 | 61.3088
3311 | 42 | 74.6788 | 25.2184 | 39.1859 | 0.48467 |  | 3311 | 33.22 | 74.6788 | 2.2679 | 39.1859
3312 | 39.66 | 38.828 | 29.6094 | 22.5036 | 0.49022 |  | 3312 | 29 | 38.828 | 2 | 22.5036
3313 | 36.02 | 33.8916 | 26.4012 | 23.1178 | 0.48637 |  | 3313 | 24.52 | 33.8916 | 2.2679 | 23.1178
3314 | 35 | 32.2873 | 28.4328 | 5.6339 | 0.48166 |  | 3314 | 24.25 | 32.2873 | 3 | 5.6339
3315 | 34.03 | 30.7645 | 29.4942 | 18.042 | 0.47198 |  | 3315 | 23.89 | 30.7645 | 4 | 18.042
3316 | 34.18 | 29.4203 | 33.0559 | 47.1059 | 0.469 |  | 3316 | 22.92 | 29.4203 | 5 | 47.1059
3317 | 33.91 | 28.5967 | 37.4552 | 90.9621 | 0.45329 |  | 3317 | 23.31 | 28.5967 | 5.7321 | 90.9621
3318 | 33.37 | 28.3066 | 236.0842 | 138.6747 | 0.44139 |  | 3318 | 24.57 | 28.3066 | 6 | 138.6747
3319 | 34.04 | 39.7254 | 31.5798 | 150.3973 | 0.4308 |  | 3319 | 31.12 | 39.7254 | 5.7321 | 150.3973
3320 | 35.07 | 53.5821 | 32.0556 | 140.6378 | 0.42562 |  | 3320 | 37.06 | 53.5821 | 5 | 140.6378
3321 | 35.02 | 44.538 | 38.4168 | 89.1949 | 0.4224 |  | 3321 | 39.48 | 44.538 | 4 | 89.1949
3322 | 34.08 | 44.3949 | 32.7043 | 83.5089 | 0.41936 |  | 3322 | 35.31 | 44.3949 | 3 | 83.5089
3323 | 34.1 | 47.0882 | 42.3379 | 70.2532 | 0.41826 |  | 3323 | 32.58 | 47.0882 | 2.2679 | 70.2532
3324 | 33.8 | 49.5755 | 47.5299 | 84.7934 | 0.41276 |  | 3324 | 31.73 | 49.5755 | 2 | 84.7934
3325 | 29.64 | 51.4139 | 48.0037 | 67.3995 | 0.40009 |  | 3325 | 31.77 | 51.4139 | 2.2679 | 67.3995
3326 | 27.41 | 55.0434 | 45.1027 | 56.6227 | 0.38415 |  | 3326 | 31.42 | 55.0434 | 3 | 56.6227
3327 | 27.49 | 60.5581 | 40.3975 | 56.3257 | 0.37811 |  | 3327 | 31.04 | 60.5581 | 4 | 56.3257
3328 | 30.28 | 76.7658 | 44.5115 | 53.3136 | 0.38728 |  | 3328 | 30.85 | 76.7658 | 5 | 53.3136
3329 | 34.47 | 96.2741 | 40.676 | 82.821 | 0.4113 |  | 3329 | 31.32 | 96.2741 | 5.7321 | 82.821
3330 | 38.28 | 138.8103 | 55.555 | 77.0421 | 0.425 |  | 3330 | 31.69 | 138.8103 | 6 | 77.0421
3331 | 42.28 | 147.838 | 33.9009 | 127.1165 | 0.43503 |  | 3331 | 33.08 | 147.838 | 5.7321 | 127.1165
3332 | 42.34 | 125.8386 | 34.7351 | 116.8056 | 0.45164 |  | 3332 | 34.94 | 125.8386 | 5 | 116.8056
3333 | 41.71 | 98.0093 | 32.4057 | 82.2361 | 0.46449 |  | 3333 | 34.64 | 98.0093 | 4 | 82.2361
3334 | 43.33 | 102.5756 | 29.8794 | 82.4691 | 0.45989 |  | 3334 | 34.95 | 102.5756 | 3 | 82.4691
3335 | 38.94 | 77.7466 | 34.188 | 52.2324 | 0.46316 |  | 3335 | 33.09 | 77.7466 | 2.2679 | 52.2324
3336 | 37.3 | 39.7123 | 23.0481 | 32.1596 | 0.45799 |  | 3336 | 27.2 | 39.7123 | 2 | 32.1596
3337 | 35 | 35.3835 | 30.6216 | 22.9756 | 0.46015 |  | 3337 | 25.29 | 35.3835 | 2.2679 | 22.9756
3338 | 34.55 | 33.6665 | 32.3765 | 7.414 | 0.45281 |  | 3338 | 22.91 | 33.6665 | 3 | 7.414
3339 | 34.9 | 31.8372 | 39.7977 | 22.1693 | 0.45653 |  | 3339 | 22.23 | 31.8372 | 4 | 22.1693
3340 | 33.77 | 30.2157 | 37.0851 | 48.662 | 0.47547 |  | 3340 | 21.85 | 30.2157 | 5 | 48.662
3341 | 36.04 | 29.0582 | 29.8198 | 84.1752 | 0.48274 |  | 3341 | 22.29 | 29.0582 | 5.7321 | 84.1752
3342 | 47.8 | 28.1252 | 35.7167 | 104.6165 | 0.48993 |  | 3342 | 23.9 | 28.1252 | 6 | 104.6165
3343 | 60.4 | 27.6431 | 32.5085 | 171.4001 | 0.48679 |  | 3343 | 31.58 | 27.6431 | 5.7321 | 171.4001
3344 | 62.67 | 29.7975 | 30.8435 | 138.2269 | 0.48496 |  | 3344 | 39.4 | 29.7975 | 5 | 138.2269
3345 | 57.7 | 47.9314 | 40.026 | 121.1763 | 0.48124 |  | 3345 | 46 | 47.9314 | 4 | 121.1763
3346 | 56.63 | 66.5928 | 42.6697 | 71.9821 | 0.4752 |  | 3346 | 44.13 | 66.5928 | 3 | 71.9821
3347 | 55.5 | 74.9257 | 56.4883 | 73.9388 | 0.47445 |  | 3347 | 45 | 74.9257 | 2.2679 | 73.9388
3348 | 51.99 | 72.9682 | 62.8589 | 74.2041 | 0.47456 |  | 3348 | 44.91 | 72.9682 | 2 | 74.2041
3349 | 50.29 | 78.3892 | 43.9801 | 62.4127 | 0.47639 |  | 3349 | 40.07 | 78.3892 | 2.2679 | 62.4127
3350 | 47.59 | 75.2572 | 50.7985 | 80.6445 | 0.47668 |  | 3350 | 38.96 | 75.2572 | 3 | 80.6445
3351 | 45.63 | 68.7374 | 45.1892 | 52.1178 | 0.47038 |  | 3351 | 35 | 68.7374 | 4 | 52.1178
3352 | 44.37 | 73.9826 | 25.0289 | 69.842 | 0.46637 |  | 3352 | 33.06 | 73.9826 | 5 | 69.842
3353 | 46.09 | 74.3343 | 49.8665 | 63.5568 | 0.46865 |  | 3353 | 31.91 | 74.3343 | 5.7321 | 63.5568
3354 | 47.91 | 105.1316 | 48.8867 | 81.6402 | 0.46764 |  | 3354 | 32.35 | 105.1316 | 6 | 81.6402
3355 | 49.39 | 148.013 | 41.5016 | 99.953 | 0.46526 |  | 3355 | 34 | 148.013 | 5.7321 | 99.953
3356 | 46.18 | 140.4114 | 36.6741 | 96.5973 | 0.46482 |  | 3356 | 36.08 | 140.4114 | 5 | 96.5973
3357 | 45.8 | 98.8164 | 28.9616 | 93.0227 | 0.46846 |  | 3357 | 34.96 | 98.8164 | 4 | 93.0227
3358 | 44.17 | 99.657 | 33.7395 | 67.9652 | 0.47079 |  | 3358 | 33.85 | 99.657 | 3 | 67.9652
3359 | 37.66 | 91.5939 | 26.6979 | 52.9753 | 0.4691 |  | 3359 | 32.08 | 91.5939 | 2.2679 | 52.9753
3360 | 35.2 | 41.6087 | 26.6732 | 21.5917 | 0.46028 |  | 3360 | 29.14 | 41.6087 | 2 | 21.5917
3361 | 34.44 | 35.5577 | 32.8984 | 25.4211 | 0.44342 |  | 3361 | 24.73 | 35.5577 | 2.2679 | 25.4211
3362 | 33.12 | 33.7772 | 23.7404 | 5.2702 | 0.43311 |  | 3362 | 23.42 | 33.7772 | 3 | 5.2702
3363 | 31.49 | 31.9643 | 31.559 | 22.5034 | 0.43138 |  | 3363 | 21.5 | 31.9643 | 4 | 22.5034
3364 | 32.37 | 30.2783 | 33.4525 | 49.6051 | 0.43159 |  | 3364 | 21.34 | 30.2783 | 5 | 49.6051
3365 | 34.25 | 29.0162 | 36.0945 | 103.6545 | 0.43873 |  | 3365 | 21.52 | 29.0162 | 5.7321 | 103.6545
3366 | 40.52 | 28.3344 | 28.9339 | 130.3208 | 0.44978 |  | 3366 | 23.23 | 28.3344 | 6 | 130.3208
3367 | 49.92 | 27.9891 | 24.7975 | 130.4227 | 0.44946 |  | 3367 | 27.71 | 27.9891 | 5.7321 | 130.4227
3368 | 57.61 | 30.5326 | 42.5631 | 124.0291 | 0.45193 |  | 3368 | 33.07 | 30.5326 | 5 | 124.0291
3369 | 55 | 49.6001 | 43.4421 | 103.5242 | 0.45451 |  | 3369 | 34.97 | 49.6001 | 4 | 103.5242
3370 | 52.52 | 68.6099 | 39.7577 | 67.1457 | 0.45158 |  | 3370 | 32.37 | 68.6099 | 3 | 67.1457
3371 | 51.15 | 73.8179 | 52.7402 | 71.6823 | 0.45042 |  | 3371 | 29.94 | 73.8179 | 2.2679 | 71.6823
3372 | 49.85 | 75.3427 | 50.3283 | 88.5866 | 0.44833 |  | 3372 | 28 | 75.3427 | 2 | 88.5866
3373 | 46.27 | 75.6321 | 47.6919 | 83.6844 | 0.44662 |  | 3373 | 27.44 | 75.6321 | 2.2679 | 83.6844
3374 | 43.95 | 78.4825 | 34.6744 | 60.8094 | 0.44367 |  | 3374 | 26.4 | 78.4825 | 3 | 60.8094
3375 | 41.14 | 76.975 | 251.4478 | 69.6708 | 0.44591 |  | 3375 | 27.72 | 76.975 | 4 | 69.6708
3376 | 40.52 | 74.551 | 35.4781 | 51.0145 | 0.44567 |  | 3376 | 30.11 | 74.551 | 5 | 51.0145
3377 | 42.45 | 77.4664 | 38.4082 | 74.7816 | 0.4439 |  | 3377 | 27.72 | 77.4664 | 5.7321 | 74.7816
3378 | 45.95 | 117.1002 | 42.9915 | 92.5256 | 0.44526 |  | 3378 | 28.9 | 117.1002 | 6 | 92.5256
3379 | 46.96 | 129.2317 | 35.7009 | 86.2652 | 0.44591 |  | 3379 | 32.69 | 129.2317 | 5.7321 | 86.2652
3380 | 44.87 | 130.114 | 29.3203 | 102.2049 | 0.44939 |  | 3380 | 33.92 | 130.114 | 5 | 102.2049
3381 | 44.11 | 102.2992 | 30.6894 | 75.7826 | 0.45113 |  | 3381 | 34.06 | 102.2992 | 4 | 75.7826
3382 | 41.49 | 97.5456 | 32.04 | 65.0223 | 0.45585 |  | 3382 | 33.21 | 97.5456 | 3 | 65.0223
3383 | 35.18 | 90.7838 | 29.9065 | 54.786 | 0.44429 |  | 3383 | 33.66 | 90.7838 | 2.2679 | 54.786
3384 | 32.66 | 41.9079 | 30.9515 | 31.2744 | 0.44153 |  | 3384 | 31 | 41.9079 | 2 | 31.2744
3385 | 32.5 | 34.8685 | 29.2278 | 23.26 | 0.43863 |  | 3385 | 28.26 | 34.8685 | 2.2679 | 23.26
3386 | 29.66 | 33.098 | 30.8129 | 7.363 | 0.4321 |  | 3386 | 23.49 | 33.098 | 3 | 7.363
3387 | 29 | 31.3519 | 26.1858 | 20.4398 | 0.42731 |  | 3387 | 22.6 | 31.3519 | 4 | 20.4398
3388 | 29.61 | 29.8448 | 45.444 | 55.2163 | 0.42928 |  | 3388 | 22.12 | 29.8448 | 5 | 55.2163
3389 | 33.09 | 28.9395 | 60.5766 | 103.5664 | 0.45095 |  | 3389 | 22.19 | 28.9395 | 5.7321 | 103.5664
3390 | 37.6 | 28.6352 | 80.7938 | 144.9722 | 0.47237 |  | 3390 | 21.34 | 28.6352 | 6 | 144.9722
3391 | 46.6 | 40.656 | 50.1859 | 139.5288 | 0.47642 |  | 3391 | 21.14 | 40.656 | 5.7321 | 139.5288
3392 | 50.35 | 55.9973 | 57.6724 | 131.3959 | 0.47928 |  | 3392 | 24.41 | 55.9973 | 5 | 131.3959
3393 | 48.37 | 44.3172 | 51.4598 | 90.2333 | 0.47863 |  | 3393 | 24.27 | 44.3172 | 4 | 90.2333
3394 | 45.77 | 42.3852 | 98.6346 | 85.5241 | 0.47911 |  | 3394 | 24.94 | 42.3852 | 3 | 85.5241
3395 | 42.41 | 46.9506 | 81.8815 | 74.4654 | 0.48064 |  | 3395 | 24.25 | 46.9506 | 2.2679 | 74.4654
3396 | 40.99 | 47.8304 | 58.9091 | 65.1953 | 0.4808 |  | 3396 | 24.12 | 47.8304 | 2 | 65.1953
3397 | 38.65 | 52.3332 | 47.9897 | 66.1528 | 0.47972 |  | 3397 | 23.63 | 52.3332 | 2.2679 | 66.1528
3398 | 36.99 | 51.9017 | 40.1196 | 82.3603 | 0.47599 |  | 3398 | 21.61 | 51.9017 | 3 | 82.3603
3399 | 36.02 | 59.9379 | 40.3141 | 69.7309 | 0.47585 |  | 3399 | 21.24 | 59.9379 | 4 | 69.7309
3400 | 35.71 | 72.9478 | 44.5415 | 69.0342 | 0.47919 |  | 3400 | 21.5 | 72.9478 | 5 | 69.0342
3401 | 39 | 93.8115 | 63.0969 | 64.6186 | 0.48288 |  | 3401 | 21.5 | 93.8115 | 5.7321 | 64.6186
3402 | 42.85 | 124.2584 | 46.5804 | 90.2735 | 0.48392 |  | 3402 | 22.87 | 124.2584 | 6 | 90.2735
3403 | 47.47 | 154.4254 | 50.336 | 123.4027 | 0.49094 |  | 3403 | 24.37 | 154.4254 | 5.7321 | 123.4027
3404 | 48.99 | 134.5117 | 26.7798 | 113.7373 | 0.49955 |  | 3404 | 26.28 | 134.5117 | 5 | 113.7373
3405 | 48.14 | 103.7673 | 27.5845 | 79.286 | 0.50514 |  | 3405 | 38.68 | 103.7673 | 4 | 79.286
3406 | 48.45 | 102.6638 | 32.4132 | 57.385 | 0.50741 |  | 3406 | 37.96 | 102.6638 | 3 | 57.385
3407 | 41.16 | 77.9884 | 35.1967 | 48.936 | 0.5071 |  | 3407 | 30.2 | 77.9884 | 2.2679 | 48.936
3408 | 35.8 | 41.0316 | 29.8266 | 22.5305 | 0.4902 |  | 3408 | 29.94 | 41.0316 | 2 | 22.5305
3409 | 33.32 | 35.0154 | 25.5663 | 32.8711 | 0.47346 |  | 3409 | 20.5 | 35.0154 | 2.2679 | 32.8711
3410 | 32.37 | 33.2102 | 30.5039 | 6.189 | 0.45771 |  | 3410 | 21.7 | 33.2102 | 3 | 6.189
3411 | 31.15 | 31.4854 | 227.158 | 23.0341 | 0.44465 |  | 3411 | 19.65 | 31.4854 | 4 | 23.0341
3412 | 30.72 | 30.05 | 41.9549 | 45.4556 | 0.44742 |  | 3412 | 21.11 | 30.05 | 5 | 45.4556
3413 | 33.72 | 29.0364 | 74.8221 | 94.4878 | 0.44903 |  | 3413 | 21.35 | 29.0364 | 5.7321 | 94.4878
3414 | 39.18 | 28.5958 | 84.3253 | 152.555 | 0.45942 |  | 3414 | 22.1 | 28.5958 | 6 | 152.555
3415 | 46.77 | 40.187 | 40.7297 | 157.4472 | 0.45472 |  | 3415 | 20.95 | 40.187 | 5.7321 | 157.4472
3416 | 47.06 | 55.4264 | 61.1006 | 135.682 | 0.45417 |  | 3416 | 21.48 | 55.4264 | 5 | 135.682
3417 | 40.86 | 43.7225 | 70.0453 | 90.8563 | 0.45356 |  | 3417 | 22.58 | 43.7225 | 4 | 90.8563
3418 | 35.85 | 42.0033 | 79.7031 | 90.9247 | 0.44469 |  | 3418 | 26.2 | 42.0033 | 3 | 90.9247
3419 | 35.6 | 44.4408 | 57.97 | 64.4614 | 0.43927 |  | 3419 | 27 | 44.4408 | 2.2679 | 64.4614
3420 | 35.56 | 44.721 | 81.6758 | 81.3953 | 0.4343 |  | 3420 | 36 | 44.721 | 2 | 81.3953
3421 | 35.74 | 47.8559 | 52.6056 | 80.0223 | 0.43735 |  | 3421 | 50.04 | 47.8559 | 2.2679 | 80.0223
3422 | 35.55 | 51.2787 | 38.3091 | 76.8696 | 0.44504 |  | 3422 | 50.75 | 51.2787 | 3 | 76.8696
3423 | 36.76 | 57.5373 | 37.2129 | 53.5004 | 0.45573 |  | 3423 | 38.2 | 57.5373 | 4 | 53.5004
3424 | 37.57 | 74.3358 | 47.2863 | 52.4437 | 0.45994 |  | 3424 | 32.44 | 74.3358 | 5 | 52.4437
3425 | 43.04 | 93.2494 | 52.4271 | 80.1665 | 0.47187 |  | 3425 | 25.56 | 93.2494 | 5.7321 | 80.1665
3426 | 48.55 | 139.1877 | 51.9714 | 111.575 | 0.47848 |  | 3426 | 22.56 | 139.1877 | 6 | 111.575
3427 | 52.38 | 147.8055 | 39.3758 | 103.2424 | 0.48561 |  | 3427 | 22.58 | 147.8055 | 5.7321 | 103.2424
3428 | 54.95 | 120.0825 | 33.1127 | 88.3448 | 0.4903 |  | 3428 | 23.99 | 120.0825 | 5 | 88.3448
3429 | 51.98 | 97.1219 | 34.2423 | 83.0659 | 0.49514 |  | 3429 | 25.32 | 97.1219 | 4 | 83.0659
3430 | 49.41 | 99.7013 | 22.7174 | 59.0666 | 0.49594 |  | 3430 | 26.11 | 99.7013 | 3 | 59.0666
3431 | 45.08 | 75.2914 | 32.5334 | 49.7717 | 0.49438 |  | 3431 | 29.94 | 75.2914 | 2.2679 | 49.7717
3432 | 39.9 | 40.0631 | 32.7497 | 31.8109 | 0.48584 |  | 3432 | 33.49 | 40.0631 | 2 | 31.8109
3433 | 35.24 | 34.7427 | 23.0275 | 25.8191 | 0.4688 |  | 3433 | 22.8 | 34.7427 | 2.2679 | 25.8191
3434 | 34.93 | 33.0065 | 33.8662 | 6.2081 | 0.4553 |  | 3434 | 20.89 | 33.0065 | 3 | 6.2081
3435 | 33.87 | 31.452 | 23.7753 | 16.568 | 0.44559 |  | 3435 | 19.51 | 31.452 | 4 | 16.568
3436 | 34.46 | 29.8796 | 36.5353 | 52.7643 | 0.44167 |  | 3436 | 18.91 | 29.8796 | 5 | 52.7643
3437 | 34.98 | 28.8828 | 48.1827 | 89.2874 | 0.44116 |  | 3437 | 19.46 | 28.8828 | 5.7321 | 89.2874
3438 | 40.16 | 28.5669 | 86.2951 | 107.958 | 0.4527 |  | 3438 | 20.69 | 28.5669 | 6 | 107.958
3439 | 49.74 | 40.1483 | 55.8365 | 136.2976 | 0.45496 |  | 3439 | 28.05 | 40.1483 | 5.7321 | 136.2976
3440 | 50.95 | 53.7774 | 69.2993 | 160.461 | 0.45549 |  | 3440 | 34.51 | 53.7774 | 5 | 160.461
3441 | 45.94 | 42.2993 | 30.7046 | 88.2604 | 0.45467 |  | 3441 | 37.5 | 42.2993 | 4 | 88.2604
3442 | 43.78 | 40.6024 | 52.4874 | 88.5065 | 0.45267 |  | 3442 | 35.73 | 40.6024 | 3 | 88.5065
3443 | 39.54 | 46.1929 | 78.7198 | 64.0853 | 0.44443 |  | 3443 | 36 | 46.1929 | 2.2679 | 64.0853
3444 | 37.48 | 45.8092 | 109.1924 | 80.368 | 0.42945 |  | 3444 | 35.94 | 45.8092 | 2 | 80.368
3445 | 35.85 | 46.9731 | 22.9209 | 67.2436 | 0.42215 |  | 3445 | 33.91 | 46.9731 | 2.2679 | 67.2436
3446 | 35.35 | 51.1188 | 38.8197 | 59.6426 | 0.41841 |  | 3446 | 33.54 | 51.1188 | 3 | 59.6426
3447 | 35 | 58.337 | 43.723 | 62.7578 | 0.42236 |  | 3447 | 32.5 | 58.337 | 4 | 62.7578
3448 | 35.08 | 74.6335 | 41.8988 | 54.3699 | 0.42489 |  | 3448 | 32.78 | 74.6335 | 5 | 54.3699
3449 | 36.64 | 98.1942 | 28.6869 | 70.231 | 0.43644 |  | 3449 | 31.96 | 98.1942 | 5.7321 | 70.231
3450 | 41.64 | 142.5323 | 49.9528 | 95.5285 | 0.45031 |  | 3450 | 31.68 | 142.5323 | 6 | 95.5285
3451 | 44.88 | 146.6434 | 48.6797 | 104.3034 | 0.4527 |  | 3451 | 32.49 | 146.6434 | 5.7321 | 104.3034
3452 | 45.55 | 121.6234 | 27.8005 | 121.7783 | 0.45537 |  | 3452 | 33.09 | 121.6234 | 5 | 121.7783
3453 | 45.51 | 97.0128 | 34.2164 | 106.5751 | 0.46178 |  | 3453 | 34.04 | 97.0128 | 4 | 106.5751
3454 | 45.06 | 100.6033 | 23.9287 | 73.7107 | 0.46512 |  | 3454 | 32.42 | 100.6033 | 3 | 73.7107
3455 | 41.89 | 79.228 | 34.513 | 53.3931 | 0.47113 |  | 3455 | 26.3 | 79.228 | 2.2679 | 53.3931
3456 | 41.97 | 40.377 | 31.7143 | 24.2739 | 0.48346 |  | 3456 | 24.66 | 40.377 | 2 | 24.2739
3457 | 37.15 | 33.6383 | 30.101 | 27.6106 | 0.47727 |  | 3457 | 21.99 | 33.6383 | 2.2679 | 27.6106
3458 | 35.07 | 32.1025 | 31.2331 | 6.878 | 0.46786 |  | 3458 | 21.75 | 32.1025 | 3 | 6.878
3459 | 34.03 | 30.54 | 32.3385 | 18.4154 | 0.46737 |  | 3459 | 20.48 | 30.54 | 4 | 18.4154
3460 | 33.84 | 29.2512 | 33.2009 | 40.9289 | 0.46834 |  | 3460 | 20 | 29.2512 | 5 | 40.9289
3461 | 33.09 | 28.4841 | 32.7384 | 99.6 | 0.46572 |  | 3461 | 20.72 | 28.4841 | 5.7321 | 99.6
3462 | 34.05 | 28.3942 | 51.9141 | 106.5443 | 0.46429 |  | 3462 | 22.61 | 28.3942 | 6 | 106.5443
3463 | 35.11 | 39.5559 | 25.3458 | 120.2885 | 0.46749 |  | 3463 | 26.13 | 39.5559 | 5.7321 | 120.2885
3464 | 37.7 | 55.0872 | 44.6891 | 128.3153 | 0.47318 |  | 3464 | 34.38 | 55.0872 | 5 | 128.3153
3465 | 37.56 | 44.9339 | 41.3678 | 96.1519 | 0.47327 |  | 3465 | 37.09 | 44.9339 | 4 | 96.1519
3466 | 36.32 | 43.3869 | 50.3746 | 90.6023 | 0.46595 |  | 3466 | 36.19 | 43.3869 | 3 | 90.6023
3467 | 35.2 | 46.9116 | 50.0911 | 78.828 | 0.45855 |  | 3467 | 36.94 | 46.9116 | 2.2679 | 78.828
3468 | 34.24 | 47.7534 | 28.3548 | 74.3621 | 0.44971 |  | 3468 | 36.06 | 47.7534 | 2 | 74.3621
3469 | 33.01 | 51.2299 | 39.0443 | 91.1646 | 0.44821 |  | 3469 | 33.09 | 51.2299 | 2.2679 | 91.1646
3470 | 31.42 | 53.0842 | 48.228 | 72.0653 | 0.44918 |  | 3470 | 33 | 53.0842 | 3 | 72.0653
3471 | 31.35 | 62.203 | 48.6793 | 68.6489 | 0.4538 |  | 3471 | 32.69 | 62.203 | 4 | 68.6489
3472 | 32.08 | 78.7073 | 36.9527 | 70.3391 | 0.45302 |  | 3472 | 30.92 | 78.7073 | 5 | 70.3391
3473 | 34.19 | 95.7841 | 36.0815 | 85.0963 | 0.46223 |  | 3473 | 29.12 | 95.7841 | 5.7321 | 85.0963
3474 | 37.48 | 134.3126 | 38.779 | 100.4081 | 0.47314 |  | 3474 | 29.8 | 134.3126 | 6 | 100.4081
3475 | 41.12 | 138.4036 | 40.3255 | 97.5126 | 0.49297 |  | 3475 | 31.25 | 138.4036 | 5.7321 | 97.5126
3476 | 44.47 | 128.0458 | 31.6481 | 103.6861 | 0.4992 |  | 3476 | 32.2 | 128.0458 | 5 | 103.6861
3477 | 44.71 | 100.0804 | 26.1659 | 103.6249 | 0.50133 |  | 3477 | 31.64 | 100.0804 | 4 | 103.6249
3478 | 44.47 | 102.2875 | 25.216 | 81.9085 | 0.50172 |  | 3478 | 32.38 | 102.2875 | 3 | 81.9085
3479 | 40.58 | 77.5709 | 25.5734 | 53.8574 | 0.50128 |  | 3479 | 30.77 | 77.5709 | 2.2679 | 53.8574
3480 | 36.4 | 39.0409 | 25.4696 | 23.9252 | 0.48717 |  | 3480 | 25.83 | 39.0409 | 2 | 23.9252
3481 | 33.04 | 35.7738 | 32.045 | 28.6911 | 0.45087 |  | 3481 | 23.99 | 35.7738 | 2.2679 | 28.6911
3482 | 29.37 | 33.8175 | 31.7061 | 5.3595 | 0.41558 |  | 3482 | 22.57 | 33.8175 | 3 | 5.3595
3483 | 27.81 | 31.9616 | 38.6412 | 23.545 | 0.38526 |  | 3483 | 21.57 | 31.9616 | 4 | 23.545
3484 | 23.01 | 30.1902 | 28.5821 | 55.735 | 0.3719 |  | 3484 | 21.06 | 30.1902 | 5 | 55.735
3485 | 18.15 | 29.0853 | 30.9078 | 96.515 | 0.36807 |  | 3485 | 21.63 | 29.0853 | 5.7321 | 96.515
3486 | 14.63 | 28.8373 | 25.3358 | 105.1306 | 0.3692 |  | 3486 | 22.99 | 28.8373 | 6 | 105.1306
3487 | 18.65 | 38.7042 | 24.2277 | 175.9531 | 0.35874 |  | 3487 | 30.92 | 38.7042 | 5.7321 | 175.9531
3488 | 24.58 | 53.5746 | 39.9358 | 141.1736 | 0.35729 |  | 3488 | 35.8 | 53.5746 | 5 | 141.1736
3489 | 28.3 | 43.7857 | 42.3781 | 106.1201 | 0.35415 |  | 3489 | 39.2 | 43.7857 | 4 | 106.1201
3490 | 18.69 | 42.9239 | 27.8804 | 95.2775 | 0.359 |  | 3490 | 50.95 | 42.9239 | 3 | 95.2775
3491 | 28.3 | 48.2906 | 241.7726 | 69.8019 | 0.34598 |  | 3491 | 53.11 | 48.2906 | 2.2679 | 69.8019
3492 | 29.1 | 48.217 | 41.5862 | 71.3592 | 0.33051 |  | 3492 | 52.44 | 48.217 | 2 | 71.3592
3493 | 27.4 | 51.9998 | 42.3199 | 70.9837 | 0.31731 |  | 3493 | 51 | 51.9998 | 2.2679 | 70.9837
3494 | 15.4 | 52.5639 | 53.8096 | 73.7125 | 0.31797 |  | 3494 | 50.67 | 52.5639 | 3 | 73.7125
3495 | 5 | 58.9096 | 46.9096 | 66.7252 | 0.31058 |  | 3495 | 35.92 | 58.9096 | 4 | 66.7252
3496 | 4.67 | 75.3001 | 37.8807 | 56.7311 | 0.32493 |  | 3496 | 35.9 | 75.3001 | 5 | 56.7311
3497 | 31.74 | 93.149 | 39.4771 | 87.1441 | 0.31807 |  | 3497 | 37.6 | 93.149 | 5.7321 | 87.1441
3498 | 33.01 | 135.2022 | 33.8975 | 100.8773 | 0.32332 |  | 3498 | 37.6 | 135.2022 | 6 | 100.8773
3499 | 36.63 | 139.9104 | 50.6423 | 119.9012 | 0.33661 |  | 3499 | 35.8 | 139.9104 | 5.7321 | 119.9012
3500 | 37.16 | 132.5738 | 27.042 | 119.9796 | 0.34056 |  | 3500 | 36.61 | 132.5738 | 5 | 119.9796
3501 | 36.59 | 101.3177 | 28.7612 | 81.3142 | 0.34253 |  | 3501 | 36.76 | 101.3177 | 4 | 81.3142
3502 | 36.37 | 99.0193 | 29.4056 | 66.0033 | 0.36582 |  | 3502 | 35.49 | 99.0193 | 3 | 66.0033
3503 | 32.45 | 79.4687 | 36.5164 | 49.3538 | 0.38127 |  | 3503 | 34.92 | 79.4687 | 2.2679 | 49.3538
3504 | 33.23 | 41.4867 | 31.7437 | 29.1019 | 0.39445 |  | 3504 | 35.13 | 41.4867 | 2 | 29.1019
3505 | 27.4 | 33.9911 | 25.8722 | 25.876 | 0.40333 |  | 3505 | 25.74 | 33.9911 | 2.2679 | 25.876
3506 | 25.63 | 32.5377 | 19.5028 | 5.6211 | 0.41477 |  | 3506 | 24.16 | 32.5377 | 3 | 5.6211
3507 | 23.25 | 30.8735 | 32.8111 | 18.0224 | 0.41661 |  | 3507 | 23.42 | 30.8735 | 4 | 18.0224
3508 | 23.51 | 29.4974 | 25.2329 | 54.2261 | 0.40843 |  | 3508 | 23.27 | 29.4974 | 5 | 54.2261
3509 | 28.76 | 28.5954 | 37.4751 | 70.7777 | 0.41937 |  | 3509 | 23.33 | 28.5954 | 5.7321 | 70.7777
3510 | 36.65 | 27.9508 | 31.5778 | 135.7187 | 0.4398 |  | 3510 | 23.79 | 27.9508 | 6 | 135.7187
3511 | 46.17 | 27.7198 | 25.9243 | 168.6095 | 0.44429 |  | 3511 | 26.15 | 27.7198 | 5.7321 | 168.6095
3512 | 43.35 | 29.548 | 37.595 | 149.344 | 0.442 |  | 3512 | 30.96 | 29.548 | 5 | 149.344
3513 | 42.37 | 48.779 | 33.1692 | 94.3867 | 0.44718 |  | 3513 | 39.43 | 48.779 | 4 | 94.3867
3514 | 39.74 | 67.9228 | 249.1828 | 90.1993 | 0.43219 |  | 3514 | 46.83 | 67.9228 | 3 | 90.1993
3515 | 39.27 | 75.5395 | 45.1439 | 72.8106 | 0.42726 |  | 3515 | 37.6 | 75.5395 | 2.2679 | 72.8106
3516 | 38.03 | 76.1302 | 35.6953 | 66.0646 | 0.42524 |  | 3516 | 48.46 | 76.1302 | 2 | 66.0646
3517 | 38 | 79.3117 | 40.4766 | 76.438 | 0.43051 |  | 3517 | 37.6 | 79.3117 | 2.2679 | 76.438
3518 | 36.43 | 75.2108 | 57.4336 | 67.4668 | 0.43032 |  | 3518 | 39.18 | 75.2108 | 3 | 67.4668
3519 | 35.89 | 70.885 | 43.5589 | 51.156 | 0.42578 |  | 3519 | 36.04 | 70.885 | 4 | 51.156
3520 | 35.46 | 74.3438 | 26.4795 | 54.432 | 0.4276 |  | 3520 | 32.44 | 74.3438 | 5 | 54.432
3521 | 37.27 | 78.8757 | 43.7299 | 71.1411 | 0.43076 |  | 3521 | 29.94 | 78.8757 | 5.7321 | 71.1411
3522 | 40.48 | 117.6932 | 43.388 | 98.5313 | 0.43889 |  | 3522 | 28.07 | 117.6932 | 6 | 98.5313
3523 | 45.39 | 138.9946 | 41.3555 | 101.2263 | 0.44909 |  | 3523 | 34 | 138.9946 | 5.7321 | 101.2263
3524 | 48 | 129.4704 | 19.5089 | 107.495 | 0.45862 |  | 3524 | 35.27 | 129.4704 | 5 | 107.495
3525 | 45.7 | 98.2898 | 33.3631 | 98.8309 | 0.46216 |  | 3525 | 34.95 | 98.2898 | 4 | 98.8309
3526 | 42.79 | 94.4443 | 23.3456 | 57.8054 | 0.47624 |  | 3526 | 32.94 | 94.4443 | 3 | 57.8054
3527 | 38.64 | 89.4138 | 33.7885 | 55.0646 | 0.48418 |  | 3527 | 33.1 | 89.4138 | 2.2679 | 55.0646
3528 | 34.07 | 40.428 | 31.8329 | 30.9794 | 0.47484 |  | 3528 | 27.22 | 40.428 | 2 | 30.9794
3529 | 33.1 | 32.3652 | 32.5621 | 23.459 | 0.46659 |  | 3529 | 24.43 | 32.3652 | 2.2679 | 23.459
3530 | 32.71 | 30.9948 | 24.4048 | 5.6594 | 0.46823 |  | 3530 | 23.61 | 30.9948 | 3 | 5.6594
3531 | 33.29 | 29.829 | 27.8719 | 18.7496 | 0.463 |  | 3531 | 21.95 | 29.829 | 4 | 18.7496
3532 | 33.12 | 28.7698 | 43.9114 | 42.815 | 0.4662 |  | 3532 | 20.61 | 28.7698 | 5 | 42.815
3533 | 34.45 | 28.032 | 89.6304 | 101.6272 | 0.48082 |  | 3533 | 21.69 | 28.032 | 5.7321 | 101.6272
3534 | 46.23 | 27.5034 | 123.0683 | 125.694 | 0.48916 |  | 3534 | 23.45 | 27.5034 | 6 | 125.694
3535 | 50.48 | 27.2717 | 111.3279 | 139.235 | 0.48564 |  | 3535 | 27.88 | 27.2717 | 5.7321 | 139.235
3536 | 56.83 | 29.4107 | 65.0524 | 142.9148 | 0.48584 |  | 3536 | 32.99 | 29.4107 | 5 | 142.9148
3537 | 57.71 | 47.7789 | 44.5486 | 87.845 | 0.48495 |  | 3537 | 35.48 | 47.7789 | 4 | 87.845
3538 | 50.66 | 68.2413 | 45.9095 | 74.8033 | 0.48585 |  | 3538 | 45.07 | 68.2413 | 3 | 74.8033
3539 | 48.08 | 74.7174 | 34.1668 | 77.098 | 0.4852 |  | 3539 | 44.19 | 74.7174 | 2.2679 | 77.098
3540 | 44.95 | 75.3415 | 34.6028 | 75.3104 | 0.48092 |  | 3540 | 39.94 | 75.3415 | 2 | 75.3104
3541 | 44.9 | 82.152 | 57.9939 | 91.0867 | 0.48044 |  | 3541 | 39.94 | 82.152 | 2.2679 | 91.0867
3542 | 40.21 | 75.5304 | 39.8515 | 62.4566 | 0.47833 |  | 3542 | 38.16 | 75.5304 | 3 | 62.4566
3543 | 39.65 | 76.2595 | 43.0627 | 57.9488 | 0.4742 |  | 3543 | 40.83 | 76.2595 | 4 | 57.9488
3544 | 39.67 | 78.4 | 43.6824 | 73.3838 | 0.46624 |  | 3544 | 35.29 | 78.4 | 5 | 73.3838
3545 | 42.17 | 76.7754 | 37.8312 | 74.099 | 0.45856 |  | 3545 | 35.41 | 76.7754 | 5.7321 | 74.099
3546 | 42.29 | 107.9487 | 41.3411 | 75.916 | 0.46238 |  | 3546 | 39.57 | 107.9487 | 6 | 75.916
3547 | 42.64 | 119.914 | 38.8975 | 122.5539 | 0.46473 |  | 3547 | 32.91 | 119.914 | 5.7321 | 122.5539
3548 | 43.1 | 136.0308 | 29.3553 | 102.4165 | 0.47251 |  | 3548 | 33.2 | 136.0308 | 5 | 102.4165
3549 | 41.79 | 96.6049 | 27.2934 | 86.2926 | 0.48038 |  | 3549 | 32.19 | 96.6049 | 4 | 86.2926
3550 | 38.77 | 88.1981 | 38.7809 | 58.8564 | 0.48528 |  | 3550 | 31.85 | 88.1981 | 3 | 58.8564
3551 | 34.07 | 85.4093 | 27.3134 | 50.2824 | 0.47771 |  | 3551 | 38.88 | 85.4093 | 2.2679 | 50.2824
3552 | 34.4 | 38.4859 | 28.9982 | 22.4232 | 0.47356 |  | 3552 | 42.16 | 38.4859 | 2 | 22.4232
3553 | 33.07 | 36.1296 | 24.7892 | 23.8002 | 0.47062 |  | 3553 | 28.92 | 36.1296 | 2.2679 | 23.8002
3554 | 30.57 | 34.1275 | 25.8895 | 6.8398 | 0.46541 |  | 3554 | 24.38 | 34.1275 | 3 | 6.8398
3555 | 30.8 | 32.2104 | 32.2775 | 18.6513 | 0.46353 |  | 3555 | 22.79 | 32.2104 | 4 | 18.6513
3556 | 32.88 | 30.4835 | 43.8929 | 45.3141 | 0.46318 |  | 3556 | 22.14 | 30.4835 | 5 | 45.3141
3557 | 33.1 | 29.3623 | 98.343 | 80.297 | 0.47799 |  | 3557 | 22.4 | 29.3623 | 5.7321 | 80.297
3558 | 41.05 | 28.8148 | 41.9294 | 144.8437 | 0.49631 |  | 3558 | 21.91 | 28.8148 | 6 | 144.8437
3559 | 47.67 | 40.0345 | 35.2141 | 127.1915 | 0.49066 |  | 3559 | 22.56 | 40.0345 | 5.7321 | 127.1915
3560 | 50.62 | 55.9015 | 45.8561 | 134.3426 | 0.48177 |  | 3560 | 24.22 | 55.9015 | 5 | 134.3426
3561 | 47.8 | 43.8213 | 49.3999 | 98.3325 | 0.47413 |  | 3561 | 26.57 | 43.8213 | 4 | 98.3325
3562 | 45.97 | 42.5813 | 50.3631 | 78.0276 | 0.47111 |  | 3562 | 33.73 | 42.5813 | 3 | 78.0276
3563 | 44.65 | 44.6919 | 54.9211 | 68.5984 | 0.47319 |  | 3563 | 37.76 | 44.6919 | 2.2679 | 68.5984
3564 | 40.89 | 48.3958 | 35.0341 | 89.93 | 0.47143 |  | 3564 | 37.25 | 48.3958 | 2 | 89.93
3565 | 39.9 | 50.5969 | 30.2268 | 72.9317 | 0.4717 |  | 3565 | 31.61 | 50.5969 | 2.2679 | 72.9317
3566 | 39.92 | 52.3462 | 36.2832 | 74.1243 | 0.47241 |  | 3566 | 25.92 | 52.3462 | 3 | 74.1243
3567 | 38.29 | 59.4549 | 45.2231 | 55.0032 | 0.4724 |  | 3567 | 22.81 | 59.4549 | 4 | 55.0032
3568 | 40.15 | 75.2279 | 41.9095 | 67.4187 | 0.47407 |  | 3568 | 22.63 | 75.2279 | 5 | 67.4187
3569 | 45.24 | 92.8963 | 46.1062 | 63.2534 | 0.4759 |  | 3569 | 22.91 | 92.8963 | 5.7321 | 63.2534
3570 | 49.63 | 144.8663 | 39.1654 | 76.9483 | 0.48001 |  | 3570 | 23.74 | 144.8663 | 6 | 76.9483
3571 | 51.89 | 142.128 | 43.9703 | 100.2714 | 0.48155 |  | 3571 | 29.56 | 142.128 | 5.7321 | 100.2714
3572 | 52 | 134.5684 | 32.7437 | 112.4677 | 0.48229 |  | 3572 | 26.42 | 134.5684 | 5 | 112.4677
3573 | 47.13 | 104.1289 | 30.24 | 103.1639 | 0.47947 |  | 3573 | 30.75 | 104.1289 | 4 | 103.1639
3574 | 40.77 | 102.2076 | 27.4799 | 62.0795 | 0.47463 |  | 3574 | 27.44 | 102.2076 | 3 | 62.0795
3575 | 34.55 | 79.5668 | 31.0566 | 39.2324 | 0.44807 |  | 3575 | 53.12 | 79.5668 | 2.2679 | 39.2324
3576 | 32.1 | 41.9801 | 29.1846 | 22.2623 | 0.42245 |  | 3576 | 44.71 | 41.9801 | 2 | 22.2623
3577 | 29.3 | 35.7754 | 37.3406 | 32.473 | 0.40012 |  | 3577 | 21.41 | 35.7754 | 2.2679 | 32.473
3578 | 30.71 | 33.9561 | 27.8151 | 6.9929 | 0.39002 |  | 3578 | 20.76 | 33.9561 | 3 | 6.9929
3579 | 26.76 | 32.0391 | 30.5539 | 16.0963 | 0.37135 |  | 3579 | 18.96 | 32.0391 | 4 | 16.0963
3580 | 23.36 | 30.4045 | 32.7279 | 40.7403 | 0.36717 |  | 3580 | 17.91 | 30.4045 | 5 | 40.7403
3581 | 20.17 | 29.2341 | 64.357 | 84.1752 | 0.36669 |  | 3581 | 22.1 | 29.2341 | 5.7321 | 84.1752
3582 | 24.89 | 28.855 | 99.9523 | 139.4458 | 0.36572 |  | 3582 | 16.07 | 28.855 | 6 | 139.4458
3583 | 31.38 | 39.1327 | 65.75 | 138.2069 | 0.37751 |  | 3583 | 15.83 | 39.1327 | 5.7321 | 138.2069
3584 | 31.38 | 55.1948 | 66.9361 | 121.8861 | 0.37343 |  | 3584 | 19.56 | 55.1948 | 5 | 121.8861
3585 | 33.11 | 44.3834 | 104.7083 | 120.761 | 0.37897 |  | 3585 | 21.31 | 44.3834 | 4 | 120.761
3586 | 36.07 | 42.9139 | 63.3909 | 95.5193 | 0.37876 |  | 3586 | 21.57 | 42.9139 | 3 | 95.5193
3587 | 36.04 | 46.2971 | 46.5957 | 68.7488 | 0.37779 |  | 3587 | 21.99 | 46.2971 | 2.2679 | 68.7488
3588 | 36.51 | 47.3537 | 49.046 | 69.1465 | 0.37469 |  | 3588 | 23.43 | 47.3537 | 2 | 69.1465
3589 | 35.51 | 49.1548 | 37.183 | 67.6332 | 0.37201 |  | 3589 | 24.94 | 49.1548 | 2.2679 | 67.6332
3590 | 34.84 | 51.7361 | 40.9511 | 71.7907 | 0.36891 |  | 3590 | 23.25 | 51.7361 | 3 | 71.7907
3591 | 31.38 | 59.3303 | 53.7467 | 71.2938 | 0.36402 |  | 3591 | 22.69 | 59.3303 | 4 | 71.2938
3592 | 29.9 | 76.2113 | 46.1212 | 61.8263 | 0.36541 |  | 3592 | 22 | 76.2113 | 5 | 61.8263
3593 | 29.1 | 98.0498 | 34.5376 | 82.8969 | 0.36644 |  | 3593 | 21.82 | 98.0498 | 5.7321 | 82.8969
3594 | 34.49 | 128.8489 | 37.9147 | 97.9683 | 0.37367 |  | 3594 | 23.3 | 128.8489 | 6 | 97.9683
3595 | 36.17 | 145.2754 | 40.8289 | 122.8722 | 0.39047 |  | 3595 | 27.44 | 145.2754 | 5.7321 | 122.8722
3596 | 37.02 | 129.2172 | 36.1802 | 110.9864 | 0.41947 |  | 3596 | 28.83 | 129.2172 | 5 | 110.9864
3597 | 38.01 | 100.2543 | 33.1545 | 92.7461 | 0.4339 |  | 3597 | 26.74 | 100.2543 | 4 | 92.7461
3598 | 40.34 | 97.5278 | 32.9589 | 63.9013 | 0.4311 |  | 3598 | 27.44 | 97.5278 | 3 | 63.9013
3599 | 36.69 | 77.8702 | 25.182 | 47.8681 | 0.43507 |  | 3599 | 24.3 | 77.8702 | 2.2679 | 47.8681
3600 | 32.02 | 41.7233 | 30.5857 | 29.6919 | 0.43146 |  | 3600 | 20.68 | 41.7233 | 2 | 29.6919
3601 | 29.49 | 33.5999 | 32.9188 | 23.8571 | 0.42234 |  | 3601 | 18.07 | 33.5999 | 2.2679 | 23.8571
3602 | 28.38 | 32.1192 | 27.5558 | 7.6437 | 0.4142 |  | 3602 | 19.5 | 32.1192 | 3 | 7.6437
3603 | 28.6 | 30.6686 | 26.3904 | 21.5993 | 0.41786 |  | 3603 | 12.99 | 30.6686 | 4 | 21.5993
3604 | 29.07 | 29.3679 | 38.9956 | 38.4769 | 0.43709 |  | 3604 | 11.28 | 29.3679 | 5 | 38.4769
3605 | 29.07 | 28.4393 | 62.3274 | 86.3787 | 0.45486 |  | 3605 | 11.86 | 28.4393 | 5.7321 | 86.3787
3606 | 35 | 28.2502 | 113.9892 | 127.3648 | 0.46324 |  | 3606 | 18.01 | 28.2502 | 6 | 127.3648
3607 | 41.05 | 39.8158 | 275.3719 | 166.9939 | 0.46812 |  | 3607 | 26.16 | 39.8158 | 5.7321 | 166.9939
3608 | 41.49 | 54.9255 | 40.5689 | 117.4661 | 0.46788 |  | 3608 | 34.94 | 54.9255 | 5 | 117.4661
3609 | 39.78 | 43.4981 | 46.8206 | 103.1089 | 0.46321 |  | 3609 | 35.25 | 43.4981 | 4 | 103.1089
3610 | 37 | 41.7578 | 41.0102 | 65.3723 | 0.45685 |  | 3610 | 35.43 | 41.7578 | 3 | 65.3723
3611 | 35.63 | 43.373 | 37.7932 | 83.2658 | 0.4443 |  | 3611 | 34.79 | 43.373 | 2.2679 | 83.2658
3612 | 34.17 | 46.1707 | 41.6839 | 82.5807 | 0.43413 |  | 3612 | 40.01 | 46.1707 | 2 | 82.5807
3613 | 30.51 | 48.7566 | 47.716 | 82.9052 | 0.42527 |  | 3613 | 44.27 | 48.7566 | 2.2679 | 82.9052
3614 | 30 | 49.3859 | 243.4264 | 59.8485 | 0.41992 |  | 3614 | 43.17 | 49.3859 | 3 | 59.8485
3615 | 29.14 | 56.5968 | 39.1566 | 54.5825 | 0.42151 |  | 3615 | 38.95 | 56.5968 | 4 | 54.5825
3616 | 33.51 | 74.4454 | 36.482 | 50.0203 | 0.42965 |  | 3616 | 32.44 | 74.4454 | 5 | 50.0203
3617 | 37.04 | 90.9502 | 39.3159 | 75.3884 | 0.44599 |  | 3617 | 25.09 | 90.9502 | 5.7321 | 75.3884
3618 | 40.6 | 131.4936 | 43.9321 | 92.901 | 0.45745 |  | 3618 | 27.63 | 131.4936 | 6 | 92.901
3619 | 45.8 | 147.3286 | 52.2583 | 124.3577 | 0.46505 |  | 3619 | 28.74 | 147.3286 | 5.7321 | 124.3577
3620 | 47.26 | 124.3407 | 39.4351 | 87.3926 | 0.47292 |  | 3620 | 28.99 | 124.3407 | 5 | 87.3926
3621 | 45.19 | 98.2038 | 21.0495 | 97.6324 | 0.47547 |  | 3621 | 25.48 | 98.2038 | 4 | 97.6324
3622 | 43.98 | 98.7597 | 36.1539 | 73.9909 | 0.47508 |  | 3622 | 24.71 | 98.7597 | 3 | 73.9909
3623 | 40 | 78.6644 | 33.9292 | 55.2503 | 0.47628 |  | 3623 | 34.9 | 78.6644 | 2.2679 | 55.2503
3624 | 33.63 | 39.6869 | 36.547 | 30.1211 | 0.46862 |  | 3624 | 25.14 | 39.6869 | 2 | 30.1211
3625 | 31.03 | 35.4336 | 28.4102 | 32.9848 | 0.46255 |  | 3625 | 21.17 | 35.4336 | 2.2679 | 32.9848
3626 | 28.23 | 33.7042 | 30.0504 | 5.2574 | 0.44027 |  | 3626 | 19.25 | 33.7042 | 3 | 5.2574
3627 | 27.62 | 31.9275 | 30.167 | 20.538 | 0.42786 |  | 3627 | 16.44 | 31.9275 | 4 | 20.538
3628 | 27.29 | 30.2903 | 36.481 | 43.9467 | 0.42922 |  | 3628 | 21.12 | 30.2903 | 5 | 43.9467
3629 | 27 | 29.0688 | 68.1943 | 72.3642 | 0.43416 |  | 3629 | 22.12 | 29.0688 | 5.7321 | 72.3642
3630 | 28.8 | 28.5677 | 58.4733 | 106.1587 | 0.4417 |  | 3630 | 23.51 | 28.5677 | 6 | 106.1587
3631 | 31.51 | 38.4605 | 29.4824 | 146.138 | 0.44408 |  | 3631 | 24.52 | 38.4605 | 5.7321 | 146.138
3632 | 32.16 | 53.8832 | 44.4537 | 114.5194 | 0.44287 |  | 3632 | 32.93 | 53.8832 | 5 | 114.5194
3633 | 34.69 | 44.7738 | 46.5278 | 95.7366 | 0.44377 |  | 3633 | 35.81 | 44.7738 | 4 | 95.7366
3634 | 33.83 | 43.8329 | 47.4838 | 72.7075 | 0.44401 |  | 3634 | 35.47 | 43.8329 | 3 | 72.7075
3635 | 32.74 | 47.0124 | 46.818 | 86.3497 | 0.44543 |  | 3635 | 34.94 | 47.0124 | 2.2679 | 86.3497
3636 | 32.05 | 49.7064 | 29.6957 | 78.2343 | 0.44434 |  | 3636 | 35.8 | 49.7064 | 2 | 78.2343
3637 | 30 | 49.7764 | 44.1217 | 69.5812 | 0.44638 |  | 3637 | 32.78 | 49.7764 | 2.2679 | 69.5812
3638 | 29.9 | 51.7138 | 41.7695 | 59.9171 | 0.45059 |  | 3638 | 30.94 | 51.7138 | 3 | 59.9171
3639 | 29.5 | 59.7911 | 49.9801 | 55.7847 | 0.45686 |  | 3639 | 32.65 | 59.7911 | 4 | 55.7847
3640 | 27.57 | 75.3578 | 49.3504 | 63.6905 | 0.46172 |  | 3640 | 35.84 | 75.3578 | 5 | 63.6905
3641 | 29.09 | 95.3834 | 47.4717 | 66.5905 | 0.47827 |  | 3641 | 38 | 95.3834 | 5.7321 | 66.5905
3642 | 36.87 | 134.8079 | 39.3771 | 80.608 | 0.49051 |  | 3642 | 34 | 134.8079 | 6 | 80.608
3643 | 40.15 | 152.6125 | 37.7305 | 127.1165 | 0.51249 |  | 3643 | 34.94 | 152.6125 | 5.7321 | 127.1165
3644 | 41.8 | 126.0865 | 24.7697 | 124.0001 | 0.524 |  | 3644 | 35.92 | 126.0865 | 5 | 124.0001
3645 | 40.94 | 103.5485 | 28.356 | 101.2279 | 0.52726 |  | 3645 | 32.95 | 103.5485 | 4 | 101.2279
3646 | 40.36 | 102.8072 | 23.4645 | 82.6092 | 0.5211 |  | 3646 | 31.98 | 102.8072 | 3 | 82.6092
3647 | 37.6 | 79.1542 | 26.5969 | 52.0931 | 0.50309 |  | 3647 | 30.78 | 79.1542 | 2.2679 | 52.0931
3648 | 28.49 | 41.3632 | 28.734 | 23.9252 | 0.48594 |  | 3648 | 32.73 | 41.3632 | 2 | 23.9252
3649 | 28.99 | 35.0262 | 34.99 | 22.9188 | 0.47093 |  | 3649 | 24 | 35.0262 | 2.2679 | 22.9188
3650 | 31.52 | 33.2694 | 28.1898 | 6.4378 | 0.45472 |  | 3650 | 22.23 | 33.2694 | 3 | 6.4378
3651 | 32.88 | 31.5257 | 41.1431 | 15.7426 | 0.44212 |  | 3651 | 21.07 | 31.5257 | 4 | 15.7426
3652 | 27.5 | 29.9175 | 19.8151 | 44.8426 | 0.42883 |  | 3652 | 20.08 | 29.9175 | 5 | 44.8426
3653 | 24.52 | 28.9452 | 19.7992 | 96.1625 | 0.41993 |  | 3653 | 20.18 | 28.9452 | 5.7321 | 96.1625
3654 | 23.98 | 28.5783 | 30.8269 | 139.5743 | 0.42403 |  | 3654 | 23.1 | 28.5783 | 6 | 139.5743
3655 | 22.74 | 40.8228 | 33.2924 | 169.3439 | 0.42897 |  | 3655 | 29.9 | 40.8228 | 5.7321 | 169.3439
3656 | 27.5 | 55.1379 | 55.5449 | 135.0123 | 0.43238 |  | 3656 | 37.49 | 55.1379 | 5 | 135.0123
3657 | 28.54 | 43.8924 | 52.9374 | 103.3166 | 0.42458 |  | 3657 | 40.87 | 43.8924 | 4 | 103.3166
3658 | 11.76 | 43.8455 | 45.9727 | 76.4961 | 0.41358 |  | 3658 | 41 | 43.8455 | 3 | 76.4961
3659 | 11.9 | 47.8675 | 45.4531 | 82.2128 | 0.40526 |  | 3659 | 40.44 | 47.8675 | 2.2679 | 82.2128
3660 | 8.91 | 49.8307 | 47.3176 | 70.0948 | 0.39664 |  | 3660 | 40.51 | 49.8307 | 2 | 70.0948
3661 | 3.5 | 54.2079 | 21.4808 | 73.0096 | 0.38885 |  | 3661 | 36.64 | 54.2079 | 2.2679 | 73.0096
3662 | -9.02 | 55.9981 | 45.5389 | 72.5457 | 0.38775 |  | 3662 | 39.6 | 55.9981 | 3 | 72.5457
3663 | -0.48 | 63.4202 | 39.744 | 71.7747 | 0.39069 |  | 3663 | 41.21 | 63.4202 | 4 | 71.7747
3664 | 3.5 | 78.8733 | 52.9596 | 54.9291 | 0.39955 |  | 3664 | 39.12 | 78.8733 | 5 | 54.9291
3665 | 30.27 | 95.6631 | 45.5699 | 78.4979 | 0.41777 |  | 3665 | 38.05 | 95.6631 | 5.7321 | 78.4979
3666 | 31.74 | 136.8332 | 40.8027 | 106.7892 | 0.43246 |  | 3666 | 30.11 | 136.8332 | 6 | 106.7892
3667 | 37.41 | 145.9843 | 47.6522 | 104.834 | 0.46532 |  | 3667 | 32.66 | 145.9843 | 5.7321 | 104.834
3668 | 38.13 | 125.9746 | 25.7166 | 106.2253 | 0.47948 |  | 3668 | 32.92 | 125.9746 | 5 | 106.2253
3669 | 37.14 | 102.0051 | 23.747 | 107.2204 | 0.48427 |  | 3669 | 30.95 | 102.0051 | 4 | 107.2204
3670 | 37.12 | 98.1729 | 23.3517 | 60.8183 | 0.47742 |  | 3670 | 29.57 | 98.1729 | 3 | 60.8183
3671 | 29.85 | 78.9311 | 26.1737 | 46.2431 | 0.45087 |  | 3671 | 30.9 | 78.9311 | 2.2679 | 46.2431
3672 | 26.8 | 41.1359 | 29.798 | 23.9252 | 0.43324 |  | 3672 | 28.19 | 41.1359 | 2 | 23.9252
3673 | 23.51 | 35.6262 | 27.4331 | 29.402 | 0.42972 |  | 3673 | 21.96 | 35.6262 | 2.2679 | 29.402
3674 | 20.78 | 33.6821 | 28.031 | 6.2783 | 0.4184 |  | 3674 | 20.75 | 33.6821 | 3 | 6.2783
3675 | 19.84 | 31.8395 | 23.8687 | 18.2582 | 0.43495 |  | 3675 | 20.73 | 31.8395 | 4 | 18.2582
3676 | 19.33 | 30.2722 | 23.9385 | 50.8782 | 0.41873 |  | 3676 | 20 | 30.2722 | 5 | 50.8782
3677 | 23.87 | 29.1452 | 22.4551 | 98.1897 | 0.44085 |  | 3677 | 22.28 | 29.1452 | 5.7321 | 98.1897
3678 | 39.22 | 28.5377 | 29.192 | 153.1976 | 0.46814 |  | 3678 | 25.4 | 28.5377 | 6 | 153.1976
3679 | 44.64 | 28.1635 | 26.5923 | 126.0165 | 0.47996 |  | 3679 | 31.33 | 28.1635 | 5.7321 | 126.0165
3680 | 45.02 | 30.5753 | 49.4262 | 130.7262 | 0.4859 |  | 3680 | 43.09 | 30.5753 | 5 | 130.7262
3681 | 41.81 | 49.5548 | 45.791 | 89.1949 | 0.48072 |  | 3681 | 39.54 | 49.5548 | 4 | 89.1949
3682 | 39.36 | 69.0623 | 40.591 | 76.2543 | 0.47679 |  | 3682 | 37.98 | 69.0623 | 3 | 76.2543
3683 | 37.71 | 74.5552 | 28.6744 | 84.8454 | 0.46893 |  | 3683 | 37.09 | 74.5552 | 2.2679 | 84.8454
3684 | 36.25 | 77.398 | 48.2117 | 72.5446 | 0.46251 |  | 3684 | 36.37 | 77.398 | 2 | 72.5446
3685 | 35.46 | 80.7175 | 44.586 | 77.9185 | 0.46438 |  | 3685 | 32.08 | 80.7175 | 2.2679 | 77.9185
3686 | 35.23 | 78.2756 | 33.551 | 80.164 | 0.4623 |  | 3686 | 33.88 | 78.2756 | 3 | 80.164
3687 | 35.68 | 72.3343 | 39.3682 | 67.2663 | 0.46246 |  | 3687 | 26.68 | 72.3343 | 4 | 67.2663
3688 | 35.69 | 74.6577 | 28.5336 | 65.9895 | 0.47315 |  | 3688 | 25.95 | 74.6577 | 5 | 65.9895
3689 | 42.1 | 81.9133 | 39.2726 | 87.9784 | 0.4885 |  | 3689 | 31.16 | 81.9133 | 5.7321 | 87.9784
3690 | 45.42 | 129.3509 | 43.0496 | 78.7312 | 0.49482 |  | 3690 | 37.44 | 129.3509 | 6 | 78.7312
3691 | 50.5 | 142.6016 | 228.7791 | 121.0684 | 0.50539 |  | 3691 | 31.84 | 142.6016 | 5.7321 | 121.0684
3692 | 48.98 | 133.5099 | 33.6075 | 115.6417 | 0.51857 |  | 3692 | 32.96 | 133.5099 | 5 | 115.6417
3693 | 48.12 | 102.6129 | 23.2956 | 82.4205 | 0.52494 |  | 3693 | 31.96 | 102.6129 | 4 | 82.4205
3694 | 45.96 | 95.4605 | 28.4988 | 63.9013 | 0.52885 |  | 3694 | 35 | 95.4605 | 3 | 63.9013
3695 | 41.4 | 90.6022 | 24.6176 | 38.2109 | 0.53057 |  | 3695 | 35 | 90.6022 | 2.2679 | 38.2109
3696 | 34.74 | 43.1184 | 26.784 | 22.2086 | 0.51165 |  | 3696 | 24.59 | 43.1184 | 2 | 22.2086
3697 | 32.99 | 35.6566 | 24.1695 | 33.9232 | 0.49528 |  | 3697 | 24.1 | 35.6566 | 2.2679 | 33.9232
3698 | 31.86 | 33.8582 | 39.3794 | 6.8142 | 0.48832 |  | 3698 | 21.68 | 33.8582 | 3 | 6.8142
3699 | 30.99 | 31.9859 | 39.8862 | 16.5484 | 0.4878 |  | 3699 | 22.03 | 31.9859 | 4 | 16.5484
3700 | 32.23 | 30.333 | 90.0641 | 48.9921 | 0.49571 |  | 3700 | 23.59 | 30.333 | 5 | 48.9921
3701 | 33.29 | 29.2625 | 116.4556 | 101.6272 | 0.50334 |  | 3701 | 23.31 | 29.2625 | 5.7321 | 101.6272
3702 | 42 | 28.4183 | 117.5406 | 113.3559 | 0.52409 |  | 3702 | 22.5 | 28.4183 | 6 | 113.3559
3703 | 41.9 | 27.7331 | 99.5352 | 175.9531 | 0.51994 |  | 3703 | 27.46 | 27.7331 | 5.7321 | 175.9531
3704 | 54.7 | 29.8672 | 131.508 | 119.877 | 0.51074 |  | 3704 | 35.45 | 29.8672 | 5 | 119.877
3705 | 46.93 | 48.7176 | 134.2551 | 118.6843 | 0.50629 |  | 3705 | 40.08 | 48.7176 | 4 | 118.6843
3706 | 42.24 | 67.7331 | 83.1877 | 74.4809 | 0.50358 |  | 3706 | 40 | 67.7331 | 3 | 74.4809
3707 | 41 | 74.0895 | 73.903 | 71.0806 | 0.50257 |  | 3707 | 40.11 | 74.0895 | 2.2679 | 71.0806
3708 | 37.56 | 78.2544 | 99.1064 | 67.8821 | 0.49799 |  | 3708 | 40 | 78.2544 | 2 | 67.8821
3709 | 36.5 | 79.9384 | 89.4166 | 71.0616 | 0.49668 |  | 3709 | 42.71 | 79.9384 | 2.2679 | 71.0616
3710 | 35.19 | 80.6648 | 60.8485 | 55.1814 | 0.48829 |  | 3710 | 49.94 | 80.6648 | 3 | 55.1814
3711 | 34.47 | 76.3361 | 47.1219 | 69.3702 | 0.48749 |  | 3711 | 45 | 76.3361 | 4 | 69.3702
3712 | 36.65 | 74.0152 | 54.7083 | 65.3682 | 0.49211 |  | 3712 | 29.94 | 74.0152 | 5 | 65.3682
3713 | 41.86 | 75.8669 | 42.1523 | 75.8434 | 0.48982 |  | 3713 | 30 | 75.8669 | 5.7321 | 75.8434
3714 | 45.13 | 117.6158 | 20.2985 | 88.3028 | 0.48438 |  | 3714 | 28 | 117.6158 | 6 | 88.3028
3715 | 46.17 | 126.6124 | 35.4261 | 116.1874 | 0.48734 |  | 3715 | 31.82 | 126.6124 | 5.7321 | 116.1874
3716 | 44.72 | 129.4229 | 37.2616 | 106.0137 | 0.48351 |  | 3716 | 33.61 | 129.4229 | 5 | 106.0137
3717 | 38.28 | 100.4532 | 28.5476 | 101.5045 | 0.46591 |  | 3717 | 31.98 | 100.4532 | 4 | 101.5045
3718 | 33.83 | 94.1431 | 225.4204 | 63.8312 | 0.45832 |  | 3718 | 30.66 | 94.1431 | 3 | 63.8312
3719 | 28.01 | 89.4307 | 28.6618 | 43.8752 | 0.44045 |  | 3719 | 32.16 | 89.4307 | 2.2679 | 43.8752
3720 | 27.48 | 42.0142 | 22.0222 | 31.3281 | 0.43916 |  | 3720 | 28.94 | 42.0142 | 2 | 31.3281
3721 | 26.06 | 34.5661 | 33.0071 | 30.6247 | 0.43367 |  | 3721 | 47.71 | 34.5661 | 2.2679 | 30.6247
3722 | 24.55 | 32.9566 | 31.3048 | 5.5701 | 0.43138 |  | 3722 | 23.21 | 32.9566 | 3 | 5.5701
3723 | 24.54 | 31.4201 | 33.1471 | 19.634 | 0.43449 |  | 3723 | 21.63 | 31.4201 | 4 | 19.634
3724 | 25.31 | 30.0007 | 24.8334 | 41.7305 | 0.44133 |  | 3724 | 21.29 | 30.0007 | 5 | 41.7305
3725 | 27.53 | 28.8438 | 42.2895 | 101.8917 | 0.45733 |  | 3725 | 21.26 | 28.8438 | 5.7321 | 101.8917
3726 | 36.66 | 28.2059 | 70.0013 | 115.6693 | 0.47228 |  | 3726 | 21.3 | 28.2059 | 6 | 115.6693
3727 | 44.27 | 39.8947 | 106.2198 | 158.1816 | 0.49323 |  | 3727 | 21.53 | 39.8947 | 5.7321 | 158.1816
3728 | 44.99 | 54.2881 | 140.3093 | 148.1385 | 0.49598 |  | 3728 | 23.5 | 54.2881 | 5 | 148.1385
3729 | 43.97 | 42.3608 | 118.0421 | 117.5421 | 0.49164 |  | 3729 | 27.49 | 42.3608 | 4 | 117.5421
3730 | 41.38 | 39.4247 | 105.5905 | 93.3429 | 0.4997 |  | 3730 | 28.98 | 39.4247 | 3 | 93.3429
3731 | 40.46 | 43.2174 | 109.1866 | 81.0093 | 0.50405 |  | 3731 | 26.56 | 43.2174 | 2.2679 | 81.0093
3732 | 38.85 | 44.4827 | 107.5264 | 66.6968 | 0.50783 |  | 3732 | 26.91 | 44.4827 | 2 | 66.6968
3733 | 36.32 | 45.3965 | 100.1322 | 66.7761 | 0.51072 |  | 3733 | 25.73 | 45.3965 | 2.2679 | 66.7761
3734 | 36.19 | 48.9468 | 47.4518 | 63.4174 | 0.50595 |  | 3734 | 22.78 | 48.9468 | 3 | 63.4174
3735 | 38.01 | 54.8255 | 39.7541 | 65.6432 | 0.51296 |  | 3735 | 22.3 | 54.8255 | 4 | 65.6432
3736 | 39 | 70.6157 | 51.0975 | 59.7758 | 0.51078 |  | 3736 | 22.12 | 70.6157 | 5 | 59.7758
3737 | 43.37 | 90.1311 | 43.6471 | 61.6607 | 0.51005 |  | 3737 | 22.03 | 90.1311 | 5.7321 | 61.6607
3738 | 48.28 | 142.2281 | 31.57 | 108.4783 | 0.51144 |  | 3738 | 25.29 | 142.2281 | 6 | 108.4783
3739 | 56.52 | 150.1644 | 35.9198 | 107.9111 | 0.50969 |  | 3739 | 28.19 | 150.1644 | 5.7321 | 107.9111
3740 | 49.41 | 131.4658 | 25.2131 | 88.4506 | 0.50842 |  | 3740 | 30.07 | 131.4658 | 5 | 88.4506
3741 | 43.22 | 102.2111 | 27.1905 | 76.8889 | 0.5018 |  | 3741 | 29.87 | 102.2111 | 4 | 76.8889
3742 | 39.99 | 98.0214 | 27.6369 | 72.6597 | 0.47775 |  | 3742 | 29.88 | 98.0214 | 3 | 72.6597
3743 | 32.09 | 74.7196 | 23.7851 | 47.961 | 0.45045 |  | 3743 | 30.99 | 74.7196 | 2.2679 | 47.961
3744 | 28.5 | 40.0927 | 28.2094 | 26.071 | 0.42005 |  | 3744 | 28.88 | 40.0927 | 2 | 26.071
3745 | 26.5 | 34.9715 | 27.3746 | 30.6531 | 0.41333 |  | 3745 | 24.43 | 34.9715 | 2.2679 | 30.6531
3746 | 24.64 | 33.3544 | 26.3373 | 7.5288 | 0.4267 |  | 3746 | 22 | 33.3544 | 3 | 7.5288
3747 | 24.03 | 31.6853 | 29.0654 | 23.2699 | 0.4497 |  | 3747 | 20.08 | 31.6853 | 4 | 23.2699
3748 | 24.06 | 30.0284 | 21.1074 | 45.4084 | 0.44727 |  | 3748 | 20.39 | 30.0284 | 5 | 45.4084
3749 | 27.54 | 28.9362 | 34.8792 | 102.9494 | 0.449 |  | 3749 | 21.93 | 28.9362 | 5.7321 | 102.9494
3750 | 32.16 | 28.3938 | 77.8871 | 147.7997 | 0.46074 |  | 3750 | 19.41 | 28.3938 | 6 | 147.7997
3751 | 40.73 | 40.4355 | 100.0202 | 168.6095 | 0.46932 |  | 3751 | 20.84 | 40.4355 | 5.7321 | 168.6095
3752 | 42.91 | 53.5207 | 125.2017 | 132.6014 | 0.46668 |  | 3752 | 21.78 | 53.5207 | 5 | 132.6014
3753 | 39.93 | 43.5396 | 124.1778 | 102.5897 | 0.4557 |  | 3753 | 17.89 | 43.5396 | 4 | 102.5897
3754 | 34.11 | 42.0774 | 66.8391 | 77.7858 | 0.45881 |  | 3754 | 20.83 | 42.0774 | 3 | 77.7858
3755 | 33.62 | 45.7988 | 46.8648 | 61.2271 | 0.45238 |  | 3755 | 21.07 | 45.7988 | 2.2679 | 61.2271
3756 | 32.31 | 46.0791 | 61.8512 | 71.8334 | 0.45019 |  | 3756 | 20.53 | 46.0791 | 2 | 71.8334
3757 | 32 | 49.5548 | 33.8581 | 63.2698 | 0.44247 |  | 3757 | 20.84 | 49.5548 | 2.2679 | 63.2698
3758 | 32 | 51.2535 | 26.3421 | 55.3873 | 0.44956 |  | 3758 | 20.81 | 51.2535 | 3 | 55.3873
3759 | 32.53 | 55.5351 | 27.7706 | 61.6758 | 0.45269 |  | 3759 | 20.85 | 55.5351 | 4 | 61.6758
3760 | 33.58 | 71.3024 | 54.6286 | 53.5621 | 0.46004 |  | 3760 | 20.84 | 71.3024 | 5 | 53.5621
3761 | 35.76 | 92.7052 | 33.0389 | 82.9727 | 0.48376 |  | 3761 | 20.63 | 92.7052 | 5.7321 | 82.9727
3762 | 42.75 | 144.9813 | 50.6022 | 78.1682 | 0.49655 |  | 3762 | 20.4 | 144.9813 | 6 | 78.1682
3763 | 51.62 | 142.0271 | 51.4047 | 120.3256 | 0.50614 |  | 3763 | 23.91 | 142.0271 | 5.7321 | 120.3256
3764 | 58.43 | 115.9316 | 30.5809 | 101.3584 | 0.51729 |  | 3764 | 26.92 | 115.9316 | 5 | 101.3584
3765 | 54.6 | 95.2913 | 31.9952 | 98.0011 | 0.52215 |  | 3765 | 28.85 | 95.2913 | 4 | 98.0011
3766 | 47.66 | 94.9458 | 28.3854 | 76.7236 | 0.51706 |  | 3766 | 29.14 | 94.9458 | 3 | 76.7236
3767 | 41.4 | 74.8691 | 30.0901 | 38.9073 | 0.50754 |  | 3767 | 30.74 | 74.8691 | 2.2679 | 38.9073
3768 | 40.38 | 40.5308 | 225.4308 | 29.7188 | 0.49712 |  | 3768 | 30.09 | 40.5308 | 2 | 29.7188
3769 | 34.05 | 34.4313 | 23.2696 | 32.018 | 0.4912 |  | 3769 | 24.59 | 34.4313 | 2.2679 | 32.018
3770 | 32.46 | 32.7524 | 24.7776 | 7.3311 | 0.48156 |  | 3770 | 22.76 | 32.7524 | 3 | 7.3311
3771 | 33.14 | 31.1439 | 31.0904 | 17.6686 | 0.47353 |  | 3771 | 21.87 | 31.1439 | 4 | 17.6686
3772 | 32.09 | 29.7305 | 47.4439 | 40.2216 | 0.47007 |  | 3772 | 22.41 | 29.7305 | 5 | 40.2216
3773 | 32.41 | 28.716 | 107.2309 | 74.9203 | 0.47864 |  | 3773 | 23.33 | 28.716 | 5.7321 | 74.9203
3774 | 36.12 | 28.3493 | 103.9127 | 142.4018 | 0.48746 |  | 3774 | 24.07 | 28.3493 | 6 | 142.4018
3775 | 43.04 | 40.0078 | 112.4158 | 145.9912 | 0.4951 |  | 3775 | 32.8 | 40.0078 | 5.7321 | 145.9912
3776 | 51.17 | 53.2501 | 136.1435 | 155.9071 | 0.48198 |  | 3776 | 40.44 | 53.2501 | 5 | 155.9071
3777 | 45.82 | 43.2065 | 91.2104 | 108.716 | 0.46847 |  | 3777 | 37.82 | 43.2065 | 4 | 108.716
3778 | 37.21 | 41.4432 | 93.5102 | 71.9821 | 0.44448 |  | 3778 | 34.94 | 41.4432 | 3 | 71.9821
3779 | 33.39 | 43.0377 | 122.1647 | 67.6206 | 0.41485 |  | 3779 | 32.57 | 43.0377 | 2.2679 | 67.6206
3780 | 30.09 | 45.004 | 100.7609 | 78.7875 | 0.37835 |  | 3780 | 39.4 | 45.004 | 2 | 78.7875
3781 | 27.7 | 48.3274 | 48.5776 | 75.5809 | 0.3618 |  | 3781 | 39.4 | 48.3274 | 2.2679 | 75.5809
3782 | 27.07 | 51.3434 | 43.6955 | 61.7702 | 0.36256 |  | 3782 | 39.4 | 51.3434 | 3 | 61.7702
3783 | 27.21 | 55.8162 | 42.0141 | 52.3583 | 0.37443 |  | 3783 | 39.4 | 55.8162 | 4 | 52.3583
3784 | 28.57 | 70.996 | 39.6236 | 56.9797 | 0.38484 |  | 3784 | 38.53 | 70.996 | 5 | 56.9797
3785 | 31.27 | 99.0118 | 49.0809 | 79.4081 | 0.38925 |  | 3785 | 38.28 | 99.0118 | 5.7321 | 79.4081
3786 | 38.99 | 130.311 | 60.3114 | 94.6839 | 0.38912 |  | 3786 | 39.4 | 130.311 | 6 | 94.6839
3787 | 41.28 | 143.1225 | 34.6119 | 118.2035 | 0.38057 |  | 3787 | 38.76 | 143.1225 | 5.7321 | 118.2035
3788 | 40.07 | 123.7984 | 27.8641 | 124.6349 | 0.38227 |  | 3788 | 41.06 | 123.7984 | 5 | 124.6349
3789 | 32.02 | 102.6438 | 33.0486 | 93.7603 | 0.38174 |  | 3789 | 37.31 | 102.6438 | 4 | 93.7603
3790 | 30.04 | 97.0141 | 32.3529 | 74.5515 | 0.38188 |  | 3790 | 34.2 | 97.0141 | 3 | 74.5515
3791 | 28.8 | 76.8466 | 26.9459 | 55.111 | 0.36961 |  | 3791 | 33.81 | 76.8466 | 2.2679 | 55.111
3792 | 42.6 | 40.3289 | 26.7567 | 23.1206 | 0.35881 |  | 3792 | 34.12 | 40.3289 | 2 | 23.1206
3793 | 35 | 34.6992 | 36.3011 | 24.0846 | 0.34497 |  | 3793 | 24.85 | 34.6992 | 2.2679 | 24.0846
3794 | 27.1 | 32.9337 | 26.7721 | 5.6658 | 0.328 |  | 3794 | 23.34 | 32.9337 | 3 | 5.6658
3795 | 28.1 | 31.2835 | 33.648 | 23.545 | 0.31719 |  | 3795 | 22.59 | 31.2835 | 4 | 23.545
3796 | 27.1 | 29.7544 | 33.0121 | 45.1727 | 0.31298 |  | 3796 | 22.77 | 29.7544 | 5 | 45.1727
3797 | 25.5 | 28.7548 | 67.0364 | 88.8467 | 0.30945 |  | 3797 | 22.5 | 28.7548 | 5.7321 | 88.8467
3798 | 23.5 | 28.6798 | 59.5147 | 119.3964 | 0.31035 |  | 3798 | 22.68 | 28.6798 | 6 | 119.3964
3799 | 27.1 | 39.7209 | 26.4023 | 146.5787 | 0.31327 |  | 3799 | 32.4 | 39.7209 | 5.7321 | 146.5787
3800 | 28.1 | 54.2493 | 44.0966 | 119.6091 | 0.31566 |  | 3800 | 37.23 | 54.2493 | 5 | 119.6091
3801 | 29.9 | 43.4473 | 44.1806 | 85.0415 | 0.3234 |  | 3801 | 39.48 | 43.4473 | 4 | 85.0415
3802 | 27.4 | 41.8074 | 51.8312 | 65.8559 | 0.32629 |  | 3802 | 39.7 | 41.8074 | 3 | 65.8559
3803 | 26.2 | 43.4758 | 51.6351 | 82.7393 | 0.32455 |  | 3803 | 39.7 | 43.4758 | 2.2679 | 82.7393
3804 | 22.6 | 46.8439 | 36.6206 | 76.8909 | 0.3158 |  | 3804 | 38.97 | 46.8439 | 2 | 76.8909
3805 | 23.2 | 48.389 | 46.3276 | 80.4898 | 0.30924 |  | 3805 | 37.44 | 48.389 | 2.2679 | 80.4898
3806 | 20.1 | 52.653 | 46.0903 | 69.6631 | 0.30819 |  | 3806 | 34.07 | 52.653 | 3 | 69.6631
3807 | 16.5 | 57.9361 | 54.0052 | 64.3808 | 0.31067 |  | 3807 | 35.62 | 57.9361 | 4 | 64.3808
3808 | 16 | 77.8121 | 44.0114 | 64.8089 | 0.31161 |  | 3808 | 30.37 | 77.8121 | 5 | 64.8089
3809 | 26.3 | 95.4584 | 41.97 | 70.0793 | 0.31577 |  | 3809 | 34.94 | 95.4584 | 5.7321 | 70.0793
3810 | 26.7 | 129.3753 | 35.0925 | 78.1682 | 0.32469 |  | 3810 | 32.13 | 129.3753 | 6 | 78.1682
3811 | 25.8 | 141.012 | 49.5585 | 120.2195 | 0.3381 |  | 3811 | 36.02 | 141.012 | 5.7321 | 120.2195
3812 | 34.9 | 124.7071 | 29.6558 | 99.3482 | 0.35127 |  | 3812 | 38.48 | 124.7071 | 5 | 99.3482
3813 | 39 | 106.1277 | 31.3391 | 107.5892 | 0.35854 |  | 3813 | 35.71 | 106.1277 | 4 | 107.5892
3814 | 48 | 98.4175 | 28.4209 | 59.487 | 0.36452 |  | 3814 | 32.97 | 98.4175 | 3 | 59.487
3815 | 41 | 76.2381 | 24.9064 | 45.8252 | 0.36705 |  | 3815 | 32.59 | 76.2381 | 2.2679 | 45.8252
3816 | 27.7 | 40.0564 | 26.987 | 31.3549 | 0.35981 |  | 3816 | 27.54 | 40.0564 | 2 | 31.3549
3817 | 33.24 | 32.6402 | 27.9988 | 22.8619 | 0.36547 |  | 3817 | 25.98 | 32.6402 | 2.2679 | 22.8619
3818 | 36.43 | 31.3067 | 221.0422 | 6.9355 | 0.37199 |  | 3818 | 23.89 | 31.3067 | 3 | 6.9355
3819 | 38.09 | 29.8153 | 17.4639 | 18.5727 | 0.38305 |  | 3819 | 22.83 | 29.8153 | 4 | 18.5727
3820 | 30 | 28.7208 | 26.3249 | 41.0232 | 0.38801 |  | 3820 | 22.89 | 28.7208 | 5 | 41.0232
3821 | 27.7 | 28.1691 | 23.5313 | 95.3692 | 0.39065 |  | 3821 | 22.43 | 28.1691 | 5.7321 | 95.3692
3822 | 19.35 | 28.1908 | 32.0481 | 121.9669 | 0.3811 |  | 3822 | 23.59 | 28.1908 | 6 | 121.9669
3823 | 25 | 39.1609 | 21.8429 | 149.9567 | 0.39439 |  | 3823 | 28.59 | 39.1609 | 5.7321 | 149.9567
3824 | 26.57 | 54.2619 | 50.5488 | 136.7535 | 0.3906 |  | 3824 | 35.07 | 54.2619 | 5 | 136.7535
3825 | 30.29 | 43.5514 | 36.57 | 96.5672 | 0.3906 |  | 3825 | 41.31 | 43.5514 | 4 | 96.5672
3826 | 30.1 | 42.8372 | 21.3533 | 80.3652 | 0.38915 |  | 3826 | 37.33 | 42.8372 | 3 | 80.3652
3827 | 27.66 | 46.084 | 40.6071 | 69.4258 | 0.38245 |  | 3827 | 36.78 | 46.084 | 2.2679 | 69.4258
3828 | 29.9 | 46.4331 | 28.1568 | 86.4529 | 0.38316 |  | 3828 | 35 | 46.4331 | 2 | 86.4529
3829 | 23.4 | 51.385 | 34.4218 | 79.1652 | 0.38941 |  | 3829 | 30 | 51.385 | 2.2679 | 79.1652
3830 | 18.47 | 50.7268 | 38.6581 | 76.801 | 0.39715 |  | 3830 | 27.6 | 50.7268 | 3 | 76.801
3831 | 17.94 | 59.9288 | 38.5624 | 48.5712 | 0.41167 |  | 3831 | 27.18 | 59.9288 | 4 | 48.5712
3832 | 28.49 | 74.641 | 46.2937 | 50.3931 | 0.42545 |  | 3832 | 26.37 | 74.641 | 5 | 50.3931
3833 | 38.14 | 93.8198 | 31.1307 | 81.9109 | 0.43111 |  | 3833 | 26 | 93.8198 | 5.7321 | 81.9109
3834 | 43.81 | 145.2099 | 50.574 | 82.391 | 0.43725 |  | 3834 | 28.24 | 145.2099 | 6 | 82.391
3835 | 48.77 | 141.8642 | 41.8877 | 105.1523 | 0.4393 |  | 3835 | 30.68 | 141.8642 | 5.7321 | 105.1523
3836 | 58.1 | 116.1866 | 29.5681 | 85.6997 | 0.43936 |  | 3836 | 32.9 | 116.1866 | 5 | 85.6997
3837 | 57.11 | 95.815 | 31.4787 | 78.9172 | 0.43687 |  | 3837 | 32.12 | 95.815 | 4 | 78.9172
3838 | 41.49 | 89.481 | 27.5133 | 60.468 | 0.43358 |  | 3838 | 32.55 | 89.481 | 3 | 60.468
3839 | 35.6 | 75.1547 | 29.1241 | 54.136 | 0.43454 |  | 3839 | 30.9 | 75.1547 | 2.2679 | 54.136
3840 | 33.32 | 37.7039 | 33.6987 | 23.7911 | 0.42945 |  | 3840 | 26.5 | 37.7039 | 2 | 23.7911
3841 | 28.84 | 35.1642 | 33.1043 | 28.4921 | 0.4327 |  | 3841 | 23.67 | 35.1642 | 2.2679 | 28.4921
3842 | 27.78 | 33.2978 | 26.7437 | 5.4297 | 0.43803 |  | 3842 | 21.87 | 33.2978 | 3 | 5.4297
3843 | 27 | 31.6299 | 21.0322 | 19.1623 | 0.43171 |  | 3843 | 20.81 | 31.6299 | 4 | 19.1623
3844 | 27.01 | 30.0834 | 30.4131 | 54.4618 | 0.42614 |  | 3844 | 27.58 | 30.0834 | 5 | 54.4618
3845 | 25.83 | 29.0126 | 236.305 | 70.6014 | 0.4149 |  | 3845 | 30.86 | 29.0126 | 5.7321 | 70.6014
3846 | 26.84 | 28.3498 | 28.779 | 146.1289 | 0.40594 |  | 3846 | 29.8 | 28.3498 | 6 | 146.1289
3847 | 30.03 | 28.0834 | 27.4862 | 118.3792 | 0.39796 |  | 3847 | 28.5 | 28.0834 | 5.7321 | 118.3792
3848 | 33.54 | 30.233 | 38.007 | 140.3699 | 0.39002 |  | 3848 | 33.95 | 30.233 | 5 | 140.3699
3849 | 30.92 | 49.7962 | 36.3029 | 87.1182 | 0.37906 |  | 3849 | 43.08 | 49.7962 | 4 | 87.1182
3850 | 30.06 | 68.2293 | 39.0213 | 84.315 | 0.37586 |  | 3850 | 44 | 68.2293 | 3 | 84.315
3851 | 29.55 | 74.3746 | 57.9904 | 62.0545 | 0.37064 |  | 3851 | 42.89 | 74.3746 | 2.2679 | 62.0545
3852 | 28.69 | 77.001 | 41.4674 | 71.1221 | 0.37038 |  | 3852 | 41.4 | 77.001 | 2 | 71.1221
3853 | 28.03 | 79.0992 | 42.1317 | 82.9832 | 0.36986 |  | 3853 | 34.99 | 79.0992 | 2.2679 | 82.9832
3854 | 27.3 | 79.6007 | 44.3375 | 69.9376 | 0.37151 |  | 3854 | 33.93 | 79.6007 | 3 | 69.9376
3855 | 27.45 | 78.4107 | 49.9971 | 68.8292 | 0.38146 |  | 3855 | 32.44 | 78.4107 | 4 | 68.8292
3856 | 28.08 | 81.0509 | 35.1343 | 71.7683 | 0.39355 |  | 3856 | 29.94 | 81.0509 | 5 | 71.7683
3857 | 31.19 | 84.511 | 42.0496 | 74.5541 | 0.40238 |  | 3857 | 30 | 84.511 | 5.7321 | 74.5541
3858 | 36.52 | 136.7556 | 40.273 | 82.1094 | 0.40778 |  | 3858 | 28.88 | 136.7556 | 6 | 82.1094
3859 | 40 | 156.5819 | 46.8537 | 107.6989 | 0.409 |  | 3859 | 32.95 | 156.5819 | 5.7321 | 107.6989
3860 | 41.04 | 118.6339 | 28.7741 | 102.0991 | 0.41066 |  | 3860 | 34.94 | 118.6339 | 5 | 102.0991
3861 | 39.9 | 100.5096 | 27.3437 | 101.1357 | 0.41685 |  | 3861 | 33.7 | 100.5096 | 4 | 101.1357
3862 | 40 | 93.2373 | 24.375 | 83.1697 | 0.42781 |  | 3862 | 31.51 | 93.2373 | 3 | 83.1697
3863 | 35.06 | 92.0601 | 29.9671 | 39.4181 | 0.438 |  | 3863 | 30.49 | 92.0601 | 2.2679 | 39.4181
3864 | 43.65 | 42.2319 | 34.4735 | 22.6378 | 0.44827 |  | 3864 | 31.42 | 42.2319 | 2 | 22.6378
3865 | 29.21 | 34.5606 | 33.5026 | 23.2315 | 0.44191 |  | 3865 | 27.35 | 34.5606 | 2.2679 | 23.2315
3866 | 28.28 | 33.0349 | 25.8952 | 7.4778 | 0.44393 |  | 3866 | 23.71 | 33.0349 | 3 | 7.4778
3867 | 27.14 | 31.3997 | 27.5836 | 16.5877 | 0.45296 |  | 3867 | 21.03 | 31.3997 | 4 | 16.5877
3868 | 26.53 | 29.9074 | 40.8063 | 44.5597 | 0.44905 |  | 3868 | 19.91 | 29.9074 | 5 | 44.5597
3869 | 29.13 | 28.7698 | 79.9373 | 79.5037 | 0.44258 |  | 3869 | 20.55 | 28.7698 | 5.7321 | 79.5037
3870 | 42.32 | 28.0652 | 116.3777 | 143.3014 | 0.44004 |  | 3870 | 20.97 | 28.0652 | 6 | 143.3014
3871 | 47.07 | 27.7358 | 107.3291 | 157.8878 | 0.43331 |  | 3871 | 27.25 | 27.7358 | 5.7321 | 157.8878
3872 | 52.41 | 30.1253 | 94.9107 | 144.9239 | 0.43055 |  | 3872 | 33.94 | 30.1253 | 5 | 144.9239
3873 | 50.03 | 48.794 | 52.2568 | 101.759 | 0.42092 |  | 3873 | 35.95 | 48.794 | 4 | 101.759
3874 | 52.22 | 66.7855 | 51.8283 | 73.9973 | 0.41846 |  | 3874 | 39.7 | 66.7855 | 3 | 73.9973
3875 | 53.37 | 75.3045 | 90.4193 | 63.634 | 0.41785 |  | 3875 | 50.31 | 75.3045 | 2.2679 | 63.634
3876 | 47.38 | 73.7269 | 47.7366 | 85.9788 | 0.42068 |  | 3876 | 50.03 | 73.7269 | 2 | 85.9788
3877 | 45.72 | 81.0897 | 68.6866 | 74.4121 | 0.42833 |  | 3877 | 50.65 | 81.0897 | 2.2679 | 74.4121
3878 | 45 | 77.6908 | 43.0419 | 75.2224 | 0.43057 |  | 3878 | 52.75 | 77.6908 | 3 | 75.2224
3879 | 46.19 | 76.1644 | 34.7634 | 57.6482 | 0.43072 |  | 3879 | 49.5 | 76.1644 | 4 | 57.6482
3880 | 49.12 | 76.4822 | 37.4477 | 69.9663 | 0.4314 |  | 3880 | 39.04 | 76.4822 | 5 | 69.9663
3881 | 55.71 | 78.8949 | 58.8117 | 70.3068 | 0.43546 |  | 3881 | 29.65 | 78.8949 | 5.7321 | 70.3068
3882 | 59.38 | 119.3559 | 38.7773 | 80.4203 | 0.43935 |  | 3882 | 29.94 | 119.3559 | 6 | 80.4203
3883 | 59.93 | 128.9736 | 39.0998 | 86.5835 | 0.45085 |  | 3883 | 30.01 | 128.9736 | 5.7321 | 86.5835
3884 | 54 | 141.026 | 71.8801 | 105.3789 | 0.46758 |  | 3884 | 32.85 | 141.026 | 5 | 105.3789
3885 | 51.25 | 101.4642 | 94.2698 | 96.0651 | 0.48113 |  | 3885 | 32.06 | 101.4642 | 4 | 96.0651
3886 | 46.1 | 93.4088 | 95.4344 | 59.9775 | 0.48616 |  | 3886 | 31.67 | 93.4088 | 3 | 59.9775
3887 | 40.93 | 90.2996 | 27.8682 | 44.2931 | 0.48904 |  | 3887 | 32.86 | 90.2996 | 2.2679 | 44.2931
3888 | 37.69 | 41.1865 | 28.7208 | 23.7106 | 0.47939 |  | 3888 | 35.23 | 41.1865 | 2 | 23.7106
3889 | 35.65 | 34.4274 | 23.6741 | 23.5159 | 0.48263 |  | 3889 | 26.14 | 34.4274 | 2.2679 | 23.5159
3890 | 33.43 | 32.7001 | 21.9597 | 5.5063 | 0.48598 |  | 3890 | 24.2 | 32.7001 | 3 | 5.5063
3891 | 33.04 | 31.0469 | 27.9857 | 19.4571 | 0.48658 |  | 3891 | 23.01 | 31.0469 | 4 | 19.4571
3892 | 32.64 | 29.5845 | 38.4724 | 39.7972 | 0.48591 |  | 3892 | 22.31 | 29.5845 | 5 | 39.7972
3893 | 34.74 | 28.7485 | 52.0726 | 72.1879 | 0.49549 |  | 3893 | 23.93 | 28.7485 | 5.7321 | 72.1879
3894 | 46.66 | 28.3614 | 126.2288 | 104.488 | 0.50114 |  | 3894 | 24.13 | 28.3614 | 6 | 104.488
3895 | 55.72 | 40.1864 | 112.4821 | 168.1689 | 0.49546 |  | 3895 | 24.45 | 40.1864 | 5.7321 | 168.1689
3896 | 62.61 | 56.6172 | 65.6407 | 143.1827 | 0.49731 |  | 3896 | 25.13 | 56.6172 | 5 | 143.1827
3897 | 57.86 | 44.9175 | 92.117 | 94.9059 | 0.49269 |  | 3897 | 26.06 | 44.9175 | 4 | 94.9059
3898 | 52.31 | 42.961 | 85.5771 | 95.4387 | 0.48707 |  | 3898 | 29.47 | 42.961 | 3 | 95.4387
3899 | 50.54 | 44.5033 | 31.1031 | 66.5675 | 0.48116 |  | 3899 | 29.46 | 44.5033 | 2.2679 | 66.5675
3900 | 45.98 | 47.9925 | 35.8016 | 79.6568 | 0.47507 |  | 3900 | 30.03 | 47.9925 | 2 | 79.6568
3901 | 42.91 | 50.1695 | 39.4885 | 69.8929 | 0.47007 |  | 3901 | 28.49 | 50.1695 | 2.2679 | 69.8929
3902 | 39.05 | 52.8611 | 43.9611 | 58.5445 | 0.47924 |  | 3902 | 25.69 | 52.8611 | 3 | 58.5445
3903 | 34.09 | 57.7389 | 48.6892 | 62.7578 | 0.48329 |  | 3903 | 24.82 | 57.7389 | 4 | 62.7578
3904 | 34.9 | 71.1313 | 44.0043 | 60.5836 | 0.47609 |  | 3904 | 24.22 | 71.1313 | 5 | 60.5836
3905 | 42.14 | 94.0396 | 33.1424 | 62.4191 | 0.46562 |  | 3905 | 24.9 | 94.0396 | 5.7321 | 62.4191
3906 | 48.5 | 131.0639 | 59.8953 | 75.5407 | 0.4762 |  | 3906 | 32.74 | 131.0639 | 6 | 75.5407
3907 | 51.44 | 147.2284 | 97.5381 | 96.8759 | 0.48611 |  | 3907 | 32.67 | 147.2284 | 5.7321 | 96.8759
3908 | 50.56 | 130.055 | 86.8164 | 85.4881 | 0.49026 |  | 3908 | 34.35 | 130.055 | 5 | 85.4881
3909 | 47.7 | 100.4864 | 107.2753 | 101.4123 | 0.4888 |  | 3909 | 36.32 | 100.4864 | 4 | 101.4123
3910 | 44.64 | 95.1326 | 70.5421 | 58.7163 | 0.49817 |  | 3910 | 29.47 | 95.1326 | 3 | 58.7163
3911 | 38.7 | 77.4743 | 65.9281 | 55.111 | 0.49955 |  | 3911 | 30.94 | 77.4743 | 2.2679 | 55.111
3912 | 29.78 | 40.2982 | 60.0061 | 31.3281 | 0.49633 |  | 3912 | 33.19 | 40.2982 | 2 | 31.3281
3913 | 28.34 | 33.3877 | 109.8183 | 30.71 | 0.47031 |  | 3913 | 39.08 | 33.3877 | 2.2679 | 30.71
3914 | 27.32 | 31.9595 | 57.3196 | 6.9036 | 0.45283 |  | 3914 | 24.65 | 31.9595 | 3 | 6.9036
3915 | 27.35 | 30.5142 | 21.6144 | 23.093 | 0.4393 |  | 3915 | 22.64 | 30.5142 | 4 | 23.093
3916 | 27.45 | 29.3495 | 27.978 | 39.7029 | 0.43963 |  | 3916 | 22.42 | 29.3495 | 5 | 39.7029
3917 | 29.1 | 28.2952 | 37.6333 | 70.6895 | 0.44836 |  | 3917 | 24.33 | 28.2952 | 5.7321 | 70.6895
3918 | 36.56 | 27.8608 | 277.6479 | 110.1429 | 0.45085 |  | 3918 | 22.54 | 27.8608 | 6 | 110.1429
3919 | 45.32 | 38.2135 | 85.7523 | 151.2786 | 0.4447 |  | 3919 | 22.82 | 38.2135 | 5.7321 | 151.2786
3920 | 44.49 | 52.2387 | 71.3766 | 143.3166 | 0.43441 |  | 3920 | 22.6 | 52.2387 | 5 | 143.3166
3921 | 36.42 | 42.5901 | 86.4753 | 93.556 | 0.428 |  | 3921 | 24.65 | 42.5901 | 4 | 93.556
3922 | 32.9 | 41.1564 | 309.764 | 81.4937 | 0.41808 |  | 3922 | 23.01 | 41.1564 | 3 | 81.4937
3923 | 30.18 | 43.3677 | 82.6668 | 80.0315 | 0.40587 |  | 3923 | 24.94 | 43.3677 | 2.2679 | 80.0315
3924 | 28.42 | 46.1487 | 74.695 | 81.3163 | 0.4033 |  | 3924 | 25.3 | 46.1487 | 2 | 81.3163
3925 | 28.66 | 47.2269 | 93.9495 | 82.1261 | 0.40688 |  | 3925 | 35.01 | 47.2269 | 2.2679 | 82.1261
3926 | 28.85 | 47.8076 | 78.7388 | 59.7112 | 0.40552 |  | 3926 | 26.7 | 47.8076 | 3 | 59.7112
3927 | 29.95 | 55.8284 | 40.1606 | 67.6269 | 0.40598 |  | 3927 | 24.7 | 55.8284 | 4 | 67.6269
3928 | 31.11 | 68.1691 | 42.3149 | 67.0459 | 0.41546 |  | 3928 | 24.68 | 68.1691 | 5 | 67.0459
3929 | 33.68 | 91.1038 | 46.3908 | 81.1525 | 0.43754 |  | 3929 | 24.76 | 91.1038 | 5.7321 | 81.1525
3930 | 48.71 | 131.2664 | 46.1155 | 101.1588 | 0.45717 |  | 3930 | 29.56 | 131.2664 | 6 | 101.1588
3931 | 62.06 | 144.8192 | 86.6762 | 110.0332 | 0.46952 |  | 3931 | 32.44 | 144.8192 | 5.7321 | 110.0332
3932 | 72.87 | 131.7098 | 107.2009 | 99.983 | 0.47556 |  | 3932 | 34.94 | 131.7098 | 5 | 99.983
3933 | 60.28 | 93.8958 | 90.8565 | 76.6124 | 0.47086 |  | 3933 | 34.94 | 93.8958 | 4 | 76.6124
3934 | 47.56 | 94.8126 | 75.1172 | 83.3099 | 0.46952 |  | 3934 | 30.03 | 94.8126 | 3 | 83.3099
3935 | 41.03 | 74.5015 | 48.2545 | 41.7395 | 0.4684 |  | 3935 | 32.44 | 74.5015 | 2.2679 | 41.7395
3936 | 33.44 | 38.3411 | 40.4504 | 24.864 | 0.4551 |  | 3936 | 37.97 | 38.3411 | 2 | 24.864
3937 | 29.78 | 35.4779 | 88.7714 | 30.7669 | 0.4448 |  | 3937 | 25.61 | 35.4779 | 2.2679 | 30.7669
3938 | 28.22 | 33.769 | 59.1978 | 5.519 | 0.43684 |  | 3938 | 24.83 | 33.769 | 3 | 5.519
3939 | 27.98 | 31.9677 | 21.0403 | 16.6466 | 0.43776 |  | 3939 | 24.35 | 31.9677 | 4 | 16.6466
3940 | 27.99 | 30.3454 | 22.5944 | 52.8586 | 0.45083 |  | 3940 | 22.61 | 30.3454 | 5 | 52.8586
3941 | 29.55 | 29.162 | 30.3718 | 96.0743 | 0.46196 |  | 3941 | 23.9 | 29.162 | 5.7321 | 96.0743
3942 | 39.26 | 28.5513 | 32.2804 | 132.7627 | 0.47923 |  | 3942 | 23.02 | 28.5513 | 6 | 132.7627
3943 | 51.87 | 39.7025 | 21.5424 | 165.8189 | 0.48545 |  | 3943 | 28.99 | 39.7025 | 5.7321 | 165.8189
3944 | 58.68 | 53.7347 | 50.8983 | 112.2424 | 0.48606 |  | 3944 | 37 | 53.7347 | 5 | 112.2424
3945 | 49.04 | 40.7742 | 33.2445 | 108.1968 | 0.48417 |  | 3945 | 39.36 | 40.7742 | 4 | 108.1968
3946 | 42.91 | 38.9905 | 47.4793 | 70.1281 | 0.48012 |  | 3946 | 48.03 | 38.9905 | 3 | 70.1281
3947 | 41.01 | 40.9028 | 92.1646 | 82.965 | 0.48288 |  | 3947 | 53.62 | 40.9028 | 2.2679 | 82.965
3948 | 34.9 | 41.9229 | 44.6058 | 75.8636 | 0.47413 |  | 3948 | 55.52 | 41.9229 | 2 | 75.8636
3949 | 33.02 | 43.8368 | 40.7558 | 81.7365 | 0.47195 |  | 3949 | 51.85 | 43.8368 | 2.2679 | 81.7365
3950 | 33.28 | 46.5973 | 50.6899 | 65.2706 | 0.47357 |  | 3950 | 61.54 | 46.5973 | 3 | 65.2706
3951 | 34.06 | 52.6812 | 42.9951 | 64.9219 | 0.4836 |  | 3951 | 46.8 | 52.6812 | 4 | 64.9219
3952 | 36.34 | 70.1005 | 34.7204 | 61.7021 | 0.4874 |  | 3952 | 43.11 | 70.1005 | 5 | 61.7021
3953 | 47.79 | 90.2297 | 45.2202 | 69.6243 | 0.49442 |  | 3953 | 46.8 | 90.2297 | 5.7321 | 69.6243
3954 | 56.82 | 121.2849 | 42.8211 | 86.7076 | 0.50433 |  | 3954 | 61.47 | 121.2849 | 6 | 86.7076
3955 | 62.76 | 145.6563 | 34.9597 | 120.4317 | 0.51093 |  | 3955 | 45.01 | 145.6563 | 5.7321 | 120.4317
3956 | 57.36 | 139.5044 | 28.8081 | 122.0957 | 0.5146 |  | 3956 | 43.72 | 139.5044 | 5 | 122.0957
3957 | 49.07 | 98.9867 | 31.6171 | 74.5841 | 0.51549 |  | 3957 | 40.12 | 98.9867 | 4 | 74.5841
3958 | 43.49 | 91.9061 | 35.0397 | 66.4237 | 0.51958 |  | 3958 | 35.22 | 91.9061 | 3 | 66.4237
3959 | 37.94 | 76.8373 | 68.4867 | 39.1859 | 0.52925 |  | 3959 | 36.56 | 76.8373 | 2.2679 | 39.1859
3960 | 33.29 | 40.7891 | 105.6587 | 29.9333 | 0.52235 |  | 3960 | 37.65 | 40.7891 | 2 | 29.9333
3961 | 31.47 | 33.9722 | 94.7911 | 23.2315 | 0.50223 |  | 3961 | 26.27 | 33.9722 | 2.2679 | 23.2315
3962 | 29.92 | 32.4899 | 39.2885 | 5.7104 | 0.48725 |  | 3962 | 24.39 | 32.4899 | 3 | 5.7104
3963 | 28.26 | 30.9596 | 33.6361 | 21.2456 | 0.47807 |  | 3963 | 23.25 | 30.9596 | 4 | 21.2456
3964 | 27.48 | 29.5171 | 30.3014 | 38.9013 | 0.47132 |  | 3964 | 22.25 | 29.5171 | 5 | 38.9013
3965 | 25.98 | 28.6197 | 36.3834 | 81.9717 | 0.47477 |  | 3965 | 24.3 | 28.6197 | 5.7321 | 81.9717
3966 | 26.68 | 28.1941 | 65.9575 | 152.9405 | 0.48041 |  | 3966 | 24.41 | 28.1941 | 6 | 152.9405
3967 | 29.99 | 38.6134 | 116.2777 | 151.1317 | 0.47481 |  | 3967 | 27.4 | 38.6134 | 5.7321 | 151.1317
3968 | 33 | 54.514 | 131.9595 | 121.0825 | 0.46995 |  | 3968 | 35.29 | 54.514 | 5 | 121.0825
3969 | 40 | 43.7233 | 114.6307 | 122.007 | 0.46389 |  | 3969 | 40 | 43.7233 | 4 | 122.007
3970 | 39.5 | 42.8062 | 112.9073 | 95.7612 | 0.4415 |  | 3970 | 38.44 | 42.8062 | 3 | 95.7612
3971 | 47.8 | 46.0441 | 117.7317 | 88.5311 | 0.41731 |  | 3971 | 37.76 | 46.0441 | 2.2679 | 88.5311
3972 | 40.66 | 47.4396 | 104.1663 | 94.0393 | 0.42893 |  | 3972 | 42.44 | 47.4396 | 2 | 94.0393
3973 | 26 | 49.9934 | 136.4877 | 67.3215 | 0.44518 |  | 3973 | 44.94 | 49.9934 | 2.2679 | 67.3215
3974 | 24.31 | 51.6203 | 128.8522 | 77.7619 | 0.42858 |  | 3974 | 49.94 | 51.6203 | 3 | 77.7619
3975 | 24.42 | 59.0591 | 62.4658 | 56.5061 | 0.42002 |  | 3975 | 42.54 | 59.0591 | 4 | 56.5061
3976 | 24.92 | 75.2153 | 44.1302 | 54.1214 | 0.43827 |  | 3976 | 37.83 | 75.2153 | 5 | 54.1214
3977 | 32.37 | 90.8019 | 37.0705 | 79.8631 | 0.4614 |  | 3977 | 38 | 90.8019 | 5.7321 | 79.8631
3978 | 35.34 | 133.4308 | 41.1766 | 103.2233 | 0.49404 |  | 3978 | 42.44 | 133.4308 | 6 | 103.2233
3979 | 40.1 | 157.1308 | 34.5526 | 111.0943 | 0.51489 |  | 3979 | 35.08 | 157.1308 | 5.7321 | 111.0943
3980 | 51.02 | 109.2632 | 24.1526 | 115.8533 | 0.52608 |  | 3980 | 37.5 | 109.2632 | 5 | 115.8533
3981 | 50.19 | 97.7095 | 22.5343 | 102.1498 | 0.53504 |  | 3981 | 36 | 97.7095 | 4 | 102.1498
3982 | 42.79 | 94.4753 | 25.9216 | 62.7101 | 0.54073 |  | 3982 | 32.01 | 94.4753 | 3 | 62.7101
3983 | 34.31 | 75.1105 | 24.3711 | 40.4859 | 0.5375 |  | 3983 | 33.85 | 75.1105 | 2.2679 | 40.4859
3984 | 30.17 | 39.3835 | 32.296 | 23.6302 | 0.52544 |  | 3984 | 33.1 | 39.3835 | 2 | 23.6302
3985 | 28.43 | 33.4797 | 38.0922 | 24.9661 | 0.50528 |  | 3985 | 27.72 | 33.4797 | 2.2679 | 24.9661
3986 | 30.46 | 31.8749 | 25.4865 | 6.5718 | 0.49078 |  | 3986 | 26.83 | 31.8749 | 3 | 6.5718
3987 | 27.85 | 30.4508 | 30.4873 | 21.5797 | 0.46924 |  | 3987 | 25.01 | 30.4508 | 4 | 21.5797
3988 | 28.1 | 29.1513 | 35.8835 | 43.5223 | 0.45002 |  | 3988 | 23.73 | 29.1513 | 5 | 43.5223
3989 | 27.79 | 28.2803 | 70.5091 | 100.6577 | 0.44709 |  | 3989 | 24.3 | 28.2803 | 5.7321 | 100.6577
3990 | 29.03 | 28.1424 | 92.9656 | 122.8665 | 0.44226 |  | 3990 | 25.31 | 28.1424 | 6 | 122.8665
3991 | 33.41 | 39.578 | 113.9884 | 166.4064 | 0.44468 |  | 3991 | 28.37 | 39.578 | 5.7321 | 166.4064
3992 | 32.6 | 55.3074 | 117.2883 | 113.7157 | 0.43092 |  | 3992 | 36.61 | 55.3074 | 5 | 113.7157
3993 | 31.55 | 45.3291 | 67.4848 | 84.0031 | 0.42442 |  | 3993 | 42.76 | 45.3291 | 4 | 84.0031
3994 | 28.35 | 44.8998 | 50.4463 | 65.2917 | 0.43092 |  | 3994 | 56.18 | 44.8998 | 3 | 65.2917
3995 | 27.98 | 49.0956 | 101.7162 | 60.5501 | 0.42809 |  | 3995 | 61.02 | 49.0956 | 2.2679 | 60.5501
3996 | 27.17 | 51.6437 | 138.0817 | 63.5358 | 0.42681 |  | 3996 | 58.65 | 51.6437 | 2 | 63.5358
3997 | 23.92 | 52.9163 | 119.3368 | 82.9052 | 0.438 |  | 3997 | 54 | 52.9163 | 2.2679 | 82.9052
3998 | 25.93 | 55.2937 | 116.9648 | 69.114 | 0.43952 |  | 3998 | 52.66 | 55.2937 | 3 | 69.114
3999 | 27.51 | 61.5131 | 132.8766 | 64.8617 | 0.44114 |  | 3999 | 48.69 | 61.5131 | 4 | 64.8617
4000 | 29.48 | 76.0428 | 268.2489 | 54.432 | 0.44431 |  | 4000 | 40.5 | 76.0428 | 5 | 54.432
4001 | 34.2 | 94.9308 | 39.304 | 75.6917 | 0.46982 |  | 4001 | 44.22 | 94.9308 | 5.7321 | 75.6917
4002 | 37.75 | 137.0033 | 38.1644 | 76.8544 | 0.49514 |  | 4002 | 62.2 | 137.0033 | 6 | 76.8544
4003 | 44.44 | 139.2045 | 42.6436 | 110.2454 | 0.50868 |  | 4003 | 61.09 | 139.2045 | 5.7321 | 110.2454
4004 | 49.26 | 113.83 | 30.109 | 100.512 | 0.51538 |  | 4004 | 54.78 | 113.83 | 5 | 100.512
4005 | 52.15 | 96.9245 | 28.7538 | 78.1796 | 0.51519 |  | 4005 | 47.64 | 96.9245 | 4 | 78.1796
4006 | 47.8 | 92.3051 | 29.8997 | 76.7236 | 0.51501 |  | 4006 | 42.44 | 92.3051 | 3 | 76.7236
4007 | 40.91 | 74.9574 | 25.2213 | 46.9395 | 0.50317 |  | 4007 | 43.49 | 74.9574 | 2.2679 | 46.9395
4008 | 33.06 | 38.4651 | 32.2998 | 23.6302 | 0.48412 |  | 4008 | 36.89 | 38.4651 | 2 | 23.6302
4009 | 30.28 | 33.6114 | 25.2521 | 25.0514 | 0.46887 |  | 4009 | 31.86 | 33.6114 | 2.2679 | 25.0514
4010 | 30.5 | 32.1345 | 24.1092 | 6.0996 | 0.47307 |  | 4010 | 26.52 | 32.1345 | 3 | 6.0996
4011 | 30.46 | 30.6395 | 23.1315 | 21.9531 | 0.4773 |  | 4011 | 26.04 | 30.6395 | 4 | 21.9531
4012 | 29.52 | 29.352 | 25.3002 | 51.5855 | 0.49379 |  | 4012 | 25.12 | 29.352 | 5 | 51.5855
4013 | 30.69 | 28.5913 | 59.0478 | 103.1256 | 0.50624 |  | 4013 | 25.55 | 28.5913 | 5.7321 | 103.1256
4014 | 44.22 | 27.9461 | 112.7818 | 129.1641 | 0.51597 |  | 4014 | 24.95 | 27.9461 | 6 | 129.1641
4015 | 50.8 | 27.6806 | 120.7847 | 167.2877 | 0.51098 |  | 4015 | 29.84 | 27.6806 | 5.7321 | 167.2877
4016 | 49.02 | 29.9822 | 139.6144 | 147.7367 | 0.50304 |  | 4016 | 37.82 | 29.9822 | 5 | 147.7367
4017 | 39.19 | 48.2966 | 114.644 | 88.0527 | 0.49717 |  | 4017 | 41.64 | 48.2966 | 4 | 88.0527
4018 | 34.64 | 68.5181 | 134.2638 | 79.801 | 0.48734 |  | 4018 | 44.74 | 68.5181 | 3 | 79.801
4019 | 33.7 | 76.0021 | 128.6323 | 60.2493 | 0.47304 |  | 4019 | 44.72 | 76.0021 | 2.2679 | 60.2493
4020 | 33.99 | 75.469 | 332.14 | 70.8851 | 0.46619 |  | 4020 | 44.72 | 75.469 | 2 | 70.8851
4021 | 35.16 | 79.0045 | 107.7343 | 83.6844 | 0.48127 |  | 4021 | 40 | 79.0045 | 2.2679 | 83.6844
4022 | 34.76 | 76.2258 | 51.9377 | 78.4482 | 0.49589 |  | 4022 | 44.75 | 76.2258 | 3 | 78.4482
4023 | 35.5 | 73.9251 | 46.3695 | 55.9049 | 0.50639 |  | 4023 | 44.92 | 73.9251 | 4 | 55.9049
4024 | 39.17 | 76.4807 | 51.5646 | 73.8188 | 0.50789 |  | 4024 | 39.96 | 76.4807 | 5 | 73.8188
4025 | 44.97 | 79.567 | 42.1493 | 83.8828 | 0.51051 |  | 4025 | 41.51 | 79.567 | 5.7321 | 83.8828
4026 | 55.55 | 118.9193 | 39.8355 | 82.8602 | 0.51358 |  | 4026 | 51.02 | 118.9193 | 6 | 82.8602
4027 | 70.1 | 133.4886 | 52.9958 | 117.0363 | 0.51978 |  | 4027 | 47.44 | 133.4886 | 5.7321 | 117.0363
4028 | 69.52 | 125.9934 | 27.833 | 121.6725 | 0.5271 |  | 4028 | 45.5 | 125.9934 | 5 | 121.6725
4029 | 58.24 | 98.1171 | 33.6719 | 98.8309 | 0.53359 |  | 4029 | 47.44 | 98.1171 | 4 | 98.8309
4030 | 46.67 | 90.9087 | 24.8912 | 58.9265 | 0.54047 |  | 4030 | 33.02 | 90.9087 | 3 | 58.9265
4031 | 39.1 | 88.6422 | 35.7015 | 50.6074 | 0.54003 |  | 4031 | 35.01 | 88.6422 | 2.2679 | 50.6074
4032 | 32.97 | 40.4211 | 25.8582 | 32.0255 | 0.52864 |  | 4032 | 37.64 | 40.4211 | 2 | 32.0255
4033 | 32.85 | 33.5704 | 33.2531 | 32.7289 | 0.51675 |  | 4033 | 36.76 | 33.5704 | 2.2679 | 32.7289
4034 | 31.71 | 32.018 | 26.9946 | 6.7377 | 0.51533 |  | 4034 | 25.88 | 32.018 | 3 | 6.7377
4035 | 32.87 | 30.6272 | 31.3916 | 17.8651 | 0.51833 |  | 4035 | 25.2 | 30.6272 | 4 | 17.8651
4036 | 32.6 | 29.3648 | 29.7689 | 39.2314 | 0.53151 |  | 4036 | 23.34 | 29.3648 | 5 | 39.2314
4037 | 32.03 | 28.3963 | 40.9946 | 105.5936 | 0.54003 |  | 4037 | 23.36 | 28.3963 | 5.7321 | 105.5936
4038 | 40.16 | 27.8053 | 63.1008 | 109.5003 | 0.54258 |  | 4038 | 23.89 | 27.8053 | 6 | 109.5003
4039 | 51.74 | 27.4873 | 37.1715 | 138.7944 | 0.53177 |  | 4039 | 27.85 | 27.4873 | 5.7321 | 138.7944
4040 | 49.75 | 29.4983 | 47.5243 | 157.7822 | 0.52088 |  | 4040 | 35.3 | 29.4983 | 5 | 157.7822
4041 | 45.11 | 47.386 | 83.1925 | 123.1492 | 0.51506 |  | 4041 | 39.7 | 47.386 | 4 | 123.1492
4042 | 39.92 | 67.11 | 78.6708 | 73.2718 | 0.51471 |  | 4042 | 60.95 | 67.11 | 3 | 73.2718
4043 | 38.9 | 75.5857 | 47.5736 | 80.8589 | 0.51245 |  | 4043 | 67.01 | 75.5857 | 2.2679 | 80.8589
4044 | 37.12 | 76.7365 | 47.6935 | 90.4041 | 0.51242 |  | 4044 | 62.18 | 76.7365 | 2 | 90.4041
4045 | 36.1 | 83.6477 | 43.0743 | 72.8538 | 0.51521 |  | 4045 | 57.8 | 83.6477 | 2.2679 | 72.8538
4046 | 36.06 | 79.7595 | 53.3861 | 72.1339 | 0.51575 |  | 4046 | 51.41 | 79.7595 | 3 | 72.1339
4047 | 38.37 | 78.6196 | 37.7253 | 52.2982 | 0.51577 |  | 4047 | 39.94 | 78.6196 | 4 | 52.2982
4048 | 42.92 | 75.5351 | 51.6992 | 62.9448 | 0.51496 |  | 4048 | 37.07 | 75.5351 | 5 | 62.9448
4049 | 53.74 | 74.7963 | 42.1235 | 71.9754 | 0.51219 |  | 4049 | 37.02 | 74.7963 | 5.7321 | 71.9754
4050 | 58.8 | 114.0402 | 37.0333 | 101.8157 | 0.51121 |  | 4050 | 32.44 | 114.0402 | 6 | 101.8157
4051 | 66.16 | 118.1669 | 50.2722 | 89.5545 | 0.51614 |  | 4051 | 32.35 | 118.1669 | 5.7321 | 89.5545
4052 | 67.12 | 138.3054 | 35.7492 | 98.925 | 0.51563 |  | 4052 | 32.15 | 138.3054 | 5 | 98.925
4053 | 53.2 | 100.0721 | 20.3483 | 88.3209 | 0.51694 |  | 4053 | 30.59 | 100.0721 | 4 | 88.3209
4054 | 47 | 88.8829 | 36.4541 | 60.1877 | 0.5176 |  | 4054 | 28.16 | 88.8829 | 3 | 60.1877
4055 | 37.08 | 89.1 | 29.8523 | 49.4931 | 0.51483 |  | 4055 | 37.44 | 89.1 | 2.2679 | 49.4931
4056 | 34.12 | 40.6641 | 27.752 | 28.4581 | 0.50205 |  | 4056 | 30.02 | 40.6641 | 2 | 28.4581
4057 | 35.32 | 32.8113 | 27.8167 | 29.5157 | 0.4908 |  | 4057 | 30.09 | 32.8113 | 2.2679 | 29.5157
4058 | 35.06 | 31.449 | 17.5071 | 7.3566 | 0.4913 |  | 4058 | 25.09 | 31.449 | 3 | 7.3566
4059 | 35.39 | 30.0236 | 25.5526 | 22.5034 | 0.491 |  | 4059 | 24.85 | 30.0236 | 4 | 22.5034
4060 | 35.01 | 28.7099 | 25.7138 | 37.8168 | 0.50122 |  | 4060 | 26.42 | 28.7099 | 5 | 37.8168
4061 | 32.04 | 28.0559 | 41.9737 | 81.2665 | 0.51092 |  | 4061 | 28.69 | 28.0559 | 5.7321 | 81.2665
4062 | 40.96 | 27.8885 | 67.5772 | 127.3648 | 0.50793 |  | 4062 | 26.1 | 27.8885 | 6 | 127.3648
4063 | 52.3 | 38.8156 | 46.8997 | 117.9385 | 0.49979 |  | 4063 | 26.25 | 38.8156 | 5.7321 | 117.9385
4064 | 58.42 | 54.6414 | 57.0739 | 131.3959 | 0.49562 |  | 4064 | 32.8 | 54.6414 | 5 | 131.3959
4065 | 48.83 | 43.5658 | 69.5525 | 83.4839 | 0.4918 |  | 4065 | 36.83 | 43.5658 | 4 | 83.4839
4066 | 42.98 | 41.618 | 98.7811 | 78.0276 | 0.49412 |  | 4066 | 35.01 | 41.618 | 3 | 78.0276
4067 | 40.81 | 44.5996 | 73.4467 | 88.3806 | 0.49228 |  | 4067 | 32.68 | 44.5996 | 2.2679 | 88.3806
4068 | 37.01 | 46.5414 | 34.4723 | 80.8422 | 0.49808 |  | 4068 | 34 | 46.5414 | 2 | 80.8422
4069 | 36.93 | 48.5964 | 45.1536 | 63.7373 | 0.50312 |  | 4069 | 36.93 | 48.5964 | 2.2679 | 63.7373
4070 | 36.29 | 51.3516 | 26.8328 | 73.6438 | 0.50246 |  | 4070 | 31.12 | 51.3516 | 3 | 73.6438
4071 | 36.09 | 60.7825 | 52.721 | 64.3207 | 0.50479 |  | 4071 | 25.9 | 60.7825 | 4 | 64.3207
4072 | 34.91 | 74.3124 | 46.2463 | 67.1701 | 0.50243 |  | 4072 | 25.33 | 74.3124 | 5 | 67.1701
4073 | 41.78 | 94.888 | 44.2142 | 71.9754 | 0.50187 |  | 4073 | 27 | 94.888 | 5.7321 | 71.9754
4074 | 49.94 | 138.4142 | 41.2496 | 76.6668 | 0.50819 |  | 4074 | 27.99 | 138.4142 | 6 | 76.6668
4075 | 53.17 | 143.2807 | 40.9808 | 87.9629 | 0.51334 |  | 4075 | 32.09 | 143.2807 | 5.7321 | 87.9629
4076 | 51.07 | 118.923 | 233.8047 | 117.5462 | 0.51611 |  | 4076 | 30.94 | 118.923 | 5 | 117.5462
4077 | 45.64 | 97.2355 | 31.0897 | 88.5975 | 0.52816 |  | 4077 | 36.04 | 97.2355 | 4 | 88.5975
4078 | 40.08 | 91.1329 | 34.4248 | 75.3923 | 0.53098 |  | 4078 | 36.97 | 91.1329 | 3 | 75.3923
4079 | 34.99 | 71.5344 | 30.5092 | 46.986 | 0.53229 |  | 4079 | 28 | 71.5344 | 2.2679 | 46.986
4080 | 30.8 | 38.184 | 30.3457 | 22.2086 | 0.52214 |  | 4080 | 30.01 | 38.184 | 2 | 22.2086
4081 | 31.23 | 34.6188 | 28.8563 | 25.4495 | 0.50494 |  | 4081 | 25.85 | 34.6188 | 2.2679 | 25.4495
4082 | 30.08 | 32.8347 | 33.2672 | 5.1426 | 0.4986 |  | 4082 | 22.75 | 32.8347 | 3 | 5.1426
4083 | 30 | 31.2026 | 22.6683 | 16.568 | 0.49493 |  | 4083 | 21.04 | 31.2026 | 4 | 16.568
4084 | 31.7 | 29.7383 | 27.6075 | 51.2554 | 0.49569 |  | 4084 | 19.72 | 29.7383 | 5 | 51.2554
4085 | 30.03 | 28.7817 | 51.3956 | 87.789 | 0.49422 |  | 4085 | 18.5 | 28.7817 | 5.7321 | 87.789
4086 | 31.98 | 28.574 | 89.6994 | 147.7997 | 0.50438 |  | 4086 | 19.94 | 28.574 | 6 | 147.7997
4087 | 36.09 | 40.2027 | 81.674 | 124.1072 | 0.51039 |  | 4087 | 18.3 | 40.2027 | 5.7321 | 124.1072
4088 | 41.76 | 55.7828 | 63.1741 | 113.046 | 0.51157 |  | 4088 | 20.38 | 55.7828 | 5 | 113.046
4089 | 50.07 | 43.5954 | 41.0701 | 101.3437 | 0.50524 |  | 4089 | 21.89 | 43.5954 | 4 | 101.3437
4090 | 44.9 | 42.6371 | 30.452 | 77.7052 | 0.49715 |  | 4090 | 24.91 | 42.6371 | 3 | 77.7052
4091 | 39.29 | 45.7746 | 46.7211 | 84.3189 | 0.48854 |  | 4091 | 25.9 | 45.7746 | 2.2679 | 84.3189
4092 | 36.08 | 48.9236 | 36.2918 | 78.9456 | 0.4813 |  | 4092 | 29.64 | 48.9236 | 2 | 78.9456
4093 | 34.09 | 50.734 | 47.2834 | 91.7879 | 0.47475 |  | 4093 | 26.48 | 50.734 | 2.2679 | 91.7879
4094 | 33.17 | 51.6076 | 48.167 | 75.1538 | 0.46425 |  | 4094 | 24.09 | 51.6076 | 3 | 75.1538
4095 | 33.93 | 59.106 | 47.8253 | 68.5887 | 0.47153 |  | 4095 | 23.99 | 59.106 | 4 | 68.5887
4096 | 33.54 | 76.901 | 40.1752 | 62.1992 | 0.48347 |  | 4096 | 23.9 | 76.901 | 5 | 62.1992
4097 | 36.71 | 96.6339 | 31.3156 | 68.1074 | 0.49736 |  | 4097 | 24.29 | 96.6339 | 5.7321 | 68.1074
4098 | 39.62 | 134.2578 | 42.0318 | 91.8687 | 0.50049 |  | 4098 | 37.53 | 134.2578 | 6 | 91.8687
4099 | 44.82 | 149.4025 | 36.2664 | 93.6927 | 0.50212 |  | 4099 | 37.14 | 149.4025 | 5.7321 | 93.6927
4100 | 51.96 | 134.7269 | 28.3278 | 107.495 | 0.508 |  | 4100 | 37.27 | 134.7269 | 5 | 107.495
4101 | 50 | 99.6712 | 30.8401 | 74.5841 | 0.51635 |  | 4101 | 36 | 99.6712 | 4 | 74.5841
4102 | 46.52 | 96.0023 | 37.281 | 80.4371 | 0.51906 |  | 4102 | 39.79 | 96.0023 | 3 | 80.4371
4103 | 39.28 | 76.588 | 26.1955 | 55.7146 | 0.5255 |  | 4103 | 37.44 | 76.588 | 2.2679 | 55.7146
4104 | 34.3 | 40.0918 | 27.3786 | 31.5427 | 0.51632 |  | 4104 | 35.66 | 40.0918 | 2 | 31.5427
4105 | 32.03 | 34.0008 | 29.4147 | 32.9564 | 0.496 |  | 4105 | 26.38 | 34.0008 | 2.2679 | 32.9564
4106 | 31.52 | 32.4728 | 29.1685 | 5.7423 | 0.49244 |  | 4106 | 24.71 | 32.4728 | 3 | 5.7423
4107 | 31.81 | 30.9359 | 29.5078 | 20.8722 | 0.48874 |  | 4107 | 21.62 | 30.9359 | 4 | 20.8722
4108 | 32.04 | 29.5435 | 30.0764 | 40.3631 | 0.48732 |  | 4108 | 21.72 | 29.5435 | 5 | 40.3631
4109 | 33.19 | 28.6025 | 35.5374 | 92.2842 | 0.49987 |  | 4109 | 18.74 | 28.6025 | 5.7321 | 92.2842
4110 | 39.51 | 28.2537 | 98.7091 | 136.4898 | 0.50902 |  | 4110 | 19.99 | 28.2537 | 6 | 136.4898
4111 | 45.38 | 39.8316 | 104.0835 | 128.954 | 0.51556 |  | 4111 | 28.97 | 39.8316 | 5.7321 | 128.954
4112 | 47.09 | 55.5413 | 110.5417 | 142.513 | 0.50911 |  | 4112 | 34.42 | 55.5413 | 5 | 142.513
4113 | 44.41 | 42.9385 | 120.2855 | 122.7339 | 0.50299 |  | 4113 | 34.94 | 42.9385 | 4 | 122.7339
4114 | 43.93 | 41.4816 | 90.9752 | 79.0755 | 0.49973 |  | 4114 | 35.36 | 41.4816 | 3 | 79.0755
4115 | 41.04 | 43.2135 | 41.9089 | 62.9571 | 0.49513 |  | 4115 | 33 | 43.2135 | 2.2679 | 62.9571
4116 | 36.21 | 44.4667 | 33.9907 | 68.9094 | 0.49106 |  | 4116 | 34.94 | 44.4667 | 2 | 68.9094
4117 | 33.53 | 47.4228 | 42.2132 | 77.1393 | 0.49008 |  | 4117 | 31.88 | 47.4228 | 2.2679 | 77.1393
4118 | 32.41 | 48.4023 | 41.7238 | 59.1622 | 0.48507 |  | 4118 | 32.97 | 48.4023 | 3 | 59.1622
4119 | 32.26 | 54.719 | 45.5305 | 71.1736 | 0.48217 |  | 4119 | 31.5 | 54.719 | 4 | 71.1736
4120 | 32.22 | 72.8535 | 227.8324 | 70.4013 | 0.48666 |  | 4120 | 39.47 | 72.8535 | 5 | 70.4013
4121 | 34.98 | 93.3162 | 48.303 | 64.4669 | 0.49391 |  | 4121 | 39.7 | 93.3162 | 5.7321 | 64.4669
4122 | 40.79 | 121.8444 | 48.1462 | 109.3229 | 0.50364 |  | 4122 | 39.52 | 121.8444 | 6 | 109.3229
4123 | 44.5 | 137.2584 | 31.7489 | 97.937 | 0.51219 |  | 4123 | 32.97 | 137.2584 | 5.7321 | 97.937
4124 | 47.84 | 128.6201 | 26.8352 | 108.6588 | 0.52073 |  | 4124 | 34.96 | 128.6201 | 5 | 108.6588
4125 | 49.91 | 96.2526 | 31.5466 | 89.9803 | 0.52902 |  | 4125 | 33.57 | 96.2526 | 4 | 89.9803
4126 | 44.26 | 92.5238 | 28.4512 | 62.8503 | 0.53192 |  | 4126 | 31.76 | 92.5238 | 3 | 62.8503
4127 | 36.95 | 75.488 | 23.7331 | 54.2753 | 0.53529 |  | 4127 | 38 | 75.488 | 2.2679 | 54.2753
4128 | 35.58 | 39.7353 | 24.9372 | 31.9986 | 0.5365 |  | 4128 | 44.5 | 39.7353 | 2 | 31.9986
4129 | 31.84 | 34.9211 | 36.1872 | 34.1222 | 0.53077 |  | 4129 | 27.28 | 34.9211 | 2.2679 | 34.1222
4130 | 29.44 | 33.2831 | 33.0471 | 6.6803 | 0.52347 |  | 4130 | 24.14 | 33.2831 | 3 | 6.6803
4131 | 29.28 | 31.5612 | 35.0225 | 16.2536 | 0.5119 |  | 4131 | 23.64 | 31.5612 | 4 | 16.2536
4132 | 28.98 | 30.107 | 33.6426 | 49.6522 | 0.49726 |  | 4132 | 21.23 | 30.107 | 5 | 49.6522
4133 | 28.59 | 29.0086 | 33.1499 | 97.5727 | 0.48679 |  | 4133 | 21.89 | 29.0086 | 5.7321 | 97.5727
4134 | 29.48 | 28.5071 | 27.4158 | 122.8665 | 0.48442 |  | 4134 | 23.93 | 28.5071 | 6 | 122.8665
4135 | 32.36 | 40.1562 | 28.1296 | 122.6385 | 0.48377 |  | 4135 | 29.54 | 40.1562 | 5.7321 | 122.6385
4136 | 34.46 | 54.2864 | 43.2216 | 145.8615 | 0.47261 |  | 4136 | 38.73 | 54.2864 | 5 | 145.8615
4137 | 31.86 | 43.4493 | 42.4326 | 85.6645 | 0.45818 |  | 4137 | 40.78 | 43.4493 | 4 | 85.6645
4138 | 30.92 | 42.8294 | 33.8003 | 71.4984 | 0.45293 |  | 4138 | 43.5 | 42.8294 | 3 | 71.4984
4139 | 29.79 | 43.5755 | 43.9807 | 76.8723 | 0.4514 |  | 4139 | 41.79 | 43.5755 | 2.2679 | 76.8723
4140 | 29.97 | 46.9134 | 36.9747 | 77.5231 | 0.45117 |  | 4140 | 43.73 | 46.9134 | 2 | 77.5231
4141 | 28.55 | 48.5838 | 39.4808 | 68.3345 | 0.44936 |  | 4141 | 39.59 | 48.5838 | 2.2679 | 68.3345
4142 | 28.18 | 50.4189 | 41.7422 | 55.8677 | 0.44277 |  | 4142 | 37.64 | 50.4189 | 3 | 55.8677
4143 | 28.21 | 56.2313 | 32.0483 | 59.692 | 0.43846 |  | 4143 | 35.84 | 56.2313 | 4 | 59.692
4144 | 29.41 | 74.5929 | 33.1679 | 68.91 | 0.43519 |  | 4144 | 34.16 | 74.5929 | 5 | 68.91
4145 | 32.37 | 95.4359 | 40.7763 | 72.2029 | 0.42453 |  | 4145 | 32.45 | 95.4359 | 5.7321 | 72.2029
4146 | 34.37 | 134.2706 | 39.4067 | 105.3816 | 0.4251 |  | 4146 | 33.05 | 134.2706 | 6 | 105.3816
4147 | 37.91 | 142.4955 | 42.3963 | 91.3583 | 0.43502 |  | 4147 | 34.94 | 142.4955 | 5.7321 | 91.3583
4148 | 35.38 | 122.8444 | 30.518 | 96.0683 | 0.44143 |  | 4148 | 35.91 | 122.8444 | 5 | 96.0683
4149 | 32.63 | 101.5741 | 24.3154 | 80.761 | 0.43998 |  | 4149 | 37.44 | 101.5741 | 4 | 80.761
4150 | 34.03 | 95.8865 | 29.7448 | 74.2712 | 0.43627 |  | 4150 | 34.98 | 95.8865 | 3 | 74.2712
4151 | 29.58 | 76.2699 | 31.0277 | 49.6324 | 0.43604 |  | 4151 | 35 | 76.2699 | 2.2679 | 49.6324
4152 | 28.1 | 39.8543 | 21.5355 | 26.6611 | 0.42773 |  | 4152 | 32.06 | 39.8543 | 2 | 26.6611
4153 | 26.94 | 34.0478 | 26.3507 | 29.601 | 0.41929 |  | 4153 | 28.06 | 34.0478 | 2.2679 | 29.601
4154 | 31.62 | 32.5337 | 232.2044 | 5.6977 | 0.44226 |  | 4154 | 24.95 | 32.5337 | 3 | 5.6977
4155 | 36.39 | 31.0414 | 22.3246 | 23.545 | 0.45026 |  | 4155 | 24.74 | 31.0414 | 4 | 23.545
4156 | 37.62 | 29.6911 | 29.0848 | 47.8604 | 0.45697 |  | 4156 | 23.14 | 29.6911 | 5 | 47.8604
4157 | 32.12 | 28.657 | 20.9887 | 74.9203 | 0.43896 |  | 4157 | 22.97 | 28.657 | 5.7321 | 74.9203
4158 | 31.53 | 28.1812 | 26.2524 | 126.8507 | 0.44132 |  | 4158 | 24.06 | 28.1812 | 6 | 126.8507
4159 | 34.8 | 39.3658 | 27.4363 | 171.1063 | 0.44501 |  | 4159 | 29.98 | 39.3658 | 5.7321 | 171.1063
4160 | 32.64 | 55.1553 | 46.052 | 125.9043 | 0.43846 |  | 4160 | 40 | 55.1553 | 5 | 125.9043
4161 | 32.59 | 44.3667 | 47.0349 | 101.2399 | 0.43202 |  | 4161 | 42 | 44.3667 | 4 | 101.2399
4162 | 24.8 | 43.5631 | 36.3937 | 69.4833 | 0.40732 |  | 4162 | 40 | 43.5631 | 3 | 69.4833
4163 | 24.8 | 45.6392 | 41.0546 | 68.9745 | 0.40283 |  | 4163 | 37.27 | 45.6392 | 2.2679 | 68.9745
4164 | 19 | 47.8583 | 41.8308 | 64.8792 | 0.39769 |  | 4164 | 36.73 | 47.8583 | 2 | 64.8792
4165 | 14.9 | 51.4012 | 28.3624 | 65.919 | 0.38879 |  | 4165 | 42 | 51.4012 | 2.2679 | 65.919
4166 | 16.86 | 52.3559 | 49.934 | 56.6914 | 0.38089 |  | 4166 | 41.3 | 52.3559 | 3 | 56.6914
4167 | 22.55 | 59.2077 | 46.0785 | 65.3426 | 0.37932 |  | 4167 | 39.42 | 59.2077 | 4 | 65.3426
4168 | 24.59 | 76.0251 | 51.0649 | 50.766 | 0.39672 |  | 4168 | 38.86 | 76.0251 | 5 | 50.766
4169 | 32.13 | 93.3129 | 41.0357 | 87.5991 | 0.42259 |  | 4169 | 39.22 | 93.3129 | 5.7321 | 87.5991
4170 | 32.44 | 130.9308 | 41.603 | 89.6166 | 0.43816 |  | 4170 | 38.44 | 130.9308 | 6 | 89.6166
4171 | 41.18 | 141.5566 | 49.0047 | 90.6156 | 0.44204 |  | 4171 | 38.12 | 141.5566 | 5.7321 | 90.6156
4172 | 47.87 | 125.0646 | 29.9235 | 123.1537 | 0.44279 |  | 4172 | 39.8 | 125.0646 | 5 | 123.1537
4173 | 32.95 | 98.036 | 22.9598 | 101.5045 | 0.44259 |  | 4173 | 38.3 | 98.036 | 4 | 101.5045
4174 | 34.19 | 93.0502 | 30.5755 | 69.2964 | 0.43126 |  | 4174 | 37.39 | 93.0502 | 3 | 69.2964
4175 | 34.4 | 76.3971 | 31.8417 | 39.1859 | 0.41846 |  | 4175 | 40.01 | 76.3971 | 2.2679 | 39.1859
4176 | 26.97 | 39.1773 | 27.7644 | 30.6844 | 0.39829 |  | 4176 | 39.99 | 39.1773 | 2 | 30.6844
4177 | 25.68 | 35.9823 | 27.6207 | 25.5632 | 0.39353 |  | 4177 | 28.09 | 35.9823 | 2.2679 | 25.5632
4178 | 24 | 34.1243 | 26.2927 | 7.3374 | 0.41013 |  | 4178 | 25.64 | 34.1243 | 3 | 7.3374
4179 | 24.71 | 32.1597 | 29.1545 | 21.8745 | 0.41407 |  | 4179 | 24.38 | 32.1597 | 4 | 21.8745
4180 | 27.85 | 30.4333 | 23.7802 | 43.9938 | 0.4175 |  | 4180 | 24.11 | 30.4333 | 5 | 43.9938
4181 | 26.03 | 29.2614 | 21.1197 | 92.0198 | 0.42116 |  | 4181 | 24 | 29.2614 | 5.7321 | 92.0198
4182 | 35.27 | 28.5696 | 32.815 | 118.6253 | 0.43832 |  | 4182 | 24.14 | 28.5696 | 6 | 118.6253
4183 | 48.18 | 28.2756 | 26.96 | 153.9525 | 0.45868 |  | 4183 | 28.16 | 28.2756 | 5.7321 | 153.9525
4184 | 42.78 | 30.0301 | 38.4534 | 124.6989 | 0.46789 |  | 4184 | 35.91 | 30.0301 | 5 | 124.6989
4185 | 36.24 | 47.7129 | 41.0558 | 119.2034 | 0.47286 |  | 4185 | 35.91 | 47.7129 | 4 | 119.2034
4186 | 32.67 | 67.5099 | 48.928 | 75.2064 | 0.46424 |  | 4186 | 34.97 | 67.5099 | 3 | 75.2064
4187 | 32.74 | 74.4878 | 43.5692 | 66.8684 | 0.46128 |  | 4187 | 41.41 | 74.4878 | 2.2679 | 66.8684
4188 | 34.56 | 73.3048 | 42.5622 | 72.4656 | 0.45578 |  | 4188 | 45.12 | 73.3048 | 2 | 72.4656
4189 | 34.13 | 77.6588 | 44.2317 | 69.8149 | 0.452 |  | 4189 | 48.66 | 77.6588 | 2.2679 | 69.8149
4190 | 33.91 | 77.0824 | 35.6328 | 74.2616 | 0.45402 |  | 4190 | 50.03 | 77.0824 | 3 | 74.2616
4191 | 33.28 | 73.7278 | 41.58 | 52.3583 | 0.46392 |  | 4191 | 50 | 73.7278 | 4 | 52.3583
4192 | 33.87 | 76.2645 | 45.6097 | 53.8728 | 0.46932 |  | 4192 | 47.78 | 76.2645 | 5 | 53.8728
4193 | 35.95 | 81.1554 | 48.7075 | 89.5711 | 0.47643 |  | 4193 | 52.44 | 81.1554 | 5.7321 | 89.5711
4194 | 48.09 | 120.1402 | 34.9009 | 86.1445 | 0.47978 |  | 4194 | 57.83 | 120.1402 | 6 | 86.1445
4195 | 57.4 | 134.9487 | 46.2036 | 95.2843 | 0.48787 |  | 4195 | 49.9 | 134.9487 | 5.7321 | 95.2843
4196 | 58.43 | 128.7346 | 23.8786 | 117.652 | 0.49653 |  | 4196 | 43.85 | 128.7346 | 5 | 117.652
4197 | 44.47 | 98.1606 | 32.6627 | 89.1506 | 0.49829 |  | 4197 | 39.94 | 98.1606 | 4 | 89.1506
4198 | 34.3 | 89.0392 | 28.7602 | 56.5442 | 0.49316 |  | 4198 | 32.72 | 89.0392 | 3 | 56.5442
4199 | 29 | 90.1642 | 28.0302 | 47.9145 | 0.47905 |  | 4199 | 43.81 | 90.1642 | 2.2679 | 47.9145
4200 | 30.71 | 42.9772 | 23.1305 | 30.7916 | 0.46766 |  | 4200 | 38.97 | 42.9772 | 2 | 30.7916
4201 | 25.6 | 35.6466 | 29.9756 | 32.3592 | 0.45933 |  | 4201 | 40.12 | 35.6466 | 2.2679 | 32.3592
4202 | 24.48 | 33.7678 | 21.7072 | 7.0695 | 0.45946 |  | 4202 | 25.53 | 33.7678 | 3 | 7.0695
4203 | 25.69 | 31.8772 | 41.5941 | 21.3045 | 0.46843 |  | 4203 | 25.69 | 31.8772 | 4 | 21.3045
4204 | 27 | 30.1759 | 64.1515 | 53.3302 | 0.4717 |  | 4204 | 24.13 | 30.1759 | 5 | 53.3302
4205 | 29.09 | 29.0768 | 88.1702 | 89.1111 | 0.48537 |  | 4205 | 24.48 | 29.0768 | 5.7321 | 89.1111
4206 | 33.11 | 28.3107 | 98.2064 | 125.951 | 0.49672 |  | 4206 | 26.43 | 28.3107 | 6 | 125.951
4207 | 43.91 | 27.7353 | 102.8108 | 162.1471 | 0.50116 |  | 4207 | 31.86 | 27.7353 | 5.7321 | 162.1471
4208 | 49.18 | 30.1542 | 93.8527 | 143.4506 | 0.50258 |  | 4208 | 37.03 | 30.1542 | 5 | 143.4506
4209 | 40.96 | 49.0458 | 62.1941 | 90.9601 | 0.50378 |  | 4209 | 45 | 49.0458 | 4 | 90.9601
4210 | 37.77 | 66.7809 | 83.4296 | 81.7355 | 0.50409 |  | 4210 | 58 | 66.7809 | 3 | 81.7355
4211 | 36.45 | 73.2902 | 88.2768 | 75.368 | 0.50447 |  | 4211 | 62.96 | 73.2902 | 2.2679 | 75.368
4212 | 35.07 | 74.5998 | 105.0984 | 85.1885 | 0.50405 |  | 4212 | 64.17 | 74.5998 | 2 | 85.1885
4213 | 34.92 | 76.6922 | 102.5069 | 69.1916 | 0.50448 |  | 4213 | 60.8 | 76.6922 | 2.2679 | 69.1916
4214 | 35.02 | 74.2127 | 92.3009 | 67.5355 | 0.50453 |  | 4214 | 57.05 | 74.2127 | 3 | 67.5355
4215 | 34.91 | 73.117 | 76.5036 | 50.9757 | 0.50777 |  | 4215 | 48.32 | 73.117 | 4 | 50.9757
4216 | 36.93 | 74.7849 | 42.8747 | 64.4361 | 0.50889 |  | 4216 | 39.32 | 74.7849 | 5 | 64.4361
4217 | 55.88 | 75.5935 | 48.7452 | 76.4502 | 0.51382 |  | 4217 | 38.16 | 75.5935 | 5.7321 | 76.4502
4218 | 71.5 | 112.5798 | 48.8457 | 89.3351 | 0.51036 |  | 4218 | 34.94 | 112.5798 | 6 | 89.3351
4219 | 83.62 | 129.9459 | 27.6409 | 96.5576 | 0.51085 |  | 4219 | 34.98 | 129.9459 | 5.7321 | 96.5576
4220 | 80 | 136.8491 | 30.2064 | 118.8158 | 0.50701 |  | 4220 | 35.53 | 136.8491 | 5 | 118.8158
4221 | 66.74 | 101.0472 | 216.457 | 108.9721 | 0.50484 |  | 4221 | 34.95 | 101.0472 | 4 | 108.9721
4222 | 46.5 | 89.0921 | 38.8241 | 66.7039 | 0.51783 |  | 4222 | 33.28 | 89.0921 | 3 | 66.7039
4223 | 37.4 | 89.0411 | 27.5555 | 51.3967 | 0.52588 |  | 4223 | 34.12 | 89.0411 | 2.2679 | 51.3967
4224 | 39.95 | 41.7103 | 22.7354 | 28.8068 | 0.53072 |  | 4224 | 39.94 | 41.7103 | 2 | 28.8068
4225 | 33.96 | 35.6993 | 31.3733 | 25.6485 | 0.52015 |  | 4225 | 30.14 | 35.6993 | 2.2679 | 25.6485
4226 | 34.8 | 33.8619 | 28.0252 | 6.7887 | 0.50736 |  | 4226 | 34 | 33.8619 | 3 | 6.7887
4227 | 35.81 | 32.0588 | 30.1706 | 17.3738 | 0.50016 |  | 4227 | 27.35 | 32.0588 | 4 | 17.3738
4228 | 34.36 | 30.5097 | 28.4517 | 43.6638 | 0.5018 |  | 4228 | 24.98 | 30.5097 | 5 | 43.6638
4229 | 34.3 | 29.2323 | 41.7836 | 101.0102 | 0.50836 |  | 4229 | 26.13 | 29.2323 | 5.7321 | 101.0102
4230 | 43.88 | 28.5472 | 86.1067 | 150.6272 | 0.51589 |  | 4230 | 25.85 | 28.5472 | 6 | 150.6272
4231 | 60.08 | 39.6827 | 112.9043 | 150.5442 | 0.51026 |  | 4231 | 27.35 | 39.6827 | 5.7321 | 150.5442
4232 | 59.44 | 55.5066 | 301.0981 | 116.2606 | 0.50259 |  | 4232 | 31.43 | 55.5066 | 5 | 116.2606
4233 | 51.83 | 44.5565 | 97.4351 | 92.4138 | 0.50008 |  | 4233 | 31.55 | 44.5565 | 4 | 92.4138
4234 | 38.65 | 42.2347 | 93.9789 | 70.0475 | 0.49826 |  | 4234 | 37.52 | 42.2347 | 3 | 70.0475
4235 | 36.7 | 45.482 | 102.5337 | 68.1471 | 0.48982 |  | 4235 | 50.04 | 45.482 | 2.2679 | 68.1471
4236 | 35.08 | 46.8187 | 130.8599 | 68.9094 | 0.48847 |  | 4236 | 43.11 | 46.8187 | 2 | 68.9094
4237 | 33.09 | 48.9814 | 98.3881 | 70.5162 | 0.48218 |  | 4237 | 30.06 | 48.9814 | 2.2679 | 70.5162
4238 | 31.88 | 51.3578 | 57.767 | 75.9088 | 0.47301 |  | 4238 | 29.75 | 51.3578 | 3 | 75.9088
4239 | 30.89 | 59.9122 | 37.2208 | 62.3971 | 0.46628 |  | 4239 | 27.44 | 59.9122 | 4 | 62.3971
4240 | 31.47 | 74.3953 | 31.8009 | 72.2032 | 0.4555 |  | 4240 | 29.31 | 74.3953 | 5 | 72.2032
4241 | 34.27 | 93.9322 | 42.3427 | 77.1328 | 0.46011 |  | 4241 | 29.94 | 93.9322 | 5.7321 | 77.1328
4242 | 38.98 | 131.3724 | 52.8022 | 80.8895 | 0.47202 |  | 4242 | 36.62 | 131.3724 | 6 | 80.8895
4243 | 49.92 | 153.2491 | 49.8348 | 100.908 | 0.48666 |  | 4243 | 40.44 | 153.2491 | 5.7321 | 100.908
4244 | 50.1 | 141.2835 | 31.7277 | 89.9318 | 0.49666 |  | 4244 | 35.65 | 141.2835 | 5 | 89.9318
4245 | 42.95 | 108.529 | 21.938 | 95.3275 | 0.49804 |  | 4245 | 36.38 | 108.529 | 4 | 95.3275
4246 | 36.7 | 97.4967 | 27.0798 | 67.9652 | 0.49438 |  | 4246 | 33.76 | 97.4967 | 3 | 67.9652
4247 | 30.45 | 78.1897 | 21.179 | 42.5288 | 0.48642 |  | 4247 | 29.61 | 78.1897 | 2.2679 | 42.5288
4248 | 28 | 42.2084 | 29.4693 | 24.9176 | 0.47743 |  | 4248 | 30.65 | 42.2084 | 2 | 24.9176
4249 | 27 | 32.9419 | 27.8638 | 33.5819 | 0.48393 |  | 4249 | 17.29 | 32.9419 | 2.2679 | 33.5819
4250 | 27.31 | 31.6203 | 30.6409 | 5.4807 | 0.47999 |  | 4250 | 12.78 | 31.6203 | 3 | 5.4807
4251 | 28.22 | 30.3063 | 28.425 | 19.3981 | 0.47741 |  | 4251 | 20.27 | 30.3063 | 4 | 19.3981
4252 | 29.42 | 29.0693 | 28.6482 | 45.4084 | 0.46445 |  | 4252 | 19.92 | 29.0693 | 5 | 45.4084
4253 | 29.78 | 28.2899 | 37.5591 | 86.7313 | 0.47029 |  | 4253 | 19.79 | 28.2899 | 5.7321 | 86.7313
4254 | 35.06 | 28.0363 | 90.5135 | 105.1306 | 0.48656 |  | 4254 | 19.63 | 28.0363 | 6 | 105.1306
4255 | 43.29 | 38.5334 | 96.8806 | 173.8969 | 0.49169 |  | 4255 | 20.89 | 38.5334 | 5.7321 | 173.8969
4256 | 42.1 | 55.0631 | 76.6269 | 133.5389 | 0.49133 |  | 4256 | 20.07 | 55.0631 | 5 | 133.5389
4257 | 36.5 | 43.2471 | 53.8644 | 106.847 | 0.48158 |  | 4257 | 20.46 | 43.2471 | 4 | 106.847
4258 | 34.56 | 41.619 | 106.0034 | 87.6198 | 0.47202 |  | 4258 | 20 | 41.619 | 3 | 87.6198
4259 | 34.47 | 44.7782 | 107.8123 | 87.478 | 0.46748 |  | 4259 | 19.94 | 44.7782 | 2.2679 | 87.478
4260 | 31.97 | 44.7323 | 126.8535 | 74.5992 | 0.45528 |  | 4260 | 20.97 | 44.7323 | 2 | 74.5992
4261 | 31.95 | 47.9264 | 100.2391 | 84.1519 | 0.45192 |  | 4261 | 20.94 | 47.9264 | 2.2679 | 84.1519
4262 | 30.91 | 48.0195 | 54.4449 | 64.5842 | 0.45324 |  | 4262 | 20 | 48.0195 | 3 | 64.5842
4263 | 31.31 | 55.362 | 52.2011 | 49.8335 | 0.44787 |  | 4263 | 20.92 | 55.362 | 4 | 49.8335
4264 | 31.94 | 70.3562 | 43.9612 | 54.3699 | 0.4473 |  | 4264 | 19.94 | 70.3562 | 5 | 54.3699
4265 | 35.98 | 87.6002 | 33.1806 | 61.509 | 0.45863 |  | 4265 | 18.72 | 87.6002 | 5.7321 | 61.509
4266 | 41.9 | 127.6322 | 28.6709 | 105.2878 | 0.47313 |  | 4266 | 26 | 127.6322 | 6 | 105.2878
4267 | 54.11 | 132.7167 | 45.4737 | 105.3645 | 0.48015 |  | 4267 | 25.42 | 132.7167 | 5.7321 | 105.3645
4268 | 52.23 | 122.3259 | 27.0427 | 99.6656 | 0.48694 |  | 4268 | 31.92 | 122.3259 | 5 | 99.6656
4269 | 44.02 | 95.6165 | 29.4854 | 88.0443 | 0.49243 |  | 4269 | 39.51 | 95.6165 | 4 | 88.0443
4270 | 41.17 | 85.8516 | 24.8768 | 82.6092 | 0.4979 |  | 4270 | 38.75 | 85.8516 | 3 | 82.6092
4271 | 35.58 | 73.6613 | 30.1057 | 53.6717 | 0.49533 |  | 4271 | 31.91 | 73.6613 | 2.2679 | 53.6717
4272 | 31.33 | 38.2338 | 23.1979 | 30.3625 | 0.48601 |  | 4272 | 28.12 | 38.2338 | 2 | 30.3625
4273 | 31.46 | 33.8372 | 29.5139 | 24.0846 | 0.47659 |  | 4273 | 24.1 | 33.8372 | 2.2679 | 24.0846
4274 | 32.71 | 32.2677 | 28.5794 | 7.3821 | 0.46237 |  | 4274 | 20.99 | 32.2677 | 3 | 7.3821
4275 | 33.38 | 30.6967 | 30.1312 | 20.8328 | 0.45843 |  | 4275 | 19.04 | 30.6967 | 4 | 20.8328
4276 | 32.38 | 29.4218 | 31.5074 | 49.6994 | 0.46287 |  | 4276 | 21.1 | 29.4218 | 5 | 49.6994
4277 | 32.58 | 28.527 | 28.5228 | 86.2025 | 0.48043 |  | 4277 | 19.48 | 28.527 | 5.7321 | 86.2025
4278 | 44.4 | 28.1319 | 64.944 | 119.782 | 0.49067 |  | 4278 | 19.02 | 28.1319 | 6 | 119.782
4279 | 57.51 | 39.6569 | 105.1994 | 156.4191 | 0.48534 |  | 4279 | 27.75 | 39.6569 | 5.7321 | 156.4191
4280 | 60.2 | 54.347 | 115.2802 | 109.2957 | 0.4823 |  | 4280 | 33.07 | 54.347 | 5 | 109.2957
4281 | 48.82 | 43.762 | 97.6949 | 102.6936 | 0.47856 |  | 4281 | 34.26 | 43.762 | 4 | 102.6936
4282 | 43.99 | 41.6136 | 100.4655 | 87.0556 | 0.47432 |  | 4282 | 33.5 | 41.6136 | 3 | 87.0556
4283 | 39.53 | 45.053 | 92.2473 | 67.6958 | 0.46256 |  | 4283 | 45.39 | 45.053 | 2.2679 | 67.6958
4284 | 36.75 | 44.7254 | 88.5669 | 94.8295 | 0.46018 |  | 4284 | 46.41 | 44.7254 | 2 | 94.8295
4285 | 34.33 | 47.8546 | 133.7601 | 78.6197 | 0.4458 |  | 4285 | 41.5 | 47.8546 | 2.2679 | 78.6197
4286 | 33.89 | 50.7943 | 126.6531 | 62.3879 | 0.43646 |  | 4286 | 40.19 | 50.7943 | 3 | 62.3879
4287 | 33.91 | 54.5545 | 121.6344 | 52.1779 | 0.43632 |  | 4287 | 38.65 | 54.5545 | 4 | 52.1779
4288 | 34.4 | 70.2842 | 55.8353 | 72.5761 | 0.44842 |  | 4288 | 36.74 | 70.2842 | 5 | 72.5761
4289 | 39.04 | 94.5643 | 50.8307 | 81.9867 | 0.46145 |  | 4289 | 37.87 | 94.5643 | 5.7321 | 81.9867
4290 | 53.64 | 135.1872 | 40.7761 | 112.6072 | 0.47393 |  | 4290 | 44.94 | 135.1872 | 6 | 112.6072
4291 | 65.63 | 144.6981 | 44.4791 | 97.0881 | 0.48247 |  | 4291 | 38.82 | 144.6981 | 5.7321 | 97.0881
4292 | 65 | 116.1839 | 34.5489 | 123.4711 | 0.4863 |  | 4292 | 39.05 | 116.1839 | 5 | 123.4711
4293 | 54.25 | 95.3863 | 26.6921 | 90.1647 | 0.4878 |  | 4293 | 38.31 | 95.3863 | 4 | 90.1647
4294 | 48.54 | 93.193 | 22.5659 | 81.4881 | 0.48005 |  | 4294 | 36.52 | 93.193 | 3 | 81.4881
4295 | 39.05 | 75.7721 | 25.7539 | 55.111 | 0.46535 |  | 4295 | 46.77 | 75.7721 | 2.2679 | 55.111
4296 | 35.24 | 39.0587 | 19.5012 | 30.5771 | 0.44263 |  | 4296 | 49.94 | 39.0587 | 2 | 30.5771
4297 | 31.64 | 33.4956 | 25.6042 | 27.6106 | 0.41294 |  | 4297 | 26.84 | 33.4956 | 2.2679 | 27.6106
4298 | 30.26 | 32.0988 | 36.6349 | 5.7232 | 0.4051 |  | 4298 | 24.4 | 32.0988 | 3 | 5.7232
4299 | 29.15 | 30.746 | 20.3799 | 17.8848 | 0.40617 |  | 4299 | 24.09 | 30.746 | 4 | 17.8848
4300 | 29.58 | 29.3446 | 30.9875 | 50.5481 | 0.4085 |  | 4300 | 23.13 | 29.3446 | 5 | 50.5481
4301 | 28.79 | 28.378 | 50.4711 | 103.1256 | 0.40625 |  | 4301 | 22.76 | 28.378 | 5.7321 | 103.1256
4302 | 30.16 | 28.1293 | 78.302 | 113.613 | 0.40746 |  | 4302 | 24.19 | 28.1293 | 6 | 113.613
4303 | 31.48 | 39.0818 | 87.4648 | 128.0727 | 0.41006 |  | 4303 | 29.86 | 39.0818 | 5.7321 | 128.0727
4304 | 30.11 | 53.8503 | 97.9765 | 129.5207 | 0.40792 |  | 4304 | 40.08 | 53.8503 | 5 | 129.5207
4305 | 30.15 | 43.6977 | 113.4909 | 89.8179 | 0.4075 |  | 4305 | 41.91 | 43.6977 | 4 | 89.8179
4306 | 28.07 | 43.1677 | 81.9165 | 76.0124 | 0.40405 |  | 4306 | 41.98 | 43.1677 | 3 | 76.0124
4307 | 28.01 | 45.2492 | 97.0482 | 82.965 | 0.40128 |  | 4307 | 38.94 | 45.2492 | 2.2679 | 82.965
4308 | 28.01 | 48.8154 | 124.3594 | 68.5143 | 0.40175 |  | 4308 | 37.88 | 48.8154 | 2 | 68.5143
4309 | 25.82 | 49.5036 | 92.3164 | 62.4906 | 0.39974 |  | 4309 | 35.36 | 49.5036 | 2.2679 | 62.4906
4310 | 25.06 | 50.0973 | 245.561 | 56.5541 | 0.39932 |  | 4310 | 34.85 | 50.0973 | 3 | 56.5541
4311 | 25.19 | 57.0953 | 44.1775 | 70.8129 | 0.40123 |  | 4311 | 39.94 | 57.0953 | 4 | 70.8129
4312 | 26.39 | 73.7022 | 46.7474 | 63.3798 | 0.40289 |  | 4312 | 34.94 | 73.7022 | 5 | 63.3798
4313 | 30.18 | 91.423 | 39.5733 | 80.8491 | 0.40622 |  | 4313 | 31.06 | 91.423 | 5.7321 | 80.8491
4314 | 40 | 135.6156 | 29.9397 | 95.0593 | 0.40821 |  | 4314 | 36.04 | 135.6156 | 6 | 95.0593
4315 | 52.46 | 139.3308 | 51.7757 | 123.9333 | 0.41046 |  | 4315 | 39.85 | 139.3308 | 5.7321 | 123.9333
4316 | 56.23 | 111.2308 | 22.0391 | 96.3857 | 0.41111 |  | 4316 | 41.74 | 111.2308 | 5 | 96.3857
4317 | 49.89 | 98.5443 | 27.4249 | 104.9156 | 0.40613 |  | 4317 | 38.99 | 98.5443 | 4 | 104.9156
4318 | 41.03 | 93.9042 | 23.1426 | 78.1249 | 0.40287 |  | 4318 | 34.56 | 93.9042 | 3 | 78.1249
4319 | 35.61 | 74.484 | 29.2458 | 41.2288 | 0.39229 |  | 4319 | 33.84 | 74.484 | 2.2679 | 41.2288
4320 | 30.41 | 38.7706 | 31.2493 | 23.7375 | 0.38022 |  | 4320 | 28.34 | 38.7706 | 2 | 23.7375
4321 | 26.9 | 33.0465 | 28.0501 | 23.0041 | 0.36371 |  | 4321 | 24.03 | 33.0465 | 2.2679 | 23.0041
4322 | 27.39 | 31.677 | 229.3584 | 6.693 | 0.33381 |  | 4322 | 22.14 | 31.677 | 3 | 6.693
4323 | 24.78 | 30.2868 | 30.8697 | 22.5034 | 0.31373 |  | 4323 | 20.64 | 30.2868 | 4 | 22.5034
4324 | 19.6 | 29.0521 | 26.6693 | 53.9431 | 0.30059 |  | 4324 | 19.35 | 29.0521 | 5 | 53.9431
4325 | 10.16 | 28.2739 | 30.8964 | 95.5455 | 0.28731 |  | 4325 | 18.95 | 28.2739 | 5.7321 | 95.5455
4326 | 12.27 | 27.9794 | 15.7347 | 105.3876 | 0.28511 |  | 4326 | 19.72 | 27.9794 | 6 | 105.3876
4327 | 14.55 | 38.4894 | 26.8911 | 160.2378 | 0.28415 |  | 4327 | 24.58 | 38.4894 | 5.7321 | 160.2378
4328 | 20.67 | 54.0153 | 49.0152 | 118.2697 | 0.29016 |  | 4328 | 32.91 | 54.0153 | 5 | 118.2697
4329 | 17.24 | 44.1682 | 27.1568 | 119.6188 | 0.29696 |  | 4329 | 34.94 | 44.1682 | 4 | 119.6188
4330 | 17.4 | 43.1674 | 47.7693 | 69.1608 | 0.31023 |  | 4330 | 31.82 | 43.1674 | 3 | 69.1608
4331 | 20.1 | 45.5206 | 47.5215 | 68.3727 | 0.31584 |  | 4331 | 42.38 | 45.5206 | 2.2679 | 68.3727
4332 | 33.05 | 47.0958 | 46.1773 | 69.1465 | 0.31779 |  | 4332 | 42.16 | 47.0958 | 2 | 69.1465
4333 | 24.36 | 48.8244 | 51.0915 | 75.8147 | 0.32688 |  | 4333 | 39.94 | 48.8244 | 2.2679 | 75.8147
4334 | 21.72 | 53.9669 | 44.0746 | 78.9973 | 0.33692 |  | 4334 | 40.4 | 53.9669 | 3 | 78.9973
4335 | 25.84 | 56.0296 | 41.3908 | 57.0471 | 0.34775 |  | 4335 | 38.61 | 56.0296 | 4 | 57.0471
4336 | 22.5 | 70.6936 | 31.9678 | 64.8089 | 0.34691 |  | 4336 | 29.94 | 70.6936 | 5 | 64.8089
4337 | 20.05 | 92.5066 | 44.4332 | 71.5962 | 0.35451 |  | 4337 | 26.73 | 92.5066 | 5.7321 | 71.5962
4338 | 28.83 | 126.6031 | 46.576 | 98.719 | 0.38607 |  | 4338 | 26.54 | 126.6031 | 6 | 98.719
4339 | 36.63 | 145.5899 | 38.246 | 99.5286 | 0.41014 |  | 4339 | 33.46 | 145.5899 | 5.7321 | 99.5286
4340 | 37.94 | 116.6919 | 21.8013 | 100.512 | 0.4252 |  | 4340 | 38.99 | 116.6919 | 5 | 100.512
4341 | 37.07 | 94.7499 | 30.534 | 108.9721 | 0.43488 |  | 4341 | 37.49 | 94.7499 | 4 | 108.9721
4342 | 43.19 | 89.8574 | 31.85 | 59.2068 | 0.43686 |  | 4342 | 34.98 | 89.8574 | 3 | 59.2068
4343 | 36.72 | 73.9726 | 28.4316 | 40.7645 | 0.4372 |  | 4343 | 34.94 | 73.9726 | 2.2679 | 40.7645
4344 | 28.98 | 38.4547 | 33.1516 | 21.8867 | 0.43715 |  | 4344 | 29.96 | 38.4547 | 2 | 21.8867
4345 | 26.23 | 34.1887 | 28.6264 | 26.4447 | 0.41771 |  | 4345 | 25.16 | 34.1887 | 2.2679 | 26.4447
4346 | 25.02 | 32.4754 | 34.8612 | 7.1205 | 0.4113 |  | 4346 | 23.34 | 32.4754 | 3 | 7.1205
4347 | 24.87 | 30.8713 | 28.0311 | 19.123 | 0.41098 |  | 4347 | 22.08 | 30.8713 | 4 | 19.123
4348 | 25.9 | 29.5383 | 27.9065 | 46.3986 | 0.41177 |  | 4348 | 20.11 | 29.5383 | 5 | 46.3986
4349 | 26.89 | 28.5421 | 22.3091 | 74.3915 | 0.41444 |  | 4349 | 19.82 | 28.5421 | 5.7321 | 74.3915
4350 | 38.3 | 28.0212 | 24.0556 | 114.8982 | 0.41892 |  | 4350 | 21.58 | 28.0212 | 6 | 114.8982
4351 | 51.55 | 27.8422 | 34.0983 | 132.9195 | 0.41156 |  | 4351 | 26.61 | 27.8422 | 5.7321 | 132.9195
4352 | 52.34 | 30.4465 | 50.5197 | 143.4506 | 0.40637 |  | 4352 | 34.94 | 30.4465 | 5 | 143.4506
4353 | 41.13 | 48.1319 | 42.4138 | 123.4607 | 0.40061 |  | 4353 | 39.86 | 48.1319 | 4 | 123.4607
4354 | 37.57 | 66.8804 | 43.7647 | 79.4785 | 0.39682 |  | 4354 | 40.72 | 66.8804 | 3 | 79.4785
4355 | 32.85 | 71.8858 | 39.8692 | 83.1906 | 0.39407 |  | 4355 | 38.49 | 71.8858 | 2.2679 | 83.1906
4356 | 29.46 | 76.1864 | 54.323 | 64.326 | 0.38651 |  | 4356 | 39.9 | 76.1864 | 2 | 64.326
4357 | 27.41 | 78.1627 | 48.5759 | 78.8535 | 0.37918 |  | 4357 | 42.44 | 78.1627 | 2.2679 | 78.8535
4358 | 27.28 | 75.7198 | 37.5717 | 77.9678 | 0.37779 |  | 4358 | 40.23 | 75.7198 | 3 | 77.9678
4359 | 27 | 70.3336 | 52.1897 | 66.4848 | 0.37913 |  | 4359 | 36.42 | 70.3336 | 4 | 66.4848
4360 | 27.6 | 75.6501 | 40.2814 | 58.8438 | 0.37896 |  | 4360 | 34.73 | 75.6501 | 5 | 58.8438
4361 | 28.41 | 78.6056 | 32.0941 | 79.4839 | 0.38312 |  | 4361 | 36.02 | 78.6056 | 5.7321 | 79.4839
4362 | 31.03 | 119.6728 | 51.2519 | 91.8687 | 0.38811 |  | 4362 | 31.96 | 119.6728 | 6 | 91.8687
4363 | 36.49 | 130.6855 | 50.9375 | 115.5508 | 0.4004 |  | 4363 | 34.23 | 130.6855 | 5.7321 | 115.5508
4364 | 36.32 | 134.9588 | 26.1847 | 113.7373 | 0.40969 |  | 4364 | 38.28 | 134.9588 | 5 | 113.7373
4365 | 34.93 | 100.5143 | 28.8511 | 108.7877 | 0.41479 |  | 4365 | 34.91 | 100.5143 | 4 | 108.7877
4366 | 38.9 | 93.0326 | 34.6715 | 62.1496 | 0.42231 |  | 4366 | 31.11 | 93.0326 | 3 | 62.1496
4367 | 31.97 | 90.4435 | 32.3852 | 51.3503 | 0.42308 |  | 4367 | 32.38 | 90.4435 | 2.2679 | 51.3503
4368 | 28.9 | 41.6007 | 30.5701 | 25.8296 | 0.41288 |  | 4368 | 27.72 | 41.6007 | 2 | 25.8296
4369 | 26.97 | 32.2773 | 27.6681 | 30.1413 | 0.40036 |  | 4369 | 29.36 | 32.2773 | 2.2679 | 30.1413
4370 | 25.48 | 31.142 | 24.838 | 5.3914 | 0.39994 |  | 4370 | 24.69 | 31.142 | 3 | 5.3914
4371 | 24.75 | 29.9232 | 32.5395 | 16.0963 | 0.39409 |  | 4371 | 23.42 | 29.9232 | 4 | 16.0963
4372 | 24.91 | 28.692 | 57.5505 | 54.8862 | 0.39183 |  | 4372 | 21.91 | 28.692 | 5 | 54.8862
4373 | 26.99 | 27.9495 | 108.3715 | 78.8867 | 0.39661 |  | 4373 | 20.19 | 27.9495 | 5.7321 | 78.8867
4374 | 31 | 27.3988 | 90.0722 | 103.4598 | 0.40717 |  | 4374 | 22.44 | 27.3988 | 6 | 103.4598
4375 | 36.12 | 27.209 | 96.6411 | 167.7283 | 0.41636 |  | 4375 | 26.84 | 27.209 | 5.7321 | 167.7283
4376 | 36.1 | 29.1871 | 88.0368 | 132.7353 | 0.41874 |  | 4376 | 33.58 | 29.1871 | 5 | 132.7353
4377 | 39.94 | 47.6646 | 60.3506 | 116.5037 | 0.41963 |  | 4377 | 35.78 | 47.6646 | 4 | 116.5037
4378 | 41.5 | 67.3506 | 44.6309 | 75.6094 | 0.424 |  | 4378 | 36.38 | 67.3506 | 3 | 75.6094
4379 | 41.48 | 75.7186 | 77.5277 | 74.691 | 0.4272 |  | 4379 | 40.01 | 75.7186 | 2.2679 | 74.691
4380 | 40.98 | 74.628 | 88.7857 | 69.0675 | 0.43229 |  | 4380 | 40.5 | 74.628 | 2 | 69.0675
4381 | 40.1 | 80.0975 | 45.9036 | 72.2304 | 0.43361 |  | 4381 | 40 | 80.0975 | 2.2679 | 72.2304
4382 | 38.26 | 78.8304 | 41.8227 | 62.8684 | 0.4334 |  | 4382 | 40.5 | 78.8304 | 3 | 62.8684
4383 | 33 | 76.4853 | 236.842 | 63.419 | 0.43021 |  | 4383 | 36.11 | 76.4853 | 4 | 63.419
4384 | 29.96 | 70.684 | 45.3096 | 65.8031 | 0.42848 |  | 4384 | 28.45 | 70.684 | 5 | 65.8031
4385 | 33.05 | 71.9714 | 45.5788 | 75.4642 | 0.42854 |  | 4385 | 27.96 | 71.9714 | 5.7321 | 75.4642
4386 | 38.02 | 107.6056 | 42.8071 | 102.2849 | 0.4247 |  | 4386 | 28.75 | 107.6056 | 6 | 102.2849
4387 | 44 | 123.9335 | 49.4468 | 109.821 | 0.43046 |  | 4387 | 32.43 | 123.9335 | 5.7321 | 109.821
4388 | 52.42 | 132.7161 | 73.3867 | 120.9318 | 0.43832 |  | 4388 | 33.95 | 132.7161 | 5 | 120.9318
4389 | 47.65 | 99.6088 | 98.5209 | 80.1157 | 0.44614 |  | 4389 | 32.67 | 99.6088 | 4 | 80.1157
4390 | 42.14 | 86.5474 | 83.8811 | 73.8508 | 0.44877 |  | 4390 | 30.07 | 86.5474 | 3 | 73.8508
4391 | 37.05 | 84.2414 | 38.8735 | 39.6038 | 0.44957 |  | 4391 | 31.91 | 84.2414 | 2.2679 | 39.6038
4392 | 30.94 | 38.297 | 26.217 | 26.6342 | 0.44187 |  | 4392 | 39.13 | 38.297 | 2 | 26.6342
4393 | 28.07 | 34.9634 | 29.241 | 27.639 | 0.43295 |  | 4393 | 22.03 | 34.9634 | 2.2679 | 27.639
4394 | 27.6 | 33.1176 | 30.8636 | 5.4999 | 0.43468 |  | 4394 | 20.38 | 33.1176 | 3 | 5.4999
4395 | 27.33 | 31.4488 | 28.0574 | 19.5554 | 0.43079 |  | 4395 | 19.4 | 31.4488 | 4 | 19.5554
4396 | 27.93 | 30.0235 | 25.7677 | 47.0116 | 0.43284 |  | 4396 | 17.09 | 30.0235 | 5 | 47.0116
4397 | 29 | 28.9948 | 44.5534 | 84.6159 | 0.42644 |  | 4397 | 16.79 | 28.9948 | 5.7321 | 84.6159
4398 | 38.22 | 28.485 | 103.8668 | 114.5126 | 0.42674 |  | 4398 | 16.58 | 28.485 | 6 | 114.5126
4399 | 47.6 | 40.0278 | 108.0302 | 121.9041 | 0.42682 |  | 4399 | 17.99 | 40.0278 | 5.7321 | 121.9041
4400 | 48 | 54.789 | 124.7751 | 150.2815 | 0.41832 |  | 4400 | 20.05 | 54.789 | 5 | 150.2815
4401 | 37.53 | 43.0601 | 105.0336 | 90.7524 | 0.41911 |  | 4401 | 21.41 | 43.0601 | 4 | 90.7524
4402 | 33.68 | 41.6225 | 110.2817 | 89.3126 | 0.41719 |  | 4402 | 24.21 | 41.6225 | 3 | 89.3126
4403 | 33.4 | 42.9182 | 135.1453 | 82.8145 | 0.41472 |  | 4403 | 23.38 | 42.9182 | 2.2679 | 82.8145
4404 | 31.19 | 46.0894 | 143.6228 | 65.0372 | 0.41552 |  | 4404 | 22.76 | 46.0894 | 2 | 65.0372
4405 | 30.14 | 48.5527 | 121.9768 | 87.6583 | 0.41809 |  | 4405 | 22.59 | 48.5527 | 2.2679 | 87.6583
4406 | 30.1 | 52.1946 | 53.578 | 64.3097 | 0.41867 |  | 4406 | 21.41 | 52.1946 | 3 | 64.3097
4407 | 29.98 | 55.5995 | 46.5159 | 70.8129 | 0.41595 |  | 4407 | 20.18 | 55.5995 | 4 | 70.8129
4408 | 30.08 | 69.668 | 45.2818 | 54.1835 | 0.41301 |  | 4408 | 19.68 | 69.668 | 5 | 54.1835
4409 | 33 | 91.6891 | 41.5143 | 66.8939 | 0.41438 |  | 4409 | 20 | 91.6891 | 5.7321 | 66.8939
4410 | 36.49 | 128.6288 | 38.3715 | 82.2033 | 0.41189 |  | 4410 | 21 | 128.6288 | 6 | 82.2033
4411 | 43.07 | 141.7354 | 54.5705 | 105.895 | 0.40985 |  | 4411 | 23.11 | 141.7354 | 5.7321 | 105.895
4412 | 50.69 | 137.4643 | 29.8185 | 99.8772 | 0.41903 |  | 4412 | 25.33 | 137.4643 | 5 | 99.8772
4413 | 41.4 | 101.2542 | 33.8698 | 103.4405 | 0.42651 |  | 4413 | 25.48 | 101.2542 | 4 | 103.4405
4414 | 37.57 | 96.2763 | 74.5345 | 82.5391 | 0.43798 |  | 4414 | 25.03 | 96.2763 | 3 | 82.5391
4415 | 33.41 | 76.0103 | 59.8328 | 38.8145 | 0.43897 |  | 4415 | 34.94 | 76.0103 | 2.2679 | 38.8145
4416 | 29.93 | 40.314 | 49.3157 | 23.657 | 0.44207 |  | 4416 | 37.18 | 40.314 | 2 | 23.657
4417 | 28.83 | 33.5941 | 77.8758 | 33.2407 | 0.44349 |  | 4417 | 18.07 | 33.5941 | 2.2679 | 33.2407
4418 | 27.98 | 32.185 | 43.9011 | 5.8189 | 0.44546 |  | 4418 | 21.17 | 32.185 | 3 | 5.8189
4419 | 28.89 | 30.6848 | 30.9695 | 21.9138 | 0.44835 |  | 4419 | 24.64 | 30.6848 | 4 | 21.9138
4420 | 29.42 | 29.3585 | 24.9729 | 39.7029 | 0.44581 |  | 4420 | 22.8 | 29.3585 | 5 | 39.7029
4421 | 30.71 | 28.4859 | 39.0053 | 76.2425 | 0.44408 |  | 4421 | 12.63 | 28.4859 | 5.7321 | 76.2425
4422 | 36.7 | 28.1197 | 301.5751 | 128.1359 | 0.44154 |  | 4422 | 12.54 | 28.1197 | 6 | 128.1359
4423 | 44.31 | 39.0659 | 127.7571 | 148.1943 | 0.43515 |  | 4423 | 15.45 | 39.0659 | 5.7321 | 148.1943
4424 | 39.72 | 54.2392 | 92.643 | 148.9421 | 0.42721 |  | 4424 | 18.99 | 54.2392 | 5 | 148.9421
4425 | 34.77 | 42.9177 | 109.1629 | 93.7637 | 0.42654 |  | 4425 | 13.09 | 42.9177 | 4 | 93.7637
4426 | 31.88 | 41.5008 | 72.2063 | 67.5487 | 0.42123 |  | 4426 | 24.99 | 41.5008 | 3 | 67.5487
4427 | 30.89 | 44.2436 | 62.6153 | 79.5049 | 0.4133 |  | 4427 | 25.19 | 44.2436 | 2.2679 | 79.5049
4428 | 29.97 | 46.6349 | 55.535 | 68.6724 | 0.40893 |  | 4428 | 27.73 | 46.6349 | 2 | 68.6724
4429 | 29.65 | 48.7656 | 49.413 | 88.5154 | 0.40257 |  | 4429 | 35 | 48.7656 | 2.2679 | 88.5154
4430 | 29.53 | 50.6798 | 28.2711 | 66.9864 | 0.39734 |  | 4430 | 29.94 | 50.6798 | 3 | 66.9864
4431 | 29.85 | 54.2903 | 36.0911 | 61.1347 | 0.39747 |  | 4431 | 21.28 | 54.2903 | 4 | 61.1347
4432 | 29.8 | 72.7193 | 42.724 | 68.9721 | 0.3968 |  | 4432 | 21 | 72.7193 | 5 | 68.9721
4433 | 32.98 | 91.6211 | 43.7434 | 76.7535 | 0.40229 |  | 4433 | 18.79 | 91.6211 | 5.7321 | 76.7535
4434 | 36.92 | 132.7204 | 40.1342 | 106.9769 | 0.4104 |  | 4434 | 21.52 | 132.7204 | 6 | 106.9769
4435 | 43.58 | 139.5033 | 49.6744 | 105.5767 | 0.41371 |  | 4435 | 24.47 | 139.5033 | 5.7321 | 105.5767
4436 | 44.98 | 129.0831 | 41.7873 | 91.5188 | 0.42017 |  | 4436 | 26.76 | 129.0831 | 5 | 91.5188
4437 | 39.9 | 96.9487 | 98.528 | 76.5202 | 0.42579 |  | 4437 | 27.97 | 96.9487 | 4 | 76.5202
4438 | 39.06 | 93.5128 | 61.1438 | 63.9013 | 0.43079 |  | 4438 | 40 | 93.5128 | 3 | 63.9013
4439 | 34.9 | 75.5063 | 57.0993 | 40.8574 | 0.43338 |  | 4439 | 32.35 | 75.5063 | 2.2679 | 40.8574
4440 | 29.8 | 38.6852 | 40.2474 | 25.2395 | 0.42571 |  | 4440 | 33.91 | 38.6852 | 2 | 25.2395
4441 | 29 | 34.1019 | 37.9765 | 33.6673 | 0.42098 |  | 4441 | 39.63 | 34.1019 | 2.2679 | 33.6673
4442 | 27.8 | 32.5312 | 46.8086 | 7.3183 | 0.41506 |  | 4442 | 24.22 | 32.5312 | 3 | 7.3183
4443 | 27.64 | 30.9939 | 27.8158 | 17.0397 | 0.41305 |  | 4443 | 22.26 | 30.9939 | 4 | 17.0397
4444 | 27.9 | 29.589 | 39.7767 | 54.8391 | 0.41932 |  | 4444 | 21.65 | 29.589 | 5 | 54.8391
4445 | 29.08 | 28.593 | 82.7714 | 89.8163 | 0.4308 |  | 4445 | 21.69 | 28.593 | 5.7321 | 89.8163
4446 | 34.62 | 28.3583 | 89.0924 | 124.5373 | 0.43579 |  | 4446 | 23.37 | 28.3583 | 6 | 124.5373
4447 | 42.89 | 39.9168 | 71.4238 | 175.6594 | 0.42782 |  | 4447 | 31.93 | 39.9168 | 5.7321 | 175.6594
4448 | 45.92 | 54.9839 | 86.0258 | 109.1617 | 0.42421 |  | 4448 | 35.19 | 54.9839 | 5 | 109.1617
4449 | 43.4 | 43.7644 | 35.4934 | 100.513 | 0.4232 |  | 4449 | 40.58 | 43.7644 | 4 | 100.513
4450 | 38 | 42.4376 | 50.6901 | 93.9878 | 0.4248 |  | 4450 | 52.87 | 42.4376 | 3 | 93.9878
4451 | 36.6 | 44.5117 | 296.5557 | 85.5223 | 0.42371 |  | 4451 | 56.77 | 44.5117 | 2.2679 | 85.5223
4452 | 33.02 | 47.6437 | 121.7626 | 86.769 | 0.42117 |  | 4452 | 62.57 | 47.6437 | 2 | 86.769
4453 | 31.05 | 48.9492 | 98.9358 | 83.139 | 0.41792 |  | 4453 | 63.73 | 48.9492 | 2.2679 | 83.139
4454 | 29.68 | 51.7559 | 95.0926 | 64.9274 | 0.4144 |  | 4454 | 54.94 | 51.7559 | 3 | 64.9274
4455 | 29.23 | 58.1421 | 76.307 | 64.9219 | 0.41186 |  | 4455 | 52.44 | 58.1421 | 4 | 64.9219
4456 | 30.4 | 74.3381 | 61.5537 | 59.403 | 0.41349 |  | 4456 | 52.31 | 74.3381 | 5 | 59.403
4457 | 32.97 | 93.3583 | 92.566 | 90.1778 | 0.42439 |  | 4457 | 50.01 | 93.3583 | 5.7321 | 90.1778
4458 | 35.35 | 123.9803 | 121.5319 | 106.1323 | 0.43284 |  | 4458 | 54.87 | 123.9803 | 6 | 106.1323
4459 | 40.15 | 139.523 | 72.5916 | 119.9012 | 0.44296 |  | 4459 | 40 | 139.523 | 5.7321 | 119.9012
4460 | 45.86 | 123.9744 | 25.6601 | 98.1844 | 0.45012 |  | 4460 | 42.21 | 123.9744 | 5 | 98.1844
4461 | 45.75 | 98.2415 | 33.5241 | 96.7104 | 0.45489 |  | 4461 | 38.65 | 98.2415 | 4 | 96.7104
4462 | 42.07 | 93.8121 | 64.1792 | 84.0105 | 0.45609 |  | 4462 | 35.56 | 93.8121 | 3 | 84.0105
4463 | 38.09 | 75.8758 | 83.7831 | 41.8324 | 0.45105 |  | 4463 | 42.88 | 75.8758 | 2.2679 | 41.8324
4464 | 37.97 | 39.7408 | 30.0563 | 31.6231 | 0.43803 |  | 4464 | 39.39 | 39.7408 | 2 | 31.6231
4465 | 34.1 | 33.7125 | 22.2761 | 33.6957 | 0.42367 |  | 4465 | 29.93 | 33.7125 | 2.2679 | 33.6957
4466 | 30.99 | 32.2837 | 22.5288 | 5.6339 | 0.42064 |  | 4466 | 27 | 32.2837 | 3 | 5.6339
4467 | 30.52 | 30.7377 | 29.0898 | 16.1553 | 0.40999 |  | 4467 | 25.46 | 30.7377 | 4 | 16.1553
4468 | 30 | 29.4169 | 24.9835 | 53.6602 | 0.40582 |  | 4468 | 23.88 | 29.4169 | 5 | 53.6602
4469 | 29.23 | 28.4959 | 39.8615 | 78.5341 | 0.38557 |  | 4469 | 23.43 | 28.4959 | 5.7321 | 78.5341
4470 | 29.21 | 28.1143 | 66.4162 | 127.6218 | 0.38476 |  | 4470 | 25.31 | 28.1143 | 6 | 127.6218
4471 | 29.74 | 38.8556 | 34.7791 | 169.0501 | 0.38148 |  | 4471 | 30.28 | 38.8556 | 5.7321 | 169.0501
4472 | 31.05 | 53.514 | 35.9553 | 151.487 | 0.38002 |  | 4472 | 34.94 | 53.514 | 5 | 151.487
4473 | 31.25 | 43.6969 | 72.5666 | 103.8357 | 0.37841 |  | 4473 | 36.46 | 43.6969 | 4 | 103.8357
4474 | 30.68 | 42.2717 | 85.6924 | 67.8711 | 0.3777 |  | 4474 | 35.05 | 42.2717 | 3 | 67.8711
4475 | 29.47 | 45.5224 | 34.5027 | 69.2001 | 0.38456 |  | 4475 | 40.5 | 45.5224 | 2.2679 | 69.2001
4476 | 28.43 | 46.8194 | 38.4116 | 63.8519 | 0.38278 |  | 4476 | 40.5 | 46.8194 | 2 | 63.8519
4477 | 28.07 | 49.6155 | 44.8008 | 81.3469 | 0.37643 |  | 4477 | 37.73 | 49.6155 | 2.2679 | 81.3469
4478 | 27.7 | 51.3253 | 38.3931 | 67.6041 | 0.37377 |  | 4478 | 35.4 | 51.3253 | 3 | 67.6041
4479 | 27.16 | 56.9871 | 49.2401 | 59.2111 | 0.37393 |  | 4479 | 34 | 56.9871 | 4 | 59.2111
4480 | 27.7 | 74.6968 | 41.2268 | 64.1254 | 0.37152 |  | 4480 | 31.59 | 74.6968 | 5 | 64.1254
4481 | 29.95 | 93.7455 | 40.8075 | 70.9894 | 0.37905 |  | 4481 | 30.34 | 93.7455 | 5.7321 | 70.9894
4482 | 30.73 | 133.3633 | 47.4584 | 77.699 | 0.3827 |  | 4482 | 37 | 133.3633 | 6 | 77.699
4483 | 34.9 | 139.9551 | 36.5032 | 90.5095 | 0.38752 |  | 4483 | 40.5 | 139.9551 | 5.7321 | 90.5095
4484 | 39.9 | 124.9823 | 26.8087 | 103.1571 | 0.38776 |  | 4484 | 42.44 | 124.9823 | 5 | 103.1571
4485 | 37.4 | 98.5583 | 23.5494 | 88.0443 | 0.38948 |  | 4485 | 39.98 | 98.5583 | 4 | 88.0443
4486 | 49.51 | 91.1707 | 25.1584 | 64.672 | 0.39608 |  | 4486 | 30 | 91.1707 | 3 | 64.672
4487 | 40 | 75.6418 | 26.485 | 52.0467 | 0.39623 |  | 4487 | 44.94 | 75.6418 | 2.2679 | 52.0467
4488 | 47.34 | 39.4762 | 21.456 | 26.0173 | 0.38937 |  | 4488 | 41.1 | 39.4762 | 2 | 26.0173
4489 | 37.42 | 33.7579 | 27.3453 | 31.2503 | 0.38912 |  | 4489 | 25.83 | 33.7579 | 2.2679 | 31.2503
4490 | 29 | 32.1898 | 27.3063 | 5.9593 | 0.38614 |  | 4490 | 25.8 | 32.1898 | 3 | 5.9593
4491 | 24.27 | 30.6555 | 34.8906 | 18.9068 | 0.38028 |  | 4491 | 25.8 | 30.6555 | 4 | 18.9068
4492 | 24.1 | 29.2761 | 29.0103 | 37.7696 | 0.38144 |  | 4492 | 25.8 | 29.2761 | 5 | 37.7696
4493 | 25.21 | 28.3867 | 24.0802 | 102.5087 | 0.37878 |  | 4493 | 23.44 | 28.3867 | 5.7321 | 102.5087
4494 | 26.46 | 28.2874 | 23.4372 | 105.3876 | 0.3818 |  | 4494 | 17.13 | 28.2874 | 6 | 105.3876
4495 | 26.7 | 39.5571 | 26.2293 | 124.9884 | 0.3729 |  | 4495 | 21.36 | 39.5571 | 5.7321 | 124.9884
4496 | 27.78 | 54.9325 | 35.7518 | 145.3257 | 0.3752 |  | 4496 | 27.44 | 54.9325 | 5 | 145.3257
4497 | 28.93 | 44.5078 | 41.0064 | 122.3185 | 0.37424 |  | 4497 | 38.84 | 44.5078 | 4 | 122.3185
4498 | 29.53 | 43.3386 | 42.9723 | 67.5487 | 0.37712 |  | 4498 | 47.84 | 43.3386 | 3 | 67.5487
4499 | 29 | 44.4503 | 50.2401 | 80.2571 | 0.37406 |  | 4499 | 49.13 | 44.4503 | 2.2679 | 80.2571
4500 | 27.06 | 49.6996 | 27.7456 | 87.0851 | 0.38403 |  | 4500 | 48 | 49.6996 | 2 | 87.0851
4501 | 26.85 | 49.4501 | 40.5512 | 75.8147 | 0.36792 |  | 4501 | 42.44 | 49.4501 | 2.2679 | 75.8147
4502 | 25 | 51.077 | 47.5775 | 65.4078 | 0.36541 |  | 4502 | 44.94 | 51.077 | 3 | 65.4078
4503 | 26.12 | 57.5405 | 47.2713 | 65.4629 | 0.36734 |  | 4503 | 40 | 57.5405 | 4 | 65.4629
4504 | 26.6 | 77.7739 | 37.9473 | 62.3856 | 0.36186 |  | 4504 | 37.74 | 77.7739 | 5 | 62.3856
4505 | 29.1 | 95.249 | 20.0599 | 84.3379 | 0.36799 |  | 4505 | 48.1 | 95.249 | 5.7321 | 84.3379
4506 | 29.2 | 141.9645 | 41.4465 | 84.4554 | 0.37749 |  | 4506 | 66.39 | 141.9645 | 6 | 84.4554
4507 | 31.47 | 143.0018 | 50.1116 | 122.5539 | 0.38767 |  | 4507 | 50.03 | 143.0018 | 5.7321 | 122.5539
4508 | 32.25 | 120.0265 | 23.3173 | 117.123 | 0.39758 |  | 4508 | 47.66 | 120.0265 | 5 | 117.123
4509 | 33.06 | 96.742 | 27.2687 | 109.2487 | 0.39977 |  | 4509 | 42.44 | 96.742 | 4 | 109.2487
4510 | 37.02 | 91.2292 | 27.8964 | 64.4618 | 0.40575 |  | 4510 | 29.6 | 91.2292 | 3 | 64.4618
4511 | 33.02 | 75.3862 | 24.101 | 48.1467 | 0.40087 |  | 4511 | 37.26 | 75.3862 | 2.2679 | 48.1467
4512 | 34.93 | 39.0841 | 20.3061 | 28.4581 | 0.40109 |  | 4512 | 32 | 39.0841 | 2 | 28.4581
4513 | 30.11 | 36.4031 | 27.6087 | 28.947 | 0.39692 |  | 4513 | 29.09 | 36.4031 | 2.2679 | 28.947
4514 | 29.55 | 34.338 | 35.117 | 6.3612 | 0.39472 |  | 4514 | 27.19 | 34.338 | 3 | 6.3612
4515 | 30.28 | 32.3314 | 31.8897 | 17.8455 | 0.39235 |  | 4515 | 25.7 | 32.3314 | 4 | 17.8455
4516 | 30.04 | 30.5928 | 26.2423 | 50.3595 | 0.38913 |  | 4516 | 22.11 | 30.5928 | 5 | 50.3595
4517 | 30.02 | 29.4696 | 27.5277 | 96.6913 | 0.38768 |  | 4517 | 22.98 | 29.4696 | 5.7321 | 96.6913
4518 | 34.76 | 28.7313 | 29.0599 | 132.6342 | 0.39758 |  | 4518 | 23.74 | 28.7313 | 6 | 132.6342
4519 | 39.06 | 28.2718 | 224.2116 | 146.4318 | 0.39769 |  | 4519 | 30.6 | 28.2718 | 5.7321 | 146.4318
4520 | 39.99 | 30.7819 | 38.9238 | 155.9071 | 0.39264 |  | 4520 | 34.28 | 30.7819 | 5 | 155.9071
4521 | 38.59 | 48.6575 | 33.115 | 117.1267 | 0.38901 |  | 4521 | 36.39 | 48.6575 | 4 | 117.1267
4522 | 37.29 | 68.5393 | 39.6534 | 74.1585 | 0.39748 |  | 4522 | 38.86 | 68.5393 | 3 | 74.1585
4523 | 39.94 | 77.1028 | 49.1257 | 71.4567 | 0.40188 |  | 4523 | 40.98 | 77.1028 | 2.2679 | 71.4567
4524 | 38.68 | 77.0964 | 244.6237 | 84.9514 | 0.40508 |  | 4524 | 44.94 | 77.0964 | 2 | 84.9514
4525 | 35.09 | 80.518 | 30.6465 | 63.8152 | 0.40518 |  | 4525 | 42.79 | 80.518 | 2.2679 | 63.8152
4526 | 33.48 | 78.0687 | 39.1922 | 61.3584 | 0.40435 |  | 4526 | 39.94 | 78.0687 | 3 | 61.3584
4527 | 33.76 | 74.4235 | 52.2204 | 69.25 | 0.40313 |  | 4527 | 36.26 | 74.4235 | 4 | 69.25
4528 | 34.47 | 74.2859 | 41.6226 | 56.3583 | 0.39614 |  | 4528 | 34.47 | 74.2859 | 5 | 56.3583
4529 | 34.92 | 82.1936 | 28.2898 | 76.1468 | 0.39405 |  | 4529 | 34.94 | 82.1936 | 5.7321 | 76.1468
4530 | 38 | 112.8675 | 28.7414 | 106.6015 | 0.39779 |  | 4530 | 36 | 112.8675 | 6 | 106.6015
4531 | 42.9 | 153.834 | 41.2451 | 92.95 | 0.40658 |  | 4531 | 39.94 | 153.834 | 5.7321 | 92.95
4532 | 38.35 | 126.954 | 19.4321 | 95.3277 | 0.41207 |  | 4532 | 39.44 | 126.954 | 5 | 95.3277
4533 | 37.93 | 101.7654 | 30.7558 | 87.7677 | 0.40949 |  | 4533 | 37.91 | 101.7654 | 4 | 87.7677
4534 | 39.43 | 97.877 | 29.9711 | 56.1939 | 0.41872 |  | 4534 | 32.49 | 97.877 | 3 | 56.1939
4535 | 34.63 | 93.5172 | 27.6325 | 54.2289 | 0.42352 |  | 4535 | 36.53 | 93.5172 | 2.2679 | 54.2289
4536 | 31.56 | 43.4003 | 17.7274 | 30.7648 | 0.4244 |  | 4536 | 37.28 | 43.4003 | 2 | 30.7648
4537 | 30.19 | 33.6919 | 30.1682 | 26.0466 | 0.42554 |  | 4537 | 28.62 | 33.6919 | 2.2679 | 26.0466
4538 | 29.81 | 32.0972 | 29.7873 | 6.0231 | 0.42726 |  | 4538 | 27.01 | 32.0972 | 3 | 6.0231
4539 | 29.48 | 30.5753 | 32.9086 | 20.1646 | 0.42983 |  | 4539 | 25.04 | 30.5753 | 4 | 20.1646
4540 | 30.19 | 29.3346 | 39.3664 | 54.3675 | 0.42735 |  | 4540 | 23.46 | 29.3346 | 5 | 54.3675
4541 | 30.55 | 28.5135 | 72.0686 | 89.023 | 0.42596 |  | 4541 | 23.18 | 28.5135 | 5.7321 | 89.023
4542 | 36.16 | 28.0133 | 107.4766 | 120.039 | 0.42826 |  | 4542 | 25.02 | 28.0133 | 6 | 120.039
4543 | 43.95 | 27.8501 | 109.3008 | 171.1063 | 0.41853 |  | 4543 | 30 | 27.8501 | 5.7321 | 171.1063
4544 | 44.06 | 30.4153 | 97.6076 | 133.9408 | 0.41258 |  | 4544 | 34.99 | 30.4153 | 5 | 133.9408
4545 | 41.09 | 49.6759 | 107.5758 | 115.2577 | 0.41179 |  | 4545 | 39.65 | 49.6759 | 4 | 115.2577
4546 | 38.17 | 67.6952 | 52.4713 | 77.4634 | 0.41966 |  | 4546 | 44 | 67.6952 | 3 | 77.4634
4547 | 38.04 | 75.8387 | 53.9239 | 68.1471 | 0.41748 |  | 4547 | 50.79 | 75.8387 | 2.2679 | 68.1471
4548 | 37.06 | 80.44 | 68.7576 | 64.405 | 0.41577 |  | 4548 | 49.77 | 80.44 | 2 | 64.405
4549 | 35.15 | 84.0586 | 134.9745 | 75.8147 | 0.41577 |  | 4549 | 47.04 | 84.0586 | 2.2679 | 75.8147
4550 | 34.75 | 81.7321 | 108.2673 | 66.1628 | 0.41444 |  | 4550 | 44.5 | 81.7321 | 3 | 66.1628
4551 | 34.24 | 76.2761 | 69.3164 | 65.523 | 0.41564 |  | 4551 | 38.6 | 76.2761 | 4 | 65.523
4552 | 34.74 | 73.718 | 45.4016 | 73.6324 | 0.42149 |  | 4552 | 34.67 | 73.718 | 5 | 73.6324
4553 | 36.71 | 75.5544 | 33.5779 | 86.234 | 0.42361 |  | 4553 | 26.94 | 75.5544 | 5.7321 | 86.234
4554 | 40.34 | 111.9464 | 37.5818 | 109.4167 | 0.42828 |  | 4554 | 27.38 | 111.9464 | 6 | 109.4167
4555 | 47 | 120.2736 | 38.5128 | 89.1301 | 0.43688 |  | 4555 | 28.54 | 120.2736 | 5.7321 | 89.1301
4556 | 47.9 | 140.701 | 25.3026 | 97.4438 | 0.44468 |  | 4556 | 29.79 | 140.701 | 5 | 97.4438
4557 | 45.99 | 100.3879 | 34.1072 | 75.4139 | 0.44782 |  | 4557 | 28.1 | 100.3879 | 4 | 75.4139
4558 | 43.88 | 90.9458 | 30.0028 | 74.6916 | 0.44113 |  | 4558 | 26.91 | 90.9458 | 3 | 74.6916
4559 | 36.66 | 87.3651 | 29.3333 | 46.1967 | 0.44194 |  | 4559 | 36.26 | 87.3651 | 2.2679 | 46.1967
4560 | 35.91 | 40.2757 | 31.6635 | 24.0593 | 0.44475 |  | 4560 | 44.36 | 40.2757 | 2 | 24.0593
4561 | 33.54 | 33.2763 | 32.1413 | 32.1602 | 0.44377 |  | 4561 | 26.01 | 33.2763 | 2.2679 | 32.1602
4562 | 32.98 | 31.9045 | 26.1927 | 6.0996 | 0.43708 |  | 4562 | 26.32 | 31.9045 | 3 | 6.0996
4563 | 32.92 | 30.5487 | 27.1904 | 20.4201 | 0.43473 |  | 4563 | 24.15 | 30.5487 | 4 | 20.4201
4564 | 33.3 | 29.2022 | 34.5111 | 54.4147 | 0.43404 |  | 4564 | 22.4 | 29.2022 | 5 | 54.4147
4565 | 33.38 | 28.3418 | 20.2027 | 81.7954 | 0.43827 |  | 4565 | 20.6 | 28.3418 | 5.7321 | 81.7954
4566 | 41.8 | 27.9568 | 35.7824 | 131.2204 | 0.43804 |  | 4566 | 21.51 | 27.9568 | 6 | 131.2204
4567 | 49.45 | 39.2126 | 88.9258 | 131.0102 | 0.4319 |  | 4567 | 22.33 | 39.2126 | 5.7321 | 131.0102
4568 | 48.8 | 54.6952 | 137.6358 | 150.4155 | 0.43712 |  | 4568 | 22.99 | 54.6952 | 5 | 150.4155
4569 | 43.99 | 42.6659 | 112.7913 | 118.2689 | 0.43355 |  | 4569 | 25.36 | 42.6659 | 4 | 118.2689
4570 | 41.34 | 41.3371 | 117.0384 | 79.3173 | 0.42975 |  | 4570 | 28.26 | 41.3371 | 3 | 79.3173
4571 | 42.13 | 43.0857 | 81.3988 | 65.2888 | 0.43119 |  | 4571 | 39.59 | 43.0857 | 2.2679 | 65.2888
4572 | 39.16 | 44.4587 | 29.9563 | 85.8997 | 0.43379 |  | 4572 | 34.03 | 44.4587 | 2 | 85.8997
4573 | 37.32 | 46.6428 | 53.6394 | 78.3081 | 0.43262 |  | 4573 | 37 | 46.6428 | 2.2679 | 78.3081
4574 | 36.99 | 49.6833 | 101.8857 | 75.0165 | 0.43079 |  | 4574 | 39.05 | 49.6833 | 3 | 75.0165
4575 | 37.05 | 55.8412 | 88.8038 | 54.2819 | 0.43301 |  | 4575 | 30 | 55.8412 | 4 | 54.2819
4576 | 38.84 | 71.0805 | 127.9213 | 74.378 | 0.43586 |  | 4576 | 26.1 | 71.0805 | 5 | 74.378
4577 | 44.08 | 93.351 | 124.0835 | 89.3435 | 0.43707 |  | 4577 | 22.35 | 93.351 | 5.7321 | 89.3435
4578 | 48.95 | 125.0152 | 99.4743 | 102.5664 | 0.44582 |  | 4578 | 23.09 | 125.0152 | 6 | 102.5664
4579 | 53.19 | 135.359 | 59.4546 | 111.7309 | 0.45193 |  | 4579 | 27.92 | 135.359 | 5.7321 | 111.7309
4580 | 51.47 | 147.6013 | 68.0961 | 125.1639 | 0.46046 |  | 4580 | 30.63 | 147.6013 | 5 | 125.1639
4581 | 48.06 | 102.7751 | 45.1754 | 91.3632 | 0.46608 |  | 4581 | 32.12 | 102.7751 | 4 | 91.3632
4582 | 47.73 | 93.4985 | 23.0285 | 63.1305 | 0.46874 |  | 4582 | 29.86 | 93.4985 | 3 | 63.1305
4583 | 42.65 | 74.0306 | 32.5432 | 40.6716 | 0.47014 |  | 4583 | 30.61 | 74.0306 | 2.2679 | 40.6716
4584 | 36.52 | 38.8811 | 28.8415 | 30.8989 | 0.46998 |  | 4584 | 31.29 | 38.8811 | 2 | 30.8989
4585 | 35.99 | 32.5028 | 27.5319 | 28.1508 | 0.47196 |  | 4585 | 47.44 | 32.5028 | 2.2679 | 28.1508
4586 | 35.12 | 31.3231 | 56.3379 | 5.3085 | 0.47 |  | 4586 | 25.87 | 31.3231 | 3 | 5.3085
4587 | 34.88 | 30.0036 | 98.7068 | 22.3855 | 0.46583 |  | 4587 | 24.7 | 30.0036 | 4 | 22.3855
4588 | 34.86 | 28.9063 | 65.7266 | 38.194 | 0.46342 |  | 4588 | 21.46 | 28.9063 | 5 | 38.194
4589 | 35.9 | 27.9932 | 75.9412 | 97.3964 | 0.47159 |  | 4589 | 24.7 | 27.9932 | 5.7321 | 97.3964
4590 | 42.34 | 27.8988 | 298.384 | 124.9229 | 0.47891 |  | 4590 | 22.81 | 27.8988 | 6 | 124.9229
4591 | 50.77 | 39.5199 | 95.9756 | 127.6321 | 0.47477 |  | 4591 | 21.55 | 39.5199 | 5.7321 | 127.6321
4592 | 51.73 | 52.7523 | 117.5047 | 115.4569 | 0.47254 |  | 4592 | 22.53 | 52.7523 | 5 | 115.4569
4593 | 52.84 | 42.296 | 139.1344 | 93.0368 | 0.47158 |  | 4593 | 20.25 | 42.296 | 4 | 93.0368
4594 | 51.78 | 41.1304 | 141.2422 | 71.579 | 0.47105 |  | 4594 | 22.75 | 41.1304 | 3 | 71.579
4595 | 53.99 | 43.8185 | 147.6109 | 70.4036 | 0.47121 |  | 4595 | 25.16 | 43.8185 | 2.2679 | 70.4036
4596 | 51.42 | 46.1398 | 144.0632 | 84.4773 | 0.47219 |  | 4596 | 29.27 | 46.1398 | 2 | 84.4773
4597 | 50 | 47.3357 | 155.2031 | 65.2177 | 0.47081 |  | 4597 | 36 | 47.3357 | 2.2679 | 65.2177
4598 | 46.65 | 50.8025 | 133.9536 | 79.4777 | 0.47157 |  | 4598 | 36.77 | 50.8025 | 3 | 79.4777
4599 | 45.51 | 55.3292 | 124.8341 | 68.8292 | 0.47232 |  | 4599 | 28.56 | 55.3292 | 4 | 68.8292
4600 | 46 | 69.9348 | 119.0809 | 60.4593 | 0.47577 |  | 4600 | 22.44 | 69.9348 | 5 | 60.4593
4601 | 49.72 | 92.8469 | 88.434 | 83.1244 | 0.47982 |  | 4601 | 21.93 | 92.8469 | 5.7321 | 83.1244
4602 | 52.28 | 132.0899 | 35.2434 | 75.8222 | 0.48263 |  | 4602 | 27.07 | 132.0899 | 6 | 75.8222
4603 | 53.34 | 146.461 | 45.6301 | 115.4447 | 0.48522 |  | 4603 | 32.2 | 146.461 | 5.7321 | 115.4447
4604 | 51.71 | 119.739 | 36.3913 | 126.1161 | 0.49064 |  | 4604 | 33 | 119.739 | 5 | 126.1161
4605 | 48.9 | 93.9394 | 25.0119 | 100.3982 | 0.49593 |  | 4605 | 36 | 93.9394 | 4 | 100.3982
4606 | 47.76 | 90.4172 | 43.5779 | 77.4242 | 0.49953 |  | 4606 | 35.3 | 90.4172 | 3 | 77.4242
4607 | 40.17 | 72.2206 | 88.8531 | 46.6145 | 0.4962 |  | 4607 | 31.49 | 72.2206 | 2.2679 | 46.6145
4608 | 38.94 | 37.5318 | 112.9503 | 31.489 | 0.48936 |  | 4608 | 34.11 | 37.5318 | 2 | 31.489
4609 | 37.89 | 34.0166 | 77.301 | 32.7858 | 0.47975 |  | 4609 | 37.44 | 34.0166 | 2.2679 | 32.7858
4610 | 37.38 | 32.342 | 29.7836 | 6.5335 | 0.47706 |  | 4610 | 26.27 | 32.342 | 3 | 6.5335
4611 | 37.2 | 30.8276 | 26.3371 | 19.9484 | 0.47773 |  | 4611 | 23.72 | 30.8276 | 4 | 19.9484
4612 | 37.45 | 29.3309 | 26.8626 | 52.3399 | 0.47799 |  | 4612 | 19.96 | 29.3309 | 5 | 52.3399
4613 | 37.71 | 28.579 | 24.9825 | 92.4605 | 0.48169 |  | 4613 | 19.77 | 28.579 | 5.7321 | 92.4605
4614 | 42.97 | 28.5613 | 31.9997 | 144.2011 | 0.48653 |  | 4614 | 22.1 | 28.5613 | 6 | 144.2011
4615 | 53.73 | 39.7513 | 40.5214 | 168.7564 | 0.47982 |  | 4615 | 27.67 | 39.7513 | 5.7321 | 168.7564
4616 | 58.3 | 55.0215 | 97.9661 | 133.6729 | 0.47444 |  | 4616 | 32.03 | 55.0215 | 5 | 133.6729
4617 | 56.77 | 43.8899 | 112.7 | 88.4681 | 0.47061 |  | 4617 | 32.94 | 43.8899 | 4 | 88.4681
4618 | 52.4 | 41.5344 | 137.4566 | 90.9247 | 0.4666 |  | 4618 | 36.71 | 41.5344 | 3 | 90.9247
4619 | 50.97 | 43.9587 | 109.912 | 73.9388 | 0.45722 |  | 4619 | 33.62 | 43.9587 | 2.2679 | 73.9388
4620 | 44.54 | 47.3133 | 141.8461 | 93.091 | 0.45778 |  | 4620 | 40.95 | 47.3133 | 2 | 93.091
4621 | 41.73 | 50.7655 | 98.5609 | 83.7623 | 0.45483 |  | 4621 | 38.67 | 50.7655 | 2.2679 | 83.7623
4622 | 40.73 | 50.9982 | 63.9783 | 82.0171 | 0.44994 |  | 4622 | 36.97 | 50.9982 | 3 | 82.0171
4623 | 38 | 58.8105 | 62.8511 | 55.6645 | 0.43666 |  | 4623 | 34.86 | 58.8105 | 4 | 55.6645
4624 | 38.64 | 76.7537 | 305.3764 | 59.5273 | 0.43426 |  | 4624 | 32.61 | 76.7537 | 5 | 59.5273
4625 | 41.89 | 98.5861 | 108.1332 | 61.9641 | 0.44466 |  | 4625 | 30.61 | 98.5861 | 5.7321 | 61.9641
4626 | 50.81 | 142.5064 | 107.3214 | 99.8451 | 0.44929 |  | 4626 | 27.44 | 142.5064 | 6 | 99.8451
4627 | 53.84 | 152.1976 | 84.8813 | 112.1554 | 0.45302 |  | 4627 | 34.7 | 152.1976 | 5.7321 | 112.1554
4628 | 53.81 | 129.0421 | 25.5788 | 107.3892 | 0.46449 |  | 4628 | 37.11 | 129.0421 | 5 | 107.3892
4629 | 48.21 | 100.7236 | 17.7226 | 85.5551 | 0.46821 |  | 4629 | 31.48 | 100.7236 | 4 | 85.5551
4630 | 43.88 | 94.9706 | 51.7735 | 69.0162 | 0.47465 |  | 4630 | 30.02 | 94.9706 | 3 | 69.0162
4631 | 41.42 | 75.6715 | 75.4528 | 53.9503 | 0.47382 |  | 4631 | 41.31 | 75.6715 | 2.2679 | 53.9503
4632 | 41.05 | 38.9198 | 44.1592 | 30.9526 | 0.45926 |  | 4632 | 42.73 | 38.9198 | 2 | 30.9526
4633 | 38.38 | 34.2686 | 34.3692 | 32.7289 | 0.44198 |  | 4633 | 36.78 | 34.2686 | 2.2679 | 32.7289
4634 | 36.87 | 32.4992 | 36.1708 | 6.1571 | 0.43883 |  | 4634 | 26.61 | 32.4992 | 3 | 6.1571
4635 | 36.14 | 30.8454 | 27.7854 | 18.4548 | 0.43698 |  | 4635 | 26.31 | 30.8454 | 4 | 18.4548
4636 | 37.08 | 29.5322 | 28.2 | 38.1469 | 0.43749 |  | 4636 | 22.59 | 29.5322 | 5 | 38.1469
4637 | 35.38 | 28.6809 | 18.8793 | 79.1511 | 0.44061 |  | 4637 | 22.58 | 28.6809 | 5.7321 | 79.1511
4638 | 36.1 | 28.4513 | 24.5264 | 103.2027 | 0.43841 |  | 4638 | 24.51 | 28.4513 | 6 | 103.2027
4639 | 37.79 | 39.4716 | 24.0674 | 119.8479 | 0.4311 |  | 4639 | 28.53 | 39.4716 | 5.7321 | 119.8479
4640 | 38.46 | 55.642 | 44.1882 | 133.6729 | 0.42545 |  | 4640 | 37.31 | 55.642 | 5 | 133.6729
4641 | 39.83 | 44.4361 | 32.5513 | 117.3344 | 0.41923 |  | 4641 | 36.25 | 44.4361 | 4 | 117.3344
4642 | 39.82 | 43.8415 | 50.7906 | 85.0404 | 0.41692 |  | 4642 | 50 | 43.8415 | 3 | 85.0404
4643 | 39 | 46.3032 | 91.0388 | 64.6871 | 0.41689 |  | 4643 | 50.03 | 46.3032 | 2.2679 | 64.6871
4644 | 37.87 | 48.8227 | 94.652 | 90.7202 | 0.4174 |  | 4644 | 55.51 | 48.8227 | 2 | 90.7202
4645 | 34.7 | 51.3605 | 30.0209 | 70.3604 | 0.42015 |  | 4645 | 52.19 | 51.3605 | 2.2679 | 70.3604
4646 | 33.94 | 54.1881 | 46.7304 | 63.4861 | 0.41206 |  | 4646 | 49.92 | 54.1881 | 3 | 63.4861
4647 | 33.51 | 58.552 | 38.4104 | 58.2493 | 0.40589 |  | 4647 | 45.2 | 58.552 | 4 | 58.2493
4648 | 33.56 | 75.8863 | 29.7366 | 73.446 | 0.40448 |  | 4648 | 35.05 | 75.8863 | 5 | 73.446
4649 | 34.71 | 95.7124 | 48.1429 | 78.8013 | 0.40855 |  | 4649 | 36 | 95.7124 | 5.7321 | 78.8013
4650 | 36.91 | 135.676 | 39.0719 | 103.5987 | 0.40491 |  | 4650 | 39.9 | 135.676 | 6 | 103.5987
4651 | 37.98 | 149.434 | 35.9584 | 124.3577 | 0.40851 |  | 4651 | 45.5 | 149.434 | 5.7321 | 124.3577
4652 | 37.79 | 129.1508 | 33.727 | 92.1537 | 0.4105 |  | 4652 | 46.77 | 129.1508 | 5 | 92.1537
4653 | 37.72 | 97.073 | 57.141 | 90.6257 | 0.41548 |  | 4653 | 33.06 | 97.073 | 4 | 90.6257
4654 | 41.2 | 95.2593 | 101.663 | 75.8827 | 0.42126 |  | 4654 | 33.67 | 95.2593 | 3 | 75.8827
4655 | 38.17 | 78.1816 | 62.033 | 50.236 | 0.42525 |  | 4655 | 37.88 | 78.1816 | 2.2679 | 50.236
4656 | 35.85 | 39.8234 | 26.1913 | 25.5077 | 0.42175 |  | 4656 | 39.94 | 39.8234 | 2 | 25.5077
4657 | 35.04 | 34.1272 | 28.524 | 28.3499 | 0.4237 |  | 4657 | 27.95 | 34.1272 | 2.2679 | 28.3499
4658 | 33.77 | 32.5778 | 18.9235 | 6.8589 | 0.41972 |  | 4658 | 27.16 | 32.5778 | 3 | 6.8589
4659 | 32.69 | 31.0261 | 228.5838 | 22.2283 | 0.41232 |  | 4659 | 26.05 | 31.0261 | 4 | 22.2283
4660 | 32.15 | 29.6249 | 28.1392 | 49.5579 | 0.41438 |  | 4660 | 25 | 29.6249 | 5 | 49.5579
4661 | 32.14 | 28.5811 | 34.4218 | 85.321 | 0.41217 |  | 4661 | 25.1 | 28.5811 | 5.7321 | 85.321
4662 | 32.31 | 28.3391 | 70.7324 | 126.8507 | 0.41201 |  | 4662 | 26.18 | 28.3391 | 6 | 126.8507
4663 | 36.41 | 38.4996 | 76.4194 | 163.0284 | 0.40709 |  | 4663 | 31.85 | 38.4996 | 5.7321 | 163.0284
4664 | 37.24 | 52.7732 | 56.0542 | 124.431 | 0.40891 |  | 4664 | 34.94 | 52.7732 | 5 | 124.431
4665 | 38 | 44.2083 | 37.7691 | 102.382 | 0.40696 |  | 4665 | 40.42 | 44.2083 | 4 | 102.382
4666 | 38.68 | 43.6857 | 46.6953 | 89.9575 | 0.40727 |  | 4666 | 50.35 | 43.6857 | 3 | 89.9575
4667 | 40 | 44.9264 | 42.1937 | 63.7093 | 0.40684 |  | 4667 | 52.84 | 44.9264 | 2.2679 | 63.7093
4668 | 36.43 | 47.986 | 48.6637 | 85.5836 | 0.40838 |  | 4668 | 51.02 | 47.986 | 2 | 85.5836
4669 | 34.04 | 52.4602 | 43.5085 | 93.5022 | 0.40604 |  | 4669 | 48.03 | 52.4602 | 2.2679 | 93.5022
4670 | 33.71 | 55.0265 | 45.4013 | 57.5836 | 0.40271 |  | 4670 | 43.57 | 55.0265 | 3 | 57.5836
4671 | 32.04 | 55.1808 | 45.274 | 66.0039 | 0.40347 |  | 4671 | 39.57 | 55.1808 | 4 | 66.0039
4672 | 34.01 | 73.3722 | 37.6363 | 65.8653 | 0.4053 |  | 4672 | 34.59 | 73.3722 | 5 | 65.8653
4673 | 37.97 | 87.2094 | 35.8243 | 89.2677 | 0.39914 |  | 4673 | 31.94 | 87.2094 | 5.7321 | 89.2677
4674 | 39.37 | 127.3343 | 42.4339 | 98.6252 | 0.40133 |  | 4674 | 32.94 | 127.3343 | 6 | 98.6252
4675 | 40.96 | 134.217 | 42.8421 | 119.9012 | 0.41462 |  | 4675 | 34.22 | 134.217 | 5.7321 | 119.9012
4676 | 40.85 | 119.1603 | 23.8915 | 110.5632 | 0.42957 |  | 4676 | 35.06 | 119.1603 | 5 | 110.5632
4677 | 39.72 | 93.642 | 25.3396 | 74.6763 | 0.43861 |  | 4677 | 33.01 | 93.642 | 4 | 74.6763
4678 | 43.72 | 92.5459 | 14.1065 | 75.5324 | 0.44439 |  | 4678 | 30.81 | 92.5459 | 3 | 75.5324
4679 | 39.11 | 75.3977 | 22.1088 | 48.8431 | 0.44206 |  | 4679 | 39 | 75.3977 | 2.2679 | 48.8431
4680 | 37.8 | 39.5913 | 25.1893 | 24.5421 | 0.43784 |  | 4680 | 36.47 | 39.5913 | 2 | 24.5421
4681 | 36.47 | 33.7213 | 22.3337 | 33.1554 | 0.43789 |  | 4681 | 43.69 | 33.7213 | 2.2679 | 33.1554
4682 | 36.36 | 32.2645 | 29.5244 | 7.1333 | 0.4389 |  | 4682 | 39.49 | 32.2645 | 3 | 7.1333
4683 | 34.91 | 30.7028 | 27.1882 | 19.9091 | 0.43826 |  | 4683 | 33.24 | 30.7028 | 4 | 19.9091
4684 | 34.73 | 29.3217 | 29.2559 | 53.896 | 0.43851 |  | 4684 | 22.55 | 29.3217 | 5 | 53.896
4685 | 36.75 | 28.5131 | 23.0164 | 90.6095 | 0.43691 |  | 4685 | 22 | 28.5131 | 5.7321 | 90.6095
4686 | 44.4 | 28.0111 | 30.5812 | 132.2486 | 0.44622 |  | 4686 | 22.52 | 28.0111 | 6 | 132.2486
4687 | 49.78 | 27.6951 | 29.0708 | 162.1471 | 0.44888 |  | 4687 | 24.06 | 27.6951 | 5.7321 | 162.1471
4688 | 50.06 | 29.6786 | 44.6428 | 141.8433 | 0.44494 |  | 4688 | 29.42 | 29.6786 | 5 | 141.8433
4689 | 47.94 | 48.7089 | 37.1644 | 84.4185 | 0.44225 |  | 4689 | 32.05 | 48.7089 | 4 | 84.4185
4690 | 46.2 | 68.9752 | 36.9607 | 90.9247 | 0.44137 |  | 4690 | 40.3 | 68.9752 | 3 | 90.9247
4691 | 45.3 | 74.5972 | 37.7968 | 78.0006 | 0.44116 |  | 4691 | 40.3 | 74.5972 | 2.2679 | 78.0006
4692 | 44 | 75.3854 | 39.9941 | 76.5748 | 0.43695 |  | 4692 | 37.44 | 75.3854 | 2 | 76.5748
4693 | 41 | 81.366 | 42.9975 | 68.2566 | 0.43102 |  | 4693 | 34.94 | 81.366 | 2.2679 | 68.2566
4694 | 39.19 | 76.2324 | 77.8782 | 59.0249 | 0.42379 |  | 4694 | 26 | 76.2324 | 3 | 59.0249
4695 | 39.03 | 74.7601 | 108.7024 | 57.7684 | 0.4233 |  | 4695 | 25.61 | 74.7601 | 4 | 57.7684
4696 | 38.49 | 71.7236 | 78.5453 | 59.838 | 0.42026 |  | 4696 | 25.7 | 71.7236 | 5 | 59.838
4697 | 39.02 | 76.383 | 53.5231 | 86.9924 | 0.42742 |  | 4697 | 25.7 | 76.383 | 5.7321 | 86.9924
4698 | 42.56 | 109.4725 | 34.5548 | 96.373 | 0.43474 |  | 4698 | 25.7 | 109.4725 | 6 | 96.373
4699 | 45.94 | 135.2442 | 55.8292 | 101.1202 | 0.43998 |  | 4699 | 26.52 | 135.2442 | 5.7321 | 101.1202
4700 | 44.08 | 134.1581 | 28.8598 | 91.9421 | 0.44318 |  | 4700 | 28.95 | 134.1581 | 5 | 91.9421
4701 | 43.44 | 97.7244 | 26.8624 | 89.796 | 0.44994 |  | 4701 | 33.39 | 97.7244 | 4 | 89.796
4702 | 44.6 | 92.9305 | 30.7093 | 75.1821 | 0.45532 |  | 4702 | 31.46 | 92.9305 | 3 | 75.1821
4703 | 38.47 | 88.4125 | 26.0919 | 48.286 | 0.45337 |  | 4703 | 41.86 | 88.4125 | 2.2679 | 48.286
4704 | 38.04 | 40.4945 | 15.6266 | 26.2587 | 0.45198 |  | 4704 | 43.7 | 40.4945 | 2 | 26.2587
4705 | 36.27 | 34.1497 | 22.8844 | 25.7338 | 0.44388 |  | 4705 | 26.58 | 34.1497 | 2.2679 | 25.7338
4706 | 34.93 | 32.4463 | 23.4858 | 5.7104 | 0.44685 |  | 4706 | 25.15 | 32.4463 | 3 | 5.7104
4707 | 33.89 | 30.9159 | 29.9283 | 17.8455 | 0.44805 |  | 4707 | 24.6 | 30.9159 | 4 | 17.8455
4708 | 33.13 | 29.529 | 35.362 | 41.5419 | 0.44887 |  | 4708 | 21.55 | 29.529 | 5 | 41.5419
4709 | 35.11 | 28.6048 | 44.7792 | 75.0085 | 0.45418 |  | 4709 | 20.94 | 28.6048 | 5.7321 | 75.0085
4710 | 39.21 | 28.0186 | 101.2738 | 143.0444 | 0.46143 |  | 4710 | 23.49 | 28.0186 | 6 | 143.0444
4711 | 46.95 | 27.8491 | 110.9519 | 129.2477 | 0.46508 |  | 4711 | 23.44 | 27.8491 | 5.7321 | 129.2477
4712 | 49.14 | 30.1069 | 106.3658 | 155.9071 | 0.46781 |  | 4712 | 29.08 | 30.1069 | 5 | 155.9071
4713 | 47.95 | 49.113 | 88.3456 | 92.933 | 0.46759 |  | 4713 | 30.08 | 49.113 | 4 | 92.933
4714 | 47.13 | 69.7609 | 71.8736 | 83.2671 | 0.46786 |  | 4714 | 33.15 | 69.7609 | 3 | 83.2671
4715 | 46.92 | 74.8541 | 118.4989 | 80.4076 | 0.46864 |  | 4715 | 36.96 | 74.8541 | 2.2679 | 80.4076
4716 | 42.07 | 76.2062 | 117.4387 | 63.2987 | 0.46919 |  | 4716 | 39.94 | 76.2062 | 2 | 63.2987
4717 | 39.9 | 80.8492 | 68.7479 | 92.8009 | 0.46081 |  | 4717 | 40.4 | 80.8492 | 2.2679 | 92.8009
4718 | 39.46 | 81.5473 | 47.6313 | 76.5951 | 0.45267 |  | 4718 | 40.4 | 81.5473 | 3 | 76.5951
4719 | 39.04 | 79.4152 | 53.2358 | 66.7854 | 0.44916 |  | 4719 | 40.4 | 79.4152 | 4 | 66.7854
4720 | 39.3 | 75.7521 | 43.3847 | 57.0418 | 0.46304 |  | 4720 | 40.4 | 75.7521 | 5 | 57.0418
4721 | 45.38 | 79.2144 | 33.5209 | 77.967 | 0.47379 |  | 4721 | 24.66 | 79.2144 | 5.7321 | 77.967
4722 | 48.81 | 111.1449 | 49.4846 | 103.0356 | 0.47862 |  | 4722 | 27.71 | 111.1449 | 6 | 103.0356
4723 | 52.64 | 138.3903 | 35.7671 | 113.2164 | 0.48365 |  | 4723 | 31.92 | 138.3903 | 5.7321 | 113.2164
4724 | 51.96 | 141.1864 | 30.4011 | 96.4915 | 0.48849 |  | 4724 | 34.67 | 141.1864 | 5 | 96.4915
4725 | 49.19 | 104.1611 | 29.6932 | 86.1082 | 0.4918 |  | 4725 | 32.73 | 104.1611 | 4 | 86.1082
4726 | 49 | 93.8547 | 18.8458 | 68.2454 | 0.49501 |  | 4726 | 32.25 | 93.8547 | 3 | 68.2454
4727 | 45.19 | 89.3152 | 34.9186 | 45.686 | 0.4962 |  | 4727 | 34.94 | 89.3152 | 2.2679 | 45.686
4728 | 40.02 | 40.9043 | 428.9361 | 26.3928 | 0.48851 |  | 4728 | 35.98 | 40.9043 | 2 | 26.3928
4729 | 38.87 | 33.0495 | 27.0097 | 25.7338 | 0.47937 |  | 4729 | 27.53 | 33.0495 | 2.2679 | 25.7338
4730 | 38.12 | 31.6601 | 22.648 | 5.2574 | 0.46831 |  | 4730 | 23.82 | 31.6601 | 3 | 5.2574
4731 | 37.28 | 30.3366 | 28.6753 | 17.2755 | 0.46772 |  | 4731 | 23 | 30.3366 | 4 | 17.2755
4732 | 37.9 | 29.1032 | 33.1305 | 51.5855 | 0.47722 |  | 4732 | 22 | 29.1032 | 5 | 51.5855
4733 | 39.1 | 28.3064 | 39.8033 | 102.8612 | 0.48805 |  | 4733 | 21.91 | 28.3064 | 5.7321 | 102.8612
4734 | 44.03 | 27.8532 | 86.2308 | 127.1077 | 0.49639 |  | 4734 | 21.79 | 27.8532 | 6 | 127.1077
4735 | 53.78 | 39.6451 | 78.7351 | 137.4726 | 0.48717 |  | 4735 | 22.01 | 39.6451 | 5.7321 | 137.4726
4736 | 54.68 | 55.184 | 67.134 | 131.9317 | 0.47999 |  | 4736 | 22.47 | 55.184 | 5 | 131.9317
4737 | 50.23 | 43.7527 | 61.7501 | 106.5355 | 0.47592 |  | 4737 | 23.79 | 43.7527 | 4 | 106.5355
4738 | 48.78 | 41.4429 | 72.7892 | 68.1129 | 0.47392 |  | 4738 | 32.4 | 41.4429 | 3 | 68.1129
4739 | 47.7 | 42.826 | 108.5776 | 74.3149 | 0.46996 |  | 4739 | 33.76 | 42.826 | 2.2679 | 74.3149
4740 | 45 | 47.8077 | 117.4841 | 83.0548 | 0.46803 |  | 4740 | 33.22 | 47.8077 | 2 | 83.0548
4741 | 43.14 | 48.4289 | 100.5406 | 74.4121 | 0.46621 |  | 4741 | 29.11 | 48.4289 | 2.2679 | 74.4121
4742 | 40.52 | 50.0105 | 28.0363 | 79.7522 | 0.4665 |  | 4742 | 24.71 | 50.0105 | 3 | 79.7522
4743 | 40.55 | 54.7462 | 49.7693 | 48.5712 | 0.46922 |  | 4743 | 24.4 | 54.7462 | 4 | 48.5712
4744 | 41.6 | 68.7529 | 45.1252 | 69.5935 | 0.47504 |  | 4744 | 23.3 | 68.7529 | 5 | 69.5935
4745 | 48 | 93.4128 | 30.9808 | 61.7365 | 0.48208 |  | 4745 | 23.78 | 93.4128 | 5.7321 | 61.7365
4746 | 52 | 128.5099 | 44.7207 | 87.646 | 0.48817 |  | 4746 | 25.38 | 128.5099 | 6 | 87.646
4747 | 54.01 | 138.2608 | 37.3323 | 116.1874 | 0.49518 |  | 4747 | 30.3 | 138.2608 | 5.7321 | 116.1874
4748 | 54.82 | 130.4016 | 25.6313 | 103.5803 | 0.50139 |  | 4748 | 35 | 130.4016 | 5 | 103.5803
4749 | 53.88 | 98.5477 | 30.8721 | 97.7246 | 0.50364 |  | 4749 | 30.61 | 98.5477 | 4 | 97.7246
4750 | 50.64 | 96.403 | 27.3589 | 78.9657 | 0.50419 |  | 4750 | 30.99 | 96.403 | 3 | 78.9657
4751 | 45.9 | 75.9699 | 30.8983 | 46.9395 | 0.50618 |  | 4751 | 32.16 | 75.9699 | 2.2679 | 46.9395
4752 | 40.47 | 38.4805 | 22.3561 | 22.2623 | 0.49359 |  | 4752 | 40.68 | 38.4805 | 2 | 22.2623
4753 | 39 | 34.0551 | 29.8457 | 28.1793 | 0.4723 |  | 4753 | 30 | 34.0551 | 2.2679 | 28.1793
4754 | 36.01 | 32.4294 | 30.9315 | 7.4969 | 0.46267 |  | 4754 | 24.3 | 32.4294 | 3 | 7.4969
4755 | 34.33 | 30.8256 | 30.8045 | 21.5207 | 0.45777 |  | 4755 | 22.14 | 30.8256 | 4 | 21.5207
4756 | 32.57 | 29.4103 | 31.144 | 50.8782 | 0.45421 |  | 4756 | 20.17 | 29.4103 | 5 | 50.8782
4757 | 33.52 | 28.5893 | 85.1475 | 95.1048 | 0.46335 |  | 4757 | 20.01 | 28.5893 | 5.7321 | 95.1048
4758 | 41.19 | 28.5671 | 101.9821 | 124.0232 | 0.47832 |  | 4758 | 19.4 | 28.5671 | 6 | 124.0232
4759 | 49.47 | 39.4135 | 85.4481 | 173.8969 | 0.48524 |  | 4759 | 19.01 | 39.4135 | 5.7321 | 173.8969
4760 | 48.96 | 54.2142 | 79.2032 | 146.933 | 0.47982 |  | 4760 | 20.96 | 54.2142 | 5 | 146.933
4761 | 47.5 | 44.6044 | 96.8037 | 87.222 | 0.47739 |  | 4761 | 21.13 | 44.6044 | 4 | 87.222
4762 | 44.91 | 44.6547 | 73.3503 | 88.1841 | 0.47407 |  | 4762 | 22.3 | 44.6547 | 3 | 88.1841
4763 | 43.49 | 48.2626 | 104.3608 | 61.7536 | 0.46791 |  | 4763 | 24.26 | 48.2626 | 2.2679 | 61.7536
4764 | 40.41 | 50.4848 | 102.8932 | 91.1154 | 0.46561 |  | 4764 | 24.69 | 50.4848 | 2 | 91.1154
4765 | 39.25 | 52.3752 | 98.2304 | 71.7629 | 0.46556 |  | 4765 | 24.87 | 52.3752 | 2.2679 | 71.7629
4766 | 38.99 | 55.0089 | 64.7975 | 71.1044 | 0.47006 |  | 4766 | 22.44 | 55.0089 | 3 | 71.1044
4767 | 39.72 | 60.8951 | 91.6164 | 50.1341 | 0.47172 |  | 4767 | 23.8 | 60.8951 | 4 | 50.1341
4768 | 39.21 | 75.8876 | 89.4052 | 74.0052 | 0.46426 |  | 4768 | 21.42 | 75.8876 | 5 | 74.0052
4769 | 47.72 | 93.2555 | 102.8333 | 90.7087 | 0.46779 |  | 4769 | 22.99 | 93.2555 | 5.7321 | 90.7087
4770 | 49.84 | 141.8294 | 110.1777 | 79.5758 | 0.47544 |  | 4770 | 24.3 | 141.8294 | 6 | 79.5758
4771 | 54.5 | 149.0793 | 69.541 | 120.9623 | 0.48339 |  | 4771 | 26.22 | 149.0793 | 5.7321 | 120.9623
4772 | 53.62 | 115.4783 | 53.597 | 123.0479 | 0.4913 |  | 4772 | 34.21 | 115.4783 | 5 | 123.0479
4773 | 49.16 | 96.0524 | 111.3582 | 95.7885 | 0.49812 |  | 4773 | 42.44 | 96.0524 | 4 | 95.7885
4774 | 48.01 | 93.7743 | 92.3942 | 74.5515 | 0.50198 |  | 4774 | 37.38 | 93.7743 | 3 | 74.5515
4775 | 43.73 | 76.4852 | 27.3002 | 41.9717 | 0.50599 |  | 4775 | 57.24 | 76.4852 | 2.2679 | 41.9717
4776 | 37.86 | 39.6713 | 31.5567 | 23.8447 | 0.49112 |  | 4776 | 39.94 | 39.6713 | 2 | 23.8447
4777 | 35.87 | 34.3069 | 25.0786 | 23.5443 | 0.47518 |  | 4777 | 39.09 | 34.3069 | 2.2679 | 23.5443
4778 | 35.35 | 32.7168 | 32.2415 | 7.1715 | 0.47275 |  | 4778 | 32.93 | 32.7168 | 3 | 7.1715
4779 | 33.07 | 31.0236 | 31.8238 | 18.042 | 0.47356 |  | 4779 | 24.75 | 31.0236 | 4 | 18.042
4780 | 33.41 | 29.6571 | 41.7071 | 51.3026 | 0.47696 |  | 4780 | 22.66 | 29.6571 | 5 | 51.3026
4781 | 35 | 28.6476 | 67.3668 | 95.1048 | 0.49481 |  | 4781 | 23.02 | 28.6476 | 5.7321 | 95.1048
4782 | 42.77 | 28.2528 | 68.4197 | 128.65 | 0.5089 |  | 4782 | 24.6 | 28.2528 | 6 | 128.65
4783 | 51.84 | 40.0376 | 74.0152 | 158.3285 | 0.50646 |  | 4783 | 28.82 | 40.0376 | 5.7321 | 158.3285
4784 | 52.33 | 55.3194 | 110.708 | 119.743 | 0.4994 |  | 4784 | 33.09 | 55.3194 | 5 | 119.743
4785 | 49.43 | 42.9514 | 100.3959 | 108.4045 | 0.49652 |  | 4785 | 35.39 | 42.9514 | 4 | 108.4045
4786 | 47.86 | 41.304 | 95.492 | 88.5065 | 0.49189 |  | 4786 | 38.7 | 41.304 | 3 | 88.5065
4787 | 47.03 | 42.3739 | 113.5528 | 88.0797 | 0.48861 |  | 4787 | 46.67 | 42.3739 | 2.2679 | 88.0797
4788 | 44.01 | 45.9749 | 107.1982 | 94.1183 | 0.48762 |  | 4788 | 34.94 | 45.9749 | 2 | 94.1183
4789 | 39.59 | 47.988 | 106.9798 | 79.9443 | 0.48774 |  | 4789 | 43.92 | 47.988 | 2.2679 | 79.9443
4790 | 39.4 | 50.3495 | 110.1953 | 59.9858 | 0.48624 |  | 4790 | 39.39 | 50.3495 | 3 | 59.9858
4791 | 39.2 | 55.7682 | 99.7645 | 58.1291 | 0.48668 |  | 4791 | 35 | 55.7682 | 4 | 58.1291
4792 | 39.36 | 74.2167 | 87.2373 | 56.4826 | 0.48901 |  | 4792 | 43.83 | 74.2167 | 5 | 56.4826
4793 | 46.21 | 95.2037 | 63.1233 | 82.1384 | 0.49412 |  | 4793 | 44.03 | 95.2037 | 5.7321 | 82.1384
4794 | 51.15 | 135.2366 | 67.0506 | 84.5493 | 0.49493 |  | 4794 | 48.78 | 135.2366 | 6 | 84.5493
4795 | 51.56 | 147.4558 | 25.3646 | 104.5156 | 0.49407 |  | 4795 | 48.95 | 147.4558 | 5.7321 | 104.5156
4796 | 51.61 | 128.9942 | 35.8571 | 100.512 | 0.49993 |  | 4796 | 39.39 | 128.9942 | 5 | 100.512
4797 | 49.16 | 97.3956 | 224.3932 | 74.4919 | 0.50228 |  | 4797 | 40 | 97.3956 | 4 | 74.4919
4798 | 50.6 | 97.3615 | 19.4153 | 60.3979 | 0.50176 |  | 4798 | 38.61 | 97.3615 | 3 | 60.3979
4799 | 44.92 | 75.2417 | 19.3406 | 48.5181 | 0.49869 |  | 4799 | 35.9 | 75.2417 | 2.2679 | 48.5181
4800 | 41.21 | 39.6028 | 31.01 | 29.5042 | 0.49552 |  | 4800 | 30.45 | 39.6028 | 2 | 29.5042
4801 | 38.08 | 33.4565 | 26.294 | 25.3926 | 0.47625 |  | 4801 | 27.59 | 33.4565 | 2.2679 | 25.3926
4802 | 36.81 | 31.9168 | 37.2776 | 6.4059 | 0.45077 |  | 4802 | 27.09 | 31.9168 | 3 | 6.4059
4803 | 35.54 | 30.4784 | 57.3606 | 19.6733 | 0.43079 |  | 4803 | 26.41 | 30.4784 | 4 | 19.6733
4804 | 34.32 | 29.1269 | 89.2159 | 43.8052 | 0.41517 |  | 4804 | 25.89 | 29.1269 | 5 | 43.8052
4805 | 33.98 | 28.3066 | 100.1762 | 74.5678 | 0.39849 |  | 4805 | 25.61 | 28.3066 | 5.7321 | 74.5678
4806 | 34.91 | 28.39 | 76.3464 | 103.8453 | 0.39719 |  | 4806 | 26.14 | 28.39 | 6 | 103.8453
4807 | 35.79 | 39.6733 | 81.6527 | 125.5759 | 0.39961 |  | 4807 | 31 | 39.6733 | 5.7321 | 125.5759
4808 | 36.66 | 54.5413 | 102.8503 | 151.6209 | 0.40585 |  | 4808 | 36.99 | 54.5413 | 5 | 151.6209
4809 | 36.8 | 44.2781 | 102.998 | 84.73 | 0.40422 |  | 4809 | 40.01 | 44.2781 | 4 | 84.73
4810 | 35.04 | 43.1718 | 115.1271 | 88.3453 | 0.40226 |  | 4810 | 40.25 | 43.1718 | 3 | 88.3453
4811 | 32.91 | 45.2809 | 83.413 | 66.3419 | 0.39382 |  | 4811 | 54 | 45.2809 | 2.2679 | 66.3419
4812 | 31.63 | 47.1432 | 83.2631 | 93.4071 | 0.3958 |  | 4812 | 50.03 | 47.1432 | 2 | 93.4071
4813 | 27.79 | 51.4028 | 81.6883 | 91.0088 | 0.39712 |  | 4813 | 44.85 | 51.4028 | 2.2679 | 91.0088
4814 | 27.98 | 52.1613 | 50.6079 | 78.7227 | 0.40203 |  | 4814 | 45.33 | 52.1613 | 3 | 78.7227
4815 | 28.81 | 58.4888 | 53.5929 | 50.0139 | 0.40923 |  | 4815 | 43.53 | 58.4888 | 4 | 50.0139
4816 | 31.83 | 73.6885 | 43.1865 | 65.8031 | 0.4064 |  | 4816 | 41.7 | 73.6885 | 5 | 65.8031
4817 | 35.54 | 95.936 | 35.9751 | 69.245 | 0.39906 |  | 4817 | 50.92 | 95.936 | 5.7321 | 69.245
4818 | 36.89 | 140.9674 | 42.507 | 81.4526 | 0.39647 |  | 4818 | 50.03 | 140.9674 | 6 | 81.4526
4819 | 38.38 | 151.1969 | 39.8861 | 120.5378 | 0.39325 |  | 4819 | 45 | 151.1969 | 5.7321 | 120.5378
4820 | 37.53 | 119.8061 | 28.4333 | 97.338 | 0.39556 |  | 4820 | 44 | 119.8061 | 5 | 97.338
4821 | 37.72 | 99.7778 | 26.8766 | 103.2561 | 0.40277 |  | 4821 | 37.03 | 99.7778 | 4 | 103.2561
4822 | 39.2 | 98.1332 | 16.9483 | 65.1625 | 0.40788 |  | 4822 | 36.35 | 98.1332 | 3 | 65.1625
4823 | 37.29 | 77.4704 | 23.1711 | 53.5789 | 0.41034 |  | 4823 | 30.12 | 77.4704 | 2.2679 | 53.5789
4824 | 34.5 | 39.162 | 28.9867 | 30.9258 | 0.40899 |  | 4824 | 25.45 | 39.162 | 2 | 30.9258
4825 | 32.4 | 33.0894 | 31.8408 | 26.331 | 0.40689 |  | 4825 | 28.01 | 33.0894 | 2.2679 | 26.331
4826 | 31.98 | 31.744 | 25.8257 | 5.334 | 0.40472 |  | 4826 | 26.32 | 31.744 | 3 | 5.334
4827 | 30.27 | 30.3123 | 229.3561 | 22.9358 | 0.40673 |  | 4827 | 25.1 | 30.3123 | 4 | 22.9358
4828 | 30 | 29.0947 | 62.3281 | 52.1513 | 0.4132 |  | 4828 | 24.79 | 29.0947 | 5 | 52.1513
4829 | 30.03 | 28.343 | 82.0357 | 86.2906 | 0.41619 |  | 4829 | 24.83 | 28.343 | 5.7321 | 86.2906
4830 | 29.88 | 28.1803 | 84.8652 | 147.9282 | 0.41022 |  | 4830 | 25.85 | 28.1803 | 6 | 147.9282
4831 | 30.67 | 38.8595 | 83.0369 | 170.8126 | 0.40723 |  | 4831 | 29.35 | 38.8595 | 5.7321 | 170.8126
4832 | 31.02 | 53.7976 | 92.3189 | 135.0123 | 0.40258 |  | 4832 | 33.52 | 53.7976 | 5 | 135.0123
4833 | 31.01 | 44.6128 | 90.2966 | 108.1968 | 0.40508 |  | 4833 | 38.82 | 44.6128 | 4 | 108.1968
4834 | 29.69 | 43.2712 | 58.0914 | 72.3045 | 0.40047 |  | 4834 | 50.85 | 43.2712 | 3 | 72.3045
4835 | 30.13 | 44.7769 | 62.5398 | 60.174 | 0.39683 |  | 4835 | 56.07 | 44.7769 | 2.2679 | 60.174
4836 | 29.29 | 48.4288 | 82.3252 | 64.326 | 0.39212 |  | 4836 | 52.99 | 48.4288 | 2 | 64.326
4837 | 25 | 51.9804 | 47.2822 | 93.1126 | 0.39035 |  | 4837 | 50.99 | 51.9804 | 2.2679 | 93.1126
4838 | 26.2 | 53.7018 | 31.3977 | 65.6824 | 0.39472 |  | 4838 | 45.25 | 53.7018 | 3 | 65.6824
4839 | 20.86 | 58.8876 | 48.8165 | 57.8887 | 0.39549 |  | 4839 | 45.49 | 58.8876 | 4 | 57.8887
4840 | 28.04 | 71.1664 | 44.9683 | 69.2828 | 0.40417 |  | 4840 | 45.18 | 71.1664 | 5 | 69.2828
4841 | 32.02 | 89.0634 | 40.6488 | 85.9306 | 0.42234 |  | 4841 | 46.97 | 89.0634 | 5.7321 | 85.9306
4842 | 35.9 | 123.5049 | 41.1596 | 103.411 | 0.4433 |  | 4842 | 53.74 | 123.5049 | 6 | 103.411
4843 | 42.42 | 138.5182 | 49.9598 | 107.5928 | 0.46535 |  | 4843 | 53.23 | 138.5182 | 5.7321 | 107.5928
4844 | 43.6 | 124.8159 | 23.7777 | 93.8465 | 0.48072 |  | 4844 | 48.53 | 124.8159 | 5 | 93.8465
4845 | 44.92 | 94.8508 | 33.9495 | 109.0643 | 0.48991 |  | 4845 | 39.94 | 94.8508 | 4 | 109.0643
4846 | 46.62 | 92.6246 | 27.8331 | 77.0739 | 0.49247 |  | 4846 | 31.96 | 92.6246 | 3 | 77.0739
4847 | 40 | 73.8858 | 32.5373 | 48.7503 | 0.49175 |  | 4847 | 28.94 | 73.8858 | 2.2679 | 48.7503
4848 | 37.47 | 38.8398 | 23.3942 | 30.8989 | 0.4828 |  | 4848 | 35.88 | 38.8398 | 2 | 30.8989
4849 | 35.11 | 35.59 | 27.294 | 32.1886 | 0.4753 |  | 4849 | 42.65 | 35.59 | 2.2679 | 32.1886
4850 | 33.14 | 33.7422 | 28.8432 | 5.602 | 0.47639 |  | 4850 | 26.46 | 33.7422 | 3 | 5.602
4851 | 30.07 | 32.0682 | 19.4964 | 17.8062 | 0.46769 |  | 4851 | 25.9 | 32.0682 | 4 | 17.8062
4852 | 28.15 | 30.5051 | 28.9616 | 44.041 | 0.45821 |  | 4852 | 25.52 | 30.5051 | 5 | 44.041
4853 | 30.98 | 29.1788 | 35.5941 | 72.2761 | 0.45749 |  | 4853 | 25.55 | 29.1788 | 5.7321 | 72.2761
4854 | 37.91 | 28.2685 | 79.4122 | 107.8295 | 0.45841 |  | 4854 | 27.49 | 28.2685 | 6 | 107.8295
4855 | 46.95 | 27.687 | 83.1468 | 131.7445 | 0.46314 |  | 4855 | 32.84 | 27.687 | 5.7321 | 131.7445
4856 | 48 | 29.7664 | 99.5065 | 149.344 | 0.46156 |  | 4856 | 36.61 | 29.7664 | 5 | 149.344
4857 | 43.97 | 48.1217 | 99.4791 | 96.3596 | 0.45631 |  | 4857 | 39.16 | 48.1217 | 4 | 96.3596
4858 | 43.36 | 67.6598 | 60.8565 | 76.9797 | 0.44938 |  | 4858 | 52.44 | 67.6598 | 3 | 76.9797
4859 | 40.78 | 72.1439 | 45.8911 | 68.8241 | 0.43832 |  | 4859 | 52.17 | 72.1439 | 2.2679 | 68.8241
4860 | 35.27 | 74.2684 | 37.9622 | 70.9641 | 0.42661 |  | 4860 | 49.65 | 74.2684 | 2 | 70.9641
4861 | 35.92 | 80.152 | 58.0062 | 88.0479 | 0.41729 |  | 4861 | 50.03 | 80.152 | 2.2679 | 88.0479
4862 | 35.9 | 77.4444 | 34.0994 | 70.2808 | 0.42471 |  | 4862 | 48.79 | 77.4444 | 3 | 70.2808
4863 | 36.52 | 73.7677 | 46.7104 | 57.8285 | 0.43629 |  | 4863 | 46.79 | 73.7677 | 4 | 57.8285
4864 | 38.91 | 71.0966 | 53.15 | 69.9042 | 0.44772 |  | 4864 | 44.68 | 71.0966 | 5 | 69.9042
4865 | 44.98 | 78.4464 | 243.7475 | 78.8013 | 0.45617 |  | 4865 | 44.8 | 78.4464 | 5.7321 | 78.8013
4866 | 48.98 | 125.6929 | 41.8712 | 83.6109 | 0.46388 |  | 4866 | 50.12 | 125.6929 | 6 | 83.6109
4867 | 53.94 | 135.9579 | 45.7077 | 96.4515 | 0.47358 |  | 4867 | 55 | 135.9579 | 5.7321 | 96.4515
4868 | 53.34 | 131.4846 | 22.6042 | 104.7441 | 0.48528 |  | 4868 | 39.94 | 131.4846 | 5 | 104.7441
4869 | 50.59 | 96.3054 | 24.1959 | 81.4064 | 0.49266 |  | 4869 | 35.95 | 96.3054 | 4 | 81.4064
4870 | 51.87 | 92.0182 | 21.6397 | 78.195 | 0.49721 |  | 4870 | 36.18 | 92.0182 | 3 | 78.195
4871 | 43.36 | 89.7955 | 25.5077 | 39.4645 | 0.50234 |  | 4871 | 34.22 | 89.7955 | 2.2679 | 39.4645
4872 | 38.61 | 42.6465 | 30.4587 | 28.9677 | 0.49996 |  | 4872 | 31.14 | 42.6465 | 2 | 28.9677
4873 | 37.58 | 34.7741 | 24.815 | 29.3451 | 0.49218 |  | 4873 | 29.26 | 34.7741 | 2.2679 | 29.3451
4874 | 36.98 | 33.0986 | 29.8956 | 7.4969 | 0.48113 |  | 4874 | 27.24 | 33.0986 | 3 | 7.4969
4875 | 36.52 | 31.3952 | 32.7859 | 22.8179 | 0.47763 |  | 4875 | 27.1 | 31.3952 | 4 | 22.8179
4876 | 34.59 | 29.8562 | 27.2061 | 45.4084 | 0.48008 |  | 4876 | 26.56 | 29.8562 | 5 | 45.4084
4877 | 37.7 | 28.8769 | 54.781 | 102.6849 | 0.49553 |  | 4877 | 26.5 | 28.8769 | 5.7321 | 102.6849
4878 | 45.15 | 28.3018 | 102.6676 | 139.0602 | 0.50397 |  | 4878 | 28.06 | 28.3018 | 6 | 139.0602
4879 | 48.04 | 27.9416 | 62.7749 | 140.5569 | 0.50876 |  | 4879 | 32.36 | 27.9416 | 5.7321 | 140.5569
4880 | 50.98 | 29.9662 | 114.3933 | 112.9121 | 0.50267 |  | 4880 | 35.99 | 29.9662 | 5 | 112.9121
4881 | 49.65 | 49.4951 | 88.9271 | 85.8722 | 0.49882 |  | 4881 | 43.58 | 49.4951 | 4 | 85.8722
4882 | 46.4 | 68.9025 | 91.0109 | 79.8816 | 0.4945 |  | 4882 | 55 | 68.9025 | 3 | 79.8816
4883 | 43.18 | 73.8338 | 85.5736 | 66.6427 | 0.49647 |  | 4883 | 58.1 | 73.8338 | 2.2679 | 66.6427
4884 | 40.37 | 74.9547 | 119.3366 | 73.4929 | 0.48878 |  | 4884 | 58.71 | 74.9547 | 2 | 73.4929
4885 | 40.23 | 79.8206 | 102.5647 | 77.373 | 0.48317 |  | 4885 | 59.55 | 79.8206 | 2.2679 | 77.373
4886 | 39.61 | 82.614 | 42.696 | 56.005 | 0.48239 |  | 4886 | 57.98 | 82.614 | 3 | 56.005
4887 | 40.39 | 80.3678 | 42.3825 | 62.5173 | 0.4927 |  | 4887 | 54.7 | 80.3678 | 4 | 62.5173
4888 | 44.84 | 76.2474 | 47.7306 | 55.9855 | 0.49882 |  | 4888 | 43.08 | 76.2474 | 5 | 55.9855
4889 | 52.97 | 80.3224 | 54.6051 | 71.3687 | 0.49938 |  | 4889 | 42.45 | 80.3224 | 5.7321 | 71.3687
4890 | 57.71 | 122.3996 | 40.5992 | 76.5729 | 0.50151 |  | 4890 | 42.4 | 122.3996 | 6 | 76.5729
4891 | 62.82 | 135.9915 | 43.1382 | 93.4805 | 0.50687 |  | 4891 | 43.81 | 135.9915 | 5.7321 | 93.4805
4892 | 60.6 | 130.3747 | 33.8512 | 94.2697 | 0.50486 |  | 4892 | 40.5 | 130.3747 | 5 | 94.2697
4893 | 59.34 | 97.6392 | 25.8851 | 93.2993 | 0.50005 |  | 4893 | 33.26 | 97.6392 | 4 | 93.2993
4894 | 55 | 95.551 | 29.3082 | 80.4371 | 0.49405 |  | 4894 | 31.97 | 95.551 | 3 | 80.4371
4895 | 45.5 | 88.9994 | 26.3795 | 52.4181 | 0.48893 |  | 4895 | 36.87 | 88.9994 | 2.2679 | 52.4181
4896 | 42.25 | 41.4751 | 26.5829 | 25.8564 | 0.47276 |  | 4896 | 30.27 | 41.4751 | 2 | 25.8564
4897 | 39.65 | 35.6773 | 23.013 | 24.8523 | 0.45697 |  | 4897 | 31.8 | 35.6773 | 2.2679 | 24.8523
4898 | 38.48 | 33.8623 | 17.1591 | 5.5764 | 0.44853 |  | 4898 | 30.83 | 33.8623 | 3 | 5.5764
4899 | 36.92 | 31.9415 | 22.9771 | 16.7449 | 0.44806 |  | 4899 | 29.1 | 31.9415 | 4 | 16.7449
4900 | 36.6 | 30.3004 | 31.4537 | 52.7172 | 0.44963 |  | 4900 | 27.02 | 30.3004 | 5 | 52.7172
4901 | 38.24 | 29.1492 | 51.1985 | 99.2474 | 0.45571 |  | 4901 | 25.77 | 29.1492 | 5.7321 | 99.2474
4902 | 45.55 | 28.7155 | 89.6666 | 112.8418 | 0.4745 |  | 4902 | 25.65 | 28.7155 | 6 | 112.8418
4903 | 52.8 | 40.429 | 82.858 | 145.1099 | 0.47938 |  | 4903 | 26.22 | 40.429 | 5.7321 | 145.1099
4904 | 57.35 | 53.5519 | 85.1761 | 158.7198 | 0.48454 |  | 4904 | 30.32 | 53.5519 | 5 | 158.7198
4905 | 57.75 | 44.2102 | 85.1497 | 87.3259 | 0.48779 |  | 4905 | 35.12 | 44.2102 | 4 | 87.3259
4906 | 50.02 | 42.8553 | 42.0432 | 67.5487 | 0.49324 |  | 4906 | 46.18 | 42.8553 | 3 | 67.5487
4907 | 42.4 | 46.3762 | 39.8097 | 61.3023 | 0.4968 |  | 4907 | 53.02 | 46.3762 | 2.2679 | 61.3023
4908 | 39.55 | 48.5841 | 85.9825 | 67.329 | 0.49817 |  | 4908 | 54.12 | 48.5841 | 2 | 67.329
4909 | 40.51 | 49.9763 | 93.9568 | 87.8141 | 0.50019 |  | 4909 | 51.88 | 49.9763 | 2.2679 | 87.8141
4910 | 39.91 | 51.9524 | 48.0181 | 56.3482 | 0.49533 |  | 4910 | 44.53 | 51.9524 | 3 | 56.3482
4911 | 42.95 | 56.6813 | 46.7452 | 65.9438 | 0.49494 |  | 4911 | 36.74 | 56.6813 | 4 | 65.9438
4912 | 48.4 | 72.4966 | 38.6987 | 52.7543 | 0.49752 |  | 4912 | 34.74 | 72.4966 | 5 | 52.7543
4913 | 57.75 | 92.7787 | 44.2024 | 70.0035 | 0.50356 |  | 4913 | 27.72 | 92.7787 | 5.7321 | 70.0035
4914 | 68.13 | 131.2237 | 48.2539 | 101.2527 | 0.50146 |  | 4914 | 30.57 | 131.2237 | 6 | 101.2527
4915 | 74.06 | 146.5035 | 52.8212 | 108.2294 | 0.50966 |  | 4915 | 48.36 | 146.5035 | 5.7321 | 108.2294
4916 | 68.16 | 133.5229 | 35.7832 | 89.7202 | 0.52137 |  | 4916 | 33.62 | 133.5229 | 5 | 89.7202
4917 | 59.36 | 106.2147 | 28.364 | 108.1424 | 0.52837 |  | 4917 | 32.9 | 106.2147 | 4 | 108.1424
4918 | 57.81 | 103.9689 | 25.3357 | 67.2645 | 0.52555 |  | 4918 | 32.38 | 103.9689 | 3 | 67.2645
4919 | 49.8 | 79.8369 | 24.1539 | 42.2967 | 0.52779 |  | 4919 | 52.1 | 79.8369 | 2.2679 | 42.2967
4920 | 45.62 | 41.1359 | 30.1692 | 31.5695 | 0.52798 |  | 4920 | 52.27 | 41.1359 | 2 | 31.5695
4921 | 42.05 | 34.5653 | 27.2978 | 26.6722 | 0.52623 |  | 4921 | 30.11 | 34.5653 | 2.2679 | 26.6722
4922 | 39.58 | 32.8953 | 30.4625 | 7.3374 | 0.52198 |  | 4922 | 28.11 | 32.8953 | 3 | 7.3374
4923 | 39.09 | 31.2677 | 25.9078 | 20.7935 | 0.51601 |  | 4923 | 25.99 | 31.2677 | 4 | 20.7935
4924 | 38.9 | 29.7197 | 42.0967 | 46.5873 | 0.511 |  | 4924 | 24.93 | 29.7197 | 5 | 46.5873
4925 | 40.67 | 28.7182 | 65.5835 | 71.2184 | 0.51669 |  | 4925 | 24.25 | 28.7182 | 5.7321 | 71.2184
4926 | 46.91 | 28.4066 | 96.8887 | 128.0074 | 0.52203 |  | 4926 | 24.72 | 28.4066 | 6 | 128.0074
4927 | 58.94 | 39.1476 | 98.2961 | 135.7101 | 0.51498 |  | 4927 | 24.76 | 39.1476 | 5.7321 | 135.7101
4928 | 55.3 | 52.9477 | 116.714 | 155.6392 | 0.50804 |  | 4928 | 26.51 | 52.9477 | 5 | 155.6392
4929 | 56.7 | 43.8835 | 258.8943 | 112.7656 | 0.50457 |  | 4929 | 27 | 43.8835 | 4 | 112.7656
4930 | 52.78 | 42.5364 | 62.5735 | 91.892 | 0.50335 |  | 4930 | 26.44 | 42.5364 | 3 | 91.892
4931 | 49.97 | 44.8441 | 58.2411 | 88.8319 | 0.50272 |  | 4931 | 26.42 | 44.8441 | 2.2679 | 88.8319
4932 | 47.16 | 45.9168 | 57.0397 | 83.9241 | 0.50396 |  | 4932 | 25.96 | 45.9168 | 2 | 83.9241
4933 | 46.7 | 50.599 | 120.7833 | 82.4377 | 0.50674 |  | 4933 | 26.4 | 50.599 | 2.2679 | 82.4377
4934 | 43.43 | 50.771 | 306.2177 | 66.1628 | 0.51051 |  | 4934 | 24.94 | 50.771 | 3 | 66.1628
4935 | 47.78 | 57.3182 | 71.519 | 70.0916 | 0.5151 |  | 4935 | 23.3 | 57.3182 | 4 | 70.0916
4936 | 50.15 | 77.8699 | 47.9091 | 67.0459 | 0.51678 |  | 4936 | 24.6 | 77.8699 | 5 | 67.0459
4937 | 56.85 | 97.24 | 84.7438 | 83.2761 | 0.51182 |  | 4937 | 25.37 | 97.24 | 5.7321 | 83.2761
4938 | 62.05 | 136.1022 | 101.1141 | 93.8394 | 0.49248 |  | 4938 | 26.67 | 136.1022 | 6 | 93.8394
4939 | 69.58 | 157.9825 | 89.4325 | 91.5706 | 0.48936 |  | 4939 | 29.91 | 157.9825 | 5.7321 | 91.5706
4940 | 61.86 | 120.1816 | 27.721 | 98.6076 | 0.4885 |  | 4940 | 31.94 | 120.1816 | 5 | 98.6076
4941 | 56.75 | 98.3192 | 24.2278 | 89.796 | 0.48368 |  | 4941 | 32.95 | 98.3192 | 4 | 89.796
4942 | 50.74 | 99.8676 | 50.4559 | 66.2135 | 0.4701 |  | 4942 | 35.06 | 99.8676 | 3 | 66.2135
4943 | 41.88 | 77.6433 | 97.6571 | 41.7859 | 0.46375 |  | 4943 | 41.6 | 77.6433 | 2.2679 | 41.7859
4944 | 38.61 | 40.0278 | 80.1164 | 29.7188 | 0.46052 |  | 4944 | 35.8 | 40.0278 | 2 | 29.7188
4945 | 37.73 | 33.2335 | 24.5452 | 28.0371 | 0.4403 |  | 4945 | 40.77 | 33.2335 | 2.2679 | 28.0371
4946 | 37.19 | 31.6945 | 27.3269 | 7.0312 | 0.42647 |  | 4946 | 27.32 | 31.6945 | 3 | 7.0312
4947 | 36.57 | 30.2651 | 25.7497 | 22.7786 | 0.43129 |  | 4947 | 26.32 | 30.2651 | 4 | 22.7786
4948 | 36.37 | 29.1157 | 32.5963 | 50.6896 | 0.43142 |  | 4948 | 25.93 | 29.1157 | 5 | 50.6896
4949 | 38.49 | 28.3595 | 70.889 | 73.4219 | 0.45512 |  | 4949 | 25.92 | 28.3595 | 5.7321 | 73.4219
4950 | 43.08 | 28.2189 | 83.4514 | 115.7978 | 0.46427 |  | 4950 | 27.8 | 28.2189 | 6 | 115.7978
4951 | 49.66 | 39.4105 | 82.7846 | 126.8978 | 0.45076 |  | 4951 | 35 | 39.4105 | 5.7321 | 126.8978
4952 | 54.18 | 57.2331 | 91.1847 | 129.1189 | 0.45758 |  | 4952 | 38.08 | 57.2331 | 5 | 129.1189
4953 | 55.8 | 44.2656 | 98.2711 | 121.9032 | 0.46153 |  | 4953 | 39.52 | 44.2656 | 4 | 121.9032
4954 | 53.61 | 43.0144 | 54.8629 | 77.6246 | 0.4634 |  | 4954 | 44.17 | 43.0144 | 3 | 77.6246
4955 | 48.31 | 46.1792 | 52.1418 | 77.2484 | 0.45666 |  | 4955 | 47.44 | 46.1792 | 2.2679 | 77.2484
4956 | 42.4 | 47.4583 | 63.9515 | 77.128 | 0.44793 |  | 4956 | 47.68 | 47.4583 | 2 | 77.128
4957 | 42.75 | 51.7362 | 113.0278 | 64.4386 | 0.43916 |  | 4957 | 46.49 | 51.7362 | 2.2679 | 64.4386
4958 | 41.23 | 52.9389 | 108.9094 | 63.1429 | 0.43337 |  | 4958 | 45.17 | 52.9389 | 3 | 63.1429
4959 | 40.13 | 61.3186 | 98.622 | 66.8455 | 0.42841 |  | 4959 | 43.75 | 61.3186 | 4 | 66.8455
4960 | 42.95 | 78.0696 | 108.4951 | 59.7758 | 0.42711 |  | 4960 | 37.5 | 78.0696 | 5 | 59.7758
4961 | 49.15 | 93.8725 | 97.3034 | 86.689 | 0.42968 |  | 4961 | 33.32 | 93.8725 | 5.7321 | 86.689
4962 | 52.07 | 135.3954 | 65.8857 | 92.1503 | 0.43055 |  | 4962 | 35.18 | 135.3954 | 6 | 92.1503
4963 | 53.62 | 149.9983 | 74.2521 | 111.0943 | 0.435 |  | 4963 | 35.99 | 149.9983 | 5.7321 | 111.0943
4964 | 52.06 | 117.8291 | 48.6977 | 110.7748 | 0.43505 |  | 4964 | 36.59 | 117.8291 | 5 | 110.7748
4965 | 48.97 | 101.3865 | 102.7552 | 75.7826 | 0.42149 |  | 4965 | 36.47 | 101.3865 | 4 | 75.7826
4966 | 50.05 | 100.7709 | 103.8718 | 71.6087 | 0.42972 |  | 4966 | 36.08 | 100.7709 | 3 | 71.6087
4967 | 39.95 | 77.4013 | 75.9681 | 49.9574 | 0.44383 |  | 4967 | 35.47 | 77.4013 | 2.2679 | 49.9574
4968 | 39.01 | 38.6791 | 20.1563 | 24.8372 | 0.4439 |  | 4968 | 30.48 | 38.6791 | 2 | 24.8372
4969 | 37.59 | 35.6778 | 25.9077 | 33.1839 | 0.42849 |  | 4969 | 27.98 | 35.6778 | 2.2679 | 33.1839
4970 | 37.01 | 33.9238 | 28.3661 | 5.2766 | 0.42533 |  | 4970 | 27.5 | 33.9238 | 3 | 5.2766
4971 | 36.04 | 32.1917 | 26.8544 | 19.7519 | 0.42293 |  | 4971 | 26.38 | 32.1917 | 4 | 19.7519
4972 | 35.1 | 30.4935 | 25.4327 | 42.5321 | 0.42408 |  | 4972 | 25.88 | 30.4935 | 5 | 42.5321
4973 | 35.28 | 29.2505 | 19.4628 | 99.8644 | 0.42707 |  | 4973 | 25.91 | 29.2505 | 5.7321 | 99.8644
4974 | 34.2 | 28.7239 | 28.8052 | 104.3594 | 0.42772 |  | 4974 | 26.53 | 28.7239 | 6 | 104.3594
4975 | 34.93 | 39.7025 | 27.2613 | 136.8851 | 0.42673 |  | 4975 | 30.97 | 39.7025 | 5.7321 | 136.8851
4976 | 37.42 | 54.1982 | 49.8782 | 122.4219 | 0.41895 |  | 4976 | 35.9 | 54.1982 | 5 | 122.4219
4977 | 39.43 | 43.7759 | 39.0802 | 111.0004 | 0.41729 |  | 4977 | 39.16 | 43.7759 | 4 | 111.0004
4978 | 38.16 | 42.5697 | 40.5015 | 84.2344 | 0.4211 |  | 4978 | 47.8 | 42.5697 | 3 | 84.2344
4979 | 36.89 | 44.9964 | 48.2081 | 86.0489 | 0.4251 |  | 4979 | 44.94 | 44.9964 | 2.2679 | 86.0489
4980 | 34.9 | 46.427 | 43.9809 | 74.9943 | 0.4218 |  | 4980 | 48.15 | 46.427 | 2 | 74.9943
4981 | 33.71 | 48.5702 | 43.5318 | 72.6979 | 0.41812 |  | 4981 | 44.82 | 48.5702 | 2.2679 | 72.6979
4982 | 33.34 | 50.6417 | 48.5174 | 59.8485 | 0.41869 |  | 4982 | 43.33 | 50.6417 | 3 | 59.8485
4983 | 32.74 | 57.958 | 38.1632 | 67.9876 | 0.42429 |  | 4983 | 42.67 | 57.958 | 4 | 67.9876
4984 | 33.85 | 73.9501 | 36.5032 | 71.9547 | 0.4124 |  | 4984 | 40.02 | 73.9501 | 5 | 71.9547
4985 | 35.62 | 91.5893 | 37.2292 | 77.2086 | 0.41071 |  | 4985 | 40.49 | 91.5893 | 5.7321 | 77.2086
4986 | 38.79 | 134.5719 | 38.6898 | 100.502 | 0.41704 |  | 4986 | 42.38 | 134.5719 | 6 | 100.502
4987 | 38.94 | 143.1623 | 33.4989 | 126.1615 | 0.43262 |  | 4987 | 41.71 | 143.1623 | 5.7321 | 126.1615
4988 | 37.91 | 133.7403 | 26.9608 | 110.3516 | 0.43465 |  | 4988 | 40 | 133.7403 | 5 | 110.3516
4989 | 36.19 | 103.2238 | 33.1057 | 91.9164 | 0.43522 |  | 4989 | 37.28 | 103.2238 | 4 | 91.9164
4990 | 36.19 | 100.2083 | 22.1474 | 70.2774 | 0.43867 |  | 4990 | 36.54 | 100.2083 | 3 | 70.2774
4991 | 34 | 78.4654 | 23.9476 | 40.2074 | 0.43738 |  | 4991 | 35.81 | 78.4654 | 2.2679 | 40.2074
4992 | 30.98 | 41.7762 | 25.1323 | 21.5381 | 0.42918 |  | 4992 | 33.8 | 41.7762 | 2 | 21.5381
4993 | 30.02 | 33.9051 | 27.2638 | 27.5253 | 0.42536 |  | 4993 | 28.14 | 33.9051 | 2.2679 | 27.5253
4994 | 28.2 | 32.3303 | 26.19 | 5.9082 | 0.42345 |  | 4994 | 27.61 | 32.3303 | 3 | 5.9082
4995 | 26.27 | 30.7147 | 28.653 | 22.2479 | 0.42282 |  | 4995 | 26.53 | 30.7147 | 4 | 22.2479
4996 | 27.1 | 29.3902 | 25.8555 | 52.3399 | 0.42469 |  | 4996 | 25.87 | 29.3902 | 5 | 52.3399
4997 | 26.8 | 28.5032 | 25.7644 | 101.7154 | 0.42738 |  | 4997 | 26 | 28.5032 | 5.7321 | 101.7154
4998 | 25.6 | 28.426 | 27.7528 | 123.1236 | 0.42926 |  | 4998 | 26.63 | 28.426 | 6 | 123.1236
4999 | 28.1 | 39.7623 | 19.2743 | 124.1072 | 0.43191 |  | 4999 | 31.53 | 39.7623 | 5.7321 | 124.1072
5000 | 30.05 | 54.0687 | 45.6649 | 137.825 | 0.43301 |  | 5000 | 36.43 | 54.0687 | 5 | 137.825
5001 | 30.28 | 43.7719 | 35.6053 | 115.3615 | 0.43475 |  | 5001 | 39.11 | 43.7719 | 4 | 115.3615
5002 | 32.06 | 43.2996 | 236.2795 | 69.8057 | 0.43051 |  | 5002 | 40.67 | 43.2996 | 3 | 69.8057
5003 | 32.61 | 45.4162 | 54.5323 | 81.9871 | 0.44128 |  | 5003 | 40.92 | 45.4162 | 2.2679 | 81.9871
5004 | 31.68 | 47.5096 | 38.0388 | 80.21 | 0.44131 |  | 5004 | 41.25 | 47.5096 | 2 | 80.21
5005 | 29.32 | 49.7699 | 39.3015 | 76.1263 | 0.43964 |  | 5005 | 39.94 | 49.7699 | 2.2679 | 76.1263
5006 | 28.45 | 55.5062 | 32.2624 | 57.4463 | 0.44973 |  | 5006 | 36.53 | 55.5062 | 3 | 57.4463
5007 | 28.45 | 59.5256 | 42.8425 | 69.3101 | 0.44739 |  | 5007 | 41.89 | 59.5256 | 4 | 69.3101
5008 | 33.08 | 73.7574 | 54.5239 | 70.5255 | 0.44673 |  | 5008 | 39.07 | 73.7574 | 5 | 70.5255
5009 | 40.69 | 91.1263 | 42.8976 | 82.7452 | 0.45029 |  | 5009 | 32.7 | 91.1263 | 5.7321 | 82.7452
5010 | 39.58 | 124.3483 | 36.7592 | 76.3852 | 0.45702 |  | 5010 | 33.15 | 124.3483 | 6 | 76.3852
5011 | 40.03 | 141.0846 | 36.7414 | 126.1615 | 0.46853 |  | 5011 | 35.97 | 141.0846 | 5.7321 | 126.1615
5012 | 40.3 | 128.923 | 25.3542 | 90.7782 | 0.4746 |  | 5012 | 36.61 | 128.923 | 5 | 90.7782
5013 | 40.87 | 101.1185 | 28.909 | 87.8599 | 0.48257 |  | 5013 | 36.37 | 101.1185 | 4 | 87.8599
5014 | 41.46 | 98.3864 | 19.7809 | 79.3861 | 0.48538 |  | 5014 | 35.56 | 98.3864 | 3 | 79.3861
5015 | 39.01 | 76.8603 | 30.477 | 48.8895 | 0.48217 |  | 5015 | 40.2 | 76.8603 | 2.2679 | 48.8895
5016 | 35.77 | 39.4363 | 25.0535 | 31.8645 | 0.47685 |  | 5016 | 29.94 | 39.4363 | 2 | 31.8645
5017 | 34.05 | 36.259 | 30.3669 | 26.6153 | 0.46648 |  | 5017 | 26.9 | 36.259 | 2.2679 | 26.6153
5018 | 32.65 | 34.3223 | 27.9131 | 6.2719 | 0.46455 |  | 5018 | 26.39 | 34.3223 | 3 | 6.2719
5019 | 33.27 | 32.3991 | 22.1079 | 18.5334 | 0.46452 |  | 5019 | 25.8 | 32.3991 | 4 | 18.5334
5020 | 33.69 | 30.6227 | 28.1709 | 39.1371 | 0.46514 |  | 5020 | 25.29 | 30.6227 | 5 | 39.1371
5021 | 35.09 | 29.4713 | 24.4444 | 72.1879 | 0.47369 |  | 5021 | 25.26 | 29.4713 | 5.7321 | 72.1879
5022 | 40.42 | 28.6259 | 24.7995 | 143.0444 | 0.48221 |  | 5022 | 26.39 | 28.6259 | 6 | 143.0444
5023 | 46.37 | 28.1873 | 20.6238 | 165.6721 | 0.48377 |  | 5023 | 29.92 | 28.1873 | 5.7321 | 165.6721
5024 | 47.97 | 30.4592 | 38.1814 | 139.5663 | 0.48298 |  | 5024 | 34.91 | 30.4592 | 5 | 139.5663
5025 | 49.9 | 49.1531 | 39.2757 | 115.1538 | 0.47904 |  | 5025 | 36.94 | 49.1531 | 4 | 115.1538
5026 | 46.4 | 69.8916 | 29.616 | 90.0381 | 0.47289 |  | 5026 | 41.07 | 69.8916 | 3 | 90.0381
5027 | 45.34 | 77.2853 | 46.6746 | 69.8771 | 0.47025 |  | 5027 | 53.25 | 77.2853 | 2.2679 | 69.8771
5028 | 44.48 | 76.3843 | 46.0573 | 75.8636 | 0.47085 |  | 5028 | 55.55 | 76.3843 | 2 | 75.8636
5029 | 41.5 | 80.3323 | 56.7193 | 64.7502 | 0.47091 |  | 5029 | 51.37 | 80.3323 | 2.2679 | 64.7502
5030 | 39.14 | 76.1723 | 42.3266 | 79.0659 | 0.47207 |  | 5030 | 44.5 | 76.1723 | 3 | 79.0659
5031 | 38.4 | 76.3002 | 239.7204 | 70.873 | 0.47446 |  | 5031 | 37.25 | 76.3002 | 4 | 70.873
5032 | 40.6 | 75.4716 | 41.3193 | 66.9837 | 0.47886 |  | 5032 | 31.43 | 75.4716 | 5 | 66.9837
5033 | 45.21 | 77.3879 | 42.3041 | 69.9276 | 0.48556 |  | 5033 | 31.43 | 77.3879 | 5.7321 | 69.9276
5034 | 49.37 | 130.5476 | 44.824 | 83.9862 | 0.49163 |  | 5034 | 32.98 | 130.5476 | 6 | 83.9862
5035 | 60 | 142.1658 | 41.195 | 97.3003 | 0.49458 |  | 5035 | 34.97 | 142.1658 | 5.7321 | 97.3003
5036 | 59.75 | 130.3617 | 29.3316 | 118.4984 | 0.49871 |  | 5036 | 36.72 | 130.3617 | 5 | 118.4984
5037 | 52.87 | 103.9834 | 25.6329 | 107.2204 | 0.5012 |  | 5037 | 35.5 | 103.9834 | 4 | 107.2204
5038 | 49.38 | 106.1516 | 29.5576 | 74.5515 | 0.4984 |  | 5038 | 34.04 | 106.1516 | 3 | 74.5515
5039 | 43.25 | 92.6272 | 24.4122 | 50.2824 | 0.49421 |  | 5039 | 33.93 | 92.6272 | 2.2679 | 50.2824
5040 | 35 | 43.1095 | 26.2687 | 23.4961 | 0.47981 |  | 5040 | 29.92 | 43.1095 | 2 | 23.4961
5041 | 37.12 | 33.7739 | 28.5064 | 24.9945 | 0.4732 |  | 5041 | 28.21 | 33.7739 | 2.2679 | 24.9945
5042 | 34.95 | 32.225 | 27.763 | 5.7041 | 0.47018 |  | 5042 | 27.04 | 32.225 | 3 | 5.7041
5043 | 33.82 | 30.7715 | 27.7184 | 23.0537 | 0.46556 |  | 5043 | 26.03 | 30.7715 | 4 | 23.0537
5044 | 32.17 | 29.3528 | 26.9217 | 40.4574 | 0.46417 |  | 5044 | 24.58 | 29.3528 | 5 | 40.4574
5045 | 31.73 | 28.4624 | 31.0599 | 84.7922 | 0.46646 |  | 5045 | 24.84 | 28.4624 | 5.7321 | 84.7922
5046 | 46.91 | 27.8895 | 30.7109 | 106.0302 | 0.47271 |  | 5046 | 25.95 | 27.8895 | 6 | 106.0302
5047 | 53.27 | 27.5816 | 24.3122 | 142.6131 | 0.47859 |  | 5047 | 29.68 | 27.5816 | 5.7321 | 142.6131
5048 | 54.89 | 29.6679 | 38.2802 | 126.574 | 0.48062 |  | 5048 | 33.99 | 29.6679 | 5 | 126.574
5049 | 53.46 | 47.6112 | 46.2765 | 115.1538 | 0.47546 |  | 5049 | 36.13 | 47.6112 | 4 | 115.1538
5050 | 50.12 | 69.1262 | 38.8107 | 92.7787 | 0.47059 |  | 5050 | 36.09 | 69.1262 | 3 | 92.7787
5051 | 46.44 | 76.7225 | 47.0418 | 63.634 | 0.46679 |  | 5051 | 34.94 | 76.7225 | 2.2679 | 63.634
5052 | 42.1 | 76.7056 | 48.8106 | 72.9397 | 0.46163 |  | 5052 | 39.3 | 76.7056 | 2 | 72.9397
5053 | 41.24 | 80.9414 | 36.1987 | 91.8659 | 0.45033 |  | 5053 | 32.44 | 80.9414 | 2.2679 | 91.8659
5054 | 40.41 | 78.8484 | 37.9538 | 64.3783 | 0.44911 |  | 5054 | 30.01 | 78.8484 | 3 | 64.3783
5055 | 40.28 | 76.6712 | 44.3541 | 57.6482 | 0.44764 |  | 5055 | 27.94 | 76.6712 | 4 | 57.6482
5056 | 39.94 | 74.6725 | 46.29 | 73.0731 | 0.44658 |  | 5056 | 30 | 74.6725 | 5 | 73.0731
5057 | 42.04 | 74.761 | 38.969 | 65.6046 | 0.45408 |  | 5057 | 29.1 | 74.761 | 5.7321 | 65.6046
5058 | 46.91 | 109.5113 | 46.0209 | 90.0858 | 0.46635 |  | 5058 | 29.11 | 109.5113 | 6 | 90.0858
5059 | 52.41 | 125.8039 | 31.4483 | 88.069 | 0.47997 |  | 5059 | 31.5 | 125.8039 | 5.7321 | 88.069
5060 | 51.54 | 133.0397 | 30.0142 | 112.6793 | 0.48999 |  | 5060 | 34.13 | 133.0397 | 5 | 112.6793
5061 | 46.93 | 98.8893 | 33.3783 | 109.7096 | 0.48993 |  | 5061 | 32.98 | 98.8893 | 4 | 109.7096
5062 | 43.66 | 95.4505 | 21.014 | 75.9528 | 0.48944 |  | 5062 | 30.87 | 95.4505 | 3 | 75.9528
5063 | 38.66 | 87.6529 | 30.9178 | 54.9253 | 0.47845 |  | 5063 | 33.32 | 87.6529 | 2.2679 | 54.9253
5064 | 36.76 | 40.4257 | 26.4101 | 24.8372 | 0.47144 |  | 5064 | 29.78 | 40.4257 | 2 | 24.8372
5065 | 32.84 | 34.5369 | 34.269 | 33.8379 | 0.46529 |  | 5065 | 31.07 | 34.5369 | 2.2679 | 33.8379
5066 | 29.73 | 32.8087 | 27.289 | 6.4123 | 0.45518 |  | 5066 | 26.51 | 32.8087 | 3 | 6.4123
5067 | 27.19 | 31.1311 | 30.1052 | 17.6883 | 0.44642 |  | 5067 | 25.59 | 31.1311 | 4 | 17.6883
5068 | 26.07 | 29.6579 | 26.6414 | 39.7029 | 0.44088 |  | 5068 | 24.56 | 29.6579 | 5 | 39.7029
5069 | 30.66 | 28.7195 | 31.2288 | 96.1625 | 0.44128 |  | 5069 | 24.17 | 28.7195 | 5.7321 | 96.1625
5070 | 34.99 | 28.5553 | 26.7389 | 118.4968 | 0.4437 |  | 5070 | 24.39 | 28.5553 | 6 | 118.4968
5071 | 44.56 | 41.1035 | 19.2402 | 140.41 | 0.45081 |  | 5071 | 24.72 | 41.1035 | 5.7321 | 140.41
5072 | 45 | 53.7705 | 38.0779 | 160.461 | 0.44464 |  | 5072 | 25.46 | 53.7705 | 5 | 160.461
5073 | 44.49 | 43.5377 | 48.7011 | 105.4971 | 0.43417 |  | 5073 | 26.74 | 43.5377 | 4 | 105.4971
5074 | 41.24 | 41.3857 | 233.0545 | 85.0404 | 0.42701 |  | 5074 | 28.97 | 41.3857 | 3 | 85.0404
5075 | 41.44 | 43.5984 | 36.4041 | 69.9523 | 0.42407 |  | 5075 | 28.38 | 43.5984 | 2.2679 | 69.9523
5076 | 41.22 | 44.77 | 42.3909 | 64.247 | 0.41868 |  | 5076 | 27.93 | 44.77 | 2 | 64.247
5077 | 39.5 | 49.8222 | 36.5327 | 64.5944 | 0.41026 |  | 5077 | 30.91 | 49.8222 | 2.2679 | 64.5944
5078 | 38.07 | 52.2972 | 38.7085 | 73.3007 | 0.40872 |  | 5078 | 25.38 | 52.2972 | 3 | 73.3007
5079 | 38.01 | 57.4151 | 46.336 | 51.156 | 0.41395 |  | 5079 | 29.71 | 57.4151 | 4 | 51.156
5080 | 37.79 | 74.3697 | 35.6809 | 64.0011 | 0.41465 |  | 5080 | 25.41 | 74.3697 | 5 | 64.0011
5081 | 40 | 93.242 | 29.7587 | 70.8378 | 0.42476 |  | 5081 | 25.18 | 93.242 | 5.7321 | 70.8378
5082 | 52.02 | 129.0873 | 42.9473 | 82.1094 | 0.43842 |  | 5082 | 26.1 | 129.0873 | 6 | 82.1094
5083 | 54.68 | 138.724 | 33.9993 | 104.9401 | 0.44207 |  | 5083 | 30.51 | 138.724 | 5.7321 | 104.9401
5084 | 61.87 | 139.0572 | 25.5542 | 125.3755 | 0.44567 |  | 5084 | 31.92 | 139.0572 | 5 | 125.3755
5085 | 54.98 | 104.5131 | 21.8275 | 82.2361 | 0.44741 |  | 5085 | 32.55 | 104.5131 | 4 | 82.2361
5086 | 49.15 | 105.7447 | 26.2348 | 81.9085 | 0.45279 |  | 5086 | 32.09 | 105.7447 | 3 | 81.9085
5087 | 42.2 | 80.4913 | 22.8663 | 39.1859 | 0.45756 |  | 5087 | 36.02 | 80.4913 | 2.2679 | 39.1859
5088 | 39 | 40.0294 | 27.4933 | 22.2354 | 0.44703 |  | 5088 | 34.01 | 40.0294 | 2 | 22.2354
5089 | 37.07 | 32.4174 | 3.309 | 32.3308 | 0.44089 |  | 5089 | 28.08 | 32.4174 | 2.2679 | 32.3308
5090 | 36.25 | 31.2361 | 4.407 | 6.0741 | 0.43657 |  | 5090 | 25.36 | 31.2361 | 3 | 6.0741
5091 | 34.89 | 29.932 | 4.1469 | 17.8455 | 0.43505 |  | 5091 | 23.8 | 29.932 | 4 | 17.8455
5092 | 33.86 | 28.8505 | 4.5681 | 54.0374 | 0.43649 |  | 5092 | 22.56 | 28.8505 | 5 | 54.0374
5093 | 36.66 | 28.0414 | 3.5466 | 96.1625 | 0.44323 |  | 5093 | 22.14 | 28.0414 | 5.7321 | 96.1625
5094 | 40.8 | 27.8947 | 4.9782 | 145.2293 | 0.45255 |  | 5094 | 21.65 | 27.8947 | 6 | 145.2293
5095 | 44.45 | 39.0341 | 4.17 | 150.9848 | 0.45309 |  | 5095 | 20.98 | 39.0341 | 5.7321 | 150.9848
5096 | 44.09 | 54.3678 | 14.3434 | 122.02 | 0.45302 |  | 5096 | 21.99 | 54.3678 | 5 | 122.02
5097 | 42.43 | 43.8956 | 16.5934 | 103.1089 | 0.45029 |  | 5097 | 23.8 | 43.8956 | 4 | 103.1089
5098 | 40.76 | 42.7831 | 18.7351 | 76.1736 | 0.44679 |  | 5098 | 25.12 | 42.7831 | 3 | 76.1736
5099 | 39.29 | 45.4641 | 25.329 | 66.7932 | 0.44655 |  | 5099 | 25.28 | 45.4641 | 2.2679 | 66.7932
5100 | 38.48 | 45.8271 | 24.9714 | 90.1671 | 0.44703 |  | 5100 | 26.77 | 45.8271 | 2 | 90.1671
5101 | 38.78 | 49.1584 | 19.8983 | 69.2695 | 0.44766 |  | 5101 | 26.34 | 49.1584 | 2.2679 | 69.2695
5102 | 38.75 | 49.5224 | 20.0535 | 63.1429 | 0.45071 |  | 5102 | 25.56 | 49.5224 | 3 | 63.1429
5103 | 39.78 | 57.7313 | 18.3256 | 57.2274 | 0.45631 |  | 5103 | 24.35 | 57.7313 | 4 | 57.2274
5104 | 40.13 | 73.9986 | 19.8183 | 54.1214 | 0.45469 |  | 5104 | 23.32 | 73.9986 | 5 | 54.1214
5105 | 45.33 | 92.4688 | 21.6721 | 70.0035 | 0.45966 |  | 5105 | 22.78 | 92.4688 | 5.7321 | 70.0035
5106 | 55.64 | 126.4135 | 10.7999 | 98.0621 | 0.46805 |  | 5106 | 25.25 | 126.4135 | 6 | 98.0621
5107 | 63.5 | 135.4915 | 25.9775 | 111.6248 | 0.47744 |  | 5107 | 25.09 | 135.4915 | 5.7321 | 111.6248
5108 | 66.2 | 136.2989 | 4.0538 | 101.4642 | 0.4823 |  | 5108 | 28.23 | 136.2989 | 5 | 101.4642
5109 | 58.6 | 98.0583 | 3.3646 | 99.9372 | 0.48273 |  | 5109 | 28.92 | 98.0583 | 4 | 99.9372
5110 | 51.53 | 100.9273 | 4.5363 | 62.8503 | 0.4832 |  | 5110 | 30.19 | 100.9273 | 3 | 62.8503
5111 | 44.54 | 75.1473 | 4.7637 | 40.7181 | 0.4823 |  | 5111 | 37.44 | 75.1473 | 2.2679 | 40.7181
5112 | 40 | 38.2163 | 4.3999 | 32.1327 | 0.47688 |  | 5112 | 39.94 | 38.2163 | 2 | 32.1327
5113 | 38.89 | 35.4956 | 5.4957 | 29.0323 | 0.47277 |  | 5113 | 25.6 | 35.4956 | 2.2679 | 29.0323
5114 | 37.38 | 33.5357 | 3.4441 | 5.8317 | 0.46415 |  | 5114 | 24.53 | 33.5357 | 3 | 5.8317
5115 | 34.18 | 31.727 | 5.6476 | 17.2952 | 0.46163 |  | 5115 | 23.44 | 31.727 | 4 | 17.2952
5116 | 34.03 | 30.141 | 4.7705 | 55.5463 | 0.4621 |  | 5116 | 22.14 | 30.141 | 5 | 55.5463
5117 | 36.3 | 29.1309 | 4.3992 | 102.9494 | 0.46513 |  | 5117 | 22.42 | 29.1309 | 5.7321 | 102.9494
5118 | 41.97 | 28.8946 | 3.9498 | 123.3806 | 0.47109 |  | 5118 | 23.93 | 28.8946 | 6 | 123.3806
5119 | 45.36 | 40.984 | 5.4832 | 157.4472 | 0.47011 |  | 5119 | 29.06 | 40.984 | 5.7321 | 157.4472
5120 | 48.56 | 57.2585 | 27.4499 | 136.8875 | 0.46327 |  | 5120 | 32.17 | 57.2585 | 5 | 136.8875
5121 | 50.47 | 43.8997 | 18.9688 | 114.6347 | 0.45851 |  | 5121 | 35 | 43.8997 | 4 | 114.6347
5122 | 47.95 | 42.5388 | 12.9742 | 95.1969 | 0.45325 |  | 5122 | 33.21 | 42.5388 | 3 | 95.1969
5123 | 44.96 | 45.0719 | 19.8009 | 67.6206 | 0.44874 |  | 5123 | 30.13 | 45.0719 | 2.2679 | 67.6206
5124 | 42.31 | 48.0312 | 13.9426 | 87.4802 | 0.44414 |  | 5124 | 29.8 | 48.0312 | 2 | 87.4802
5125 | 41.28 | 51.1577 | 15.0152 | 85.087 | 0.44176 |  | 5125 | 32.44 | 51.1577 | 2.2679 | 85.087
5126 | 40.08 | 51.6626 | 13.3333 | 64.3783 | 0.43809 |  | 5126 | 33.51 | 51.6626 | 3 | 64.3783
5127 | 40.22 | 59.6861 | 14.8251 | 66.7854 | 0.43645 |  | 5127 | 31.43 | 59.6861 | 4 | 66.7854
5128 | 39.21 | 76.3734 | 17.4553 | 72.2654 | 0.43823 |  | 5128 | 27.44 | 76.3734 | 5 | 72.2654
5129 | 42.79 | 96.9398 | 25.0804 | 88.13 | 0.44021 |  | 5129 | 28.48 | 96.9398 | 5.7321 | 88.13
5130 | 45.95 | 141.9432 | 17.4461 | 99.0944 | 0.43994 |  | 5130 | 32.05 | 141.9432 | 6 | 99.0944
5131 | 49.51 | 153.5701 | 16.2086 | 90.7217 | 0.44073 |  | 5131 | 35.97 | 153.5701 | 5.7321 | 90.7217
5132 | 49.72 | 121.1555 | 4.016 | 112.1503 | 0.44456 |  | 5132 | 37.15 | 121.1555 | 5 | 112.1503
5133 | 47.17 | 102.4144 | 204.0217 | 86.016 | 0.44841 |  | 5133 | 38.33 | 102.4144 | 4 | 86.016
5134 | 43.96 | 103.9905 | 3.7537 | 56.334 | 0.45176 |  | 5134 | 36.95 | 103.9905 | 3 | 56.334
5135 | 41.12 | 79.7146 | 5.3119 | 52.2788 | 0.45801 |  | 5135 | 35.99 | 79.7146 | 2.2679 | 52.2788
5136 | 38.96 | 41.1834 | 4.7562 | 24.6226 | 0.45258 |  | 5136 | 31.64 | 41.1834 | 2 | 24.6226
5137 | 36.94 | 32.6138 | 3.2435 | 28.1793 | 0.45048 |  | 5137 | 27.56 | 32.6138 | 2.2679 | 28.1793
5138 | 36.84 | 31.2394 | 3.3771 | 7.2928 | 0.45469 |  | 5138 | 25.79 | 31.2394 | 3 | 7.2928
5139 | 36.53 | 29.8148 | 4.7375 | 18.1993 | 0.45162 |  | 5139 | 25.35 | 29.8148 | 4 | 18.1993
5140 | 31.4 | 28.7319 | 3.4439 | 43.3337 | 0.43968 |  | 5140 | 24.7 | 28.7319 | 5 | 43.3337
5141 | 36.66 | 28.1419 | 3.806 | 87.7009 | 0.43768 |  | 5141 | 24.27 | 28.1419 | 5.7321 | 87.7009
5142 | 35.61 | 28.0619 | 4.4213 | 107.4439 | 0.43094 |  | 5142 | 25.9 | 28.0619 | 6 | 107.4439
5143 | 37.9 | 39.7491 | 4.4448 | 150.1036 | 0.42986 |  | 5143 | 30.43 | 39.7491 | 5.7321 | 150.1036
5144 | 37.72 | 54.5991 | 218.0889 | 135.9499 | 0.42928 |  | 5144 | 34.87 | 54.5991 | 5 | 135.9499
5145 | 38.51 | 43.6705 | 14.5309 | 116.1922 | 0.42936 |  | 5145 | 36.87 | 43.6705 | 4 | 116.1922
5146 | 37.04 | 43.8784 | 14.5786 | 84.8792 | 0.42924 |  | 5146 | 36.92 | 43.8784 | 3 | 84.8792
5147 | 35.63 | 46.3003 | 6.0064 | 68.9745 | 0.42741 |  | 5147 | 36.97 | 46.3003 | 2.2679 | 68.9745
5148 | 35.04 | 48.2357 | 12.7786 | 76.4958 | 0.42821 |  | 5148 | 38.09 | 48.2357 | 2 | 76.4958
5149 | 32.43 | 50.9812 | 21.191 | 64.1269 | 0.42623 |  | 5149 | 37.83 | 50.9812 | 2.2679 | 64.1269
5150 | 30.1 | 53.8473 | 17.2857 | 64.0351 | 0.42676 |  | 5150 | 36.85 | 53.8473 | 3 | 64.0351
5151 | 30.4 | 58.6285 | 8.6019 | 49.4729 | 0.42721 |  | 5151 | 35.98 | 58.6285 | 4 | 49.4729
5152 | 30.52 | 75.271 | 20.3152 | 52.133 | 0.4296 |  | 5152 | 35.73 | 75.271 | 5 | 52.133
5153 | 34.09 | 97.8916 | 15.9747 | 83.6553 | 0.43287 |  | 5153 | 34.92 | 97.8916 | 5.7321 | 83.6553
5154 | 38.95 | 137.0075 | 29.3797 | 91.5872 | 0.43658 |  | 5154 | 35.94 | 137.0075 | 6 | 91.5872
5155 | 41.08 | 143.5515 | 33.1624 | 125.1004 | 0.44438 |  | 5155 | 35.92 | 143.5515 | 5.7321 | 125.1004
5156 | 41.02 | 122.4777 | 4.442 | 116.4881 | 0.45017 |  | 5156 | 34.95 | 122.4777 | 5 | 116.4881
5157 | 41.58 | 98.6866 | 4.0183 | 79.286 | 0.45357 |  | 5157 | 32.83 | 98.6866 | 4 | 79.286
5158 | 41.96 | 102.7031 | 3.9473 | 74.5515 | 0.45352 |  | 5158 | 32.4 | 102.7031 | 3 | 74.5515
5159 | 39.47 | 76.2392 | 3.8725 | 49.7253 | 0.45056 |  | 5159 | 31.19 | 76.2392 | 2.2679 | 49.7253
5160 | 37.69 | 38.0682 | 4.5483 | 21.7795 | 0.44812 |  | 5160 | 28.98 | 38.0682 | 2 | 21.7795
5161 | 35 | 34.2764 | 3.2168 | 28.0087 | 0.44981 |  | 5161 | 26.03 | 34.2764 | 2.2679 | 28.0087
5162 | 35.41 | 32.7039 | 4.9938 | 6.6866 | 0.45195 |  | 5162 | 24.53 | 32.7039 | 3 | 6.6866
5163 | 35.99 | 31.2606 | 4.2061 | 23.2699 | 0.45097 |  | 5163 | 23.74 | 31.2606 | 4 | 23.2699
5164 | 35.87 | 29.7525 | 5.3555 | 52.5757 | 0.45038 |  | 5164 | 22.69 | 29.7525 | 5 | 52.5757
5165 | 33.85 | 28.606 | 4.5025 | 82.1479 | 0.44895 |  | 5165 | 22.48 | 28.606 | 5.7321 | 82.1479
5166 | 36.2 | 28.5416 | 4.4113 | 148.3138 | 0.44782 |  | 5166 | 23.66 | 28.5416 | 6 | 148.3138
5167 | 34.3 | 39.4122 | 4.2903 | 131.8914 | 0.44335 |  | 5167 | 27.06 | 39.4122 | 5.7321 | 131.8914
5168 | 33.16 | 54.6428 | 22.1918 | 111.4387 | 0.43718 |  | 5168 | 31.82 | 54.6428 | 5 | 111.4387
5169 | 31.1 | 43.0292 | 19.9445 | 108.4045 | 0.42817 |  | 5169 | 33.95 | 43.0292 | 4 | 108.4045
5170 | 28.26 | 41.9432 | 18.6125 | 92.4563 | 0.42146 |  | 5170 | 34.97 | 41.9432 | 3 | 92.4563
5171 | 28.36 | 44.5888 | 22.4594 | 66.1914 | 0.4207 |  | 5171 | 35.02 | 44.5888 | 2.2679 | 66.1914
5172 | 29.06 | 46.2583 | 11.3081 | 73.888 | 0.42344 |  | 5172 | 34.95 | 46.2583 | 2 | 73.888
5173 | 29.12 | 48.6192 | 16.1174 | 83.9182 | 0.42284 |  | 5173 | 33.57 | 48.6192 | 2.2679 | 83.9182
5174 | 29.02 | 50.8028 | 11.6679 | 55.6618 | 0.42388 |  | 5174 | 34.84 | 50.8028 | 3 | 55.6618
5175 | 28.29 | 57.2724 | 28.4367 | 71.414 | 0.42676 |  | 5175 | 31.98 | 57.2724 | 4 | 71.414
5176 | 29.97 | 71.8581 | 13.9482 | 74.5023 | 0.42912 |  | 5176 | 29.13 | 71.8581 | 5 | 74.5023
5177 | 34.23 | 92.0501 | 25.0397 | 71.8996 | 0.43656 |  | 5177 | 28.45 | 92.0501 | 5.7321 | 71.8996
5178 | 39.02 | 126.3559 | 19.6351 | 109.5105 | 0.4431 |  | 5178 | 29.95 | 126.3559 | 6 | 109.5105
5179 | 42 | 141.5019 | 22.1254 | 117.1424 | 0.45816 |  | 5179 | 32.52 | 141.5019 | 5.7321 | 117.1424
5180 | 43.99 | 125.8813 | 4.6044 | 109.5052 | 0.46367 |  | 5180 | 33 | 125.8813 | 5 | 109.5052
5181 | 47 | 98.8209 | 4.6401 | 79.286 | 0.46463 |  | 5181 | 31.25 | 98.8209 | 4 | 79.286
5182 | 46.76 | 100.9026 | 3.1952 | 63.5509 | 0.46236 |  | 5182 | 30.33 | 100.9026 | 3 | 63.5509
5183 | 42.24 | 74.8513 | 4.9198 | 55.4824 | 0.45273 |  | 5183 | 29.98 | 74.8513 | 2.2679 | 55.4824
5184 | 38.46 | 39.9734 | 3.9217 | 26.7952 | 0.44529 |  | 5184 | 27.03 | 39.9734 | 2 | 26.7952
5185 | 33.26 | 33.633 | 4.0493 | 27.7243 | 0.4426 |  | 5185 | 23.6 | 33.633 | 2.2679 | 27.7243
5186 | 31.67 | 32.2368 | 3.7332 | 6.1252 | 0.44086 |  | 5186 | 22.43 | 32.2368 | 3 | 6.1252
5187 | 29.44 | 30.6916 | 4.5513 | 20.9311 | 0.44708 |  | 5187 | 20.05 | 30.6916 | 4 | 20.9311
5188 | 30.4 | 29.394 | 3.8037 | 51.1611 | 0.44428 |  | 5188 | 19.42 | 29.394 | 5 | 51.1611
5189 | 32.8 | 28.4511 | 3.8794 | 96.4269 | 0.44411 |  | 5189 | 19.83 | 28.4511 | 5.7321 | 96.4269
5190 | 40.49 | 27.8351 | 4.5495 | 114.7697 | 0.44878 |  | 5190 | 22.42 | 27.8351 | 6 | 114.7697
5191 | 48.8 | 27.4055 | 4.8702 | 173.1626 | 0.44548 |  | 5191 | 25.49 | 27.4055 | 5.7321 | 173.1626
5192 | 47.96 | 30.0138 | 19.0176 | 126.0383 | 0.44163 |  | 5192 | 30.01 | 30.0138 | 5 | 126.0383
5193 | 51.55 | 48.3254 | 21.4822 | 124.0837 | 0.43618 |  | 5193 | 33.05 | 48.3254 | 4 | 124.0837
5194 | 51.91 | 68.1376 | 21.2653 | 91.489 | 0.43022 |  | 5194 | 32.03 | 68.1376 | 3 | 91.489
5195 | 49.3 | 76.2932 | 25.7169 | 75.368 | 0.42019 |  | 5195 | 29.53 | 76.2932 | 2.2679 | 75.368
5196 | 45.22 | 76.7285 | 15.1652 | 91.3524 | 0.41546 |  | 5196 | 29.03 | 76.7285 | 2 | 91.3524
5197 | 44.58 | 77.6389 | 16.4461 | 78.5418 | 0.41398 |  | 5197 | 27.44 | 77.6389 | 2.2679 | 78.5418
5198 | 39.29 | 73.9371 | 19.0024 | 65.3392 | 0.40712 |  | 5198 | 30.63 | 73.9371 | 3 | 65.3392
5199 | 38.22 | 71.44 | 16.1924 | 70.2118 | 0.4043 |  | 5199 | 28.1 | 71.44 | 4 | 70.2118
5200 | 38.21 | 74.4256 | 16.8477 | 58.0981 | 0.40614 |  | 5200 | 30.74 | 74.4256 | 5 | 58.0981
5201 | 39.7 | 76.4035 | 13.0481 | 69.0175 | 0.40888 |  | 5201 | 29.29 | 76.4035 | 5.7321 | 69.0175
5202 | 42.4 | 106.0114 | 22.4012 | 79.5758 | 0.4119 |  | 5202 | 32.98 | 106.0114 | 6 | 79.5758
5203 | 50.33 | 140.2275 | 15.5015 | 111.0943 | 0.41685 |  | 5203 | 34.58 | 140.2275 | 5.7321 | 111.0943
5204 | 53.4 | 133.5403 | 3.504 | 93.2117 | 0.42006 |  | 5204 | 34.9 | 133.5403 | 5 | 93.2117
5205 | 49.9 | 98.0165 | 4.7134 | 102.5186 | 0.41987 |  | 5205 | 34.58 | 98.0165 | 4 | 102.5186
5206 | 45 | 97.8491 | 4.6366 | 74.6215 | 0.41768 |  | 5206 | 34.46 | 97.8491 | 3 | 74.6215
5207 | 39.87 | 89.6528 | 3.9079 | 40.7181 | 0.41778 |  | 5207 | 33.91 | 89.6528 | 2.2679 | 40.7181
5208 | 38.48 | 40.4844 | 3.2093 | 27.0634 | 0.40648 |  | 5208 | 29.37 | 40.4844 | 2 | 27.0634
5209 | 36.92 | 36.4562 | 3.9984 | 32.8426 | 0.41203 |  | 5209 | 28.13 | 36.4562 | 2.2679 | 32.8426
5210 | 34.62 | 34.3391 | 4.3218 | 7.4523 | 0.41859 |  | 5210 | 26.83 | 34.3391 | 3 | 7.4523
5211 | 33.69 | 32.2989 | 4.2901 | 23.545 | 0.42327 |  | 5211 | 25.12 | 32.2989 | 4 | 23.545
5212 | 33.5 | 30.5326 | 3.964 | 47.6246 | 0.42633 |  | 5212 | 23.95 | 30.5326 | 5 | 47.6246
5213 | 36.68 | 29.3679 | 3.7351 | 78.0934 | 0.4263 |  | 5213 | 24.07 | 29.3679 | 5.7321 | 78.0934
5214 | 37.53 | 28.6436 | 4.3585 | 117.7257 | 0.43009 |  | 5214 | 26.24 | 28.6436 | 6 | 117.7257
5215 | 43.58 | 28.3212 | 203.7435 | 169.6376 | 0.42806 |  | 5215 | 30.45 | 28.3212 | 5.7321 | 169.6376
5216 | 45 | 30.8769 | 24.9281 | 154.5676 | 0.42254 |  | 5216 | 34.01 | 30.8769 | 5 | 154.5676
5217 | 44 | 49.3967 | 15.514 | 114.7385 | 0.4124 |  | 5217 | 37.19 | 49.3967 | 4 | 114.7385
5218 | 41.96 | 68.8096 | 32.5893 | 77.8664 | 0.4153 |  | 5218 | 38.69 | 68.8096 | 3 | 77.8664
5219 | 41.37 | 79.6291 | 23.7978 | 66.1914 | 0.41361 |  | 5219 | 38.54 | 79.6291 | 2.2679 | 66.1914
5220 | 40.02 | 77.2966 | 17.8377 | 76.5748 | 0.40766 |  | 5220 | 38 | 77.2966 | 2 | 76.5748
5221 | 38.87 | 82.5285 | 31.6828 | 72.7758 | 0.40352 |  | 5221 | 36 | 82.5285 | 2.2679 | 72.7758
5222 | 38.97 | 81.22 | 44.0079 | 80.164 | 0.40528 |  | 5222 | 33.96 | 81.22 | 3 | 80.164
5223 | 38.99 | 79.5492 | 84.4255 | 68.4685 | 0.40571 |  | 5223 | 31.39 | 79.5492 | 4 | 68.4685
5224 | 40.04 | 81.0988 | 74.0348 | 72.5139 | 0.41126 |  | 5224 | 28.23 | 81.0988 | 5 | 72.5139
5225 | 43.84 | 84.1357 | 51.9969 | 61.9641 | 0.41396 |  | 5225 | 28.46 | 84.1357 | 5.7321 | 61.9641
5226 | 48.93 | 126.8401 | 16.7024 | 82.1094 | 0.41998 |  | 5226 | 31.29 | 126.8401 | 6 | 82.1094
5227 | 54.38 | 125.8467 | 17.2881 | 84.9919 | 0.42995 |  | 5227 | 33.89 | 125.8467 | 5.7321 | 84.9919
5228 | 53.52 | 140.464 | 5.2194 | 101.1468 | 0.43287 |  | 5228 | 34.4 | 140.464 | 5 | 101.1468
5229 | 52.69 | 105.5211 | 3.8651 | 103.1639 | 0.4357 |  | 5229 | 34.15 | 105.5211 | 4 | 103.1639
5230 | 49.12 | 105.0277 | 4.3625 | 72.5195 | 0.43143 |  | 5230 | 33.02 | 105.0277 | 3 | 72.5195
5231 | 40.97 | 92.7544 | 4.4168 | 38.8609 | 0.426 |  | 5231 | 32.44 | 92.7544 | 2.2679 | 38.8609
5232 | 37.03 | 43.5939 | 3.8606 | 29.8529 | 0.40343 |  | 5232 | 28.84 | 43.5939 | 2 | 29.8529
5233 | 33.17 | 35.7953 | 4.6657 | 23.7149 | 0.39415 |  | 5233 | 29.58 | 35.7953 | 2.2679 | 23.7149
5234 | 31.53 | 33.9279 | 205.3897 | 7.0439 | 0.39414 |  | 5234 | 26.68 | 33.9279 | 3 | 7.0439
5235 | 30.92 | 32.0981 | 4.6973 | 21.7369 | 0.3963 |  | 5235 | 25.34 | 32.0981 | 4 | 21.7369
5236 | 30.74 | 30.4136 | 5.4994 | 43.9467 | 0.3954 |  | 5236 | 23.77 | 30.4136 | 5 | 43.9467
5237 | 32.87 | 29.2868 | 25.4455 | 81.2665 | 0.39319 |  | 5237 | 22.4 | 29.2868 | 5.7321 | 81.2665
5238 | 36.68 | 28.9289 | 82.1044 | 107.958 | 0.3945 |  | 5238 | 22.01 | 28.9289 | 6 | 107.958
5239 | 42.77 | 41.7444 | 46.0302 | 169.7845 | 0.39059 |  | 5239 | 22.97 | 41.7444 | 5.7321 | 169.7845
5240 | 44.71 | 55.7809 | 42.772 | 145.8615 | 0.38996 |  | 5240 | 25.02 | 55.7809 | 5 | 145.8615
5241 | 44.98 | 45.0952 | 44.3397 | 123.4607 | 0.38215 |  | 5241 | 26.36 | 45.0952 | 4 | 123.4607
5242 | 43.93 | 43.3599 | 61.2105 | 76.9797 | 0.37949 |  | 5242 | 26.47 | 43.3599 | 3 | 76.9797
5243 | 44.31 | 45.3733 | 72.8803 | 89.4337 | 0.37417 |  | 5243 | 24.94 | 45.3733 | 2.2679 | 89.4337
5244 | 42.16 | 48.0117 | 69.1216 | 64.326 | 0.37031 |  | 5244 | 24.55 | 48.0117 | 2 | 64.326
5245 | 40.09 | 50.8334 | 73.9265 | 87.5024 | 0.36597 |  | 5245 | 23.9 | 50.8334 | 2.2679 | 87.5024
5246 | 37.93 | 52.4819 | 83.5278 | 78.9286 | 0.36983 |  | 5246 | 23.42 | 52.4819 | 3 | 78.9286
5247 | 35.83 | 59.064 | 86.0017 | 54.5825 | 0.36627 |  | 5247 | 23.69 | 59.064 | 4 | 54.5825
5248 | 35.75 | 73.6158 | 95.8563 | 56.2962 | 0.36893 |  | 5248 | 23.52 | 73.6158 | 5 | 56.2962
5249 | 39.5 | 95.2625 | 97.7452 | 78.8013 | 0.37342 |  | 5249 | 23.36 | 95.2625 | 5.7321 | 78.8013
5250 | 42.7 | 132.8927 | 77.5624 | 86.2384 | 0.37523 |  | 5250 | 27.04 | 132.8927 | 6 | 86.2384
5251 | 43.15 | 150.9979 | 80.4379 | 119.0523 | 0.38282 |  | 5251 | 26.32 | 150.9979 | 5.7321 | 119.0523
5252 | 42.62 | 140.8521 | 53.7259 | 107.7066 | 0.39057 |  | 5252 | 39.94 | 140.8521 | 5 | 107.7066
5253 | 41.94 | 106.7816 | 39.0273 | 85.8317 | 0.38676 |  | 5253 | 43.97 | 106.7816 | 4 | 85.8317
5254 | 40.55 | 107.015 | 44.6835 | 62.0094 | 0.39113 |  | 5254 | 42.94 | 107.015 | 3 | 62.0094
5255 | 37.64 | 77.8251 | 36.9546 | 37.1431 | 0.3909 |  | 5255 | 45.69 | 77.8251 | 2.2679 | 37.1431
5256 | 32.74 | 41.3635 | 3.785 | 22.8523 | 0.38978 |  | 5256 | 38.93 | 41.3635 | 2 | 22.8523
5257 | 31.34 | 35.9483 | 3.1618 | 31.5915 | 0.38983 |  | 5257 | 24.6 | 35.9483 | 2.2679 | 31.5915
5258 | 27.52 | 33.9243 | 11.6979 | 6.9738 | 0.38671 |  | 5258 | 20.05 | 33.9243 | 3 | 6.9738
5259 | 26.85 | 32.0258 | 30.5781 | 16.0374 | 0.39047 |  | 5259 | 17.99 | 32.0258 | 4 | 16.0374
5260 | 27.51 | 30.4459 | 23.7552 | 41.0232 | 0.39711 |  | 5260 | 12.86 | 30.4459 | 5 | 41.0232
5261 | 30.11 | 29.4554 | 21.9329 | 91.0502 | 0.40043 |  | 5261 | 12.38 | 29.4554 | 5.7321 | 91.0502
5262 | 34.57 | 29.1624 | 55.9639 | 151.1412 | 0.39871 |  | 5262 | 12.35 | 29.1624 | 6 | 151.1412
5263 | 39.94 | 40.3054 | 48.4496 | 135.2695 | 0.3957 |  | 5263 | 12.51 | 40.3054 | 5.7321 | 135.2695
5264 | 39.98 | 55.6998 | 57.6704 | 144.9239 | 0.39143 |  | 5264 | 11.93 | 55.6998 | 5 | 144.9239
5265 | 37.47 | 45.1246 | 61.0342 | 92.1023 | 0.3861 |  | 5265 | 12.25 | 45.1246 | 4 | 92.1023
5266 | 32.56 | 44.0029 | 65.789 | 81.7355 | 0.3821 |  | 5266 | 12.79 | 44.0029 | 3 | 81.7355
5267 | 30.46 | 46.0083 | 38.6326 | 60.7758 | 0.37974 |  | 5267 | 23.53 | 46.0083 | 2.2679 | 60.7758
5268 | 28.55 | 49.4222 | 18.8248 | 66.1436 | 0.37787 |  | 5268 | 22.5 | 49.4222 | 2 | 66.1436
5269 | 28.5 | 51.88 | 16.5133 | 70.75 | 0.3751 |  | 5269 | 24.61 | 51.88 | 2.2679 | 70.75
5270 | 28.37 | 53.8252 | 20.1378 | 67.055 | 0.37667 |  | 5270 | 24.7 | 53.8252 | 3 | 67.055
5271 | 28.7 | 61.6767 | 19.7297 | 68.5286 | 0.37985 |  | 5271 | 23.38 | 61.6767 | 4 | 68.5286
5272 | 30.76 | 75.1508 | 12.0523 | 67.6051 | 0.38676 |  | 5272 | 20.5 | 75.1508 | 5 | 67.6051
5273 | 35.99 | 94.0991 | 22.5758 | 66.5147 | 0.39815 |  | 5273 | 20.61 | 94.0991 | 5.7321 | 66.5147
5274 | 39.04 | 137.2427 | 20.5507 | 97.2176 | 0.40668 |  | 5274 | 22.44 | 137.2427 | 6 | 97.2176
5275 | 43.05 | 147.757 | 26.5221 | 122.8722 | 0.41903 |  | 5275 | 24.7 | 147.757 | 5.7321 | 122.8722
5276 | 43.37 | 120.0659 | 2.8824 | 96.9148 | 0.42848 |  | 5276 | 27.77 | 120.0659 | 5 | 96.9148
5277 | 43.63 | 103.4594 | 3.5458 | 91.1789 | 0.43266 |  | 5277 | 30.48 | 103.4594 | 4 | 91.1789
5278 | 42.1 | 106.0801 | 5.1589 | 70.1372 | 0.43365 |  | 5278 | 32.37 | 106.0801 | 3 | 70.1372
5279 | 38.12 | 77.8752 | 3.3998 | 52.5574 | 0.43315 |  | 5279 | 32.65 | 77.8752 | 2.2679 | 52.5574
5280 | 34.92 | 42.2524 | 3.9845 | 23.5229 | 0.43149 |  | 5280 | 26.33 | 42.2524 | 2 | 23.5229
5281 | 33.88 | 36.2121 | 5.3986 | 31.2787 | 0.42882 |  | 5281 | 20.62 | 36.2121 | 2.2679 | 31.2787
5282 | 29.46 | 34.2703 | 4.7574 | 7.4523 | 0.42638 |  | 5282 | 16.44 | 34.2703 | 3 | 7.4523
5283 | 27.52 | 32.3768 | 4.3014 | 22.7589 | 0.42022 |  | 5283 | 12.91 | 32.3768 | 4 | 22.7589
5284 | 25.92 | 30.5683 | 3.432 | 52.3399 | 0.41764 |  | 5284 | 8.16 | 30.5683 | 5 | 52.3399
5285 | 28.1 | 29.3634 | 4.3552 | 96.9557 | 0.41524 |  | 5285 | 8.12 | 29.3634 | 5.7321 | 96.9557
5286 | 41.7 | 29.0899 | 204.0823 | 133.9194 | 0.4102 |  | 5286 | 8.94 | 29.0899 | 6 | 133.9194
5287 | 49.67 | 41.1257 | 3.8266 | 160.0909 | 0.40548 |  | 5287 | 17.85 | 41.1257 | 5.7321 | 160.0909
5288 | 48.17 | 56.1365 | 20.2658 | 145.9954 | 0.40512 |  | 5288 | 23.71 | 56.1365 | 5 | 145.9954
5289 | 42.87 | 44.1278 | 15.0616 | 110.1697 | 0.39563 |  | 5289 | 26.29 | 44.1278 | 4 | 110.1697
5290 | 40.27 | 41.802 | 31.4052 | 86.8944 | 0.38875 |  | 5290 | 24.73 | 41.802 | 3 | 86.8944
5291 | 40.4 | 45.1172 | 23.2553 | 72.5097 | 0.38939 |  | 5291 | 27.65 | 45.1172 | 2.2679 | 72.5097
5292 | 39.2 | 46.1562 | 18.9189 | 70.569 | 0.3903 |  | 5292 | 29.94 | 46.1562 | 2 | 70.569
5293 | 39.23 | 49.1983 | 26.017 | 67.0099 | 0.38406 |  | 5293 | 31.17 | 49.1983 | 2.2679 | 67.0099
5294 | 39.68 | 51.2408 | 12.5113 | 62.937 | 0.38248 |  | 5294 | 34.46 | 51.2408 | 3 | 62.937
5295 | 38.71 | 57.0876 | 19.3659 | 49.4729 | 0.37933 |  | 5295 | 32.5 | 57.0876 | 4 | 49.4729
5296 | 36.57 | 74.792 | 19.9207 | 73.0731 | 0.38748 |  | 5296 | 29.29 | 74.792 | 5 | 73.0731
5297 | 39.5 | 96.5201 | 12.4364 | 73.1131 | 0.3979 |  | 5297 | 28.13 | 96.5201 | 5.7321 | 73.1131
5298 | 42.64 | 133.6818 | 16.4857 | 105.5693 | 0.39921 |  | 5298 | 28.04 | 133.6818 | 6 | 105.5693
5299 | 45.7 | 140.8523 | 14.9378 | 99.2103 | 0.40198 |  | 5299 | 31.29 | 140.8523 | 5.7321 | 99.2103
5300 | 39.18 | 123.5675 | 3.8404 | 124.9523 | 0.40061 |  | 5300 | 34.39 | 123.5675 | 5 | 124.9523
5301 | 36.94 | 102.3551 | 4.0587 | 109.5253 | 0.39649 |  | 5301 | 33.23 | 102.3551 | 4 | 109.5253
5302 | 34.26 | 104.7371 | 4.8724 | 61.519 | 0.38369 |  | 5302 | 34 | 104.7371 | 3 | 61.519
5303 | 31.26 | 76.9257 | 3.1686 | 45.7324 | 0.38038 |  | 5303 | 33.93 | 76.9257 | 2.2679 | 45.7324
5304 | 33.75 | 41.9196 | 3.6423 | 30.8185 | 0.36925 |  | 5304 | 31.75 | 41.9196 | 2 | 30.8185
5305 | 33.57 | 34.0083 | 4.821 | 30.3688 | 0.33786 |  | 5305 | 23.88 | 34.0083 | 2.2679 | 30.3688
5306 | 27.87 | 32.5679 | 2.8492 | 5.2383 | 0.32211 |  | 5306 | 23.06 | 32.5679 | 3 | 5.2383
5307 | 23.4 | 31.0193 | 4.2589 | 15.8605 | 0.31062 |  | 5307 | 22.6 | 31.0193 | 4 | 15.8605
5308 | 16.79 | 29.602 | 3.5316 | 42.9565 | 0.29792 |  | 5308 | 20.32 | 29.602 | 5 | 42.9565
5309 | 16.66 | 28.4865 | 4.2727 | 71.7472 | 0.29558 |  | 5309 | 19.94 | 28.4865 | 5.7321 | 71.7472
5310 | 19 | 28.2698 | 4.6593 | 139.4458 | 0.29222 |  | 5310 | 22.97 | 28.2698 | 6 | 139.4458
5311 | 26.98 | 40.6582 | 3.3748 | 146.7255 | 0.28942 |  | 5311 | 28.33 | 40.6582 | 5.7321 | 146.7255
5312 | 34.11 | 55.611 | 11.6792 | 156.4428 | 0.29703 |  | 5312 | 32.86 | 55.611 | 5 | 156.4428
5313 | 34.9 | 44.2528 | 32.2322 | 118.4766 | 0.2935 |  | 5313 | 34.83 | 44.2528 | 4 | 118.4766
5314 | 28.5 | 43.0856 | 74.2144 | 68.919 | 0.29856 |  | 5314 | 35.03 | 43.0856 | 3 | 68.919
5315 | 27.7 | 47.0746 | 57.7523 | 73.8636 | 0.2919 |  | 5315 | 34.6 | 47.0746 | 2.2679 | 73.8636
5316 | 25.1 | 47.5914 | 90.8093 | 82.3436 | 0.28729 |  | 5316 | 34.26 | 47.5914 | 2 | 82.3436
5317 | 24.8 | 49.1289 | 95.2641 | 72.8538 | 0.28309 |  | 5317 | 33.6 | 49.1289 | 2.2679 | 72.8538
5318 | 19 | 51.634 | 79.8396 | 72.9575 | 0.28492 |  | 5318 | 32.78 | 51.634 | 3 | 72.9575
5319 | 15 | 58.9902 | 85.3797 | 61.7359 | 0.28937 |  | 5319 | 30.22 | 58.9902 | 4 | 61.7359
5320 | 24.68 | 73.5871 | 73.9935 | 64.9953 | 0.29698 |  | 5320 | 27.84 | 73.5871 | 5 | 64.9953
5321 | 29.45 | 90.411 | 7.3509 | 81.1525 | 0.3072 |  | 5321 | 25.97 | 90.411 | 5.7321 | 81.1525
5322 | 28.5 | 131.9131 | 22.697 | 108.2906 | 0.30974 |  | 5322 | 28.12 | 131.9131 | 6 | 108.2906
5323 | 32.92 | 154.8251 | 10.3136 | 115.5508 | 0.31593 |  | 5323 | 30.35 | 154.8251 | 5.7321 | 115.5508
5324 | 35.12 | 113.1288 | 2.8268 | 95.0103 | 0.31803 |  | 5324 | 32.02 | 113.1288 | 5 | 95.0103
5325 | 31.39 | 98.3176 | 4.8085 | 82.5127 | 0.31054 |  | 5325 | 30.91 | 98.3176 | 4 | 82.5127
5326 | 31.83 | 103.4307 | 3.1215 | 72.2393 | 0.3088 |  | 5326 | 30.47 | 103.4307 | 3 | 72.2393
5327 | 33.07 | 76.5735 | 2.5487 | 51.861 | 0.31046 |  | 5327 | 29.1 | 76.5735 | 2.2679 | 51.861
5328 | 27.01 | 39.4465 | 4.4086 | 25.7491 | 0.29667 |  | 5328 | 26.45 | 39.4465 | 2 | 25.7491
5329 | 21.87 | 35.3217 | 3.6217 | 30.3403 | 0.28301 |  | 5329 | 23.35 | 35.3217 | 2.2679 | 30.3403
5330 | 16.6 | 33.5255 | 4.7704 | 6.1953 | 0.28751 |  | 5330 | 23.11 | 33.5255 | 3 | 6.1953
5331 | 12.7 | 31.758 | 2.4673 | 17.8258 | 0.28992 |  | 5331 | 22 | 31.758 | 4 | 17.8258
5332 | 13.13 | 30.1554 | 2.8548 | 45.2198 | 0.28773 |  | 5332 | 19.99 | 30.1554 | 5 | 45.2198
5333 | 13.62 | 29.1593 | 4.932 | 85.4092 | 0.28605 |  | 5333 | 20.19 | 29.1593 | 5.7321 | 85.4092
5334 | 14.44 | 28.6681 | 204.3664 | 123.7662 | 0.28953 |  | 5334 | 23.18 | 28.6681 | 6 | 123.7662
5335 | 20.51 | 41.3873 | 3.0525 | 160.3847 | 0.29368 |  | 5335 | 26.56 | 41.3873 | 5.7321 | 160.3847
5336 | 28.17 | 54.0763 | 18.4973 | 141.0396 | 0.299 |  | 5336 | 32.21 | 54.0763 | 5 | 141.0396
5337 | 30.96 | 43.8796 | 18.6457 | 122.8377 | 0.29609 |  | 5337 | 33.95 | 43.8796 | 4 | 122.8377
5338 | 29 | 43.6969 | 14.1551 | 81.5743 | 0.29472 |  | 5338 | 33.5 | 43.6969 | 3 | 81.5743
5339 | 28 | 47.391 | 12.8293 | 89.3584 | 0.30955 |  | 5339 | 32.01 | 47.391 | 2.2679 | 89.3584
5340 | 31.1 | 48.5964 | 19.9466 | 94.7505 | 0.31724 |  | 5340 | 31.87 | 48.5964 | 2 | 94.7505
5341 | 30.94 | 51.0528 | 8.1928 | 76.8276 | 0.30987 |  | 5341 | 29.66 | 51.0528 | 2.2679 | 76.8276
5342 | 30.61 | 53.6999 | 23.5734 | 55.1814 | 0.31664 |  | 5342 | 26.91 | 53.6999 | 3 | 55.1814
5343 | 31.43 | 58.7144 | 17.5124 | 59.0308 | 0.32189 |  | 5343 | 25.43 | 58.7144 | 4 | 59.0308
5344 | 31 | 76.0632 | 11.3672 | 50.9524 | 0.32806 |  | 5344 | 24.51 | 76.0632 | 5 | 50.9524
5345 | 32.92 | 91.0427 | 14.7971 | 65.9838 | 0.3444 |  | 5345 | 24.31 | 91.0427 | 5.7321 | 65.9838
5346 | 34.16 | 134.9138 | 13.8462 | 103.974 | 0.362 |  | 5346 | 27.33 | 134.9138 | 6 | 103.974
5347 | 39.37 | 134.5 | 26.2369 | 90.8278 | 0.36452 |  | 5347 | 31.48 | 134.5 | 5.7321 | 90.8278
5348 | 41.51 | 128.7817 | 3.7456 | 88.1332 | 0.36762 |  | 5348 | 33.68 | 128.7817 | 5 | 88.1332
5349 | 41.96 | 101.5587 | 4.2206 | 93.2993 | 0.36772 |  | 5349 | 33.72 | 101.5587 | 4 | 93.2993
5350 | 40 | 102.6591 | 4.4342 | 73.2202 | 0.36577 |  | 5350 | 33.93 | 102.6591 | 3 | 73.2202
5351 | 37.29 | 77.1209 | 4.4328 | 53.161 | 0.36208 |  | 5351 | 32.93 | 77.1209 | 2.2679 | 53.161
5352 | 28.79 | 40.8354 | 4.0356 | 21.7258 | 0.36658 |  | 5352 | 28.65 | 40.8354 | 2 | 21.7258
5353 | 29.07 | 33.9153 | 3.9051 | 33.127 | 0.37339 |  | 5353 | 24.23 | 33.9153 | 2.2679 | 33.127
5354 | 27.48 | 32.1686 | 4.9918 | 5.5892 | 0.37164 |  | 5354 | 23.01 | 32.1686 | 3 | 5.5892
5355 | 26.1 | 30.6773 | 3.3135 | 22.5034 | 0.3702 |  | 5355 | 22.72 | 30.6773 | 4 | 22.5034
5356 | 25.5 | 29.3606 | 4.0884 | 53.4245 | 0.38445 |  | 5356 | 20.49 | 29.3606 | 5 | 53.4245
5357 | 27.12 | 28.4619 | 203.8123 | 79.4156 | 0.40174 |  | 5357 | 20.38 | 28.4619 | 5.7321 | 79.4156
5358 | 34.16 | 27.9719 | 3.7652 | 103.0742 | 0.41135 |  | 5358 | 22.77 | 27.9719 | 6 | 103.0742
5359 | 39.02 | 27.7252 | 4.4041 | 139.6757 | 0.41252 |  | 5359 | 27.07 | 27.7252 | 5.7321 | 139.6757
5360 | 39.07 | 30.1376 | 23.6758 | 122.8237 | 0.41013 |  | 5360 | 32.08 | 30.1376 | 5 | 122.8237
5361 | 38.19 | 48.6617 | 13.7865 | 106.7431 | 0.40651 |  | 5361 | 34.97 | 48.6617 | 4 | 106.7431
5362 | 36.7 | 69.3936 | 16.4693 | 88.7483 | 0.40131 |  | 5362 | 33.07 | 69.3936 | 3 | 88.7483
5363 | 37.9 | 74.3969 | 22.5969 | 86.6506 | 0.3995 |  | 5363 | 30.86 | 74.3969 | 2.2679 | 86.6506
5364 | 36.18 | 75.2216 | 17.0106 | 63.8519 | 0.39885 |  | 5364 | 30.48 | 75.2216 | 2 | 63.8519
5365 | 35.79 | 77.5253 | 26.6865 | 76.7497 | 0.40449 |  | 5365 | 28.57 | 77.5253 | 2.2679 | 76.7497
5366 | 36.46 | 74.4795 | 11.5909 | 69.5258 | 0.40289 |  | 5366 | 27.17 | 74.4795 | 3 | 69.5258
5367 | 35.77 | 68.4276 | 22.0297 | 71.3539 | 0.4071 |  | 5367 | 24.99 | 68.4276 | 4 | 71.3539
5368 | 34.88 | 70.8733 | 15.8273 | 55.6748 | 0.40899 |  | 5368 | 25.62 | 70.8733 | 5 | 55.6748
5369 | 44.06 | 77.5044 | 18.5062 | 85.0205 | 0.40719 |  | 5369 | 25.69 | 77.5044 | 5.7321 | 85.0205
5370 | 57.99 | 118.6878 | 28.1648 | 76.5729 | 0.40645 |  | 5370 | 31.4 | 118.6878 | 6 | 76.5729
5371 | 67.86 | 146.1375 | 29.1751 | 105.6828 | 0.41072 |  | 5371 | 34.37 | 146.1375 | 5.7321 | 105.6828
5372 | 66.78 | 132.4821 | 50.3719 | 101.57 | 0.41767 |  | 5372 | 34.95 | 132.4821 | 5 | 101.57
5373 | 61.96 | 100.417 | 10.0968 | 84.3566 | 0.42498 |  | 5373 | 35.11 | 100.417 | 4 | 84.3566
5374 | 44.63 | 103.554 | 18.7363 | 57.0347 | 0.43052 |  | 5374 | 34.82 | 103.554 | 3 | 57.0347
5375 | 36.63 | 89.3871 | 4.3027 | 37.2823 | 0.43281 |  | 5375 | 33.87 | 89.3871 | 2.2679 | 37.2823
5376 | 34.8 | 40.4466 | 4.3039 | 27.7339 | 0.43579 |  | 5376 | 28.82 | 40.4466 | 2 | 27.7339
5377 | 33.7 | 32.3083 | 4.0016 | 32.5014 | 0.43403 |  | 5377 | 24.07 | 32.3083 | 2.2679 | 32.5014
5378 | 32.4 | 31.1651 | 4.5238 | 6.8461 | 0.42614 |  | 5378 | 22.97 | 31.1651 | 3 | 6.8461
5379 | 32.43 | 29.9124 | 5.9065 | 16.1749 | 0.42682 |  | 5379 | 21.05 | 29.9124 | 4 | 16.1749
5380 | 32.24 | 28.6937 | 5.1007 | 52.4342 | 0.40961 |  | 5380 | 19.9 | 28.6937 | 5 | 52.4342
5381 | 32.75 | 27.988 | 12.6731 | 88.9348 | 0.41367 |  | 5381 | 20.05 | 27.988 | 5.7321 | 88.9348
5382 | 42.16 | 27.4794 | 24.3111 | 143.944 | 0.41681 |  | 5382 | 22.98 | 27.4794 | 6 | 143.944
5383 | 51.21 | 27.168 | 5.551 | 129.8352 | 0.40909 |  | 5383 | 27.93 | 27.168 | 5.7321 | 129.8352
5384 | 48.95 | 29.1464 | 25.3198 | 133.5389 | 0.41236 |  | 5384 | 32.55 | 29.1464 | 5 | 133.5389
5385 | 40.85 | 48.2119 | 13.9737 | 109.5467 | 0.4061 |  | 5385 | 33.8 | 48.2119 | 4 | 109.5467
5386 | 38.96 | 67.2148 | 18.0246 | 82.5416 | 0.40793 |  | 5386 | 34.04 | 67.2148 | 3 | 82.5416
5387 | 36.02 | 73.552 | 2.0164 | 87.0267 | 0.40409 |  | 5387 | 34.91 | 73.552 | 2.2679 | 87.0267
5388 | 32.1 | 73.6026 | 15.5037 | 89.3768 | 0.40605 |  | 5388 | 35.25 | 73.6026 | 2 | 89.3768
5389 | 30.94 | 81.2485 | 17.3045 | 73.2434 | 0.39872 |  | 5389 | 34.95 | 81.2485 | 2.2679 | 73.2434
5390 | 29.34 | 79.7319 | 18.4424 | 76.4578 | 0.39501 |  | 5390 | 32.1 | 79.7319 | 3 | 76.4578
5391 | 29.78 | 77.0027 | 16.2211 | 65.7634 | 0.39293 |  | 5391 | 29.5 | 77.0027 | 4 | 65.7634
5392 | 34.9 | 73.1789 | 21.8364 | 57.9117 | 0.3993 |  | 5392 | 27.12 | 73.1789 | 5 | 57.9117
5393 | 37.67 | 74.8473 | 15.9306 | 89.5711 | 0.40221 |  | 5393 | 24.2 | 74.8473 | 5.7321 | 89.5711
5394 | 38.17 | 106.4158 | 25.274 | 84.4554 | 0.40218 |  | 5394 | 26.9 | 106.4158 | 6 | 84.4554
5395 | 46.34 | 124.486 | 23.0517 | 111.3065 | 0.41416 |  | 5395 | 28.09 | 124.486 | 5.7321 | 111.3065
5396 | 48.9 | 138.1373 | 4.7385 | 98.2902 | 0.41802 |  | 5396 | 29.06 | 138.1373 | 5 | 98.2902
5397 | 47.6 | 101.6775 | 4.2462 | 94.7744 | 0.41853 |  | 5397 | 29.13 | 101.6775 | 4 | 94.7744
5398 | 41.82 | 100.9363 | 4.2044 | 65.5128 | 0.41727 |  | 5398 | 28.99 | 100.9363 | 3 | 65.5128
5399 | 36.3 | 86.2778 | 4.916 | 38.7681 | 0.41715 |  | 5399 | 28.34 | 86.2778 | 2.2679 | 38.7681
5400 | 32.39 | 38.3051 | 3.6328 | 22.2623 | 0.41929 |  | 5400 | 24.7 | 38.3051 | 2 | 22.2623
5401 | 30.35 | 34.3167 | 5.0846 | 24.3121 | 0.41923 |  | 5401 | 21.7 | 34.3167 | 2.2679 | 24.3121
5402 | 28.25 | 32.6861 | 3.8708 | 6.5207 | 0.41121 |  | 5402 | 19.97 | 32.6861 | 3 | 6.5207
5403 | 28.18 | 31.0521 | 3.6867 | 21.7369 | 0.41047 |  | 5403 | 18.09 | 31.0521 | 4 | 21.7369
5404 | 29.32 | 29.7185 | 3.2501 | 37.9582 | 0.41309 |  | 5404 | 16.89 | 29.7185 | 5 | 37.9582
5405 | 30.3 | 28.7613 | 4.1474 | 72.7168 | 0.41364 |  | 5405 | 16.1 | 28.7613 | 5.7321 | 72.7168
5406 | 37.93 | 28.2115 | 4.4283 | 136.1042 | 0.41381 |  | 5406 | 14.46 | 28.2115 | 6 | 136.1042
5407 | 47.24 | 41.9836 | 3.5461 | 132.7727 | 0.41179 |  | 5407 | 16.08 | 41.9836 | 5.7321 | 132.7727
5408 | 45.22 | 54.6773 | 18.6215 | 148.5403 | 0.40144 |  | 5408 | 18.05 | 54.6773 | 5 | 148.5403
5409 | 37.77 | 43.9347 | 14.828 | 121.2802 | 0.40031 |  | 5409 | 20.06 | 43.9347 | 4 | 121.2802
5410 | 35.67 | 42.507 | 10.1384 | 77.3021 | 0.40141 |  | 5410 | 20.27 | 42.507 | 3 | 77.3021
5411 | 34.29 | 45.3305 | 18.1283 | 75.2175 | 0.39992 |  | 5411 | 21.62 | 45.3305 | 2.2679 | 75.2175
5412 | 32.02 | 46.9393 | 22.093 | 78.2343 | 0.39552 |  | 5412 | 21.68 | 46.9393 | 2 | 78.2343
5413 | 30 | 49.4978 | 17.2992 | 90.3075 | 0.38726 |  | 5413 | 24.94 | 49.4978 | 2.2679 | 90.3075
5414 | 31.01 | 52.7422 | 19.5041 | 79.7522 | 0.38915 |  | 5414 | 24.91 | 52.7422 | 3 | 79.7522
5415 | 32.32 | 56.3943 | 10.1335 | 65.1022 | 0.39417 |  | 5415 | 24.94 | 56.3943 | 4 | 65.1022
5416 | 33.84 | 72.1913 | 32.239 | 61.6399 | 0.40092 |  | 5416 | 23.88 | 72.1913 | 5 | 61.6399
5417 | 37.83 | 87.873 | 11.5543 | 82.2901 | 0.39696 |  | 5417 | 24.23 | 87.873 | 5.7321 | 82.2901
5418 | 47.87 | 134.6776 | 11.8964 | 79.0127 | 0.39959 |  | 5418 | 26.02 | 134.6776 | 6 | 79.0127
5419 | 62.2 | 145.6038 | 21.7053 | 91.7828 | 0.41035 |  | 5419 | 24.72 | 145.6038 | 5.7321 | 91.7828
5420 | 52.35 | 122.2465 | 3.5441 | 119.3448 | 0.40743 |  | 5420 | 26.88 | 122.2465 | 5 | 119.3448
5421 | 51 | 105.0411 | 3.5682 | 79.0094 | 0.41006 |  | 5421 | 27.7 | 105.0411 | 4 | 79.0094
5422 | 39.82 | 108.7741 | 2.9512 | 73.9209 | 0.39611 |  | 5422 | 29.08 | 108.7741 | 3 | 73.9209
5423 | 35.95 | 77.4488 | 3.9332 | 43.8752 | 0.39108 |  | 5423 | 28.31 | 77.4488 | 2.2679 | 43.8752
5424 | 29.15 | 39.9549 | 4.2025 | 30.3357 | 0.38179 |  | 5424 | 25.73 | 39.9549 | 2 | 30.3357
5425 | 27.74 | 35.0621 | 3.7886 | 27.0134 | 0.3656 |  | 5425 | 23.44 | 35.0621 | 2.2679 | 27.0134
5426 | 28.4 | 33.3853 | 4.6619 | 7.1077 | 0.36021 |  | 5426 | 21.18 | 33.3853 | 3 | 7.1077
5427 | 26.81 | 31.6534 | 4.3457 | 18.7496 | 0.35036 |  | 5427 | 20.13 | 31.6534 | 4 | 18.7496
5428 | 25.1 | 30.1087 | 12.8552 | 48.8978 | 0.34452 |  | 5428 | 19.03 | 30.1087 | 5 | 48.8978
5429 | 21.43 | 28.9496 | 241.4439 | 89.9925 | 0.34925 |  | 5429 | 18.05 | 28.9496 | 5.7321 | 89.9925
5430 | 26.9 | 28.5493 | 51.4125 | 134.0479 | 0.36367 |  | 5430 | 18.08 | 28.5493 | 6 | 134.0479
5431 | 31.99 | 40.5176 | 27.0007 | 163.7627 | 0.37359 |  | 5431 | 18.06 | 40.5176 | 5.7321 | 163.7627
5432 | 35.19 | 54.8903 | 18.0074 | 118.2697 | 0.37796 |  | 5432 | 19.77 | 54.8903 | 5 | 118.2697
5433 | 43.47 | 42.9875 | 25.4292 | 104.6664 | 0.38345 |  | 5433 | 20.56 | 42.9875 | 4 | 104.6664
5434 | 42.02 | 41.046 | 30.9509 | 89.7962 | 0.38138 |  | 5434 | 19.44 | 41.046 | 3 | 89.7962
5435 | 35.28 | 42.7483 | 28.4526 | 88.9824 | 0.37018 |  | 5435 | 19.74 | 42.7483 | 2.2679 | 88.9824
5436 | 34.28 | 43.9181 | 225.1175 | 91.1154 | 0.36503 |  | 5436 | 20.62 | 43.9181 | 2 | 91.1154
5437 | 31.03 | 46.4398 | 16.7186 | 64.5944 | 0.35977 |  | 5437 | 20.24 | 46.4398 | 2.2679 | 64.5944
5438 | 27.9 | 48.6769 | 22.6048 | 79.4091 | 0.35541 |  | 5438 | 18.68 | 48.6769 | 3 | 79.4091
5439 | 28.3 | 57.3575 | 14.0231 | 68.168 | 0.35928 |  | 5439 | 16.99 | 57.3575 | 4 | 68.168
5440 | 31.92 | 71.6642 | 8.9474 | 56.7311 | 0.36545 |  | 5440 | 16.57 | 71.6642 | 5 | 56.7311
5441 | 35.37 | 91.3819 | 28.3566 | 90.557 | 0.36327 |  | 5441 | 21.05 | 91.3819 | 5.7321 | 90.557
5442 | 35.76 | 128.131 | 8.7228 | 102.4726 | 0.37072 |  | 5442 | 20.94 | 128.131 | 6 | 102.4726
5443 | 38.61 | 145.9712 | 3.749 | 117.0363 | 0.37603 |  | 5443 | 26.75 | 145.9712 | 5.7321 | 117.0363
5444 | 40.68 | 119.743 | 3.8408 | 103.4745 | 0.37835 |  | 5444 | 29.57 | 119.743 | 5 | 103.4745
5445 | 36.15 | 97.741 | 4.1874 | 97.448 | 0.38434 |  | 5445 | 31.56 | 97.741 | 4 | 97.448
5446 | 35.07 | 106.027 | 4.1317 | 72.3794 | 0.38951 |  | 5446 | 32.3 | 106.027 | 3 | 72.3794
5447 | 33.33 | 77.0577 | 3.2851 | 39.0466 | 0.3944 |  | 5447 | 31.56 | 77.0577 | 2.2679 | 39.0466
5448 | 29.83 | 40.4086 | 3.41 | 27.9217 | 0.4001 |  | 5448 | 30.9 | 40.4086 | 2 | 27.9217
5449 | 27.3 | 34.6927 | 4.048 | 23.1178 | 0.40628 |  | 5449 | 25.15 | 34.6927 | 2.2679 | 23.1178
5450 | 26.38 | 33.039 | 4.0055 | 5.9082 | 0.40878 |  | 5450 | 22.94 | 33.039 | 3 | 5.9082
5451 | 25.7 | 31.3804 | 3.4407 | 22.1693 | 0.41547 |  | 5451 | 21.61 | 31.3804 | 4 | 22.1693
5452 | 25.65 | 29.9173 | 11.5756 | 41.4476 | 0.41983 |  | 5452 | 21.01 | 29.9173 | 5 | 41.4476
5453 | 28.54 | 28.8832 | 29.7704 | 80.4733 | 0.42554 |  | 5453 | 21.5 | 28.8832 | 5.7321 | 80.4733
5454 | 34.68 | 28.6452 | 34.1518 | 120.9387 | 0.42981 |  | 5454 | 23.29 | 28.6452 | 6 | 120.9387
5455 | 40.52 | 41.9795 | 17.4905 | 157.1535 | 0.42683 |  | 5455 | 27.21 | 41.9795 | 5.7321 | 157.1535
5456 | 43.33 | 56.1785 | 8.9663 | 108.3581 | 0.42473 |  | 5456 | 31.2 | 56.1785 | 5 | 108.3581
5457 | 39.65 | 42.8418 | 15.2891 | 115.3615 | 0.41992 |  | 5457 | 32.44 | 42.8418 | 4 | 115.3615
5458 | 36.73 | 41.0679 | 31.4641 | 86.0883 | 0.41171 |  | 5458 | 30.59 | 41.0679 | 3 | 86.0883
5459 | 34.9 | 42.9466 | 11.2429 | 89.1328 | 0.40214 |  | 5459 | 28.65 | 42.9466 | 2.2679 | 89.1328
5460 | 33.06 | 45.3028 | 8.6055 | 63.6148 | 0.39056 |  | 5460 | 28.32 | 45.3028 | 2 | 63.6148
5461 | 30.54 | 48.3777 | 18.6528 | 72.8538 | 0.38677 |  | 5461 | 27.02 | 48.3777 | 2.2679 | 72.8538
5462 | 31.97 | 49.4608 | 18.7441 | 80.0954 | 0.38839 |  | 5462 | 25 | 49.4608 | 3 | 80.0954
5463 | 29.9 | 57.4932 | 8.5921 | 63.8999 | 0.38985 |  | 5463 | 23.9 | 57.4932 | 4 | 63.8999
5464 | 31.01 | 74.8266 | 16.6611 | 64.0011 | 0.38332 |  | 5464 | 24.1 | 74.8266 | 5 | 64.0011
5465 | 37.4 | 92.8215 | 18.0879 | 89.116 | 0.38806 |  | 5465 | 25.54 | 92.8215 | 5.7321 | 89.116
5466 | 45.84 | 123.1761 | 21.1043 | 94.2147 | 0.39989 |  | 5466 | 30.62 | 123.1761 | 6 | 94.2147
5467 | 55.94 | 136.2048 | 20.3939 | 111.7309 | 0.40289 |  | 5467 | 33.98 | 136.2048 | 5.7321 | 111.7309
5468 | 50.76 | 131.3461 | 3.9894 | 106.5427 | 0.40115 |  | 5468 | 35.88 | 131.3461 | 5 | 106.5427
5469 | 44.42 | 100.4365 | 3.907 | 90.9023 | 0.39932 |  | 5469 | 34.32 | 100.4365 | 4 | 90.9023
5470 | 36.76 | 102.1484 | 3.0934 | 77.9147 | 0.39583 |  | 5470 | 34.47 | 102.1484 | 3 | 77.9147
5471 | 31.19 | 75.167 | 4.4748 | 47.2181 | 0.38336 |  | 5471 | 33.22 | 75.167 | 2.2679 | 47.2181
5472 | 29.4 | 40.725 | 3.8519 | 26.8756 | 0.35881 |  | 5472 | 30.42 | 40.725 | 2 | 26.8756
5473 | 22.59 | 36.2786 | 3.8562 | 24.6249 | 0.32028 |  | 5473 | 26.26 | 36.2786 | 2.2679 | 24.6249
5474 | 18.13 | 34.2563 | 5.0559 | 5.1362 | 0.3102 |  | 5474 | 23.99 | 34.2563 | 3 | 5.1362
5475 | 16.71 | 32.3512 | 5.4341 | 20.8525 | 0.29993 |  | 5475 | 22.94 | 32.3512 | 4 | 20.8525
5476 | 13 | 30.6049 | 4.1842 | 53.5659 | 0.28922 |  | 5476 | 22.03 | 30.6049 | 5 | 53.5659
5477 | 12.51 | 29.3912 | 4.1254 | 96.2506 | 0.28969 |  | 5477 | 22.1 | 29.3912 | 5.7321 | 96.2506
5478 | 16.57 | 29.1759 | 4.0026 | 110.7855 | 0.30041 |  | 5478 | 24.1 | 29.1759 | 6 | 110.7855
5479 | 17.57 | 42.1009 | 3.9947 | 148.488 | 0.30152 |  | 5479 | 28.71 | 42.1009 | 5.7321 | 148.488
5480 | 25.13 | 55.1641 | 13.7371 | 120.8146 | 0.31299 |  | 5480 | 33.63 | 55.1641 | 5 | 120.8146
5481 | 34.21 | 44.0301 | 22.1627 | 99.9938 | 0.33041 |  | 5481 | 34.14 | 44.0301 | 4 | 99.9938
5482 | 32.26 | 43.4166 | 14.2985 | 96.003 | 0.33711 |  | 5482 | 33.9 | 43.4166 | 3 | 96.003
5483 | 31.94 | 45.3041 | 25.8827 | 77.098 | 0.34148 |  | 5483 | 31.73 | 45.3041 | 2.2679 | 77.098
5484 | 26.8 | 48.5881 | 14.0827 | 69.6207 | 0.33838 |  | 5484 | 30.13 | 48.5881 | 2 | 69.6207
5485 | 26.07 | 53.35 | 25.5762 | 79.7885 | 0.34414 |  | 5485 | 29.09 | 53.35 | 2.2679 | 79.7885
5486 | 24.07 | 55.3109 | 30.9227 | 82.0858 | 0.34238 |  | 5486 | 28.93 | 55.3109 | 3 | 82.0858
5487 | 24.04 | 60.1199 | 27.1833 | 53.9212 | 0.35994 |  | 5487 | 28.94 | 60.1199 | 4 | 53.9212
5488 | 25.1 | 75.7484 | 11.7454 | 53.065 | 0.36665 |  | 5488 | 29.29 | 75.7484 | 5 | 53.065
5489 | 31.67 | 95.6692 | 7.0257 | 62.5708 | 0.37212 |  | 5489 | 30.58 | 95.6692 | 5.7321 | 62.5708
5490 | 34.45 | 129.4852 | 18.9468 | 79.9511 | 0.37875 |  | 5490 | 33.12 | 129.4852 | 6 | 79.9511
5491 | 35.76 | 139.6153 | 16.0184 | 85.6286 | 0.38809 |  | 5491 | 34.33 | 139.6153 | 5.7321 | 85.6286
5492 | 37.95 | 126.1809 | 4.1681 | 115.6417 | 0.39332 |  | 5492 | 35.79 | 126.1809 | 5 | 115.6417
5493 | 40 | 104.8506 | 5.0408 | 100.3982 | 0.39163 |  | 5493 | 34.81 | 104.8506 | 4 | 100.3982
5494 | 42.52 | 108.1374 | 4.9699 | 66.9842 | 0.38756 |  | 5494 | 34.36 | 108.1374 | 3 | 66.9842
5495 | 34.39 | 77.268 | 3.1474 | 52.7431 | 0.39233 |  | 5495 | 27.66 | 77.268 | 2.2679 | 52.7431
5496 | 32.29 | 41.9633 | 4.4642 | 26.0173 | 0.38572 |  | 5496 | 23.8 | 41.9633 | 2 | 26.0173
5497 | 31.13 | 32.8913 | 3.2772 | 32.6152 | 0.39191 |  | 5497 | 21.09 | 32.8913 | 2.2679 | 32.6152
5498 | 31.1 | 31.4373 | 3.4809 | 7.5863 | 0.38355 |  | 5498 | 24.01 | 31.4373 | 3 | 7.5863
5499 | 34.82 | 29.945 | 3.8764 | 21.4814 | 0.3871 |  | 5499 | 23.51 | 29.945 | 4 | 21.4814
5500 | 29.9 | 28.7483 | 204.4257 | 43.9467 | 0.37815 |  | 5500 | 21.9 | 28.7483 | 5 | 43.9467
5501 | 29.42 | 28.0719 | 3.0976 | 96.1625 | 0.38035 |  | 5501 | 22.56 | 28.0719 | 5.7321 | 96.1625
5502 | 32.41 | 28.0677 | 2.9315 | 116.3119 | 0.38202 |  | 5502 | 25.05 | 28.0677 | 6 | 116.3119
5503 | 34.78 | 41.1049 | 3.9784 | 123.2259 | 0.37928 |  | 5503 | 29.74 | 41.1049 | 5.7321 | 123.2259
5504 | 34.31 | 54.7896 | 18.9681 | 123.3594 | 0.37901 |  | 5504 | 34.75 | 54.7896 | 5 | 123.3594
5505 | 33.17 | 44.4546 | 22.5137 | 108.093 | 0.37949 |  | 5505 | 36.1 | 44.4546 | 4 | 108.093
5506 | 33.8 | 44.4605 | 15.5397 | 88.9902 | 0.38104 |  | 5506 | 31.13 | 44.4605 | 3 | 88.9902
5507 | 33.75 | 46.7844 | 17.3896 | 63.634 | 0.37475 |  | 5507 | 25.1 | 46.7844 | 2.2679 | 63.634
5508 | 30.24 | 48.9772 | 21.3542 | 78.7085 | 0.38477 |  | 5508 | 25.01 | 48.9772 | 2 | 78.7085
5509 | 27.3 | 51.4401 | 10.8829 | 84.3857 | 0.38325 |  | 5509 | 23.4 | 51.4401 | 2.2679 | 84.3857
5510 | 22.14 | 53.4706 | 12.0771 | 57.1718 | 0.37366 |  | 5510 | 24.4 | 53.4706 | 3 | 57.1718
5511 | 13.87 | 60.2732 | 23.9516 | 70.9331 | 0.36489 |  | 5511 | 24.38 | 60.2732 | 4 | 70.9331
5512 | 18.25 | 73.2634 | 15.5913 | 50.3931 | 0.3544 |  | 5512 | 24.38 | 73.2634 | 5 | 50.3931
5513 | 33.23 | 92.6859 | 15.2265 | 62.4191 | 0.3579 |  | 5513 | 26.24 | 92.6859 | 5.7321 | 62.4191
5514 | 35.82 | 129.3315 | 24.1894 | 100.2204 | 0.36036 |  | 5514 | 34.49 | 129.3315 | 6 | 100.2204
5515 | 37.79 | 150.8727 | 7.4355 | 94.8599 | 0.36312 |  | 5515 | 34.17 | 150.8727 | 5.7321 | 94.8599
5516 | 40.17 | 126.0524 | 3.7767 | 105.1673 | 0.36589 |  | 5516 | 35.96 | 126.0524 | 5 | 105.1673
5517 | 38.68 | 104.9351 | 2.9982 | 107.036 | 0.36408 |  | 5517 | 36.45 | 104.9351 | 4 | 107.036
5518 | 36.97 | 103.6939 | 3.9276 | 63.3407 | 0.36407 |  | 5518 | 34.89 | 103.6939 | 3 | 63.3407
5519 | 33.81 | 75.3517 | 3.7609 | 51.211 | 0.36404 |  | 5519 | 29.48 | 75.3517 | 2.2679 | 51.211
5520 | 28.64 | 38.5378 | 3.9346 | 23.5765 | 0.36117 |  | 5520 | 24.61 | 38.5378 | 2 | 23.5765
5521 | 27.45 | 32.7212 | 4.2358 | 26.4732 | 0.35305 |  | 5521 | 23.83 | 32.7212 | 2.2679 | 26.4732
5522 | 26 | 31.3929 | 4.1914 | 6.4825 | 0.35318 |  | 5522 | 24.12 | 31.3929 | 3 | 6.4825
5523 | 25.79 | 30.0969 | 4.2477 | 22.4641 | 0.35337 |  | 5523 | 23.35 | 30.0969 | 4 | 22.4641
5524 | 27.06 | 28.9118 | 3.4398 | 43.9938 | 0.35903 |  | 5524 | 21.83 | 28.9118 | 5 | 43.9938
5525 | 28.1 | 28.0607 | 5.1438 | 72.7168 | 0.36991 |  | 5525 | 22.49 | 28.0607 | 5.7321 | 72.7168
5526 | 32.35 | 27.6022 | 4.1831 | 112.3278 | 0.38388 |  | 5526 | 25.05 | 27.6022 | 6 | 112.3278
5527 | 42.31 | 27.2705 | 4.3158 | 151.7192 | 0.38069 |  | 5527 | 30.26 | 27.2705 | 5.7321 | 151.7192
5528 | 41.87 | 29.524 | 9.9836 | 150.6834 | 0.3765 |  | 5528 | 33.79 | 29.524 | 5 | 150.6834
5529 | 36.98 | 48.2866 | 19.1538 | 90.7524 | 0.37408 |  | 5529 | 35.67 | 48.2866 | 4 | 90.7524
5530 | 34.19 | 67.932 | 15.017 | 86.0077 | 0.36982 |  | 5530 | 35.33 | 67.932 | 3 | 86.0077
5531 | 32.06 | 77.4573 | 25.2072 | 84.6197 | 0.36697 |  | 5531 | 33.66 | 77.4573 | 2.2679 | 84.6197
5532 | 29.9 | 75.4256 | 16.9886 | 68.6724 | 0.36537 |  | 5532 | 31.63 | 75.4256 | 2 | 68.6724
5533 | 27.9 | 80.7751 | 23.5468 | 79.4768 | 0.36366 |  | 5533 | 29.15 | 80.7751 | 2.2679 | 79.4768
5534 | 27.8 | 75.2976 | 22.1101 | 59.574 | 0.35876 |  | 5534 | 29.44 | 75.2976 | 3 | 59.574
5535 | 27.73 | 71.2711 | 19.5768 | 68.5887 | 0.36288 |  | 5535 | 29.63 | 71.2711 | 4 | 68.5887
5536 | 27.28 | 72.0182 | 10.1273 | 70.3391 | 0.36414 |  | 5536 | 30.31 | 72.0182 | 5 | 70.3391
5537 | 33.06 | 75.5914 | 8.082 | 72.2029 | 0.37145 |  | 5537 | 33 | 75.5914 | 5.7321 | 72.2029
5538 | 38 | 118.9447 | 18.3391 | 105.6631 | 0.37586 |  | 5538 | 35.01 | 118.9447 | 6 | 105.6631
5539 | 43.96 | 130.2484 | 207.9549 | 123.4027 | 0.38564 |  | 5539 | 36.05 | 130.2484 | 5.7321 | 123.4027
5540 | 50.7 | 128.3309 | 5.2842 | 85.0649 | 0.39353 |  | 5540 | 37.34 | 128.3309 | 5 | 85.0649
5541 | 46.81 | 97.1871 | 3.7637 | 98.7387 | 0.40069 |  | 5541 | 36.85 | 97.1871 | 4 | 98.7387
5542 | 40.5 | 101.5237 | 4.712 | 83.8003 | 0.39993 |  | 5542 | 36.01 | 101.5237 | 3 | 83.8003
5543 | 34.92 | 87.0728 | 4.6349 | 44.4788 | 0.39866 |  | 5543 | 33.33 | 87.0728 | 2.2679 | 44.4788
5544 | 31.38 | 38.884 | 4.1212 | 28.0558 | 0.40413 |  | 5544 | 26.15 | 38.884 | 2 | 28.0558
5545 | 29.74 | 33.5626 | 3.3583 | 31.819 | 0.40356 |  | 5545 | 25.42 | 33.5626 | 2.2679 | 31.819
5546 | 29.4 | 32.1236 | 4.1581 | 6.0422 | 0.40413 |  | 5546 | 26.62 | 32.1236 | 3 | 6.0422
5547 | 28.31 | 30.5794 | 4.5925 | 17.9438 | 0.40262 |  | 5547 | 25 | 30.5794 | 4 | 17.9438
5548 | 29.5 | 29.2914 | 4.0695 | 46.3043 | 0.40724 |  | 5548 | 23.91 | 29.2914 | 5 | 46.3043
5549 | 31.75 | 28.528 | 3.9075 | 74.8322 | 0.41399 |  | 5549 | 24.96 | 28.528 | 5.7321 | 74.8322
5550 | 37.16 | 27.9765 | 3.1963 | 153.0691 | 0.41739 |  | 5550 | 26.08 | 27.9765 | 6 | 153.0691
5551 | 44.5 | 27.6793 | 4.9293 | 145.1099 | 0.41912 |  | 5551 | 32.25 | 27.6793 | 5.7321 | 145.1099
5552 | 47.53 | 29.9836 | 29.7173 | 140.7717 | 0.41453 |  | 5552 | 36.25 | 29.9836 | 5 | 140.7717
5553 | 44.73 | 49.7627 | 19.3037 | 109.1314 | 0.4073 |  | 5553 | 37.27 | 49.7627 | 4 | 109.1314
5554 | 39.51 | 68.6269 | 16.6762 | 72.8688 | 0.40375 |  | 5554 | 36.45 | 68.6269 | 3 | 72.8688
5555 | 38.91 | 76.7445 | 28.2417 | 87.4028 | 0.39768 |  | 5555 | 34.48 | 76.7445 | 2.2679 | 87.4028
5556 | 37.93 | 77.3477 | 19.1156 | 75.4685 | 0.39404 |  | 5556 | 31.56 | 77.3477 | 2 | 75.4685
5557 | 37.35 | 83.4214 | 9.6099 | 65.6073 | 0.39323 |  | 5557 | 26.95 | 83.4214 | 2.2679 | 65.6073
5558 | 37.55 | 83.2825 | 15.0847 | 73.8498 | 0.39695 |  | 5558 | 26.01 | 83.2825 | 3 | 73.8498
5559 | 37.98 | 76.9867 | 16.3715 | 55.0032 | 0.40212 |  | 5559 | 25.78 | 76.9867 | 4 | 55.0032
5560 | 37.52 | 74.2331 | 20.0907 | 73.2596 | 0.40526 |  | 5560 | 27.48 | 74.2331 | 5 | 73.2596
5561 | 44.11 | 78.2722 | 14.0349 | 75.6159 | 0.40173 |  | 5561 | 31.76 | 78.2722 | 5.7321 | 75.6159
5562 | 49.34 | 118.1072 | 13.3501 | 100.2204 | 0.41082 |  | 5562 | 34.09 | 118.1072 | 6 | 100.2204
5563 | 53 | 135.1392 | 6.61 | 117.779 | 0.41613 |  | 5563 | 36.09 | 135.1392 | 5.7321 | 117.779
5564 | 53.29 | 145.4428 | 4.009 | 104.8499 | 0.42028 |  | 5564 | 36.46 | 145.4428 | 5 | 104.8499
5565 | 48.35 | 108.7042 | 4.1591 | 94.59 | 0.42582 |  | 5565 | 34.99 | 108.7042 | 4 | 94.59
5566 | 40.61 | 102.6318 | 4.3408 | 73.01 | 0.42678 |  | 5566 | 34.39 | 102.6318 | 3 | 73.01
5567 | 35.85 | 88.0846 | 2.8921 | 53.8574 | 0.42688 |  | 5567 | 29.56 | 88.0846 | 2.2679 | 53.8574
5568 | 33.07 | 40.3843 | 4.8388 | 24.4348 | 0.42609 |  | 5568 | 25.45 | 40.3843 | 2 | 24.4348
5569 | 32.96 | 32.2112 | 120.2373 | 26.985 | 0.4291 |  | 5569 | 26.54 | 32.2112 | 2.2679 | 26.985
5570 | 31.84 | 30.9212 | 118.2414 | 6.7823 | 0.42908 |  | 5570 | 25.04 | 30.9212 | 3 | 6.7823
5571 | 30.8 | 29.8403 | 100.8689 | 16.6073 | 0.42874 |  | 5571 | 23.31 | 29.8403 | 4 | 16.6073
5572 | 31.53 | 28.7651 | 273.803 | 41.8248 | 0.42965 |  | 5572 | 22.81 | 28.7651 | 5 | 41.8248
5573 | 30.63 | 27.995 | 141.5506 | 100.0407 | 0.43125 |  | 5573 | 22.32 | 27.995 | 5.7321 | 100.0407
5574 | 41.42 | 27.6408 | 178.0654 | 121.4528 | 0.43406 |  | 5574 | 22.02 | 27.6408 | 6 | 121.4528
5575 | 55.74 | 40.6593 | 123.8866 | 163.7627 | 0.42987 |  | 5575 | 22.44 | 40.6593 | 5.7321 | 163.7627
5576 | 55.23 | 54.3636 | 119.2142 | 119.877 | 0.42787 |  | 5576 | 23.08 | 54.3636 | 5 | 119.877
5577 | 41.95 | 43.8839 | 144.3667 | 119.3073 | 0.42458 |  | 5577 | 26.94 | 43.8839 | 4 | 119.3073
5578 | 38 | 41.6836 | 152.4359 | 72.3045 | 0.42122 |  | 5578 | 29.03 | 41.6836 | 3 | 72.3045
5579 | 36.97 | 44.332 | 207.7419 | 78.828 | 0.4173 |  | 5579 | 25.79 | 44.332 | 2.2679 | 78.828
5580 | 35.72 | 45.4629 | 176.3972 | 71.4382 | 0.41848 |  | 5580 | 24.22 | 45.4629 | 2 | 71.4382
5581 | 34.05 | 47.0487 | 127.9979 | 89.7621 | 0.4185 |  | 5581 | 23.12 | 47.0487 | 2.2679 | 89.7621
5582 | 33.17 | 48.5951 | 123.1464 | 80.164 | 0.41861 |  | 5582 | 22.09 | 48.5951 | 3 | 80.164
5583 | 32.99 | 54.0248 | 98.407 | 59.6319 | 0.41769 |  | 5583 | 21.71 | 54.0248 | 4 | 59.6319
5584 | 35.44 | 70.1535 | 130.6831 | 62.5099 | 0.4198 |  | 5584 | 22 | 70.1535 | 5 | 62.5099
5585 | 40.14 | 90.2205 | 93.7446 | 71.5203 | 0.42084 |  | 5585 | 20.95 | 90.2205 | 5.7321 | 71.5203
5586 | 49.26 | 131.7426 | 108.2877 | 88.8659 | 0.42673 |  | 5586 | 22.73 | 131.7426 | 6 | 88.8659
5587 | 65.36 | 145.4467 | 138.7843 | 99.3164 | 0.42997 |  | 5587 | 26.99 | 145.4467 | 5.7321 | 99.3164
5588 | 67.32 | 134.0506 | 102.8114 | 124.7407 | 0.43609 |  | 5588 | 29.34 | 134.0506 | 5 | 124.7407
5589 | 52.21 | 104.5476 | 108.5141 | 85.1863 | 0.43877 |  | 5589 | 30 | 104.5476 | 4 | 85.1863
5590 | 44.58 | 105.4486 | 111.8189 | 76.7236 | 0.43842 |  | 5590 | 30.38 | 105.4486 | 3 | 76.7236
5591 | 37.94 | 73.4897 | 129.8578 | 42.8074 | 0.43455 |  | 5591 | 29.11 | 73.4897 | 2.2679 | 42.8074
5592 | 33.26 | 37.402 | 113.4462 | 31.2476 | 0.43261 |  | 5592 | 23.44 | 37.402 | 2 | 31.2476
5593 | 31.87 | 34.5849 | 110.7778 | 33.8094 | 0.42945 |  | 5593 | 18.51 | 34.5849 | 2.2679 | 33.8094
5594 | 30.04 | 32.9408 | 136.626 | 6.6803 | 0.42602 |  | 5594 | 15.01 | 32.9408 | 3 | 6.6803
5595 | 29.79 | 31.3008 | 113.1534 | 17.2166 | 0.4245 |  | 5595 | 12.13 | 31.3008 | 4 | 17.2166
5596 | 27.91 | 29.805 | 121.5329 | 55.1691 | 0.41685 |  | 5596 | 9.72 | 29.805 | 5 | 55.1691
5597 | 28.91 | 28.7633 | 95.502 | 100.0407 | 0.41501 |  | 5597 | 9.83 | 28.7633 | 5.7321 | 100.0407
5598 | 35.94 | 28.5167 | 100.0825 | 153.4546 | 0.41625 |  | 5598 | 9.74 | 28.5167 | 6 | 153.4546
5599 | 41.12 | 42.6439 | 125.3816 | 150.1036 | 0.41142 |  | 5599 | 9.62 | 42.6439 | 5.7321 | 150.1036
5600 | 40.64 | 55.5968 | 195.8197 | 145.7276 | 0.408 |  | 5600 | 9.13 | 55.5968 | 5 | 145.7276
5601 | 37.9 | 44.257 | 173.1875 | 84.5223 | 0.40843 |  | 5601 | 11.34 | 44.257 | 4 | 84.5223
5602 | 34.91 | 43.4927 | 231.1776 | 88.2647 | 0.4067 |  | 5602 | 11.55 | 43.4927 | 3 | 88.2647
5603 | 33.01 | 45.789 | 183.2884 | 86.801 | 0.40813 |  | 5603 | 11.59 | 45.789 | 2.2679 | 86.801
5604 | 32.01 | 48.1667 | 196.1298 | 82.0275 | 0.40609 |  | 5604 | 18.98 | 48.1667 | 2 | 82.0275
5605 | 30.53 | 52.3453 | 135.9206 | 85.9441 | 0.40086 |  | 5605 | 19.31 | 52.3453 | 2.2679 | 85.9441
5606 | 31.21 | 55.0843 | 160.4296 | 68.4277 | 0.39806 |  | 5606 | 18.97 | 55.0843 | 3 | 68.4277
5607 | 31.14 | 57.5453 | 136.9819 | 54.7628 | 0.39823 |  | 5607 | 18.61 | 57.5453 | 4 | 54.7628
5608 | 31.94 | 72.9874 | 164.7892 | 51.6359 | 0.40134 |  | 5608 | 17 | 72.9874 | 5 | 51.6359
5609 | 36.99 | 92.0719 | 229.4253 | 89.0402 | 0.40379 |  | 5609 | 13.53 | 92.0719 | 5.7321 | 89.0402
5610 | 42.47 | 129.3246 | 151.5779 | 80.2327 | 0.41017 |  | 5610 | 14 | 129.3246 | 6 | 80.2327
5611 | 54.6 | 160.1636 | 178.5592 | 113.2164 | 0.41596 |  | 5611 | 22.04 | 160.1636 | 5.7321 | 113.2164
5612 | 51.07 | 119.4438 | 86.2234 | 123.5769 | 0.42125 |  | 5612 | 28.13 | 119.4438 | 5 | 123.5769
5613 | 45.4 | 103.2965 | 100.3353 | 103.5327 | 0.42708 |  | 5613 | 30.74 | 103.2965 | 4 | 103.5327
5614 | 38.48 | 108.279 | 132.9506 | 70.1372 | 0.42671 |  | 5614 | 31.9 | 108.279 | 3 | 70.1372
5615 | 33.95 | 77.4124 | 117.2379 | 46.1967 | 0.42191 |  | 5615 | 30.59 | 77.4124 | 2.2679 | 46.1967
5616 | 30.28 | 40.6621 | 152.3658 | 30.9526 | 0.42138 |  | 5616 | 29.02 | 40.6621 | 2 | 30.9526
5617 | 30.08 | 35.3187 | 184.135 | 31.0512 | 0.42364 |  | 5617 | 20.68 | 35.3187 | 2.2679 | 31.0512
5618 | 29.79 | 33.53 | 201.2234 | 5.519 | 0.42393 |  | 5618 | 19.04 | 33.53 | 3 | 5.519
5619 | 29.62 | 31.6588 | 170.6551 | 21.0687 | 0.42456 |  | 5619 | 18.78 | 31.6588 | 4 | 21.0687
5620 | 30 | 30.0376 | 124.5587 | 38.194 | 0.42544 |  | 5620 | 17.5 | 30.0376 | 5 | 38.194
5621 | 32 | 29.0025 | 111.4723 | 104.4478 | 0.42629 |  | 5621 | 18.07 | 29.0025 | 5.7321 | 104.4478
5622 | 39.47 | 28.8243 | 104.2565 | 109.7573 | 0.42831 |  | 5622 | 20.81 | 28.8243 | 6 | 109.7573
5623 | 43.4 | 41.9225 | 82.4279 | 167.7283 | 0.4275 |  | 5623 | 26.82 | 41.9225 | 5.7321 | 167.7283
5624 | 40.75 | 54.5071 | 159.1312 | 154.7016 | 0.42394 |  | 5624 | 31.42 | 54.5071 | 5 | 154.7016
5625 | 36.68 | 44.1934 | 171.18 | 114.9462 | 0.42129 |  | 5625 | 34.41 | 44.1934 | 4 | 114.9462
5626 | 34.8 | 42.9318 | 184.9131 | 85.7659 | 0.42081 |  | 5626 | 34.93 | 42.9318 | 3 | 85.7659
5627 | 34.13 | 45.1639 | 152.3228 | 81.9119 | 0.41931 |  | 5627 | 30.12 | 45.1639 | 2.2679 | 81.9119
5628 | 31.95 | 46.8588 | 121.9183 | 87.9544 | 0.41909 |  | 5628 | 26.93 | 46.8588 | 2 | 87.9544
5629 | 31.23 | 50.7436 | 122.452 | 68.1007 | 0.41922 |  | 5629 | 23.68 | 50.7436 | 2.2679 | 68.1007
5630 | 30.81 | 52.9053 | 130.5334 | 58.1327 | 0.42003 |  | 5630 | 24 | 52.9053 | 3 | 58.1327
5631 | 31.57 | 61.3839 | 121.3806 | 59.5117 | 0.42148 |  | 5631 | 23.79 | 61.3839 | 4 | 59.5117
5632 | 32.28 | 75.2838 | 130.0187 | 61.5778 | 0.42453 |  | 5632 | 23.8 | 75.2838 | 5 | 61.5778
5633 | 39.77 | 94.2933 | 165.3229 | 82.4418 | 0.42739 |  | 5633 | 24.94 | 94.2933 | 5.7321 | 82.4418
5634 | 47.4 | 129.5654 | 187.0165 | 86.3322 | 0.42994 |  | 5634 | 32.9 | 129.5654 | 6 | 86.3322
5635 | 57.33 | 134.6331 | 170.7228 | 94.7538 | 0.42962 |  | 5635 | 36.59 | 134.6331 | 5.7321 | 94.7538
5636 | 55.56 | 141.2208 | 91.1627 | 91.9421 | 0.42986 |  | 5636 | 37.71 | 141.2208 | 5 | 91.9421
5637 | 44.83 | 109.4717 | 89.0725 | 99.6606 | 0.42863 |  | 5637 | 37.4 | 109.4717 | 4 | 99.6606
5638 | 36.97 | 111.0967 | 129.6038 | 80.9276 | 0.42373 |  | 5638 | 34.34 | 111.0967 | 3 | 80.9276
5639 | 34.68 | 78.4224 | 173.638 | 39.7431 | 0.41799 |  | 5639 | 27.77 | 78.4224 | 2.2679 | 39.7431
5640 | 34.07 | 41.1459 | 407.5861 | 29.9065 | 0.41912 |  | 5640 | 23.98 | 41.1459 | 2 | 29.9065
5641 | 31.86 | 32.623 | 272.5294 | 30.7669 | 0.41687 |  | 5641 | 22.43 | 32.623 | 2.2679 | 30.7669
5642 | 30.86 | 31.2062 | 26.7862 | 7.6182 | 0.41431 |  | 5642 | 22.25 | 31.2062 | 3 | 7.6182
5643 | 30.82 | 29.8766 | 28.083 | 18.6906 | 0.41381 |  | 5643 | 21.62 | 29.8766 | 4 | 18.6906
5644 | 30.03 | 28.7383 | 36.9304 | 53.0001 | 0.41784 |  | 5644 | 20.29 | 28.7383 | 5 | 53.0001
5645 | 30.25 | 28.0537 | 38.5015 | 98.2779 | 0.4208 |  | 5645 | 22.01 | 28.0537 | 5.7321 | 98.2779
5646 | 32.79 | 27.9893 | 69.4247 | 117.7257 | 0.42297 |  | 5646 | 23.52 | 27.9893 | 6 | 117.7257
5647 | 33.96 | 41.6875 | 77.8533 | 153.041 | 0.42287 |  | 5647 | 30.56 | 41.6875 | 5.7321 | 153.041
5648 | 35.95 | 55.6994 | 103.0986 | 153.0943 | 0.42114 |  | 5648 | 35.24 | 55.6994 | 5 | 153.0943
5649 | 35.25 | 43.6664 | 95.1843 | 110.5851 | 0.4204 |  | 5649 | 37.31 | 43.6664 | 4 | 110.5851
5650 | 29.51 | 42.2375 | 104.571 | 73.6748 | 0.42039 |  | 5650 | 37.95 | 42.2375 | 3 | 73.6748
5651 | 27.5 | 43.9887 | 93.929 | 81.7615 | 0.41497 |  | 5651 | 35.13 | 43.9887 | 2.2679 | 81.7615
5652 | 26.83 | 45.3829 | 99.907 | 92.3007 | 0.41446 |  | 5652 | 32.87 | 45.3829 | 2 | 92.3007
5653 | 26.84 | 47.8213 | 75.2866 | 74.49 | 0.41214 |  | 5653 | 29.49 | 47.8213 | 2.2679 | 74.49
5654 | 27.01 | 51.4292 | 56.7146 | 65.4078 | 0.41136 |  | 5654 | 28.79 | 51.4292 | 3 | 65.4078
5655 | 28.03 | 58.2776 | 63.5949 | 56.3858 | 0.41616 |  | 5655 | 28.72 | 58.2776 | 4 | 56.3858
5656 | 28.03 | 71.1375 | 50.7053 | 65.8031 | 0.42113 |  | 5656 | 30.55 | 71.1375 | 5 | 65.8031
5657 | 33.29 | 90.5466 | 44.6871 | 90.0261 | 0.42537 |  | 5657 | 34.63 | 90.5466 | 5.7321 | 90.0261
5658 | 36.93 | 132.441 | 37.9704 | 89.1474 | 0.42664 |  | 5658 | 37.97 | 132.441 | 6 | 89.1474
5659 | 42.39 | 139.1673 | 49.1774 | 98.4675 | 0.42734 |  | 5659 | 40.2 | 139.1673 | 5.7321 | 98.4675
5660 | 38.75 | 122.2608 | 30.9011 | 113.1025 | 0.42699 |  | 5660 | 41.6 | 122.2608 | 5 | 113.1025
5661 | 36.29 | 108.6584 | 25.2941 | 88.5053 | 0.42798 |  | 5661 | 42 | 108.6584 | 4 | 88.5053
5662 | 34.95 | 109.2935 | 25.7738 | 68.9461 | 0.42039 |  | 5662 | 38.92 | 109.2935 | 3 | 68.9461
5663 | 31.67 | 77.8885 | 33.1687 | 44.5717 | 0.41334 |  | 5663 | 33.99 | 77.8885 | 2.2679 | 44.5717
5664 | 29.08 | 38.5074 | 21.0229 | 28.9677 | 0.40573 |  | 5664 | 27.44 | 38.5074 | 2 | 28.9677
5665 | 28.65 | 34.18 | 38.6784 | 29.1461 | 0.40709 |  | 5665 | 26.02 | 34.18 | 2.2679 | 29.1461
5666 | 28.7 | 32.6039 | 31.8176 | 6.106 | 0.41784 |  | 5666 | 23.9 | 32.6039 | 3 | 6.106
5667 | 28.49 | 31.1382 | 23.0724 | 16.5484 | 0.42333 |  | 5667 | 22.82 | 31.1382 | 4 | 16.5484
5668 | 28.7 | 29.7594 | 33.267 | 44.1353 | 0.42683 |  | 5668 | 22.24 | 29.7594 | 5 | 44.1353
5669 | 28.03 | 28.6493 | 33.2362 | 95.9862 | 0.42897 |  | 5669 | 22.25 | 28.6493 | 5.7321 | 95.9862
5670 | 28.28 | 28.2458 | 29.5515 | 127.8789 | 0.42957 |  | 5670 | 24.23 | 28.2458 | 6 | 127.8789
5671 | 31.64 | 42.1358 | 29.6809 | 168.7564 | 0.42803 |  | 5671 | 30.85 | 42.1358 | 5.7321 | 168.7564
5672 | 31.11 | 56.1151 | 40.9017 | 120.1449 | 0.42192 |  | 5672 | 34.9 | 56.1151 | 5 | 120.1449
5673 | 31.48 | 43.1992 | 50.6598 | 111.1043 | 0.41549 |  | 5673 | 36.02 | 43.1992 | 4 | 111.1043
5674 | 25.89 | 42.2975 | 50.2528 | 72.2239 | 0.41101 |  | 5674 | 34.93 | 42.2975 | 3 | 72.2239
5675 | 25.88 | 45.1562 | 41.1979 | 72.8106 | 0.40848 |  | 5675 | 29.96 | 45.1562 | 2.2679 | 72.8106
5676 | 25.83 | 46.2333 | 48.6069 | 83.1339 | 0.40848 |  | 5676 | 27.56 | 46.2333 | 2 | 83.1339
5677 | 25.03 | 50.0145 | 58.1659 | 86.957 | 0.40848 |  | 5677 | 26.83 | 50.0145 | 2.2679 | 86.957
5678 | 25.01 | 51.3994 | 49.2101 | 57.3777 | 0.41075 |  | 5678 | 26.24 | 51.3994 | 3 | 57.3777
5679 | 25.39 | 58.2929 | 40.2125 | 50.5549 | 0.41502 |  | 5679 | 26 | 58.2929 | 4 | 50.5549
5680 | 26.4 | 71.9693 | 38.5794 | 56.1719 | 0.42206 |  | 5680 | 35 | 71.9693 | 5 | 56.1719
5681 | 31.98 | 86.9076 | 41.1354 | 82.9727 | 0.42811 |  | 5681 | 40.97 | 86.9076 | 5.7321 | 82.9727
5682 | 40.85 | 128.2018 | 23.7685 | 76.8544 | 0.43157 |  | 5682 | 36.26 | 128.2018 | 6 | 76.8544
5683 | 46.31 | 139.831 | 35.7989 | 91.4644 | 0.43387 |  | 5683 | 38.77 | 139.831 | 5.7321 | 91.4644
5684 | 46.44 | 119.098 | 22.7759 | 109.611 | 0.43003 |  | 5684 | 39.42 | 119.098 | 5 | 109.611
5685 | 43.05 | 102.914 | 23.9717 | 77.5343 | 0.43077 |  | 5685 | 39.26 | 102.914 | 4 | 77.5343
5686 | 37.49 | 104.8474 | 27.3339 | 63.621 | 0.43402 |  | 5686 | 35.87 | 104.8474 | 3 | 63.621
5687 | 34.52 | 77.1966 | 29.5632 | 49.586 | 0.43484 |  | 5687 | 31.09 | 77.1966 | 2.2679 | 49.586
5688 | 33.67 | 39.617 | 28.3918 | 22.2086 | 0.43157 |  | 5688 | 24.59 | 39.617 | 2 | 22.2086
5689 | 32.95 | 33.1575 | 31.8252 | 31.3356 | 0.42833 |  | 5689 | 23.15 | 33.1575 | 2.2679 | 31.3356
5690 | 32.06 | 31.7625 | 21.0581 | 7.4268 | 0.43032 |  | 5690 | 22.62 | 31.7625 | 3 | 7.4268
5691 | 31.86 | 30.3592 | 22.2769 | 23.5254 | 0.43215 |  | 5691 | 21.29 | 30.3592 | 4 | 23.5254
5692 | 32.1 | 29.0221 | 27.24 | 39.1842 | 0.43583 |  | 5692 | 21.16 | 29.0221 | 5 | 39.1842
5693 | 32.65 | 28.4078 | 32.8566 | 86.1143 | 0.43996 |  | 5693 | 21.45 | 28.4078 | 5.7321 | 86.1143
5694 | 48.91 | 27.9255 | 29.557 | 112.0707 | 0.44487 |  | 5694 | 23.3 | 27.9255 | 6 | 112.0707
5695 | 66.55 | 27.7403 | 32.0684 | 154.0692 | 0.44256 |  | 5695 | 30.33 | 27.7403 | 5.7321 | 154.0692
5696 | 60.61 | 30.5365 | 43.1828 | 156.5768 | 0.43941 |  | 5696 | 34.2 | 30.5365 | 5 | 156.5768
5697 | 48.94 | 49.5434 | 39.3849 | 109.9621 | 0.43889 |  | 5697 | 35.71 | 49.5434 | 4 | 109.9621
5698 | 45.7 | 69.7348 | 54.4761 | 87.2974 | 0.44172 |  | 5698 | 40.93 | 69.7348 | 3 | 87.2974
5699 | 43.74 | 78.219 | 31.1111 | 75.0671 | 0.44565 |  | 5699 | 51.61 | 78.219 | 2.2679 | 75.0671
5700 | 40.91 | 79.1252 | 54.4369 | 87.0061 | 0.44655 |  | 5700 | 52.16 | 79.1252 | 2 | 87.0061
5701 | 38.96 | 86.0946 | 49.8491 | 65.0619 | 0.44602 |  | 5701 | 52.17 | 86.0946 | 2.2679 | 65.0619
5702 | 38.25 | 79.6026 | 43.3915 | 68.3591 | 0.4477 |  | 5702 | 50.27 | 79.6026 | 3 | 68.3591
5703 | 38.39 | 77.5162 | 39.9871 | 55.8448 | 0.44882 |  | 5703 | 48.81 | 77.5162 | 4 | 55.8448
5704 | 43.46 | 78.8803 | 43.7169 | 52.1951 | 0.45074 |  | 5704 | 42.5 | 78.8803 | 5 | 52.1951
5705 | 52.38 | 79.688 | 38.7969 | 75.7676 | 0.4507 |  | 5705 | 48.19 | 79.688 | 5.7321 | 75.7676
5706 | 55.14 | 127.6853 | 34.8099 | 108.7598 | 0.45136 |  | 5706 | 50.01 | 127.6853 | 6 | 108.7598
5707 | 65.27 | 140.1548 | 45.8633 | 126.1615 | 0.45397 |  | 5707 | 47.69 | 140.1548 | 5.7321 | 126.1615
5708 | 58.36 | 137.6924 | 25.5981 | 86.9694 | 0.45175 |  | 5708 | 39.5 | 137.6924 | 5 | 86.9694
5709 | 55.01 | 109.416 | 31.6064 | 90.4413 | 0.45126 |  | 5709 | 38.94 | 109.416 | 4 | 90.4413
5710 | 47.87 | 107.632 | 30.4714 | 82.8194 | 0.45112 |  | 5710 | 44.01 | 107.632 | 3 | 82.8194
5711 | 39.44 | 89.8548 | 27.6507 | 48.1931 | 0.45013 |  | 5711 | 30.65 | 89.8548 | 2.2679 | 48.1931
5712 | 38.33 | 40.2114 | 229.4414 | 27.1975 | 0.44231 |  | 5712 | 25.9 | 40.2114 | 2 | 27.1975
5713 | 35.26 | 32.3367 | 31.124 | 28.3214 | 0.44077 |  | 5713 | 23.67 | 32.3367 | 2.2679 | 28.3214
5714 | 34.79 | 31.0145 | 28.1178 | 7.3821 | 0.44272 |  | 5714 | 21.01 | 31.0145 | 3 | 7.3821
5715 | 34.5 | 29.7189 | 66.2924 | 18.2189 | 0.44687 |  | 5715 | 20.31 | 29.7189 | 4 | 18.2189
5716 | 34.71 | 28.7107 | 146.3412 | 54.6033 | 0.45657 |  | 5716 | 20.23 | 28.7107 | 5 | 54.6033
5717 | 35.74 | 27.8731 | 126.5709 | 101.3628 | 0.46609 |  | 5717 | 21.25 | 27.8731 | 5.7321 | 101.3628
5718 | 44.75 | 27.4332 | 88.1216 | 115.5408 | 0.47111 |  | 5718 | 23.1 | 27.4332 | 6 | 115.5408
5719 | 56.13 | 27.2251 | 97.0856 | 134.8289 | 0.46877 |  | 5719 | 29 | 27.2251 | 5.7321 | 134.8289
5720 | 53.69 | 29.3278 | 77.819 | 137.5572 | 0.46661 |  | 5720 | 34.59 | 29.3278 | 5 | 137.5572
5721 | 53.53 | 48.2273 | 93.8614 | 124.2914 | 0.4648 |  | 5721 | 37.04 | 48.2273 | 4 | 124.2914
5722 | 50.95 | 65.6578 | 98.3364 | 64.9693 | 0.46257 |  | 5722 | 39.94 | 65.6578 | 3 | 64.9693
5723 | 48.82 | 72.0083 | 129.5405 | 88.7567 | 0.46491 |  | 5723 | 39.16 | 72.0083 | 2.2679 | 88.7567
5724 | 45.15 | 70.9235 | 108.4114 | 78.8665 | 0.46403 |  | 5724 | 35 | 70.9235 | 2 | 78.8665
5725 | 44.93 | 77.7939 | 60.3352 | 75.0355 | 0.46493 |  | 5725 | 35 | 77.7939 | 2.2679 | 75.0355
5726 | 45.06 | 77.0138 | 53.4528 | 68.4277 | 0.46367 |  | 5726 | 35 | 77.0138 | 3 | 68.4277
5727 | 45.11 | 77.5866 | 42.1872 | 51.156 | 0.46565 |  | 5727 | 30.12 | 77.5866 | 4 | 51.156
5728 | 48.08 | 72.4194 | 32.2698 | 66.4866 | 0.46865 |  | 5728 | 34.94 | 72.4194 | 5 | 66.4866
5729 | 51.22 | 74.7995 | 45.2748 | 63.4809 | 0.46943 |  | 5729 | 34.13 | 74.7995 | 5.7321 | 63.4809
5730 | 56.99 | 113.5397 | 36.6454 | 107.6337 | 0.47158 |  | 5730 | 36.3 | 113.5397 | 6 | 107.6337
5731 | 63.07 | 141.8385 | 43.8794 | 107.805 | 0.47392 |  | 5731 | 39.65 | 141.8385 | 5.7321 | 107.805
5732 | 56.05 | 125.3896 | 29.1396 | 105.1673 | 0.47726 |  | 5732 | 42.67 | 125.3896 | 5 | 105.1673
5733 | 51.2 | 105.9663 | 47.2518 | 105.561 | 0.47789 |  | 5733 | 40.65 | 105.9663 | 4 | 105.561
5734 | 46.18 | 96.9497 | 91.019 | 77.144 | 0.48005 |  | 5734 | 38.53 | 96.9497 | 3 | 77.144
5735 | 37.49 | 83.7259 | 74.7708 | 42.8538 | 0.47732 |  | 5735 | 32.6 | 83.7259 | 2.2679 | 42.8538
5736 | 38.08 | 38.6991 | 46.8058 | 31.945 | 0.47293 |  | 5736 | 27.34 | 38.6991 | 2 | 31.945
5737 | 35.55 | 32.6798 | 95.7748 | 33.4682 | 0.46163 |  | 5737 | 23.72 | 32.6798 | 2.2679 | 33.4682
5738 | 34.92 | 31.4121 | 82.2358 | 7.3374 | 0.45694 |  | 5738 | 22.15 | 31.4121 | 3 | 7.3374
5739 | 34.66 | 30.0141 | 299.4437 | 21.0883 | 0.45665 |  | 5739 | 23 | 30.0141 | 4 | 21.0883
5740 | 34.08 | 28.8359 | 48.8643 | 52.1042 | 0.46152 |  | 5740 | 23.07 | 28.8359 | 5 | 52.1042
5741 | 35.33 | 28.1263 | 42.0469 | 86.3787 | 0.4665 |  | 5741 | 23.28 | 28.1263 | 5.7321 | 86.3787
5742 | 47.76 | 27.8605 | 93.0397 | 136.1042 | 0.4707 |  | 5742 | 23.18 | 27.8605 | 6 | 136.1042
5743 | 64.1 | 41.8974 | 103.8626 | 134.0945 | 0.46754 |  | 5743 | 25.28 | 41.8974 | 5.7321 | 134.0945
5744 | 65.41 | 56.3029 | 105.0613 | 151.487 | 0.46324 |  | 5744 | 26.84 | 56.3029 | 5 | 151.487
5745 | 55.75 | 44.3499 | 102.9937 | 123.1492 | 0.46358 |  | 5745 | 29.5 | 44.3499 | 4 | 123.1492
5746 | 52.79 | 42.6786 | 91.4844 | 96.003 | 0.45315 |  | 5746 | 30.41 | 42.6786 | 3 | 96.003
5747 | 51.7 | 44.328 | 99.922 | 61.1519 | 0.45218 |  | 5747 | 31.29 | 44.328 | 2.2679 | 61.1519
5748 | 46.55 | 44.9527 | 112.1127 | 76.97 | 0.45546 |  | 5748 | 32.8 | 44.9527 | 2 | 76.97
5749 | 44.73 | 48.512 | 89.4569 | 87.5024 | 0.4623 |  | 5749 | 33.05 | 48.512 | 2.2679 | 87.5024
5750 | 45 | 49.9184 | 81.3413 | 75.3597 | 0.4636 |  | 5750 | 30.85 | 49.9184 | 3 | 75.3597
5751 | 45.6 | 55.5999 | 82.2173 | 70.6927 | 0.4652 |  | 5751 | 29 | 55.5999 | 4 | 70.6927
5752 | 48.83 | 68.2119 | 52.968 | 68.6614 | 0.46805 |  | 5752 | 30.07 | 68.2119 | 5 | 68.6614
5753 | 56.52 | 91.0099 | 51.9326 | 68.0315 | 0.47 |  | 5753 | 23.78 | 91.0099 | 5.7321 | 68.0315
5754 | 71 | 125.1964 | 42.1056 | 104.1617 | 0.47079 |  | 5754 | 28.41 | 125.1964 | 6 | 104.1617
5755 | 77.83 | 147.202 | 43.6225 | 124.676 | 0.47413 |  | 5755 | 34.94 | 147.202 | 5.7321 | 124.676
5756 | 71.91 | 125.089 | 32.8503 | 106.4369 | 0.47753 |  | 5756 | 35.36 | 125.089 | 5 | 106.4369
5757 | 57.29 | 120.0087 | 53.1947 | 110.2628 | 0.47452 |  | 5757 | 34.95 | 120.0087 | 4 | 110.2628
5758 | 50.79 | 108.3552 | 75.796 | 79.1759 | 0.47256 |  | 5758 | 33.61 | 108.3552 | 3 | 79.1759
5759 | 43.92 | 77.602 | 49.6206 | 51.6753 | 0.47159 |  | 5759 | 22.98 | 77.602 | 2.2679 | 51.6753
5760 | 39.54 | 37.6675 | 51.9387 | 23.7643 | 0.46924 |  | 5760 | 22.23 | 37.6675 | 2 | 23.7643
5761 | 35.64 | 33.242 | 64.5643 | 33.4113 | 0.46761 |  | 5761 | 23.14 | 33.242 | 2.2679 | 33.4113
5762 | 34.15 | 31.7684 | 55.536 | 6.9993 | 0.46086 |  | 5762 | 20.98 | 31.7684 | 3 | 6.9993
5763 | 32.25 | 30.2962 | 81.6085 | 18.4351 | 0.45473 |  | 5763 | 21.01 | 30.2962 | 4 | 18.4351
5764 | 32.22 | 29.0392 | 90.6486 | 44.2768 | 0.45559 |  | 5764 | 21.29 | 29.0392 | 5 | 44.2768
5765 | 32.73 | 28.2485 | 80.9677 | 78.2697 | 0.45825 |  | 5765 | 20.51 | 28.2485 | 5.7321 | 78.2697
5766 | 42.84 | 28.2404 | 92.4811 | 144.2011 | 0.45595 |  | 5766 | 19.83 | 28.2404 | 6 | 144.2011
5767 | 52.1 | 42.6805 | 75.6602 | 168.1689 | 0.45129 |  | 5767 | 20.48 | 42.6805 | 5.7321 | 168.1689
5768 | 58.16 | 55.6714 | 104.7083 | 116.2606 | 0.45042 |  | 5768 | 20.18 | 55.6714 | 5 | 116.2606
5769 | 56.56 | 43.2918 | 104.4698 | 102.7974 | 0.45288 |  | 5769 | 22.07 | 43.2918 | 4 | 102.7974
5770 | 51.9 | 42.1809 | 128.4315 | 89.3932 | 0.45048 |  | 5770 | 23.19 | 42.1809 | 3 | 89.3932
5771 | 50.01 | 46.1521 | 122.2348 | 86.1241 | 0.44675 |  | 5771 | 22.05 | 46.1521 | 2.2679 | 86.1241
5772 | 42.12 | 47.3478 | 98.3746 | 69.6207 | 0.44684 |  | 5772 | 21.45 | 47.3478 | 2 | 69.6207
5773 | 39.62 | 49.4405 | 109.9647 | 62.4127 | 0.4465 |  | 5773 | 24.91 | 49.4405 | 2.2679 | 62.4127
5774 | 37.77 | 51.219 | 109.4587 | 73.9184 | 0.44966 |  | 5774 | 21.72 | 51.219 | 3 | 73.9184
5775 | 36.88 | 57.7063 | 99.2515 | 68.2882 | 0.45057 |  | 5775 | 21.39 | 57.7063 | 4 | 68.2882
5776 | 37.42 | 74.4603 | 124.5331 | 71.7061 | 0.45453 |  | 5776 | 20.32 | 74.4603 | 5 | 71.7061
5777 | 44 | 91.9789 | 93.1932 | 87.5233 | 0.45751 |  | 5777 | 18.15 | 91.9789 | 5.7321 | 87.5233
5778 | 50.85 | 131.262 | 63.9992 | 77.4175 | 0.46093 |  | 5778 | 22.26 | 131.262 | 6 | 77.4175
5779 | 60.64 | 139.5557 | 48.198 | 110.2454 | 0.46582 |  | 5779 | 29.01 | 139.5557 | 5.7321 | 110.2454
5780 | 56.19 | 130.4665 | 59.5513 | 126.3277 | 0.47192 |  | 5780 | 32.95 | 130.4665 | 5 | 126.3277
5781 | 50.96 | 109.7702 | 72.7697 | 106.5751 | 0.47386 |  | 5781 | 33.92 | 109.7702 | 4 | 106.5751
5782 | 44.95 | 107.1711 | 96.0773 | 79.7364 | 0.47667 |  | 5782 | 33.25 | 107.1711 | 3 | 79.7364
5783 | 37.4 | 75.2772 | 274.3865 | 41.6466 | 0.47473 |  | 5783 | 29.97 | 75.2772 | 2.2679 | 41.6466
5784 | 34.33 | 38.4356 | 33.0963 | 23.1206 | 0.46059 |  | 5784 | 23.3 | 38.4356 | 2 | 23.1206
5785 | 31.5 | 35.6081 | 35.3193 | 23.2031 | 0.44623 |  | 5785 | 22.16 | 35.6081 | 2.2679 | 23.2031
5786 | 29.41 | 33.7317 | 59.1105 | 6.8717 | 0.44066 |  | 5786 | 23.22 | 33.7317 | 3 | 6.8717
5787 | 28.84 | 31.9232 | 71.2272 | 19.8109 | 0.43971 |  | 5787 | 23.3 | 31.9232 | 4 | 19.8109
5788 | 28.75 | 30.2847 | 37.7921 | 47.436 | 0.44223 |  | 5788 | 23.14 | 30.2847 | 5 | 47.436
5789 | 30.1 | 29.1121 | 75.7361 | 79.5918 | 0.44215 |  | 5789 | 22.61 | 29.1121 | 5.7321 | 79.5918
5790 | 41.27 | 29.0002 | 99.3179 | 129.1641 | 0.445 |  | 5790 | 24.52 | 29.0002 | 6 | 129.1641
5791 | 51.07 | 43.7669 | 92.8291 | 136.7382 | 0.44651 |  | 5791 | 34.87 | 43.7669 | 5.7321 | 136.7382
5792 | 50.76 | 57.8533 | 98.7208 | 128.851 | 0.4464 |  | 5792 | 40.26 | 57.8533 | 5 | 128.851
5793 | 46.04 | 43.9688 | 67.2898 | 115.4654 | 0.44601 |  | 5793 | 41.8 | 43.9688 | 4 | 115.4654
5794 | 41.36 | 42.2708 | 64.292 | 85.8465 | 0.43718 |  | 5794 | 38.48 | 42.2708 | 3 | 85.8465
5795 | 38.19 | 44.6712 | 86.2341 | 84.4693 | 0.42799 |  | 5795 | 44.65 | 44.6712 | 2.2679 | 84.4693
5796 | 34.94 | 45.8404 | 37.3537 | 78.7875 | 0.42179 |  | 5796 | 42.25 | 45.8404 | 2 | 78.7875
5797 | 34.33 | 49.6272 | 44.906 | 70.2045 | 0.42003 |  | 5797 | 31.76 | 49.6272 | 2.2679 | 70.2045
5798 | 34.03 | 52.1927 | 53.0758 | 74.1243 | 0.42256 |  | 5798 | 30.34 | 52.1927 | 3 | 74.1243
5799 | 35.27 | 58.3014 | 49.1376 | 66.9657 | 0.42411 |  | 5799 | 28.68 | 58.3014 | 4 | 66.9657
5800 | 36.22 | 74.7301 | 40.1064 | 61.9506 | 0.43292 |  | 5800 | 29.21 | 74.7301 | 5 | 61.9506
5801 | 43.4 | 95.8054 | 38.2267 | 62.7225 | 0.44326 |  | 5801 | 30.35 | 95.8054 | 5.7321 | 62.7225
5802 | 50.49 | 140.6485 | 31.0185 | 79.1066 | 0.45001 |  | 5802 | 34.06 | 140.6485 | 6 | 79.1066
5803 | 52.34 | 143.0705 | 38.8201 | 111.2004 | 0.45436 |  | 5803 | 37.11 | 143.0705 | 5.7321 | 111.2004
5804 | 52.49 | 127.9071 | 33.7256 | 107.6008 | 0.4566 |  | 5804 | 38.44 | 127.9071 | 5 | 107.6008
5805 | 51.51 | 119.555 | 29.0581 | 108.2346 | 0.45945 |  | 5805 | 39.14 | 119.555 | 4 | 108.2346
5806 | 48.14 | 110.1212 | 27.2414 | 59.8374 | 0.45997 |  | 5806 | 35.91 | 110.1212 | 3 | 59.8374
5807 | 38.72 | 79.8826 | 39.1998 | 43.4109 | 0.46358 |  | 5807 | 30.89 | 79.8826 | 2.2679 | 43.4109
5808 | 37.39 | 41.5304 | 29.1381 | 22.5573 | 0.45253 |  | 5808 | 24.19 | 41.5304 | 2 | 22.5573
5809 | 32.66 | 32.5761 | 28.2341 | 29.3451 | 0.44225 |  | 5809 | 23.53 | 32.5761 | 2.2679 | 29.3451
5810 | 30.64 | 31.3352 | 27.9364 | 7.1588 | 0.44022 |  | 5810 | 22 | 31.3352 | 3 | 7.1588
5811 | 28.12 | 30.0805 | 26.0601 | 19.3981 | 0.43462 |  | 5811 | 22.49 | 30.0805 | 4 | 19.3981
5812 | 27.76 | 28.9624 | 38.1069 | 47.9075 | 0.4299 |  | 5812 | 22.91 | 28.9624 | 5 | 47.9075
5813 | 27.13 | 28.1274 | 62.809 | 97.8371 | 0.42961 |  | 5813 | 22.74 | 28.1274 | 5.7321 | 97.8371
5814 | 28.11 | 27.9704 | 99.3796 | 105.2591 | 0.43201 |  | 5814 | 23.15 | 27.9704 | 6 | 105.2591
5815 | 27.8 | 42.3302 | 80.3134 | 166.2596 | 0.43175 |  | 5815 | 31.74 | 42.3302 | 5.7321 | 166.2596
5816 | 32.06 | 54.9929 | 116.0804 | 119.0733 | 0.42946 |  | 5816 | 40.59 | 54.9929 | 5 | 119.0733
5817 | 33.72 | 42.8986 | 91.4806 | 106.9508 | 0.4274 |  | 5817 | 43.82 | 42.8986 | 4 | 106.9508
5818 | 31.29 | 42.3533 | 86.076 | 89.232 | 0.42777 |  | 5818 | 39.9 | 42.3533 | 3 | 89.232
5819 | 30.44 | 45.7736 | 48.5222 | 68.8993 | 0.42776 |  | 5819 | 34.88 | 45.7736 | 2.2679 | 68.8993
5820 | 28.6 | 46.2972 | 33.9966 | 72.5446 | 0.42849 |  | 5820 | 29 | 46.2972 | 2 | 72.5446
5821 | 28.5 | 49.3001 | 38.1275 | 83.8403 | 0.42793 |  | 5821 | 26.46 | 49.3001 | 2.2679 | 83.8403
5822 | 28.03 | 50.0848 | 45.997 | 57.515 | 0.42572 |  | 5822 | 26.97 | 50.0848 | 3 | 57.515
5823 | 28.13 | 56.3481 | 37.5203 | 61.5555 | 0.42691 |  | 5823 | 26.86 | 56.3481 | 4 | 61.5555
5824 | 29.87 | 70.3302 | 39.5206 | 52.6922 | 0.43214 |  | 5824 | 28.96 | 70.3302 | 5 | 52.6922
5825 | 32.59 | 91.2208 | 43.6064 | 88.3576 | 0.43193 |  | 5825 | 33.33 | 91.2208 | 5.7321 | 88.3576
5826 | 40.68 | 133.1165 | 34.2676 | 84.1739 | 0.42998 |  | 5826 | 38.34 | 133.1165 | 6 | 84.1739
5827 | 48.34 | 143.2854 | 35.9268 | 100.1652 | 0.43025 |  | 5827 | 41.28 | 143.2854 | 5.7321 | 100.1652
5828 | 47.45 | 122.9947 | 26.7169 | 93.0001 | 0.42527 |  | 5828 | 44.11 | 122.9947 | 5 | 93.0001
5829 | 41.42 | 110.203 | 29.2197 | 104.0859 | 0.42459 |  | 5829 | 44.94 | 110.203 | 4 | 104.0859
5830 | 37.07 | 108.0309 | 23.5334 | 76.3032 | 0.41876 |  | 5830 | 41.25 | 108.0309 | 3 | 76.3032
5831 | 33.02 | 75.6346 | 32.2444 | 54.2753 | 0.40209 |  | 5831 | 33.85 | 75.6346 | 2.2679 | 54.2753
5832 | 27.2 | 37.6111 | 27.2669 | 25.8296 | 0.39971 |  | 5832 | 25.83 | 37.6111 | 2 | 25.8296
5833 | 26.7 | 33.3416 | 35.6877 | 27.2978 | 0.40044 |  | 5833 | 22.95 | 33.3416 | 2.2679 | 27.2978
5834 | 26.47 | 31.7933 | 37.3207 | 6.1252 | 0.39845 |  | 5834 | 23.14 | 31.7933 | 3 | 6.1252
5835 | 25.93 | 30.3601 | 233.2894 | 16.5877 | 0.39242 |  | 5835 | 22.45 | 30.3601 | 4 | 16.5877
5836 | 25.34 | 29.0845 | 23.7272 | 44.9841 | 0.39649 |  | 5836 | 22.77 | 29.0845 | 5 | 44.9841
5837 | 25.99 | 28.3454 | 31.1954 | 74.3915 | 0.3952 |  | 5837 | 22.79 | 28.3454 | 5.7321 | 74.3915
5838 | 26.49 | 28.53 | 34.4809 | 116.826 | 0.40742 |  | 5838 | 23.24 | 28.53 | 6 | 116.826
5839 | 26.49 | 42.2805 | 35.5468 | 123.2259 | 0.41149 |  | 5839 | 25.17 | 42.2805 | 5.7321 | 123.2259
5840 | 26.84 | 56.9647 | 53.8848 | 132.3335 | 0.41048 |  | 5840 | 40.46 | 56.9647 | 5 | 132.3335
5841 | 30.1 | 45.0324 | 43.6508 | 103.4204 | 0.41325 |  | 5841 | 41.69 | 45.0324 | 4 | 103.4204
5842 | 29.7 | 44.2407 | 47.3409 | 76.7379 | 0.41206 |  | 5842 | 35.48 | 44.2407 | 3 | 76.7379
5843 | 30.17 | 47.6713 | 44.5395 | 64.2358 | 0.40985 |  | 5843 | 27.93 | 47.6713 | 2.2679 | 64.2358
5844 | 31.01 | 47.5501 | 42.3667 | 87.6383 | 0.40832 |  | 5844 | 26 | 47.5501 | 2 | 87.6383
5845 | 30.23 | 50.8741 | 45.6326 | 90.775 | 0.40917 |  | 5845 | 26.38 | 50.8741 | 2.2679 | 90.775
5846 | 28.39 | 52.9178 | 45.414 | 77.3501 | 0.40082 |  | 5846 | 24.94 | 52.9178 | 3 | 77.3501
5847 | 27.74 | 57.6286 | 37.505 | 51.5167 | 0.38828 |  | 5847 | 25.17 | 57.6286 | 4 | 51.5167
5848 | 27.2 | 77.2719 | 53.2934 | 62.0749 | 0.39515 |  | 5848 | 25.04 | 77.2719 | 5 | 62.0749
5849 | 29.94 | 95.1129 | 48.9326 | 64.6186 | 0.40388 |  | 5849 | 29.94 | 95.1129 | 5.7321 | 64.6186
5850 | 34.07 | 125.116 | 54.8373 | 83.6109 | 0.41694 |  | 5850 | 35.34 | 125.116 | 6 | 83.6109
5851 | 36.52 | 151.086 | 248.2936 | 93.4805 | 0.42595 |  | 5851 | 39.93 | 151.086 | 5.7321 | 93.4805
5852 | 39.67 | 133.7072 | 27.4699 | 90.4608 | 0.42543 |  | 5852 | 41.78 | 133.7072 | 5 | 90.4608
5853 | 38.76 | 111.3335 | 28.1355 | 100.3982 | 0.41056 |  | 5853 | 40.8 | 111.3335 | 4 | 100.3982
5854 | 37.33 | 103.8832 | 30.9459 | 79.8766 | 0.41115 |  | 5854 | 37.56 | 103.8832 | 3 | 79.8766
5855 | 34.35 | 75.5022 | 32.237 | 45.0824 | 0.41949 |  | 5855 | 27.2 | 75.5022 | 2.2679 | 45.0824
5856 | 29.28 | 38.7957 | 23.0765 | 25.2931 | 0.41701 |  | 5856 | 24.88 | 38.7957 | 2 | 25.2931
5857 | 26.97 | 32.5904 | 29.5448 | 24.8239 | 0.41202 |  | 5857 | 23.6 | 32.5904 | 2.2679 | 24.8239
5858 | 25.96 | 31.292 | 32.7035 | 7.1907 | 0.40962 |  | 5858 | 23.46 | 31.292 | 3 | 7.1907
5859 | 25 | 29.9417 | 36.4747 | 18.8478 | 0.41628 |  | 5859 | 23.21 | 29.9417 | 4 | 18.8478
5860 | 25.63 | 28.8372 | 28.0253 | 54.1318 | 0.42634 |  | 5860 | 22.98 | 28.8372 | 5 | 54.1318
5861 | 27.73 | 28.0883 | 29.4191 | 76.0662 | 0.43327 |  | 5861 | 23.59 | 28.0883 | 5.7321 | 76.0662
5862 | 37.88 | 27.5085 | 23.5911 | 130.0637 | 0.44544 |  | 5862 | 24.88 | 27.5085 | 6 | 130.0637
5863 | 46.09 | 27.3059 | 33.2374 | 136.4445 | 0.45258 |  | 5863 | 32.93 | 27.3059 | 5.7321 | 136.4445
5864 | 49.55 | 29.5687 | 47.0433 | 155.6392 | 0.449 |  | 5864 | 39.94 | 29.5687 | 5 | 155.6392
5865 | 48.29 | 47.8515 | 38.4221 | 89.6103 | 0.44673 |  | 5865 | 42.31 | 47.8515 | 4 | 89.6103
5866 | 44.07 | 67.0362 | 54.1857 | 93.4236 | 0.4447 |  | 5866 | 40.92 | 67.0362 | 3 | 93.4236
5867 | 41.81 | 73.6355 | 38.9454 | 87.2524 | 0.43998 |  | 5867 | 38.23 | 73.6355 | 2.2679 | 87.2524
5868 | 38.83 | 73.4974 | 39.8047 | 75.2314 | 0.43867 |  | 5868 | 35.5 | 73.4974 | 2 | 75.2314
5869 | 38.15 | 76.2485 | 41.0136 | 88.905 | 0.43838 |  | 5869 | 29.93 | 76.2485 | 2.2679 | 88.905
5870 | 36.7 | 71.8672 | 48.2162 | 75.3597 | 0.43012 |  | 5870 | 28.68 | 71.8672 | 3 | 75.3597
5871 | 35.99 | 68.0345 | 35.8829 | 64.2005 | 0.42798 |  | 5871 | 31.5 | 68.0345 | 4 | 64.2005
5872 | 37.57 | 70.2139 | 32.8006 | 50.8281 | 0.42763 |  | 5872 | 32.07 | 70.2139 | 5 | 50.8281
5873 | 40.84 | 77.5817 | 46.2222 | 61.4332 | 0.43194 |  | 5873 | 32.39 | 77.5817 | 5.7321 | 61.4332
5874 | 45.41 | 103.1242 | 51.9321 | 90.2735 | 0.43321 |  | 5874 | 35.22 | 103.1242 | 6 | 90.2735
5875 | 52.29 | 135.2888 | 42.918 | 122.7661 | 0.43411 |  | 5875 | 38.11 | 135.2888 | 5.7321 | 122.7661
5876 | 52.53 | 130.7272 | 23.9279 | 98.5018 | 0.43242 |  | 5876 | 39.95 | 130.7272 | 5 | 98.5018
5877 | 46.92 | 110.5106 | 27.0376 | 98.2777 | 0.4371 |  | 5877 | 41.36 | 110.5106 | 4 | 98.2777
5878 | 40.76 | 100.17 | 34.3735 | 74.4113 | 0.43266 |  | 5878 | 39.4 | 100.17 | 3 | 74.4113
5879 | 35.22 | 87.7469 | 27.5506 | 38.0252 | 0.41509 |  | 5879 | 32.05 | 87.7469 | 2.2679 | 38.0252
5880 | 31.81 | 38.6936 | 28.7229 | 27.0902 | 0.40528 |  | 5880 | 26.94 | 38.6936 | 2 | 27.0902
5881 | 28.12 | 32.974 | 30.4055 | 31.6199 | 0.40053 |  | 5881 | 24.5 | 32.974 | 2.2679 | 31.6199
5882 | 26.95 | 31.6584 | 31.2793 | 5.9274 | 0.39553 |  | 5882 | 23.79 | 31.6584 | 3 | 5.9274
5883 | 24.3 | 30.3813 | 28.1927 | 23.5057 | 0.39188 |  | 5883 | 23.2 | 30.3813 | 4 | 23.5057
5884 | 24.1 | 29.0369 | 37.6331 | 39.6558 | 0.39697 |  | 5884 | 21.81 | 29.0369 | 5 | 39.6558
5885 | 28.23 | 28.199 | 63.2604 | 89.7281 | 0.40865 |  | 5885 | 21.9 | 28.199 | 5.7321 | 89.7281
5886 | 32.44 | 27.5964 | 100.6489 | 153.3261 | 0.41878 |  | 5886 | 22.28 | 27.5964 | 6 | 153.3261
5887 | 40.74 | 27.3219 | 105.6292 | 151.5723 | 0.42412 |  | 5887 | 24.6 | 27.3219 | 5.7321 | 151.5723
5888 | 40.88 | 29.8906 | 133.5865 | 155.7731 | 0.42825 |  | 5888 | 37.86 | 29.8906 | 5 | 155.7731
5889 | 37.96 | 49.2541 | 119.6572 | 83.6916 | 0.42578 |  | 5889 | 40.5 | 49.2541 | 4 | 83.6916
5890 | 32.95 | 69.2581 | 54.2 | 83.6701 | 0.41996 |  | 5890 | 35 | 69.2581 | 3 | 83.6701
5891 | 32.08 | 75.9704 | 62.0577 | 81.611 | 0.41408 |  | 5891 | 29.17 | 75.9704 | 2.2679 | 81.611
5892 | 29.9 | 77.3478 | 65.3304 | 73.5719 | 0.41661 |  | 5892 | 27.44 | 77.3478 | 2 | 73.5719
5893 | 31.15 | 81.4203 | 92.0306 | 64.8282 | 0.41623 |  | 5893 | 24.94 | 81.4203 | 2.2679 | 64.8282
5894 | 31.71 | 80.7431 | 43.5286 | 65.2706 | 0.41713 |  | 5894 | 25.02 | 80.7431 | 3 | 65.2706
5895 | 32.01 | 74.4272 | 52.8398 | 70.4522 | 0.42101 |  | 5895 | 24.94 | 74.4272 | 4 | 70.4522
5896 | 33.29 | 74.9109 | 25.4761 | 51.3873 | 0.42695 |  | 5896 | 24.3 | 74.9109 | 5 | 51.3873
5897 | 39.76 | 78.9902 | 38.9545 | 73.7198 | 0.43769 |  | 5897 | 24.7 | 78.9902 | 5.7321 | 73.7198
5898 | 44.96 | 133.7016 | 40.9264 | 89.8043 | 0.44709 |  | 5898 | 31.98 | 133.7016 | 6 | 89.8043
5899 | 50.83 | 140.4492 | 28.4771 | 121.0684 | 0.45157 |  | 5899 | 35.14 | 140.4492 | 5.7321 | 121.0684
5900 | 53.1 | 133.2104 | 37.1704 | 110.3516 | 0.45536 |  | 5900 | 36.2 | 133.2104 | 5 | 110.3516
5901 | 46.12 | 118.7147 | 29.4107 | 102.1498 | 0.45723 |  | 5901 | 38.38 | 118.7147 | 4 | 102.1498
5902 | 40.9 | 106.1885 | 26.295 | 68.1053 | 0.45175 |  | 5902 | 33.85 | 106.1885 | 3 | 68.1053
5903 | 36.08 | 88.7646 | 33.9137 | 51.9074 | 0.4414 |  | 5903 | 29.98 | 88.7646 | 2.2679 | 51.9074
5904 | 31.31 | 39.326 | 21.8439 | 24.6226 | 0.4233 |  | 5904 | 24.65 | 39.326 | 2 | 24.6226
5905 | 29 | 35.2848 | 32.2349 | 25.5917 | 0.40789 |  | 5905 | 25.37 | 35.2848 | 2.2679 | 25.5917
5906 | 29 | 33.5073 | 35.0647 | 7.6054 | 0.41894 |  | 5906 | 23.19 | 33.5073 | 3 | 7.6054
5907 | 27.75 | 31.6941 | 32.8435 | 15.9784 | 0.41644 |  | 5907 | 22.65 | 31.6941 | 4 | 15.9784
5908 | 28.07 | 30.0803 | 41.5665 | 51.0197 | 0.41609 |  | 5908 | 23.99 | 30.0803 | 5 | 51.0197
5909 | 24.15 | 28.9666 | 31.0333 | 86.7313 | 0.41297 |  | 5909 | 23.85 | 28.9666 | 5.7321 | 86.7313
5910 | 39.52 | 28.6032 | 43.1887 | 133.1482 | 0.40921 |  | 5910 | 24.75 | 28.6032 | 6 | 133.1482
5911 | 42.81 | 43.702 | 50.707 | 146.8724 | 0.40242 |  | 5911 | 24.42 | 43.702 | 5.7321 | 146.8724
5912 | 45.29 | 56.208 | 33.32 | 116.5285 | 0.39781 |  | 5912 | 28.93 | 56.208 | 5 | 116.5285
5913 | 42.96 | 43.7851 | 41.6878 | 96.8788 | 0.37832 |  | 5913 | 30.5 | 43.7851 | 4 | 96.8788
5914 | 37.73 | 41.5288 | 56.2701 | 75.69 | 0.36821 |  | 5914 | 31.28 | 41.5288 | 3 | 75.69
5915 | 32.57 | 44.8574 | 113.3049 | 75.6689 | 0.36392 |  | 5915 | 27 | 44.8574 | 2.2679 | 75.6689
5916 | 30.48 | 44.7663 | 309.1763 | 85.5046 | 0.36341 |  | 5916 | 26.09 | 44.7663 | 2 | 85.5046
5917 | 29.37 | 49.4098 | 102.0795 | 68.4903 | 0.3672 |  | 5917 | 23.97 | 49.4098 | 2.2679 | 68.4903
5918 | 29.42 | 50.508 | 52.5302 | 67.8786 | 0.37157 |  | 5918 | 23.13 | 50.508 | 3 | 67.8786
5919 | 28.9 | 56.5815 | 36.2103 | 66.4848 | 0.37702 |  | 5919 | 22.65 | 56.5815 | 4 | 66.4848
5920 | 28.86 | 70.8599 | 50.8361 | 68.1643 | 0.38305 |  | 5920 | 23.66 | 70.8599 | 5 | 68.1643
5921 | 31.68 | 92.8669 | 43.5439 | 72.9614 | 0.38527 |  | 5921 | 26.68 | 92.8669 | 5.7321 | 72.9614
5922 | 38.05 | 136.7224 | 37.6651 | 110.8243 | 0.38538 |  | 5922 | 30.35 | 136.7224 | 6 | 110.8243
5923 | 40.3 | 141.5829 | 46.7173 | 109.5027 | 0.38767 |  | 5923 | 34.2 | 141.5829 | 5.7321 | 109.5027
5924 | 40.67 | 141.5457 | 30.9866 | 114.2663 | 0.39622 |  | 5924 | 37.44 | 141.5457 | 5 | 114.2663
5925 | 38.25 | 117.5929 | 33.2608 | 90.9945 | 0.39124 |  | 5925 | 38.56 | 117.5929 | 4 | 90.9945
5926 | 35.3 | 105.933 | 32.7342 | 82.6092 | 0.39315 |  | 5926 | 37.6 | 105.933 | 3 | 82.6092
5927 | 29.54 | 77.4821 | 22.8008 | 44.2931 | 0.39156 |  | 5927 | 32.91 | 77.4821 | 2.2679 | 44.2931
5928 | 28 | 40.8895 | 31.5561 | 23.0669 | 0.38236 |  | 5928 | 28.63 | 40.8895 | 2 | 23.0669
5929 | 25.96 | 35.7684 | 24.1971 | 28.4921 | 0.3756 |  | 5929 | 25 | 35.7684 | 2.2679 | 28.4921
5930 | 25.05 | 33.8526 | 31.6068 | 6.3038 | 0.37463 |  | 5930 | 24.73 | 33.8526 | 3 | 6.3038
5931 | 23.32 | 32.0385 | 35.0568 | 15.7622 | 0.36953 |  | 5931 | 23.09 | 32.0385 | 4 | 15.7622
5932 | 22.94 | 30.3637 | 35.3842 | 41.7305 | 0.37185 |  | 5932 | 22.04 | 30.3637 | 5 | 41.7305
5933 | 26.34 | 29.2055 | 27.9686 | 80.914 | 0.36343 |  | 5933 | 20.81 | 29.2055 | 5.7321 | 80.914
5934 | 33.68 | 28.7083 | 51.4621 | 124.0232 | 0.36542 |  | 5934 | 20.09 | 28.7083 | 6 | 124.0232
5935 | 39.62 | 42.8327 | 96.0731 | 168.022 | 0.36709 |  | 5935 | 20.03 | 42.8327 | 5.7321 | 168.022
5936 | 40.48 | 56.7335 | 91.2204 | 139.2984 | 0.36648 |  | 5936 | 22.02 | 56.7335 | 5 | 139.2984
5937 | 36.49 | 43.0079 | 313.6136 | 117.8536 | 0.36463 |  | 5937 | 22.38 | 43.0079 | 4 | 117.8536
5938 | 31.94 | 42.1188 | 109.7762 | 74.6421 | 0.36293 |  | 5938 | 23.5 | 42.1188 | 3 | 74.6421
5939 | 28.66 | 45.035 | 121.684 | 88.7567 | 0.36388 |  | 5939 | 23.58 | 45.035 | 2.2679 | 88.7567
5940 | 25.76 | 46.6994 | 63.1486 | 91.1944 | 0.36102 |  | 5940 | 24.99 | 46.6994 | 2 | 91.1944
5941 | 25.3 | 47.8318 | 50.7432 | 68.4124 | 0.36055 |  | 5941 | 24.31 | 47.8318 | 2.2679 | 68.4124
5942 | 25.84 | 50.7737 | 41.0433 | 76.3206 | 0.35984 |  | 5942 | 23.49 | 50.7737 | 3 | 76.3206
5943 | 27.2 | 58.1267 | 45.3116 | 57.8285 | 0.3651 |  | 5943 | 20.79 | 58.1267 | 4 | 57.8285
5944 | 29.16 | 75.3275 | 41.7798 | 59.7137 | 0.36559 |  | 5944 | 20.52 | 75.3275 | 5 | 59.7137
5945 | 32.26 | 91.4966 | 47.9255 | 79.8631 | 0.37116 |  | 5945 | 21.26 | 91.4966 | 5.7321 | 79.8631
5946 | 36.09 | 134.1022 | 81.3208 | 98.156 | 0.37672 |  | 5946 | 22.94 | 134.1022 | 6 | 98.156
5947 | 39.95 | 133.0104 | 113.9353 | 118.6279 | 0.38271 |  | 5947 | 26.94 | 133.0104 | 5.7321 | 118.6279
5948 | 40.92 | 131.4581 | 100.618 | 94.3755 | 0.39711 |  | 5948 | 30.31 | 131.4581 | 5 | 94.3755
5949 | 38.95 | 117.0342 | 78.1807 | 81.4986 | 0.40154 |  | 5949 | 33.83 | 117.0342 | 4 | 81.4986
5950 | 36.21 | 108.2704 | 27.9641 | 72.7297 | 0.40415 |  | 5950 | 31.79 | 108.2704 | 3 | 72.7297
5951 | 30.95 | 78.4277 | 33.3732 | 54.5074 | 0.41057 |  | 5951 | 28.88 | 78.4277 | 2.2679 | 54.5074
5952 | 26.28 | 41.4844 | 36.6569 | 30.3088 | 0.40693 |  | 5952 | 22.62 | 41.4844 | 2 | 30.3088
5953 | 25.64 | 32.9667 | 27.1019 | 34.0369 | 0.39727 |  | 5953 | 23.18 | 32.9667 | 2.2679 | 34.0369
5954 | 24.36 | 31.5276 | 27.0179 | 5.2064 | 0.38954 |  | 5954 | 22.3 | 31.5276 | 3 | 5.2064
5955 | 24.31 | 30.1173 | 33.8573 | 20.8918 | 0.38431 |  | 5955 | 22.3 | 30.1173 | 4 | 20.8918
5956 | 25.46 | 29.0432 | 29.2999 | 38.807 | 0.37839 |  | 5956 | 21.73 | 29.0432 | 5 | 38.807
5957 | 26.18 | 28.3231 | 37.0069 | 97.2202 | 0.37966 |  | 5957 | 22.96 | 28.3231 | 5.7321 | 97.2202
5958 | 33.44 | 28.2967 | 52.7991 | 126.0796 | 0.38134 |  | 5958 | 23.53 | 28.2967 | 6 | 126.0796
5959 | 38.23 | 43.44 | 92.0128 | 169.4908 | 0.37733 |  | 5959 | 33.6 | 43.44 | 5.7321 | 169.4908
5960 | 39.07 | 57.1783 | 114.6468 | 142.513 | 0.37605 |  | 5960 | 42.98 | 57.1783 | 5 | 142.513
5961 | 38.96 | 42.3681 | 94.2352 | 95.4251 | 0.37737 |  | 5961 | 45.2 | 42.3681 | 4 | 95.4251
5962 | 37.33 | 41.0028 | 88.3971 | 68.1129 | 0.37634 |  | 5962 | 43.31 | 41.0028 | 3 | 68.1129
5963 | 31.61 | 44.1812 | 104.6963 | 65.5145 | 0.3704 |  | 5963 | 44.97 | 44.1812 | 2.2679 | 65.5145
5964 | 27 | 44.5174 | 126.9483 | 69.4626 | 0.36261 |  | 5964 | 48.01 | 44.5174 | 2 | 69.4626
5965 | 26.5 | 49.9234 | 81.734 | 65.6853 | 0.35587 |  | 5965 | 48.79 | 49.9234 | 2.2679 | 65.6853
5966 | 28.35 | 51.587 | 47.794 | 60.878 | 0.3565 |  | 5966 | 44.22 | 51.587 | 3 | 60.878
5967 | 28.44 | 57.1232 | 46.4839 | 72.0152 | 0.36016 |  | 5967 | 45.32 | 57.1232 | 4 | 72.0152
5968 | 29.11 | 70.8776 | 62.1399 | 62.572 | 0.36171 |  | 5968 | 44.77 | 70.8776 | 5 | 62.572
5969 | 33.49 | 91.2431 | 44.6428 | 82.2901 | 0.36377 |  | 5969 | 45.32 | 91.2431 | 5.7321 | 82.2901
5970 | 38.26 | 132.313 | 46.4111 | 95.3408 | 0.36156 |  | 5970 | 42.31 | 132.313 | 6 | 95.3408
5971 | 39.31 | 149.9458 | 48.6903 | 109.0783 | 0.3616 |  | 5971 | 40.48 | 149.9458 | 5.7321 | 109.0783
5972 | 40.07 | 124.4385 | 51.8391 | 87.6042 | 0.36972 |  | 5972 | 43.12 | 124.4385 | 5 | 87.6042
5973 | 38.4 | 110.5999 | 83.3856 | 108.4189 | 0.37485 |  | 5973 | 44.75 | 110.5999 | 4 | 108.4189
5974 | 37.89 | 106.4385 | 62.666 | 69.0162 | 0.3834 |  | 5974 | 40.81 | 106.4385 | 3 | 69.0162
5975 | 34.07 | 77.1796 | 45.0251 | 47.6824 | 0.397 |  | 5975 | 32.96 | 77.1796 | 2.2679 | 47.6824
5976 | 32.01 | 38.3887 | 45.671 | 32.1596 | 0.40379 |  | 5976 | 28.07 | 38.3887 | 2 | 32.1596
5977 | 30 | 35.2307 | 103.6318 | 33.9516 | 0.40665 |  | 5977 | 22.88 | 35.2307 | 2.2679 | 33.9516
5978 | 29.44 | 33.387 | 100.6332 | 5.4425 | 0.40982 |  | 5978 | 23.44 | 33.387 | 3 | 5.4425
5979 | 28.69 | 31.666 | 83.3498 | 19.7912 | 0.41358 |  | 5979 | 24.84 | 31.666 | 4 | 19.7912
5980 | 29.32 | 30.0991 | 36.8978 | 50.2652 | 0.41086 |  | 5980 | 23.59 | 30.0991 | 5 | 50.2652
5981 | 29.84 | 29.0614 | 222.3547 | 105.7699 | 0.41078 |  | 5981 | 23.75 | 29.0614 | 5.7321 | 105.7699
5982 | 32.57 | 28.6891 | 18.1048 | 123.6377 | 0.41073 |  | 5982 | 26.25 | 28.6891 | 6 | 123.6377
5983 | 35.09 | 43.965 | 29.6176 | 172.7219 | 0.40782 |  | 5983 | 34.37 | 43.965 | 5.7321 | 172.7219
5984 | 36.27 | 58.0657 | 33.9757 | 153.6301 | 0.40314 |  | 5984 | 42.97 | 58.0657 | 5 | 153.6301
5985 | 39.83 | 44.0985 | 46.743 | 107.47 | 0.40017 |  | 5985 | 44.63 | 44.0985 | 4 | 107.47
5986 | 39.7 | 43.7658 | 54.5548 | 69.7251 | 0.39779 |  | 5986 | 43.08 | 43.7658 | 3 | 69.7251
5987 | 36.99 | 46.982 | 109.1256 | 69.8771 | 0.39597 |  | 5987 | 37.44 | 46.982 | 2.2679 | 69.8771
5988 | 36 | 48.7191 | 94.7383 | 74.1251 | 0.3964 |  | 5988 | 36.02 | 48.7191 | 2 | 74.1251
5989 | 35.05 | 52.0794 | 60.1715 | 77.8405 | 0.39515 |  | 5989 | 28.48 | 52.0794 | 2.2679 | 77.8405
5990 | 33.96 | 53.9623 | 45.9525 | 71.9966 | 0.3949 |  | 5990 | 27.98 | 53.9623 | 3 | 71.9966
5991 | 32.17 | 61.0916 | 37.2679 | 50.7352 | 0.3934 |  | 5991 | 29.69 | 61.0916 | 4 | 50.7352
5992 | 33.39 | 78.542 | 44.8079 | 63.7526 | 0.38454 |  | 5992 | 31.32 | 78.542 | 5 | 63.7526
5993 | 37.4 | 95.9195 | 57.3802 | 61.3573 | 0.37378 |  | 5993 | 43.95 | 95.9195 | 5.7321 | 61.3573
5994 | 44 | 135.7425 | 43.5143 | 92.7133 | 0.36783 |  | 5994 | 38.9 | 135.7425 | 6 | 92.7133
5995 | 46.71 | 145.7893 | 35.6359 | 89.024 | 0.36567 |  | 5995 | 42.01 | 145.7893 | 5.7321 | 89.024
5996 | 49.73 | 130.7269 | 30.3391 | 93.8465 | 0.36411 |  | 5996 | 45.16 | 130.7269 | 5 | 93.8465
5997 | 39 | 119.3394 | 36.9735 | 76.9811 | 0.36948 |  | 5997 | 43.92 | 119.3394 | 4 | 76.9811
5998 | 37.98 | 108.7488 | 31.836 | 69.3665 | 0.37767 |  | 5998 | 39.72 | 108.7488 | 3 | 69.3665
5999 | 34.78 | 78.8051 | 30.1338 | 37.7002 | 0.3815 |  | 5999 | 28.77 | 78.8051 | 2.2679 | 37.7002
6000 | 34.46 | 40.6365 | 29.4535 | 29.9602 | 0.38945 |  | 6000 | 26.7 | 40.6365 | 2 | 29.9602
6001 | 32.61 | 33.1278 | 33.0276 | 33.4966 | 0.39322 |  | 6001 | 24.8 | 33.1278 | 2.2679 | 33.4966
6002 | 32.36 | 31.8251 | 34.7718 | 6.9738 | 0.39378 |  | 6002 | 22.95 | 31.8251 | 3 | 6.9738
6003 | 32.01 | 30.4167 | 33.9844 | 16.057 | 0.39419 |  | 6003 | 22 | 30.4167 | 4 | 16.057
6004 | 31.92 | 29.0544 | 41.4933 | 50.5953 | 0.3952 |  | 6004 | 22.5 | 29.0544 | 5 | 50.5953
6005 | 31 | 28.2413 | 76.9443 | 87.172 | 0.39326 |  | 6005 | 23.18 | 28.2413 | 5.7321 | 87.172
6006 | 32.39 | 28.1351 | 79.0901 | 151.1412 | 0.39209 |  | 6006 | 23.68 | 28.1351 | 6 | 151.1412
6007 | 33.2 | 43.7677 | 26.6278 | 117.6448 | 0.40159 |  | 6007 | 32.42 | 43.7677 | 5.7321 | 117.6448
6008 | 35 | 57.821 | 53.1683 | 146.6651 | 0.40158 |  | 6008 | 37.97 | 57.821 | 5 | 146.6651
6009 | 37.27 | 43.6025 | 42.3263 | 124.1876 | 0.39647 |  | 6009 | 39 | 43.6025 | 4 | 124.1876
6010 | 36.31 | 43.0294 | 41.6441 | 80.4458 | 0.39933 |  | 6010 | 48.06 | 43.0294 | 3 | 80.4458
6011 | 36.19 | 46.2454 | 40.5054 | 69.1249 | 0.40212 |  | 6011 | 38 | 46.2454 | 2.2679 | 69.1249
6012 | 35.46 | 47.951 | 43.9187 | 75.4685 | 0.39943 |  | 6012 | 38 | 47.951 | 2 | 75.4685
6013 | 32.2 | 48.3682 | 35.161 | 80.3339 | 0.40056 |  | 6013 | 31.22 | 48.3682 | 2.2679 | 80.3339
6014 | 32.3 | 50.1135 | 32.8276 | 65.8196 | 0.39962 |  | 6014 | 35.5 | 50.1135 | 3 | 65.8196
6015 | 32.37 | 57.8487 | 43.0364 | 56.5662 | 0.4005 |  | 6015 | 35.5 | 57.8487 | 4 | 56.5662
6016 | 34.26 | 73.8221 | 45.0315 | 60.9564 | 0.40208 |  | 6016 | 42.41 | 73.8221 | 5 | 60.9564
6017 | 39.3 | 87.2434 | 39.7472 | 76.526 | 0.40426 |  | 6017 | 35.5 | 87.2434 | 5.7321 | 76.526
6018 | 45.1 | 125.981 | 48.7014 | 109.9797 | 0.4043 |  | 6018 | 48.3 | 125.981 | 6 | 109.9797
6019 | 51.88 | 144.4993 | 40.6332 | 103.7729 | 0.4081 |  | 6019 | 50 | 144.4993 | 5.7321 | 103.7729
6020 | 57.28 | 126.3149 | 25.4853 | 94.1639 | 0.41035 |  | 6020 | 44.81 | 126.3149 | 5 | 94.1639
6021 | 45.49 | 109.7195 | 29.7855 | 91.9164 | 0.41295 |  | 6021 | 43.71 | 109.7195 | 4 | 91.9164
6022 | 42.5 | 102.7132 | 28.2073 | 56.5442 | 0.41727 |  | 6022 | 38.9 | 102.7132 | 3 | 56.5442
6023 | 38.27 | 74.124 | 28.3608 | 49.4003 | 0.42413 |  | 6023 | 30.05 | 74.124 | 2.2679 | 49.4003
6024 | 38.33 | 38.4532 | 22.2734 | 26.2855 | 0.43127 |  | 6024 | 26.59 | 38.4532 | 2 | 26.2855
6025 | 34.09 | 35.719 | 24.4389 | 28.1508 | 0.43781 |  | 6025 | 23.82 | 35.719 | 2.2679 | 28.1508
6026 | 33.03 | 34.0175 | 31.4192 | 5.1043 | 0.43882 |  | 6026 | 24.07 | 34.0175 | 3 | 5.1043
6027 | 32.09 | 32.1973 | 27.9679 | 22.3855 | 0.43805 |  | 6027 | 23.5 | 32.1973 | 4 | 22.3855
6028 | 32.44 | 30.53 | 25.9253 | 40.0801 | 0.44184 |  | 6028 | 23.08 | 30.53 | 5 | 40.0801
6029 | 34.14 | 29.1254 | 27.5069 | 101.1865 | 0.45385 |  | 6029 | 23.1 | 29.1254 | 5.7321 | 101.1865
6030 | 47.98 | 28.2635 | 27.4751 | 131.606 | 0.45868 |  | 6030 | 24.24 | 28.2635 | 6 | 131.606
6031 | 62.53 | 27.9057 | 25.0736 | 161.119 | 0.4578 |  | 6031 | 31.91 | 27.9057 | 5.7321 | 161.119
6032 | 70.44 | 30.0388 | 43.0825 | 150.8173 | 0.45392 |  | 6032 | 38.71 | 30.0388 | 5 | 150.8173
6033 | 55.84 | 49.2056 | 38.8319 | 117.8536 | 0.44986 |  | 6033 | 39.62 | 49.2056 | 4 | 117.8536
6034 | 48.67 | 68.1762 | 48.1507 | 86.0883 | 0.44557 |  | 6034 | 39.52 | 68.1762 | 3 | 86.0883
6035 | 47.41 | 76.611 | 44.5767 | 82.8145 | 0.44608 |  | 6035 | 37.65 | 76.611 | 2.2679 | 82.8145
6036 | 46 | 73.4086 | 43.3509 | 69.2255 | 0.44298 |  | 6036 | 35.73 | 73.4086 | 2 | 69.2255
6037 | 45.23 | 79.777 | 40.3698 | 90.0737 | 0.44549 |  | 6037 | 32.61 | 79.777 | 2.2679 | 90.0737
6038 | 42.64 | 74.2469 | 36.8052 | 79.3404 | 0.44848 |  | 6038 | 29 | 74.2469 | 3 | 79.3404
6039 | 42.23 | 71.8832 | 247.8707 | 62.2769 | 0.44992 |  | 6039 | 28.58 | 71.8832 | 4 | 62.2769
6040 | 41.6 | 73.6825 | 50.7449 | 71.2712 | 0.45175 |  | 6040 | 30.34 | 73.6825 | 5 | 71.2712
6041 | 45.14 | 78.1862 | 50.5474 | 89.5711 | 0.45585 |  | 6041 | 30.01 | 78.1862 | 5.7321 | 89.5711
6042 | 49.99 | 123.1091 | 41.5539 | 81.5464 | 0.45802 |  | 6042 | 35.92 | 123.1091 | 6 | 81.5464
6043 | 60.64 | 141.461 | 47.2942 | 92.8438 | 0.46062 |  | 6043 | 40.41 | 141.461 | 5.7321 | 92.8438
6044 | 57.43 | 128.4876 | 33.8017 | 109.3994 | 0.46384 |  | 6044 | 42.59 | 128.4876 | 5 | 109.3994
6045 | 45.94 | 115.7537 | 35.1031 | 80.2079 | 0.46664 |  | 6045 | 41.3 | 115.7537 | 4 | 80.2079
6046 | 40.38 | 105.7525 | 18.801 | 71.2583 | 0.46892 |  | 6046 | 37.81 | 105.7525 | 3 | 71.2583
6047 | 34.35 | 91.7751 | 230.0904 | 47.961 | 0.46129 |  | 6047 | 29.27 | 91.7751 | 2.2679 | 47.961
6048 | 33.01 | 42.3772 | 40.3639 | 30.2016 | 0.45744 |  | 6048 | 24.84 | 42.3772 | 2 | 30.2016
6049 | 32.45 | 35.9967 | 27.0531 | 34.0085 | 0.4496 |  | 6049 | 24.14 | 35.9967 | 2.2679 | 34.0085
6050 | 31 | 34.0803 | 28.1879 | 7.4331 | 0.44483 |  | 6050 | 23.33 | 34.0803 | 3 | 7.4331
6051 | 29.63 | 32.115 | 57.2495 | 18.1993 | 0.4417 |  | 6051 | 22.16 | 32.115 | 4 | 18.1993
6052 | 29.01 | 30.4583 | 107.9366 | 47.9075 | 0.43989 |  | 6052 | 22.97 | 30.4583 | 5 | 47.9075
6053 | 31.8 | 29.3578 | 104.5831 | 72.5405 | 0.44267 |  | 6053 | 23.26 | 29.3578 | 5.7321 | 72.5405
6054 | 40.2 | 28.5422 | 125.4005 | 140.474 | 0.45392 |  | 6054 | 24.82 | 28.5422 | 6 | 140.474
6055 | 44.95 | 27.9803 | 101.8982 | 174.7782 | 0.45656 |  | 6055 | 33.77 | 27.9803 | 5.7321 | 174.7782
6056 | 45.93 | 30.1192 | 127.3644 | 126.0383 | 0.4547 |  | 6056 | 40.35 | 30.1192 | 5 | 126.0383
6057 | 41 | 48.8333 | 126.3312 | 106.4316 | 0.45146 |  | 6057 | 43.25 | 48.8333 | 4 | 106.4316
6058 | 36 | 66.764 | 125.8278 | 65.1305 | 0.44756 |  | 6058 | 44.94 | 66.764 | 3 | 65.1305
6059 | 32.6 | 72.085 | 127.5567 | 63.1075 | 0.4389 |  | 6059 | 38.21 | 72.085 | 2.2679 | 63.1075
6060 | 31.04 | 75.6832 | 116.0779 | 67.329 | 0.42856 |  | 6060 | 41.4 | 75.6832 | 2 | 67.329
6061 | 30.7 | 78.4912 | 129.4573 | 67.867 | 0.42956 |  | 6061 | 38.14 | 78.4912 | 2.2679 | 67.867
6062 | 31.3 | 78.7265 | 116.6844 | 75.9088 | 0.42986 |  | 6062 | 34.57 | 78.7265 | 3 | 75.9088
6063 | 32.01 | 77.5659 | 101.9853 | 66.605 | 0.43307 |  | 6063 | 29.9 | 77.5659 | 4 | 66.605
6064 | 34.1 | 76.4622 | 96.6619 | 62.0749 | 0.43984 |  | 6064 | 29.49 | 76.4622 | 5 | 62.0749
6065 | 39.18 | 75.8519 | 66.9544 | 79.1047 | 0.44804 |  | 6065 | 30.44 | 75.8519 | 5.7321 | 79.1047
6066 | 44.53 | 114.9011 | 55.5053 | 97.0299 | 0.45294 |  | 6066 | 35.89 | 114.9011 | 6 | 97.0299
6067 | 47.44 | 120.8102 | 36.5845 | 91.7828 | 0.45745 |  | 6067 | 40 | 120.8102 | 5.7321 | 91.7828
6068 | 50.67 | 153.1259 | 26.0848 | 115.9591 | 0.46067 |  | 6068 | 41.94 | 153.1259 | 5 | 115.9591
6069 | 42.75 | 119.6673 | 39.6017 | 87.2146 | 0.46368 |  | 6069 | 43.22 | 119.6673 | 4 | 87.2146
6070 | 35.89 | 107.3985 | 32.5522 | 63.1305 | 0.45675 |  | 6070 | 38.32 | 107.3985 | 3 | 63.1305
6071 | 31.7 | 90.4709 | 38.093 | 37.1895 | 0.44032 |  | 6071 | 32.11 | 90.4709 | 2.2679 | 37.1895
6072 | 31.25 | 42.6993 | 28.4697 | 21.994 | 0.41699 |  | 6072 | 28.31 | 42.6993 | 2 | 21.994
6073 | 30.23 | 33.0463 | 27.7328 | 31.1081 | 0.40458 |  | 6073 | 32 | 33.0463 | 2.2679 | 31.1081
6074 | 28.5 | 31.5294 | 25.3581 | 6.8844 | 0.394 |  | 6074 | 26.63 | 31.5294 | 3 | 6.8844
6075 | 27.1 | 30.1383 | 31.2932 | 20.0074 | 0.38006 |  | 6075 | 27.42 | 30.1383 | 4 | 20.0074
6076 | 24.97 | 29.0005 | 37.851 | 43.2865 | 0.37858 |  | 6076 | 24.25 | 29.0005 | 5 | 43.2865
6077 | 27.61 | 28.1967 | 47.0305 | 75.0085 | 0.38505 |  | 6077 | 23.75 | 28.1967 | 5.7321 | 75.0085
6078 | 37.29 | 28.1774 | 80.6661 | 141.5021 | 0.38215 |  | 6078 | 24.2 | 28.1774 | 6 | 141.5021
6079 | 42.57 | 43.9147 | 112.4346 | 151.5723 | 0.37529 |  | 6079 | 25.51 | 43.9147 | 5.7321 | 151.5723
6080 | 43.25 | 59.2494 | 126.0295 | 113.8497 | 0.37325 |  | 6080 | 29.04 | 59.2494 | 5 | 113.8497
6081 | 39.82 | 43.3654 | 104.9974 | 101.9667 | 0.36837 |  | 6081 | 29.75 | 43.3654 | 4 | 101.9667
6082 | 36.29 | 41.2904 | 118.681 | 86.572 | 0.36241 |  | 6082 | 29.94 | 41.2904 | 3 | 86.572
6083 | 33.94 | 43.9408 | 125.0626 | 88.9824 | 0.3618 |  | 6083 | 25.22 | 43.9408 | 2.2679 | 88.9824
6084 | 30.55 | 46.8817 | 109.5226 | 72.8607 | 0.35639 |  | 6084 | 23.69 | 46.8817 | 2 | 72.8607
6085 | 28.79 | 48.0167 | 54.8509 | 84.1519 | 0.35485 |  | 6085 | 23.08 | 48.0167 | 2.2679 | 84.1519
6086 | 28.68 | 49.6844 | 103.8303 | 69.5258 | 0.35245 |  | 6086 | 23.06 | 49.6844 | 3 | 69.5258
6087 | 30.02 | 55.9181 | 82.534 | 57.1673 | 0.35201 |  | 6087 | 23.06 | 55.9181 | 4 | 57.1673
6088 | 29.33 | 72.2784 | 34.55 | 55.9233 | 0.35175 |  | 6088 | 25.61 | 72.2784 | 5 | 55.9233
6089 | 33.06 | 92.2297 | 36.1198 | 89.7986 | 0.35584 |  | 6089 | 28.65 | 92.2297 | 5.7321 | 89.7986
6090 | 37.34 | 127.5051 | 38.8722 | 104.8186 | 0.35815 |  | 6090 | 31.99 | 127.5051 | 6 | 104.8186
6091 | 39.67 | 148.3648 | 54.651 | 97.7248 | 0.36262 |  | 6091 | 34.05 | 148.3648 | 5.7321 | 97.7248
6092 | 41.1 | 128.5034 | 32.4209 | 111.6213 | 0.37359 |  | 6092 | 38.7 | 128.5034 | 5 | 111.6213
6093 | 38.37 | 120.6166 | 36.9022 | 81.0376 | 0.37968 |  | 6093 | 38.98 | 120.6166 | 4 | 81.0376
6094 | 33.04 | 109.7692 | 29.3108 | 77.144 | 0.38954 |  | 6094 | 34.08 | 109.7692 | 3 | 77.144
6095 | 30.1 | 75.6695 | 26.6976 | 40.2538 | 0.39753 |  | 6095 | 24.1 | 75.6695 | 2.2679 | 40.2538
6096 | 27.88 | 38.0239 | 30.3122 | 28.9677 | 0.40288 |  | 6096 | 24.99 | 38.0239 | 2 | 28.9677
6097 | 27.21 | 33.719 | 34.2312 | 26.4732 | 0.40276 |  | 6097 | 22 | 33.719 | 2.2679 | 26.4732
6098 | 27.53 | 32.248 | 35.35 | 5.251 | 0.40448 |  | 6098 | 22.87 | 32.248 | 3 | 5.251
6099 | 27.01 | 30.7636 | 40.0378 | 19.6143 | 0.40543 |  | 6099 | 22.51 | 30.7636 | 4 | 19.6143
6100 | 28.03 | 29.3734 | 105.7633 | 38.9485 | 0.40436 |  | 6100 | 21.73 | 29.3734 | 5 | 38.9485
6101 | 30.74 | 28.5402 | 115.4765 | 103.6545 | 0.40282 |  | 6101 | 21.1 | 28.5402 | 5.7321 | 103.6545
6102 | 44.66 | 28.3467 | 99.3045 | 131.4775 | 0.4006 |  | 6102 | 22.09 | 28.3467 | 6 | 131.4775
6103 | 50.65 | 43.4725 | 104.9643 | 166.2596 | 0.40081 |  | 6103 | 22.94 | 43.4725 | 5.7321 | 166.2596
6104 | 55.25 | 60.1558 | 117.8166 | 158.318 | 0.40024 |  | 6104 | 22.93 | 60.1558 | 5 | 158.318
6105 | 47.96 | 44.553 | 131.1827 | 115.3615 | 0.39545 |  | 6105 | 24.07 | 44.553 | 4 | 115.3615
6106 | 43.93 | 43.977 | 113.0411 | 88.829 | 0.38994 |  | 6106 | 25.11 | 43.977 | 3 | 88.829
6107 | 41.97 | 47.7237 | 88.9609 | 88.3054 | 0.38754 |  | 6107 | 24.96 | 47.7237 | 2.2679 | 88.3054
6108 | 40.99 | 47.7774 | 103.4863 | 77.9182 | 0.38464 |  | 6108 | 25.48 | 47.7774 | 2 | 77.9182
6109 | 35.28 | 55.5512 | 97.1477 | 62.7244 | 0.38344 |  | 6109 | 25.16 | 55.5512 | 2.2679 | 62.7244
6110 | 32.68 | 54.0409 | 99.1964 | 81.0563 | 0.37776 |  | 6110 | 24.54 | 54.0409 | 3 | 81.0563
6111 | 32.72 | 59.6325 | 110.7257 | 65.9438 | 0.37181 |  | 6111 | 23.48 | 59.6325 | 4 | 65.9438
6112 | 32.75 | 78.4029 | 297.461 | 51.3252 | 0.36474 |  | 6112 | 23.42 | 78.4029 | 5 | 51.3252
6113 | 39.9 | 96.2456 | 54.696 | 70.3068 | 0.36683 |  | 6113 | 24.01 | 96.2456 | 5.7321 | 70.3068
6114 | 42 | 135.6025 | 43.6449 | 89.1474 | 0.3693 |  | 6114 | 28.73 | 135.6025 | 6 | 89.1474
6115 | 44.27 | 139.8457 | 32.6153 | 118.734 | 0.36988 |  | 6115 | 36.36 | 139.8457 | 5.7321 | 118.734
6116 | 44.17 | 133.3828 | 27.937 | 107.495 | 0.37205 |  | 6116 | 39.85 | 133.3828 | 5 | 107.495
6117 | 41.51 | 116.9014 | 35.3408 | 103.1639 | 0.36671 |  | 6117 | 42.57 | 116.9014 | 4 | 103.1639
6118 | 36.29 | 109.5262 | 25.9154 | 75.4623 | 0.35859 |  | 6118 | 38.93 | 109.5262 | 3 | 75.4623
6119 | 30.1 | 79.4347 | 22.8777 | 45.6395 | 0.3571 |  | 6119 | 35.78 | 79.4347 | 2.2679 | 45.6395
6120 | 30.05 | 38.8848 | 30.5046 | 22.3427 | 0.3541 |  | 6120 | 30.27 | 38.8848 | 2 | 22.3427
6121 | 28.31 | 34.6397 | 25.1085 | 30.5394 | 0.35333 |  | 6121 | 24.06 | 34.6397 | 2.2679 | 30.5394
6122 | 27.11 | 32.882 | 32.8404 | 7.0184 | 0.35829 |  | 6122 | 23.45 | 32.882 | 3 | 7.0184
6123 | 26.24 | 31.2596 | 33.1589 | 17.2362 | 0.36289 |  | 6123 | 22.88 | 31.2596 | 4 | 17.2362
6124 | 27.05 | 29.8128 | 45.507 | 49.7465 | 0.3691 |  | 6124 | 22.15 | 29.8128 | 5 | 49.7465
6125 | 30.01 | 28.8424 | 116.7942 | 100.4814 | 0.38185 |  | 6125 | 22.75 | 28.8424 | 5.7321 | 100.4814
6126 | 40.01 | 28.7304 | 97.2329 | 141.2451 | 0.38474 |  | 6126 | 23.97 | 28.7304 | 6 | 141.2451
6127 | 43.98 | 42.6717 | 103.0107 | 165.2315 | 0.39448 |  | 6127 | 36.69 | 42.6717 | 5.7321 | 165.2315
6128 | 45.72 | 60.6995 | 94.9408 | 122.154 | 0.39923 |  | 6128 | 43 | 60.6995 | 5 | 122.154
6129 | 44.69 | 42.6858 | 120.5621 | 114.8423 | 0.40271 |  | 6129 | 47.99 | 42.6858 | 4 | 114.8423
6130 | 43.65 | 41.1057 | 133.0778 | 88.1035 | 0.40042 |  | 6130 | 50.03 | 41.1057 | 3 | 88.1035
6131 | 42.21 | 45.0507 | 127.4944 | 72.7354 | 0.40125 |  | 6131 | 46.88 | 45.0507 | 2.2679 | 72.7354
6132 | 40.83 | 45.2403 | 128.262 | 74.7573 | 0.40293 |  | 6132 | 48.21 | 45.2403 | 2 | 74.7573
6133 | 38.02 | 46.6891 | 117.824 | 82.8273 | 0.40387 |  | 6133 | 48.23 | 46.6891 | 2.2679 | 82.8273
6134 | 37.03 | 49.2266 | 312.4555 | 80.6445 | 0.40452 |  | 6134 | 47.91 | 49.2266 | 3 | 80.6445
6135 | 36.25 | 59.2168 | 104.6045 | 64.9219 | 0.40669 |  | 6135 | 46.43 | 59.2168 | 4 | 64.9219
6136 | 37.53 | 75.4203 | 50.9207 | 53.3136 | 0.40649 |  | 6136 | 46.16 | 75.4203 | 5 | 53.3136
6137 | 42.48 | 97.784 | 38.539 | 84.4137 | 0.40818 |  | 6137 | 48.12 | 97.784 | 5.7321 | 84.4137
6138 | 46.13 | 135.1979 | 36.8726 | 75.2592 | 0.40776 |  | 6138 | 57.36 | 135.1979 | 6 | 75.2592
6139 | 51.1 | 144.5842 | 49.2346 | 95.6026 | 0.4079 |  | 6139 | 66.22 | 144.5842 | 5.7321 | 95.6026
6140 | 52.43 | 135.3347 | 31.0698 | 96.9148 | 0.41093 |  | 6140 | 79.03 | 135.3347 | 5 | 96.9148
6141 | 44.91 | 121.6203 | 29.9334 | 99.1075 | 0.4151 |  | 6141 | 82.48 | 121.6203 | 4 | 99.1075
6142 | 42.02 | 108.178 | 33.2091 | 74.9018 | 0.41771 |  | 6142 | 72.42 | 108.178 | 3 | 74.9018
6143 | 39 | 79.1348 | 26.9362 | 53.7646 | 0.41658 |  | 6143 | 37.44 | 79.1348 | 2.2679 | 53.7646
6144 | 39.7 | 41.0721 | 30.2856 | 27.573 | 0.41355 |  | 6144 | 28.05 | 41.0721 | 2 | 27.573
6145 | 32.5 | 34.3546 | 23.1214 | 32.1033 | 0.41311 |  | 6145 | 26.64 | 34.3546 | 2.2679 | 32.1033
6146 | 32.07 | 32.756 | 30.3581 | 7.2417 | 0.41357 |  | 6146 | 24.8 | 32.756 | 3 | 7.2417
6147 | 31.9 | 31.125 | 30.484 | 23.2502 | 0.41234 |  | 6147 | 24 | 31.125 | 4 | 23.2502
6148 | 31.83 | 29.6785 | 34.4877 | 53.6602 | 0.41271 |  | 6148 | 23.52 | 29.6785 | 5 | 53.6602
6149 | 31.93 | 28.639 | 27.4982 | 77.5646 | 0.41323 |  | 6149 | 23.55 | 28.639 | 5.7321 | 77.5646
6150 | 32.85 | 28.4205 | 52.0543 | 103.5883 | 0.41292 |  | 6150 | 26.39 | 28.4205 | 6 | 103.5883
6151 | 39.9 | 43.3859 | 100.3404 | 132.7727 | 0.40978 |  | 6151 | 37.48 | 43.3859 | 5.7321 | 132.7727
6152 | 41.49 | 59.9695 | 106.8015 | 156.041 | 0.4062 |  | 6152 | 44.44 | 59.9695 | 5 | 156.041
6153 | 41.77 | 42.179 | 110.2962 | 110.0659 | 0.40286 |  | 6153 | 47.53 | 42.179 | 4 | 110.0659
6154 | 36.49 | 41.8479 | 90.5478 | 73.1912 | 0.39697 |  | 6154 | 57.35 | 41.8479 | 3 | 73.1912
6155 | 32.54 | 43.9111 | 50.7867 | 65.5897 | 0.39398 |  | 6155 | 67.51 | 43.9111 | 2.2679 | 65.5897
6156 | 31.28 | 46.1594 | 48.9304 | 78.9456 | 0.39014 |  | 6156 | 64.94 | 46.1594 | 2 | 78.9456
6157 | 30.01 | 49.8883 | 46.519 | 81.6585 | 0.38487 |  | 6157 | 52.44 | 49.8883 | 2.2679 | 81.6585
6158 | 28.03 | 50.3579 | 42.8588 | 57.4463 | 0.38158 |  | 6158 | 57.35 | 50.3579 | 3 | 57.4463
6159 | 28.02 | 58.1934 | 40.0344 | 69.6708 | 0.38351 |  | 6159 | 61.97 | 58.1934 | 4 | 69.6708
6160 | 30 | 72.1872 | 56.3426 | 68.9721 | 0.3893 |  | 6160 | 59.52 | 72.1872 | 5 | 68.9721
6161 | 35.48 | 92.627 | 39.616 | 65.6804 | 0.39578 |  | 6161 | 64.75 | 92.627 | 5.7321 | 65.6804
6162 | 42.92 | 130.739 | 39.3035 | 89.7104 | 0.39761 |  | 6162 | 66.4 | 130.739 | 6 | 89.7104
6163 | 50.85 | 149.3263 | 49.0514 | 113.9592 | 0.39941 |  | 6163 | 66.51 | 149.3263 | 5.7321 | 113.9592
6164 | 47.99 | 128.9541 | 40.3423 | 92.1537 | 0.39818 |  | 6164 | 56.25 | 128.9541 | 5 | 92.1537
6165 | 44.05 | 118.5638 | 23.6297 | 83.4346 | 0.39559 |  | 6165 | 64.64 | 118.5638 | 4 | 83.4346
6166 | 40.95 | 107.9544 | 26.8717 | 59.2068 | 0.39194 |  | 6166 | 59.94 | 107.9544 | 3 | 59.2068
6167 | 32.89 | 77.3438 | 35.7584 | 40.4859 | 0.38569 |  | 6167 | 28.83 | 77.3438 | 2.2679 | 40.4859
6168 | 33.08 | 39.8209 | 29.9652 | 31.2476 | 0.3732 |  | 6168 | 25.31 | 39.8209 | 2 | 31.2476
6169 | 29.4 | 33.3409 | 31.8259 | 27.2978 | 0.34294 |  | 6169 | 23 | 33.3409 | 2.2679 | 27.2978
6170 | 25.35 | 31.9529 | 35.8531 | 5.7296 | 0.31355 |  | 6170 | 22.19 | 31.9529 | 3 | 5.7296
6171 | 17.86 | 30.5718 | 31.2971 | 17.5703 | 0.28772 |  | 6171 | 21.34 | 30.5718 | 4 | 17.5703
6172 | 16.8 | 29.2564 | 30.2419 | 48.8506 | 0.27744 |  | 6172 | 21.85 | 29.2564 | 5 | 48.8506
6173 | 19 | 28.3306 | 25.0304 | 76.0662 | 0.27414 |  | 6173 | 22.74 | 28.3306 | 5.7321 | 76.0662
6174 | 24.54 | 28.1216 | 28.2945 | 122.6095 | 0.28101 |  | 6174 | 23.14 | 28.1216 | 6 | 122.6095
6175 | 32.14 | 42.7786 | 31.4236 | 125.5759 | 0.28954 |  | 6175 | 33.25 | 42.7786 | 5.7321 | 125.5759
6176 | 28.05 | 59.4869 | 244.0401 | 151.8888 | 0.27624 |  | 6176 | 37.42 | 59.4869 | 5 | 151.8888
6177 | 32.15 | 43.6902 | 31.0235 | 90.4409 | 0.29621 |  | 6177 | 41.97 | 43.6902 | 4 | 90.4409
6178 | 28.16 | 42.1235 | 47.6541 | 75.4482 | 0.31217 |  | 6178 | 54.94 | 42.1235 | 3 | 75.4482
6179 | 25 | 45.138 | 39.3486 | 80.558 | 0.31929 |  | 6179 | 50.03 | 45.138 | 2.2679 | 80.558
6180 | 28 | 46.6474 | 54.7768 | 82.8178 | 0.32162 |  | 6180 | 50.04 | 46.6474 | 2 | 82.8178
6181 | 30.3 | 49.014 | 49.6179 | 85.3986 | 0.32639 |  | 6181 | 45.12 | 49.014 | 2.2679 | 85.3986
6182 | 30.3 | 51.1942 | 44.0097 | 71.7907 | 0.33035 |  | 6182 | 46 | 51.1942 | 3 | 71.7907
6183 | 30.3 | 58.6197 | 50.0206 | 64.7415 | 0.3416 |  | 6183 | 35.7 | 58.6197 | 4 | 64.7415
6184 | 29.4 | 75.0277 | 49.1367 | 64.4982 | 0.34824 |  | 6184 | 35.7 | 75.0277 | 5 | 64.4982
6185 | 32.4 | 92.876 | 47.0906 | 79.6356 | 0.36342 |  | 6185 | 41.99 | 92.876 | 5.7321 | 79.6356
6186 | 41.75 | 131.5789 | 45.6983 | 111.3873 | 0.37897 |  | 6186 | 55.56 | 131.5789 | 6 | 111.3873
6187 | 43.96 | 135.5942 | 36.1629 | 112.2615 | 0.39016 |  | 6187 | 45.99 | 135.5942 | 5.7321 | 112.2615
6188 | 48.9 | 128.6689 | 38.8882 | 109.1878 | 0.39746 |  | 6188 | 40.18 | 128.6689 | 5 | 109.1878
6189 | 47.99 | 115.6458 | 32.1143 | 107.036 | 0.39911 |  | 6189 | 37.78 | 115.6458 | 4 | 107.036
6190 | 45.91 | 106.7684 | 27.5407 | 81.4181 | 0.4048 |  | 6190 | 30.81 | 106.7684 | 3 | 81.4181
6191 | 41.17 | 74.2192 | 32.0408 | 49.911 | 0.40738 |  | 6191 | 28.3 | 74.2192 | 2.2679 | 49.911
6192 | 32.45 | 38.7332 | 28.4469 | 28.3508 | 0.40971 |  | 6192 | 23.43 | 38.7332 | 2 | 28.3508
6193 | 32.57 | 34.2849 | 26.3775 | 30.9375 | 0.41293 |  | 6193 | 23.69 | 34.2849 | 2.2679 | 30.9375
6194 | 32.09 | 32.6594 | 36.9797 | 5.6211 | 0.42261 |  | 6194 | 22.17 | 32.6594 | 3 | 5.6211
6195 | 30.43 | 31.1021 | 28.3755 | 19.123 | 0.42855 |  | 6195 | 21.62 | 31.1021 | 4 | 19.123
6196 | 30.92 | 29.6863 | 36.5574 | 49.9351 | 0.43888 |  | 6196 | 21.13 | 29.6863 | 5 | 49.9351
6197 | 33.3 | 28.7536 | 58.5515 | 86.8195 | 0.44393 |  | 6197 | 21.35 | 28.7536 | 5.7321 | 86.8195
6198 | 48.38 | 28.0078 | 87.7705 | 151.9124 | 0.44692 |  | 6198 | 23.27 | 28.0078 | 6 | 151.9124
6199 | 52.69 | 27.5896 | 38.236 | 135.4164 | 0.45078 |  | 6199 | 27.27 | 27.5896 | 5.7321 | 135.4164
6200 | 59.69 | 29.9434 | 51.0497 | 153.6301 | 0.45582 |  | 6200 | 38.59 | 29.9434 | 5 | 153.6301
6201 | 55.31 | 48.4033 | 50.9909 | 118.7881 | 0.46484 |  | 6201 | 39.14 | 48.4033 | 4 | 118.7881
6202 | 50.79 | 66.9791 | 29.7155 | 72.2239 | 0.4629 |  | 6202 | 36.06 | 66.9791 | 3 | 72.2239
6203 | 54.69 | 72.734 | 42.3769 | 76.3458 | 0.46076 |  | 6203 | 35 | 72.734 | 2.2679 | 76.3458
6204 | 50 | 72.5564 | 43.889 | 85.6627 | 0.46073 |  | 6204 | 39.94 | 72.5564 | 2 | 85.6627
6205 | 50.32 | 76.2198 | 31.8235 | 67.2436 | 0.45656 |  | 6205 | 35 | 76.2198 | 2.2679 | 67.2436
6206 | 49.39 | 71.9614 | 47.4211 | 60.3289 | 0.45946 |  | 6206 | 35 | 71.9614 | 3 | 60.3289
6207 | 48.91 | 70.1633 | 45.4111 | 70.1517 | 0.45869 |  | 6207 | 45 | 70.1633 | 4 | 70.1517
6208 | 48.11 | 70.0917 | 43.0969 | 52.7543 | 0.45707 |  | 6208 | 47.57 | 70.0917 | 5 | 52.7543
6209 | 51.93 | 76.0542 | 49.1346 | 69.6243 | 0.45656 |  | 6209 | 47.34 | 76.0542 | 5.7321 | 69.6243
6210 | 56.67 | 115.9602 | 42.0584 | 79.6696 | 0.45301 |  | 6210 | 55 | 115.9602 | 6 | 79.6696
6211 | 60.91 | 142.7927 | 35.9723 | 88.9179 | 0.45197 |  | 6211 | 50.03 | 142.7927 | 5.7321 | 88.9179
6212 | 60.16 | 134.9315 | 23.0732 | 96.1741 | 0.45022 |  | 6212 | 40.86 | 134.9315 | 5 | 96.1741
6213 | 51.09 | 113.7016 | 29.0544 | 83.4346 | 0.44694 |  | 6213 | 40.72 | 113.7016 | 4 | 83.4346
6214 | 47.85 | 103.8593 | 30.1647 | 67.6849 | 0.44919 |  | 6214 | 30.98 | 103.8593 | 3 | 67.6849
6215 | 38 | 88.8714 | 33.9269 | 49.0288 | 0.4475 |  | 6215 | 26.5 | 88.8714 | 2.2679 | 49.0288
6216 | 36.88 | 40.7698 | 31.0714 | 25.8296 | 0.42658 |  | 6216 | 24.18 | 40.7698 | 2 | 25.8296
6217 | 33.02 | 34.5443 | 33.5038 | 23.5443 | 0.41065 |  | 6217 | 23.02 | 34.5443 | 2.2679 | 23.5443
6218 | 30.91 | 32.9058 | 31.4954 | 7.4268 | 0.40055 |  | 6218 | 21.49 | 32.9058 | 3 | 7.4268
6219 | 30.5 | 31.1987 | 28.3746 | 16.4304 | 0.40074 |  | 6219 | 21.88 | 31.1987 | 4 | 16.4304
6220 | 30.57 | 29.7257 | 42.8099 | 38.6184 | 0.39934 |  | 6220 | 21.35 | 29.7257 | 5 | 38.6184
6221 | 32.88 | 28.6898 | 85.9851 | 103.1256 | 0.40324 |  | 6221 | 20.35 | 28.6898 | 5.7321 | 103.1256
6222 | 45.9 | 28.003 | 109.823 | 134.9475 | 0.40743 |  | 6222 | 22.59 | 28.003 | 6 | 134.9475
6223 | 50.91 | 27.8215 | 111.7395 | 149.0755 | 0.40757 |  | 6223 | 30.79 | 27.8215 | 5.7321 | 149.0755
6224 | 52.03 | 29.6162 | 321.9842 | 118.0018 | 0.40069 |  | 6224 | 39.99 | 29.6162 | 5 | 118.0018
6225 | 45.82 | 47.8942 | 98.2849 | 123.7722 | 0.39555 |  | 6225 | 41.13 | 47.8942 | 4 | 123.7722
6226 | 36.32 | 66.4177 | 53.5454 | 90.8441 | 0.38217 |  | 6226 | 40.37 | 66.4177 | 3 | 90.8441
6227 | 30.23 | 74.3269 | 62.1197 | 86.801 | 0.37181 |  | 6227 | 38.98 | 74.3269 | 2.2679 | 86.801
6228 | 27.7 | 74.1586 | 97.2959 | 71.4382 | 0.35865 |  | 6228 | 37.81 | 74.1586 | 2 | 71.4382
6229 | 27.51 | 76.1093 | 109.2829 | 83.8403 | 0.36005 |  | 6229 | 36 | 76.1093 | 2.2679 | 83.8403
6230 | 27.1 | 82.8084 | 46.3194 | 63.0056 | 0.34978 |  | 6230 | 31.95 | 82.8084 | 3 | 63.0056
6231 | 27.5 | 77.8162 | 52.8506 | 65.2825 | 0.34102 |  | 6231 | 30.93 | 77.8162 | 4 | 65.2825
6232 | 28 | 74.0822 | 57.5246 | 55.4884 | 0.34863 |  | 6232 | 34.17 | 74.0822 | 5 | 55.4884
6233 | 29.74 | 76.6351 | 35.6171 | 88.0542 | 0.35875 |  | 6233 | 35.61 | 76.6351 | 5.7321 | 88.0542
6234 | 35.32 | 108.6294 | 38.6972 | 93.7455 | 0.36889 |  | 6234 | 38.28 | 108.6294 | 6 | 93.7455
6235 | 41.73 | 140.6529 | 40.2544 | 123.2966 | 0.37835 |  | 6235 | 40.1 | 140.6529 | 5.7321 | 123.2966
6236 | 41.32 | 135.7999 | 27.6779 | 85.1707 | 0.3902 |  | 6236 | 41.75 | 135.7999 | 5 | 85.1707
6237 | 36.51 | 117.693 | 24.6802 | 109.1565 | 0.39103 |  | 6237 | 40.99 | 117.693 | 4 | 109.1565
6238 | 33.23 | 101.3107 | 30.3023 | 58.6462 | 0.38719 |  | 6238 | 36.5 | 101.3107 | 3 | 58.6462
6239 | 30.03 | 87.6518 | 26.5732 | 51.3967 | 0.38243 |  | 6239 | 30.74 | 87.6518 | 2.2679 | 51.3967
6240 | 27.53 | 40.5703 | 226.8489 | 31.7572 | 0.37644 |  | 6240 | 25.16 | 40.5703 | 2 | 31.7572
6241 | 27.16 | 33.5848 | 32.6413 | 24.4827 | 0.38055 |  | 6241 | 29.63 | 33.5848 | 2.2679 | 24.4827
6242 | 27 | 32.1159 | 23.6857 | 5.8827 | 0.38116 |  | 6242 | 26.32 | 32.1159 | 3 | 5.8827
6243 | 26.74 | 30.7318 | 37.8372 | 20.8132 | 0.38918 |  | 6243 | 24.08 | 30.7318 | 4 | 20.8132
6244 | 27.7 | 29.3368 | 32.7116 | 42.1077 | 0.39513 |  | 6244 | 22.81 | 29.3368 | 5 | 42.1077
6245 | 30.18 | 28.4528 | 45.4285 | 76.0662 | 0.40106 |  | 6245 | 22.25 | 28.4528 | 5.7321 | 76.0662
6246 | 39.77 | 28.1964 | 84.8469 | 106.4158 | 0.41385 |  | 6246 | 22.91 | 28.1964 | 6 | 106.4158
6247 | 49.95 | 43.6858 | 83.4687 | 127.1915 | 0.41903 |  | 6247 | 24.91 | 43.6858 | 5.7321 | 127.1915
6248 | 51.22 | 60.2808 | 113.9427 | 152.2906 | 0.42289 |  | 6248 | 27.92 | 60.2808 | 5 | 152.2906
6249 | 46.36 | 42.5284 | 90.4879 | 108.5084 | 0.42103 |  | 6249 | 31.41 | 42.5284 | 4 | 108.5084
6250 | 32.66 | 40.7596 | 40.4343 | 84.1537 | 0.412 |  | 6250 | 36.93 | 40.7596 | 3 | 84.1537
6251 | 31.99 | 42.1641 | 35.4196 | 66.1914 | 0.40818 |  | 6251 | 36.91 | 42.1641 | 2.2679 | 66.1914
6252 | 28.56 | 45.752 | 90.5628 | 87.0851 | 0.40441 |  | 6252 | 36.08 | 45.752 | 2 | 87.0851
6253 | 28.7 | 48.7827 | 109.0261 | 67.7111 | 0.40331 |  | 6253 | 32.44 | 48.7827 | 2.2679 | 67.7111
6254 | 28.7 | 50.0964 | 85.272 | 66.0942 | 0.39884 |  | 6254 | 25.1 | 50.0964 | 3 | 66.0942
6255 | 29.9 | 56.9186 | 44.5005 | 59.0909 | 0.40011 |  | 6255 | 24.94 | 56.9186 | 4 | 59.0909
6256 | 29.9 | 70.2179 | 41.3469 | 59.1545 | 0.39906 |  | 6256 | 24.49 | 70.2179 | 5 | 59.1545
6257 | 37.91 | 92.8483 | 53.1162 | 84.0345 | 0.40316 |  | 6257 | 24.93 | 92.8483 | 5.7321 | 84.0345
6258 | 48.29 | 120.993 | 38.2653 | 91.4934 | 0.41259 |  | 6258 | 27.85 | 120.993 | 6 | 91.4934
6259 | 52.27 | 138.9891 | 39.5774 | 87.3263 | 0.4154 |  | 6259 | 27.03 | 138.9891 | 5.7321 | 87.3263
6260 | 53.17 | 145.0851 | 36.7949 | 86.5461 | 0.41953 |  | 6260 | 32.52 | 145.0851 | 5 | 86.5461
6261 | 48.07 | 117.5294 | 36.8393 | 96.8948 | 0.42535 |  | 6261 | 39.26 | 117.5294 | 4 | 96.8948
6262 | 45.19 | 106.5188 | 31.119 | 75.7426 | 0.43 |  | 6262 | 30.03 | 106.5188 | 3 | 75.7426
6263 | 37 | 76.0682 | 32.1728 | 48.1467 | 0.4247 |  | 6263 | 25.5 | 76.0682 | 2.2679 | 48.1467
6264 | 33.34 | 38.8508 | 27.5216 | 31.1672 | 0.42575 |  | 6264 | 23.96 | 38.8508 | 2 | 31.1672
6265 | 31.15 | 34.5745 | 32.2637 | 24.7102 | 0.43417 |  | 6265 | 22.27 | 34.5745 | 2.2679 | 24.7102
6266 | 30.78 | 32.9142 | 29.1257 | 6.4633 | 0.43962 |  | 6266 | 23.13 | 32.9142 | 3 | 6.4633
6267 | 29.4 | 31.1961 | 25.0153 | 20.7149 | 0.44257 |  | 6267 | 21.93 | 31.1961 | 4 | 20.7149
6268 | 31.43 | 29.9065 | 29.8607 | 43.7109 | 0.44311 |  | 6268 | 20.97 | 29.9065 | 5 | 43.7109
6269 | 34.5 | 28.9275 | 55.6309 | 94.3115 | 0.4538 |  | 6269 | 18.94 | 28.9275 | 5.7321 | 94.3115
6270 | 48.73 | 28.5548 | 81.178 | 109.8859 | 0.45685 |  | 6270 | 19.53 | 28.5548 | 6 | 109.8859
6271 | 51.79 | 42.8119 | 42.4177 | 169.7845 | 0.46239 |  | 6271 | 20.89 | 42.8119 | 5.7321 | 169.7845
6272 | 54 | 62.0478 | 60.1485 | 144.656 | 0.46411 |  | 6272 | 20.73 | 62.0478 | 5 | 144.656
6273 | 52 | 43.2524 | 53.6021 | 97.7094 | 0.47067 |  | 6273 | 22.77 | 43.2524 | 4 | 97.7094
6274 | 50.19 | 42.4201 | 61.917 | 77.7052 | 0.46465 |  | 6274 | 24.78 | 42.4201 | 3 | 77.7052
6275 | 44.2 | 46.1173 | 100.2407 | 71.3815 | 0.46075 |  | 6275 | 24.56 | 46.1173 | 2.2679 | 71.3815
6276 | 37.73 | 48.0321 | 39.5349 | 94.7505 | 0.45549 |  | 6276 | 24.98 | 48.0321 | 2 | 94.7505
6277 | 36.3 | 52.1527 | 41.0742 | 63.8931 | 0.44951 |  | 6277 | 24 | 52.1527 | 2.2679 | 63.8931
6278 | 36 | 53.6349 | 53.6514 | 64.6528 | 0.44568 |  | 6278 | 24.89 | 53.6349 | 3 | 64.6528
6279 | 36.38 | 62.0901 | 40.1877 | 51.3965 | 0.45421 |  | 6279 | 23.6 | 62.0901 | 4 | 51.3965
6280 | 38.88 | 75.2473 | 44.2169 | 64.7468 | 0.46702 |  | 6280 | 22.93 | 75.2473 | 5 | 64.7468
6281 | 50 | 95.3804 | 43.1809 | 84.1103 | 0.4789 |  | 6281 | 23.2 | 95.3804 | 5.7321 | 84.1103
6282 | 52.2 | 140.5483 | 40.7652 | 98.156 | 0.48465 |  | 6282 | 27.16 | 140.5483 | 6 | 98.156
6283 | 70.04 | 150.7505 | 50.8278 | 104.9401 | 0.48119 |  | 6283 | 32.54 | 150.7505 | 5.7321 | 104.9401
6284 | 60.66 | 137.3607 | 27.7718 | 94.1639 | 0.48015 |  | 6284 | 42.94 | 137.3607 | 5 | 94.1639
6285 | 51.24 | 118.6206 | 25.7311 | 77.6265 | 0.48481 |  | 6285 | 60.88 | 118.6206 | 4 | 77.6265
6286 | 48.09 | 110.1097 | 36.6198 | 68.806 | 0.48501 |  | 6286 | 54.94 | 110.1097 | 3 | 68.806
6287 | 38.58 | 77.7517 | 35.0089 | 46.0574 | 0.48374 |  | 6287 | 27.94 | 77.7517 | 2.2679 | 46.0574
6288 | 37.37 | 40.3005 | 28.641 | 31.5427 | 0.47676 |  | 6288 | 25.46 | 40.3005 | 2 | 31.5427
6289 | 32.83 | 33.0316 | 28.663 | 31.4777 | 0.45502 |  | 6289 | 24.72 | 33.0316 | 2.2679 | 31.4777
6290 | 31.02 | 31.5288 | 30.8788 | 6.1252 | 0.44665 |  | 6290 | 24.2 | 31.5288 | 3 | 6.1252
6291 | 29.51 | 30.206 | 30.172 | 17.2362 | 0.44525 |  | 6291 | 23.78 | 30.206 | 4 | 17.2362
6292 | 30.56 | 28.9225 | 32.5526 | 50.9253 | 0.44583 |  | 6292 | 22.44 | 28.9225 | 5 | 50.9253
6293 | 31.94 | 28.1304 | 31.6815 | 87.3483 | 0.45163 |  | 6293 | 22.05 | 28.1304 | 5.7321 | 87.3483
6294 | 46.33 | 28.2824 | 29.6904 | 130.3208 | 0.46115 |  | 6294 | 23.91 | 28.2824 | 6 | 130.3208
6295 | 53.47 | 43.2628 | 27.6004 | 156.4191 | 0.46715 |  | 6295 | 36.06 | 43.2628 | 5.7321 | 156.4191
6296 | 60.73 | 63.4831 | 52.6045 | 128.0474 | 0.46748 |  | 6296 | 42.31 | 63.4831 | 5 | 128.0474
6297 | 52.09 | 43.6775 | 57.1266 | 100.0977 | 0.46286 |  | 6297 | 44.6 | 43.6775 | 4 | 100.0977
6298 | 49.48 | 42.6596 | 42.2559 | 82.461 | 0.46 |  | 6298 | 43.91 | 42.6596 | 3 | 82.461
6299 | 41.52 | 44.8632 | 44.8537 | 79.2793 | 0.45037 |  | 6299 | 43.95 | 44.8632 | 2.2679 | 79.2793
6300 | 33.37 | 47.4792 | 46.2067 | 93.9602 | 0.441 |  | 6300 | 43.97 | 47.4792 | 2 | 93.9602
6301 | 31.15 | 51.4492 | 58.5944 | 80.8794 | 0.42391 |  | 6301 | 41.27 | 51.4492 | 2.2679 | 80.8794
6302 | 30.9 | 52.6943 | 94.0756 | 57.5836 | 0.41785 |  | 6302 | 39.31 | 52.6943 | 3 | 57.5836
6303 | 32.96 | 58.2649 | 99.3299 | 57.2875 | 0.41901 |  | 6303 | 37.68 | 58.2649 | 4 | 57.2875
6304 | 33.98 | 73.3679 | 243.407 | 69.2828 | 0.42708 |  | 6304 | 37.93 | 73.3679 | 5 | 69.2828
6305 | 46.13 | 96.5822 | 32.2483 | 77.7395 | 0.43293 |  | 6305 | 37.78 | 96.5822 | 5.7321 | 77.7395
6306 | 50.41 | 137.6082 | 57.4783 | 81.0772 | 0.43227 |  | 6306 | 39.22 | 137.6082 | 6 | 81.0772
6307 | 56.94 | 143.9046 | 38.5964 | 99.2103 | 0.43338 |  | 6307 | 39.9 | 143.9046 | 5.7321 | 99.2103
6308 | 51.22 | 139.3945 | 34.6348 | 104.3209 | 0.43463 |  | 6308 | 41.99 | 139.3945 | 5 | 104.3209
6309 | 44.08 | 118.5305 | 31.1164 | 78.9172 | 0.433 |  | 6309 | 40.1 | 118.5305 | 4 | 78.9172
6310 | 38.5 | 104.9425 | 33.3049 | 64.9523 | 0.42581 |  | 6310 | 30 | 104.9425 | 3 | 64.9523
6311 | 31.01 | 77.3401 | 27.3479 | 49.0753 | 0.41897 |  | 6311 | 28.01 | 77.3401 | 2.2679 | 49.0753
6312 | 33.07 | 38.9979 | 33.3103 | 27.6535 | 0.41343 |  | 6312 | 25.99 | 38.9979 | 2 | 27.6535
6313 | 28.43 | 35.9967 | 29.4361 | 23.3453 | 0.4043 |  | 6313 | 24.79 | 35.9967 | 2.2679 | 23.3453
6314 | 27.72 | 34.192 | 32.2949 | 5.9146 | 0.40761 |  | 6314 | 24.79 | 34.192 | 3 | 5.9146
6315 | 25.29 | 32.268 | 34.5334 | 19.8305 | 0.40744 |  | 6315 | 23.51 | 32.268 | 4 | 19.8305
6316 | 26.42 | 30.5328 | 29.1793 | 56.1593 | 0.41153 |  | 6316 | 23.06 | 30.5328 | 5 | 56.1593
6317 | 27.1 | 29.3001 | 75.2267 | 164.0691 | 0.41205 |  | 6317 | 23.44 | 29.3001 | 5.7321 | 164.0691
6318 | 29.49 | 28.9122 | 100.0749 | 275.4128 | 0.41269 |  | 6318 | 24.73 | 28.9122 | 6 | 275.4128
6319 | 31.08 | 44.1511 | 71.762 | 312.5469 | 0.40933 |  | 6319 | 32.73 | 44.1511 | 5.7321 | 312.5469
6320 | 36.5 | 60.7676 | 98.5889 | 283.215 | 0.40604 |  | 6320 | 43.54 | 60.7676 | 5 | 283.215
6321 | 36.5 | 44.2334 | 95.5985 | 147.1367 | 0.40513 |  | 6321 | 51.65 | 44.2334 | 4 | 147.1367
6322 | 31.33 | 41.8857 | 77.8578 | 91.0053 | 0.40272 |  | 6322 | 58.17 | 41.8857 | 3 | 91.0053
6323 | 29.83 | 43.0515 | 55.5247 | 67.0941 | 0.39979 |  | 6323 | 42.55 | 43.0515 | 2.2679 | 67.0941
6324 | 28.18 | 45.799 | 293.1961 | 65.7485 | 0.3976 |  | 6324 | 46.07 | 45.799 | 2 | 65.7485
6325 | 27.15 | 48.8997 | 48.6013 | 82.7494 | 0.38964 |  | 6325 | 40.25 | 48.8997 | 2.2679 | 82.7494
6326 | 26.65 | 51.4299 | 49.452 | 82.1544 | 0.38569 |  | 6326 | 39.94 | 51.4299 | 3 | 82.1544
6327 | 27.2 | 59.1387 | 54.6022 | 51.3965 | 0.3832 |  | 6327 | 40.75 | 59.1387 | 4 | 51.3965
6328 | 27.32 | 73.2604 | 53.9555 | 72.7625 | 0.38799 |  | 6328 | 44.94 | 73.2604 | 5 | 72.7625
6329 | 34 | 93.2476 | 97.5328 | 88.5851 | 0.39406 |  | 6329 | 55 | 93.2476 | 5.7321 | 88.5851
6330 | 43.3 | 130.7405 | 43.4066 | 78.5435 | 0.39879 |  | 6330 | 56.82 | 130.7405 | 6 | 78.5435
6331 | 50 | 150.2403 | 42.4333 | 104.7279 | 0.39951 |  | 6331 | 52 | 150.2403 | 5.7321 | 104.7279
6332 | 46.32 | 130.6523 | 24.3108 | 111.7271 | 0.38969 |  | 6332 | 50 | 130.6523 | 5 | 111.7271
6333 | 34.93 | 117.4281 | 29.5062 | 93.9446 | 0.37839 |  | 6333 | 59.61 | 117.4281 | 4 | 93.9446
6334 | 33.1 | 110.5076 | 28.1853 | 68.3155 | 0.37753 |  | 6334 | 39.94 | 110.5076 | 3 | 68.3155
6335 | 30.56 | 78.5527 | 31.2851 | 54.8789 | 0.37751 |  | 6335 | 28.54 | 78.5527 | 2.2679 | 54.8789
6336 | 27.62 | 41.5953 | 23.4303 | 83.2577 | 0.37558 |  | 6336 | 26.03 | 41.5953 | 2 | 83.2577
6337 | 28.14 | 35.1261 | 26.4315 | 188.7517 | 0.37757 |  | 6337 | 24.82 | 35.1261 | 2.2679 | 188.7517
6338 | 29.16 | 33.3584 | 26.0217 | 203.3781 | 0.37964 |  | 6338 | 24.55 | 33.3584 | 3 | 203.3781
6339 | 28.54 | 31.5692 | 26.3304 | 243.0556 | 0.38261 |  | 6339 | 24.11 | 31.5692 | 4 | 243.0556
6340 | 29.87 | 29.9685 | 37.6278 | 300.3214 | 0.38585 |  | 6340 | 24.13 | 29.9685 | 5 | 300.3214
6341 | 28.21 | 28.9831 | 55.3752 | 360.2095 | 0.38473 |  | 6341 | 24.09 | 28.9831 | 5.7321 | 360.2095
6342 | 27.96 | 28.8325 | 104.7936 | 391.8153 | 0.3839 |  | 6342 | 24.91 | 28.8325 | 6 | 391.8153
6343 | 28.47 | 43.2241 | 94.4643 | 416.7746 | 0.38496 |  | 6343 | 36.97 | 43.2241 | 5.7321 | 416.7746
6344 | 26 | 61.6954 | 107.5715 | 330.1155 | 0.38702 |  | 6344 | 48.19 | 61.6954 | 5 | 330.1155
6345 | 28.07 | 45.0849 | 78.6543 | 219.6085 | 0.39002 |  | 6345 | 49.71 | 45.0849 | 4 | 219.6085
6346 | 26.24 | 44.2437 | 44.0778 | 82.4626 | 0.3915 |  | 6346 | 45.7 | 44.2437 | 3 | 82.4626
6347 | 26.91 | 45.5802 | 41.9865 | 87.5532 | 0.38978 |  | 6347 | 42.07 | 45.5802 | 2.2679 | 87.5532
6348 | 26.58 | 47.9458 | 69.0027 | 89.4558 | 0.38896 |  | 6348 | 38.87 | 47.9458 | 2 | 89.4558
6349 | 24.9 | 51.6901 | 98.3088 | 84.074 | 0.38536 |  | 6349 | 33.53 | 51.6901 | 2.2679 | 84.074
6350 | 25.05 | 55.1571 | 60.6545 | 74.1243 | 0.383 |  | 6350 | 33.43 | 55.1571 | 3 | 74.1243
6351 | 26.49 | 59.1925 | 46.3062 | 64.6814 | 0.38216 |  | 6351 | 32.07 | 59.1925 | 4 | 64.6814
6352 | 27.27 | 76.5273 | 58.6439 | 56.4204 | 0.39041 |  | 6352 | 34.99 | 76.5273 | 5 | 56.4204
6353 | 34.99 | 94.8884 | 35.7291 | 83.5036 | 0.40532 |  | 6353 | 36.8 | 94.8884 | 5.7321 | 83.5036
6354 | 39.01 | 137.1596 | 44.5818 | 94.9654 | 0.40871 |  | 6354 | 42.7 | 137.1596 | 6 | 94.9654
6355 | 40.97 | 142.3205 | 38.8529 | 107.1683 | 0.41087 |  | 6355 | 45 | 142.3205 | 5.7321 | 107.1683
6356 | 38.5 | 134.7998 | 37.0449 | 124.8465 | 0.40935 |  | 6356 | 48.75 | 134.7998 | 5 | 124.8465
6357 | 34.44 | 116.1162 | 31.3802 | 109.7096 | 0.40494 |  | 6357 | 43.87 | 116.1162 | 4 | 109.7096
6358 | 33.4 | 106.6979 | 23.7302 | 62.57 | 0.39713 |  | 6358 | 37.96 | 106.6979 | 3 | 62.57
6359 | 31.99 | 77.7734 | 25.7037 | 40.5788 | 0.39566 |  | 6359 | 28.49 | 77.7734 | 2.2679 | 40.5788
6360 | 27.66 | 41.1056 | 35.9368 | 32.1864 | 0.4003 |  | 6360 | 27.09 | 41.1056 | 2 | 32.1864
6361 | 27.2 | 34.7293 | 23.4538 | 24.8523 | 0.40779 |  | 6361 | 25.86 | 34.7293 | 2.2679 | 24.8523
6362 | 27.38 | 33.028 | 38.6866 | 5.2319 | 0.41172 |  | 6362 | 25.09 | 33.028 | 3 | 5.2319
6363 | 26.33 | 31.3395 | 25.1021 | 73.4939 | 0.41442 |  | 6363 | 24.73 | 31.3395 | 4 | 73.4939
6364 | 25.33 | 29.8876 | 37.7805 | 162.0629 | 0.42051 |  | 6364 | 24.26 | 29.8876 | 5 | 162.0629
6365 | 31.31 | 28.862 | 30.9258 | 263.2429 | 0.43382 |  | 6365 | 24.24 | 28.862 | 5.7321 | 263.2429
6366 | 38.37 | 28.1833 | 33.2887 | 311.7108 | 0.44774 |  | 6366 | 25.98 | 28.1833 | 6 | 311.7108
6367 | 48.99 | 27.7083 | 31.758 | 355.8072 | 0.45074 |  | 6367 | 38.19 | 27.7083 | 5.7321 | 355.8072
6368 | 50 | 30.1498 | 48.3117 | 319.5213 | 0.45295 |  | 6368 | 43.89 | 30.1498 | 5 | 319.5213
6369 | 49.84 | 48.0154 | 254.935 | 197.1172 | 0.45165 |  | 6369 | 43.63 | 48.0154 | 4 | 197.1172
6370 | 49.99 | 67.9937 | 43.3252 | 88.9096 | 0.44844 |  | 6370 | 38.71 | 67.9937 | 3 | 88.9096
6371 | 49.27 | 72.1611 | 49.1025 | 89.9602 | 0.45437 |  | 6371 | 29.16 | 72.1611 | 2.2679 | 89.9602
6372 | 45.48 | 74.1911 | 57.8031 | 71.6753 | 0.46366 |  | 6372 | 36.6 | 74.1911 | 2 | 71.6753
6373 | 43.37 | 77.3548 | 37.8575 | 90.5412 | 0.46152 |  | 6373 | 36.6 | 77.3548 | 2.2679 | 90.5412
6374 | 40.13 | 75.2404 | 39.1035 | 78.4482 | 0.45581 |  | 6374 | 36.6 | 75.2404 | 3 | 78.4482
6375 | 40.59 | 71.2729 | 35.1047 | 54.9431 | 0.45428 |  | 6375 | 41.28 | 71.2729 | 4 | 54.9431
6376 | 41.7 | 71.9163 | 37.886 | 62.9448 | 0.45505 |  | 6376 | 31.09 | 71.9163 | 5 | 62.9448
6377 | 50.1 | 79.8532 | 51.7366 | 76.3743 | 0.46523 |  | 6377 | 33.36 | 79.8532 | 5.7321 | 76.3743
6378 | 52.69 | 115.3076 | 51.7666 | 93.1825 | 0.46709 |  | 6378 | 40.84 | 115.3076 | 6 | 93.1825
6379 | 61.3 | 143.2543 | 46.4157 | 94.8599 | 0.46953 |  | 6379 | 43.56 | 143.2543 | 5.7321 | 94.8599
6380 | 52.85 | 142.5008 | 33.2741 | 89.297 | 0.47144 |  | 6380 | 49.06 | 142.5008 | 5 | 89.297
6381 | 49.21 | 116.5309 | 26.2245 | 105.8375 | 0.47201 |  | 6381 | 46.61 | 116.5309 | 4 | 105.8375
6382 | 42.85 | 102.2621 | 30.821 | 66.3536 | 0.46616 |  | 6382 | 39.95 | 102.2621 | 3 | 66.3536
6383 | 32.71 | 88.9177 | 22.033 | 47.636 | 0.44642 |  | 6383 | 30.64 | 88.9177 | 2.2679 | 47.636
6384 | 32.7 | 41.0581 | 30.603 | 23.8716 | 0.44067 |  | 6384 | 26.47 | 41.0581 | 2 | 23.8716
6385 | 30.4 | 32.6679 | 35.4725 | 32.4445 | 0.43899 |  | 6385 | 25.84 | 32.6679 | 2.2679 | 32.4445
6386 | 30.73 | 31.3482 | 22.9642 | 6.8908 | 0.43951 |  | 6386 | 24.75 | 31.3482 | 3 | 6.8908
6387 | 30.26 | 30.0357 | 37.0638 | 22.9554 | 0.43715 |  | 6387 | 24.68 | 30.0357 | 4 | 22.9554
6388 | 29.62 | 28.9143 | 94.9574 | 52.4814 | 0.43946 |  | 6388 | 24.78 | 28.9143 | 5 | 52.4814
6389 | 32.57 | 28.0871 | 116.4975 | 98.8948 | 0.43871 |  | 6389 | 25.14 | 28.0871 | 5.7321 | 98.8948
6390 | 40.1 | 27.6758 | 109.4141 | 129.6782 | 0.44219 |  | 6390 | 26.47 | 27.6758 | 6 | 129.6782
6391 | 50.1 | 27.5353 | 81.3587 | 137.6194 | 0.44612 |  | 6391 | 36.06 | 27.5353 | 5.7321 | 137.6194
6392 | 65.19 | 30.1707 | 115.5017 | 112.3763 | 0.44652 |  | 6392 | 43.37 | 30.1707 | 5 | 112.3763
6393 | 53.04 | 49.567 | 133.5859 | 107.9892 | 0.4493 |  | 6393 | 43.74 | 49.567 | 4 | 107.9892
6394 | 51.93 | 69.6041 | 74.8079 | 89.635 | 0.44775 |  | 6394 | 39.6 | 69.6041 | 3 | 89.635
6395 | 50.86 | 74.4044 | 72.5583 | 70.178 | 0.43943 |  | 6395 | 37.22 | 74.4044 | 2.2679 | 70.178
6396 | 47.46 | 78.6651 | 115.8082 | 88.8236 | 0.43316 |  | 6396 | 33.08 | 78.6651 | 2 | 88.8236
6397 | 44.57 | 79.994 | 70.618 | 78.1522 | 0.43368 |  | 6397 | 28.91 | 79.994 | 2.2679 | 78.1522
6398 | 42.22 | 79.1298 | 276.6787 | 80.4386 | 0.43256 |  | 6398 | 28.64 | 79.1298 | 3 | 80.4386
6399 | 41.76 | 77.7114 | 53.4738 | 58.61 | 0.4339 |  | 6399 | 27.81 | 77.7114 | 4 | 58.61
6400 | 48.04 | 72.5381 | 35.2642 | 58.5331 | 0.43863 |  | 6400 | 28.59 | 72.5381 | 5 | 58.5331
6401 | 54.96 | 76.9166 | 43.8031 | 83.2002 | 0.43982 |  | 6401 | 29.1 | 76.9166 | 5.7321 | 83.2002
6402 | 60.2 | 105.9168 | 45.6992 | 104.1617 | 0.43203 |  | 6402 | 32.97 | 105.9168 | 6 | 104.1617
6403 | 54.06 | 119.7831 | 60.3221 | 118.8401 | 0.4311 |  | 6403 | 37.54 | 119.7831 | 5.7321 | 118.8401
6404 | 50 | 155.1631 | 112.2121 | 111.0922 | 0.43173 |  | 6404 | 42.48 | 155.1631 | 5 | 111.0922
6405 | 45.42 | 117.4534 | 84.5368 | 105.3766 | 0.43497 |  | 6405 | 41.95 | 117.4534 | 4 | 105.3766
6406 | 35.23 | 101.4013 | 60.7817 | 65.0924 | 0.43082 |  | 6406 | 32.55 | 101.4013 | 3 | 65.0924
6407 | 32.2 | 86.4955 | 30.8027 | 41.9252 | 0.42717 |  | 6407 | 29.32 | 86.4955 | 2.2679 | 41.9252
6408 | 31.09 | 39.2007 | 24.7373 | 24.0593 | 0.43093 |  | 6408 | 26.79 | 39.2007 | 2 | 24.0593
6409 | 30.17 | 33.8218 | 31.0281 | 23.9709 | 0.43003 |  | 6409 | 25.8 | 33.8218 | 2.2679 | 23.9709
6410 | 29.44 | 32.3472 | 47.9992 | 5.2638 | 0.43014 |  | 6410 | 24.68 | 32.3472 | 3 | 5.2638
6411 | 28.19 | 30.8542 | 89.8174 | 22.0317 | 0.43243 |  | 6411 | 24.39 | 30.8542 | 4 | 22.0317
6412 | 27.22 | 29.486 | 75.1776 | 38.8542 | 0.43849 |  | 6412 | 24.58 | 29.486 | 5 | 38.8542
6413 | 30.76 | 28.638 | 58.8746 | 103.1256 | 0.44676 |  | 6413 | 24.65 | 28.638 | 5.7321 | 103.1256
6414 | 36.88 | 28.3164 | 104.681 | 130.0637 | 0.45325 |  | 6414 | 24.59 | 28.3164 | 6 | 130.0637
6415 | 48.06 | 44.0759 | 112.6732 | 156.2722 | 0.45501 |  | 6415 | 27.04 | 44.0759 | 5.7321 | 156.2722
6416 | 62.08 | 63.8232 | 95.5477 | 145.1918 | 0.4577 |  | 6416 | 31.15 | 63.8232 | 5 | 145.1918
6417 | 56.64 | 44.5651 | 85.4326 | 123.6684 | 0.45918 |  | 6417 | 34.48 | 44.5651 | 4 | 123.6684
6418 | 49.86 | 41.658 | 111.4153 | 69.4027 | 0.45628 |  | 6418 | 31.16 | 41.658 | 3 | 69.4027
6419 | 42.4 | 44.5285 | 111.9044 | 73.9388 | 0.45841 |  | 6419 | 29 | 44.5285 | 2.2679 | 73.9388
6420 | 40.6 | 46.0324 | 91.4961 | 73.7299 | 0.45834 |  | 6420 | 25.43 | 46.0324 | 2 | 73.7299
6421 | 39.9 | 49.5028 | 58.1767 | 83.4507 | 0.45845 |  | 6421 | 24.32 | 49.5028 | 2.2679 | 83.4507
6422 | 39.17 | 52.0383 | 50.1496 | 59.7112 | 0.456 |  | 6422 | 24.34 | 52.0383 | 3 | 59.7112
6423 | 39.9 | 60.2097 | 43.1955 | 55.9049 | 0.45843 |  | 6423 | 24.4 | 60.2097 | 4 | 55.9049
6424 | 40.6 | 72.2965 | 50.9742 | 73.5702 | 0.4597 |  | 6424 | 24.93 | 72.2965 | 5 | 73.5702
6425 | 49.99 | 91.2874 | 34.7655 | 74.7058 | 0.46212 |  | 6425 | 28.01 | 91.2874 | 5.7321 | 74.7058
6426 | 54.19 | 132.147 | 46.4688 | 99.8451 | 0.46386 |  | 6426 | 34.58 | 132.147 | 6 | 99.8451
6427 | 59.66 | 133.6812 | 63.8783 | 97.1942 | 0.46249 |  | 6427 | 38.08 | 133.6812 | 5.7321 | 97.1942
6428 | 51.74 | 140.5843 | 97.0071 | 104.0035 | 0.46288 |  | 6428 | 42.63 | 140.5843 | 5 | 104.0035
6429 | 40.6 | 119.6042 | 90.0761 | 87.3067 | 0.46036 |  | 6429 | 40.99 | 119.6042 | 4 | 87.3067
6430 | 33.58 | 107.7379 | 88.4434 | 71.6087 | 0.45092 |  | 6430 | 34.53 | 107.7379 | 3 | 71.6087
6431 | 33.3 | 78.2226 | 52.0386 | 50.8396 | 0.43394 |  | 6431 | 31.15 | 78.2226 | 2.2679 | 50.8396
6432 | 29.61 | 40.3698 | 32.7935 | 27.0097 | 0.42898 |  | 6432 | 25.46 | 40.3698 | 2 | 27.0097
6433 | 32.57 | 34.2868 | 227.0886 | 33.6673 | 0.42038 |  | 6433 | 24.57 | 34.2868 | 2.2679 | 33.6673
6434 | 30.1 | 32.5714 | 23.1164 | 6.5271 | 0.41903 |  | 6434 | 22.49 | 32.5714 | 3 | 6.5271
6435 | 26.36 | 31.0208 | 43.1234 | 18.042 | 0.41987 |  | 6435 | 20.55 | 31.0208 | 4 | 18.042
6436 | 27.03 | 29.6047 | 81.2859 | 54.0374 | 0.42286 |  | 6436 | 17.84 | 29.6047 | 5 | 54.0374
6437 | 30.35 | 28.5886 | 96.8182 | 101.3628 | 0.4236 |  | 6437 | 17.7 | 28.5886 | 5.7321 | 101.3628
6438 | 43.5 | 28.3414 | 75.233 | 115.1552 | 0.42982 |  | 6438 | 19.68 | 28.3414 | 6 | 115.1552
6439 | 50.29 | 43.5508 | 80.9624 | 123.8134 | 0.44103 |  | 6439 | 20.09 | 43.5508 | 5.7321 | 123.8134
6440 | 51.51 | 62.1914 | 94.4996 | 132.7353 | 0.44112 |  | 6440 | 21.47 | 62.1914 | 5 | 132.7353
6441 | 50.38 | 43.6172 | 119.2344 | 103.0051 | 0.43868 |  | 6441 | 22.45 | 43.6172 | 4 | 103.0051
6442 | 48.69 | 41.7393 | 115.4103 | 89.4738 | 0.43324 |  | 6442 | 22.95 | 41.7393 | 3 | 89.4738
6443 | 46.32 | 44.1591 | 94.8482 | 79.0536 | 0.42883 |  | 6443 | 21.72 | 44.1591 | 2.2679 | 79.0536
6444 | 42.4 | 45.744 | 87.9011 | 93.7232 | 0.42502 |  | 6444 | 23.63 | 45.744 | 2 | 93.7232
6445 | 37.93 | 49.7032 | 33.186 | 76.7497 | 0.42151 |  | 6445 | 23.4 | 49.7032 | 2.2679 | 76.7497
6446 | 36.8 | 50.4719 | 45.2478 | 58.9563 | 0.41659 |  | 6446 | 23.34 | 50.4719 | 3 | 58.9563
6447 | 35.11 | 58.7938 | 53.3233 | 58.61 | 0.41398 |  | 6447 | 22.53 | 58.7938 | 4 | 58.61
6448 | 35.35 | 74.8626 | 29.6684 | 70.7119 | 0.41587 |  | 6448 | 20.39 | 74.8626 | 5 | 70.7119
6449 | 41.22 | 94.3878 | 52.556 | 84.262 | 0.41951 |  | 6449 | 19.76 | 94.3878 | 5.7321 | 84.262
6450 | 45 | 132.705 | 46.0963 | 107.3522 | 0.41858 |  | 6450 | 26.55 | 132.705 | 6 | 107.3522
6451 | 39 | 141.5141 | 108.1739 | 92.8438 | 0.41864 |  | 6451 | 35.09 | 141.5141 | 5.7321 | 92.8438
6452 | 36.59 | 135.907 | 91.7719 | 108.3414 | 0.41277 |  | 6452 | 40.95 | 135.907 | 5 | 108.3414
6453 | 33.14 | 114.223 | 87.5332 | 85.9239 | 0.39946 |  | 6453 | 47.84 | 114.223 | 4 | 85.9239
6454 | 30.61 | 104.7767 | 77.261 | 61.589 | 0.39661 |  | 6454 | 34.27 | 104.7767 | 3 | 61.589
6455 | 29.77 | 75.7762 | 64.124 | 45.1288 | 0.40239 |  | 6455 | 29.57 | 75.7762 | 2.2679 | 45.1288
6456 | 29.05 | 39.6751 | 101.7563 | 24.7835 | 0.39475 |  | 6456 | 24.52 | 39.6751 | 2 | 24.7835
6457 | 27.74 | 34.9557 | 99.2365 | 30.8806 | 0.38711 |  | 6457 | 24.27 | 34.9557 | 2.2679 | 30.8806
6458 | 27.41 | 33.3423 | 120.6722 | 5.2447 | 0.38774 |  | 6458 | 24.2 | 33.3423 | 3 | 5.2447
6459 | 24.8 | 31.5686 | 81.5194 | 18.3958 | 0.38877 |  | 6459 | 23.42 | 31.5686 | 4 | 18.3958
6460 | 24.26 | 30.0544 | 63.622 | 50.3595 | 0.3917 |  | 6460 | 23.28 | 30.0544 | 5 | 50.3595
6461 | 26.58 | 28.928 | 48.4917 | 85.7618 | 0.40008 |  | 6461 | 23.49 | 28.928 | 5.7321 | 85.7618
6462 | 41.1 | 28.3725 | 89.4036 | 165.451 | 0.41536 |  | 6462 | 25.45 | 28.3725 | 6 | 165.451
6463 | 48.37 | 43.3654 | 78.964 | 215.8757 | 0.41553 |  | 6463 | 39.14 | 43.3654 | 5.7321 | 215.8757
6464 | 50.31 | 63.7257 | 282.582 | 174.3314 | 0.41363 |  | 6464 | 46.53 | 63.7257 | 5 | 174.3314
6465 | 50.04 | 43.1642 | 97.6585 | 159.7571 | 0.40693 |  | 6465 | 49 | 43.1642 | 4 | 159.7571
6466 | 45.87 | 40.3019 | 112.7371 | 78.7531 | 0.4002 |  | 6466 | 46.84 | 40.3019 | 3 | 78.7531
6467 | 41.16 | 43.6096 | 88.4536 | 76.7219 | 0.39144 |  | 6467 | 39.97 | 43.6096 | 2.2679 | 76.7219
6468 | 34.68 | 43.1648 | 82.1898 | 66.5387 | 0.3863 |  | 6468 | 38.3 | 43.1648 | 2 | 66.5387
6469 | 32.7 | 45.424 | 88.867 | 89.5283 | 0.38678 |  | 6469 | 34.94 | 45.424 | 2.2679 | 89.5283
6470 | 30.71 | 47.1625 | 75.6607 | 75.1538 | 0.38534 |  | 6470 | 40 | 47.1625 | 3 | 75.1538
6471 | 31.89 | 54.2231 | 50.7984 | 51.3364 | 0.38237 |  | 6471 | 32.44 | 54.2231 | 4 | 51.3364
6472 | 32.67 | 69.8752 | 49.8485 | 68.4129 | 0.38556 |  | 6472 | 35 | 69.8752 | 5 | 68.4129
6473 | 41.1 | 91.7624 | 40.4151 | 62.95 | 0.39735 |  | 6473 | 39.87 | 91.7624 | 5.7321 | 62.95
6474 | 45.13 | 132.9772 | 56.2668 | 99.4697 | 0.39338 |  | 6474 | 44.66 | 132.9772 | 6 | 99.4697
6475 | 48.29 | 157.0052 | 115.2011 | 92.1011 | 0.39242 |  | 6475 | 49.55 | 157.0052 | 5.7321 | 92.1011
6476 | 47.49 | 135.148 | 83.1086 | 92.1537 | 0.38705 |  | 6476 | 54.12 | 135.148 | 5 | 92.1537
6477 | 35.14 | 116.4618 | 84.3691 | 102.7952 | 0.373 |  | 6477 | 51.23 | 116.4618 | 4 | 102.7952
6478 | 33.08 | 109.1764 | 77.2816 | 70.3474 | 0.36291 |  | 6478 | 38.62 | 109.1764 | 3 | 70.3474
6479 | 29.99 | 78.281 | 89.5238 | 51.9538 | 0.35795 |  | 6479 | 31.85 | 78.281 | 2.2679 | 51.9538
6480 | 26.5 | 40.5872 | 80.1641 | 27.3316 | 0.32988 |  | 6480 | 28.4 | 40.5872 | 2 | 27.3316
6481 | 22.5 | 33.4666 | 72.2703 | 32.2739 | 0.28657 |  | 6481 | 31.33 | 33.4666 | 2.2679 | 32.2739
6482 | 23 | 31.9294 | 80.4416 | 5.8253 | 0.27305 |  | 6482 | 30.74 | 31.9294 | 3 | 5.8253
6483 | 20.64 | 30.512 | 82.4618 | 15.9391 | 0.28844 |  | 6483 | 29.75 | 30.512 | 4 | 15.9391
6484 | 20.86 | 29.1846 | 65.8189 | 46.5401 | 0.30367 |  | 6484 | 28.73 | 29.1846 | 5 | 46.5401
6485 | 22.73 | 28.3307 | 41.5869 | 175.1776 | 0.30703 |  | 6485 | 27.84 | 28.3307 | 5.7321 | 175.1776
6486 | 24.8 | 28.2831 | 68.9221 | 279.218 | 0.30648 |  | 6486 | 29.35 | 28.2831 | 6 | 279.218
6487 | 27.46 | 43.6964 | 86.7912 | 280.0152 | 0.30916 |  | 6487 | 41.15 | 43.6964 | 5.7321 | 280.0152
6488 | 33.2 | 65.7588 | 99.4788 | 247.8742 | 0.31237 |  | 6488 | 49 | 65.7588 | 5 | 247.8742
6489 | 34.58 | 44.8885 | 79.4291 | 197.31 | 0.30509 |  | 6489 | 50 | 44.8885 | 4 | 197.31
6490 | 33.16 | 43.9711 | 77.8258 | 120.175 | 0.29769 |  | 6490 | 45.57 | 43.9711 | 3 | 120.175
6491 | 32.42 | 46.0554 | 71.3511 | 68.5232 | 0.29342 |  | 6491 | 41.71 | 46.0554 | 2.2679 | 68.5232
6492 | 30.83 | 48.39 | 68.5417 | 77.7602 | 0.29236 |  | 6492 | 37 | 48.39 | 2 | 77.7602
6493 | 29.32 | 51.3039 | 82.9979 | 86.3337 | 0.29705 |  | 6493 | 29.98 | 51.3039 | 2.2679 | 86.3337
6494 | 29.04 | 51.5903 | 47.9185 | 79.1345 | 0.29301 |  | 6494 | 29.8 | 51.5903 | 3 | 79.1345
6495 | 28.98 | 59.6592 | 38.699 | 67.8674 | 0.29319 |  | 6495 | 28.19 | 59.6592 | 4 | 67.8674
6496 | 27.12 | 75.4622 | 39.8558 | 60.2729 | 0.29559 |  | 6496 | 28.57 | 75.4622 | 5 | 60.2729
6497 | 32.28 | 93.4366 | 52.6649 | 80.6974 | 0.31794 |  | 6497 | 30.33 | 93.4366 | 5.7321 | 80.6974
6498 | 38.19 | 134.1863 | 116.5507 | 102.1911 | 0.32508 |  | 6498 | 38.96 | 134.1863 | 6 | 102.1911
6499 | 43.69 | 147.7282 | 322.6829 | 85.7347 | 0.33298 |  | 6499 | 45.2 | 147.7282 | 5.7321 | 85.7347
6500 | 34.9 | 136.9982 | 74.7436 | 101.3584 | 0.33488 |  | 6500 | 48.97 | 136.9982 | 5 | 101.3584
6501 | 30.12 | 114.449 | 26.5757 | 108.1424 | 0.33822 |  | 6501 | 41.91 | 114.449 | 4 | 108.1424
6502 | 30.68 | 109.5388 | 35.9259 | 56.8945 | 0.33308 |  | 6502 | 29.94 | 109.5388 | 3 | 56.8945
6503 | 30.83 | 77.228 | 25.0349 | 44.5717 | 0.32922 |  | 6503 | 27.83 | 77.228 | 2.2679 | 44.5717
6504 | 31.75 | 39.0039 | 24.8055 | 28.0826 | 0.32248 |  | 6504 | 23.9 | 39.0039 | 2 | 28.0826
6505 | 31.08 | 36.0445 | 35.7207 | 44.9326 | 0.31718 |  | 6505 | 24.01 | 36.0445 | 2.2679 | 44.9326
6506 | 28.2 | 34.1456 | 25.4596 | 130.9578 | 0.3117 |  | 6506 | 21.4 | 34.1456 | 3 | 130.9578
6507 | 23 | 32.2232 | 36.3928 | 203.3869 | 0.30145 |  | 6507 | 16.86 | 32.2232 | 4 | 203.3869
6508 | 17.57 | 30.5041 | 43.0038 | 254.5842 | 0.29168 |  | 6508 | 15.65 | 30.5041 | 5 | 254.5842
6509 | 13.08 | 29.3785 | 102.8618 | 330.7489 | 0.27902 |  | 6509 | 15.47 | 29.3785 | 5.7321 | 330.7489
6510 | 18.11 | 28.9602 | 113.586 | 364.7452 | 0.30113 |  | 6510 | 19.98 | 28.9602 | 6 | 364.7452
6511 | 23.09 | 43.564 | 111.8689 | 362.473 | 0.30837 |  | 6511 | 28.52 | 43.564 | 5.7321 | 362.473
6512 | 24.02 | 64.3321 | 113.9863 | 402.9248 | 0.2989 |  | 6512 | 38.23 | 64.3321 | 5 | 402.9248
6513 | 26.62 | 45.334 | 120.8143 | 267.0265 | 0.30737 |  | 6513 | 38.87 | 45.334 | 4 | 267.0265
6514 | 32.01 | 43.4829 | 124.151 | 138.3194 | 0.31632 |  | 6514 | 47.49 | 43.4829 | 3 | 138.3194
6515 | 30.88 | 47.8584 | 121.5434 | 84.4693 | 0.31875 |  | 6515 | 38.2 | 47.8584 | 2.2679 | 84.4693
6516 | 31.8 | 49.7014 | 110.2567 | 69.1465 | 0.3167 |  | 6516 | 28 | 49.7014 | 2 | 69.1465
6517 | 31.63 | 53.1663 | 130.8698 | 89.0608 | 0.31595 |  | 6517 | 25.64 | 53.1663 | 2.2679 | 89.0608
6518 | 31.65 | 54.8164 | 123.9095 | 77.6246 | 0.31568 |  | 6518 | 25.74 | 54.8164 | 3 | 77.6246
6519 | 31.55 | 61.1468 | 110.075 | 50.1341 | 0.31439 |  | 6519 | 27.44 | 61.1468 | 4 | 50.1341
6520 | 31.72 | 75.3696 | 96.8643 | 65.8031 | 0.32443 |  | 6520 | 27.09 | 75.3696 | 5 | 65.8031
6521 | 32.44 | 98.4941 | 121.738 | 71.4445 | 0.3353 |  | 6521 | 32.44 | 98.4941 | 5.7321 | 71.4445
6522 | 33.45 | 134.6843 | 120.1564 | 84.5493 | 0.33925 |  | 6522 | 30.44 | 134.6843 | 6 | 84.5493
6523 | 36.81 | 143.9373 | 102.5872 | 102.8179 | 0.33962 |  | 6523 | 35.73 | 143.9373 | 5.7321 | 102.8179
6524 | 38 | 144.7722 | 99.6466 | 124.0001 | 0.34311 |  | 6524 | 41.44 | 144.7722 | 5 | 124.0001
6525 | 34 | 118.8917 | 119.9599 | 85.0019 | 0.34593 |  | 6525 | 37.09 | 118.8917 | 4 | 85.0019
6526 | 33 | 110.0561 | 69.8047 | 73.6406 | 0.34695 |  | 6526 | 31.72 | 110.0561 | 3 | 73.6406
6527 | 29.7 | 80.0907 | 232.6046 | 42.0181 | 0.34428 |  | 6527 | 29.39 | 80.0907 | 2.2679 | 42.0181
6528 | 24.5 | 42.3705 | 30.6583 | 23.4424 | 0.32552 |  | 6528 | 23.93 | 42.3705 | 2 | 23.4424
6529 | 23 | 35.4611 | 22.2006 | 23.459 | 0.30028 |  | 6529 | 20.71 | 35.4611 | 2.2679 | 23.459
6530 | 24.4 | 33.5979 | 34.0768 | 12.3168 | 0.30656 |  | 6530 | 19.45 | 33.5979 | 3 | 12.3168
6531 | 25.2 | 31.8266 | 30.5159 | 100.2257 | 0.31245 |  | 6531 | 21.18 | 31.8266 | 4 | 100.2257
6532 | 24.9 | 30.228 | 27.0941 | 184.4165 | 0.31535 |  | 6532 | 14.57 | 30.228 | 5 | 184.4165
6533 | 24 | 29.1447 | 43.6206 | 221.1806 | 0.31998 |  | 6533 | 14.15 | 29.1447 | 5.7321 | 221.1806
6534 | 29.9 | 28.4235 | 113.3714 | 275.0424 | 0.34742 |  | 6534 | 21.08 | 28.4235 | 6 | 275.0424
6535 | 45.7 | 28.0874 | 92.4617 | 282.7175 | 0.3671 |  | 6535 | 28.93 | 28.0874 | 5.7321 | 282.7175
6536 | 44.02 | 30.6946 | 123.6332 | 238.1487 | 0.37943 |  | 6536 | 37.97 | 30.6946 | 5 | 238.1487
6537 | 48.42 | 50.6496 | 113.8602 | 188.5462 | 0.38248 |  | 6537 | 44.35 | 50.6496 | 4 | 188.5462
6538 | 31 | 68.6831 | 97.5693 | 93.8266 | 0.38029 |  | 6538 | 35.01 | 68.6831 | 3 | 93.8266
6539 | 28.2 | 74.5668 | 73.6168 | 78.2262 | 0.37259 |  | 6539 | 26.43 | 74.5668 | 2.2679 | 78.2262
6540 | 24.5 | 76.5874 | 62.5685 | 73.1768 | 0.3657 |  | 6540 | 37 | 76.5874 | 2 | 73.1768
6541 | 27.4 | 86.3054 | 84.8463 | 74.8796 | 0.37101 |  | 6541 | 25.74 | 86.3054 | 2.2679 | 74.8796
6542 | 28.2 | 76.8195 | 43.8003 | 81.3994 | 0.37723 |  | 6542 | 29.68 | 76.8195 | 3 | 81.3994
6543 | 33.64 | 75.1532 | 40.278 | 55.4841 | 0.38237 |  | 6543 | 35.73 | 75.1532 | 4 | 55.4841
6544 | 40.13 | 77.245 | 41.2322 | 70.277 | 0.39061 |  | 6544 | 37 | 77.245 | 5 | 70.277
6545 | 50.92 | 84.1012 | 45.5319 | 64.8461 | 0.40214 |  | 6545 | 24.2 | 84.1012 | 5.7321 | 64.8461
6546 | 55.15 | 110.4091 | 50.718 | 95.9038 | 0.41089 |  | 6546 | 28.86 | 110.4091 | 6 | 95.9038
6547 | 64.37 | 149.697 | 39.8082 | 126.6921 | 0.42189 |  | 6547 | 30.21 | 149.697 | 5.7321 | 126.6921
6548 | 57.34 | 155.8228 | 32.0125 | 94.1639 | 0.4287 |  | 6548 | 38.52 | 155.8228 | 5 | 94.1639
6549 | 49.27 | 115.3088 | 25.6447 | 76.7046 | 0.43338 |  | 6549 | 32.76 | 115.3088 | 4 | 76.7046
6550 | 44.58 | 102.7324 | 34.5652 | 70.908 | 0.43213 |  | 6550 | 28.35 | 102.7324 | 3 | 70.908
6551 | 34.6 | 90.8801 | 31.0793 | 43.1788 | 0.42495 |  | 6551 | 27.44 | 90.8801 | 2.2679 | 43.1788
6552 | 33.09 | 42.3805 | 19.3349 | 24.5153 | 0.4169 |  | 6552 | 23.54 | 42.3805 | 2 | 24.5153
6553 | 30.26 | 35.0479 | 28.0176 | 33.1839 | 0.41218 |  | 6553 | 25.89 | 35.0479 | 2.2679 | 33.1839
6554 | 27.66 | 33.2786 | 31.1271 | 6.4888 | 0.41065 |  | 6554 | 25.7 | 33.2786 | 3 | 6.4888
6555 | 30.2 | 31.5801 | 36.0212 | 18.3565 | 0.41432 |  | 6555 | 24.71 | 31.5801 | 4 | 18.3565
6556 | 25.8 | 30.0101 | 50.2637 | 114.9147 | 0.41115 |  | 6556 | 23.09 | 30.0101 | 5 | 114.9147
6557 | 33.01 | 29.0005 | 108.1155 | 210.6813 | 0.41387 |  | 6557 | 24.02 | 29.0005 | 5.7321 | 210.6813
6558 | 45.44 | 28.3112 | 93.2683 | 324.2423 | 0.41782 |  | 6558 | 25.95 | 28.3112 | 6 | 324.2423
6559 | 50.98 | 27.7882 | 86.5814 | 312.9283 | 0.41737 |  | 6559 | 39.68 | 27.7882 | 5.7321 | 312.9283
6560 | 51.04 | 30.6472 | 96.2105 | 346.3345 | 0.42591 |  | 6560 | 49.66 | 30.6472 | 5 | 346.3345
6561 | 49.63 | 48.389 | 89.4108 | 188.2337 | 0.42803 |  | 6561 | 49.68 | 48.389 | 4 | 188.2337
6562 | 46.86 | 68.4617 | 57.4371 | 120.8694 | 0.42867 |  | 6562 | 43.91 | 68.4617 | 3 | 120.8694
6563 | 44.92 | 76.6962 | 257.1462 | 88.155 | 0.43108 |  | 6563 | 48.54 | 76.6962 | 2.2679 | 88.155
6564 | 42.17 | 77.0254 | 53.6505 | 65.1953 | 0.43365 |  | 6564 | 47.23 | 77.0254 | 2 | 65.1953
6565 | 41.04 | 79.5093 | 109.2098 | 64.984 | 0.44074 |  | 6565 | 34.94 | 79.5093 | 2.2679 | 64.984
6566 | 39.49 | 80.9774 | 101.1846 | 59.0249 | 0.44629 |  | 6566 | 29.25 | 80.9774 | 3 | 59.0249
6567 | 39.38 | 77.5156 | 77.132 | 64.2606 | 0.45482 |  | 6567 | 25.4 | 77.5156 | 4 | 64.2606
6568 | 42.88 | 77.264 | 58.6955 | 51.8844 | 0.462 |  | 6568 | 25.49 | 77.264 | 5 | 51.8844
6569 | 48.2 | 78.3362 | 60.9274 | 71.8996 | 0.46082 |  | 6569 | 31.19 | 78.3362 | 5.7321 | 71.8996
6570 | 50.16 | 105.7381 | 46.9596 | 111.7627 | 0.45393 |  | 6570 | 31.13 | 105.7381 | 6 | 111.7627
6571 | 54.99 | 126.7211 | 34.0619 | 109.2905 | 0.4481 |  | 6571 | 37.99 | 126.7211 | 5.7321 | 109.2905
6572 | 52.92 | 148.8992 | 27.6825 | 88.0274 | 0.44329 |  | 6572 | 43.32 | 148.8992 | 5 | 88.0274
6573 | 50.02 | 117.1708 | 29.9527 | 105.4688 | 0.43906 |  | 6573 | 39.55 | 117.1708 | 4 | 105.4688
6574 | 45.06 | 106.1541 | 23.0972 | 81.348 | 0.4421 |  | 6574 | 32.97 | 106.1541 | 3 | 81.348
6575 | 35.44 | 90.1264 | 28.9359 | 50.9788 | 0.43739 |  | 6575 | 30.93 | 90.1264 | 2.2679 | 50.9788
6576 | 33.49 | 42.0742 | 31.3289 | 27.9217 | 0.42151 |  | 6576 | 28.43 | 42.0742 | 2 | 27.9217
6577 | 30.14 | 35.0648 | 30.4567 | 27.9233 | 0.41231 |  | 6577 | 27.14 | 35.0648 | 2.2679 | 27.9233
6578 | 29.25 | 33.2658 | 21.3122 | 5.6147 | 0.41377 |  | 6578 | 30.34 | 33.2658 | 3 | 5.6147
6579 | 26.71 | 31.465 | 27.6926 | 18.7299 | 0.40912 |  | 6579 | 23.93 | 31.465 | 4 | 18.7299
6580 | 26.74 | 30.0272 | 24.7581 | 56.3458 | 0.40787 |  | 6580 | 24.86 | 30.0272 | 5 | 56.3458
6581 | 28.2 | 28.9692 | 41.1436 | 186.1845 | 0.42269 |  | 6581 | 24.76 | 28.9692 | 5.7321 | 186.1845
6582 | 43.75 | 28.4435 | 88.9687 | 285.4601 | 0.43675 |  | 6582 | 24.76 | 28.4435 | 6 | 285.4601
6583 | 51.79 | 44.329 | 106.0777 | 361.7164 | 0.44167 |  | 6583 | 27.12 | 44.329 | 5.7321 | 361.7164
6584 | 52.4 | 65.0636 | 85.7812 | 309.6167 | 0.4429 |  | 6584 | 30.62 | 65.0636 | 5 | 309.6167
6585 | 51.75 | 44.9159 | 86.687 | 263.0983 | 0.4382 |  | 6585 | 38.35 | 44.9159 | 4 | 263.0983
6586 | 50 | 42.5829 | 77.746 | 148.6996 | 0.4346 |  | 6586 | 38.11 | 42.5829 | 3 | 148.6996
6587 | 46.38 | 45.2014 | 61.2557 | 64.3862 | 0.43099 |  | 6587 | 39.55 | 45.2014 | 2.2679 | 64.3862
6588 | 36.96 | 49.6633 | 47.9081 | 78.5504 | 0.42359 |  | 6588 | 36.29 | 49.6633 | 2 | 78.5504
6589 | 34.9 | 51.1249 | 264.6452 | 69.3474 | 0.41233 |  | 6589 | 28.04 | 51.1249 | 2.2679 | 69.3474
6590 | 34.47 | 52.4523 | 56.1565 | 55.5932 | 0.40668 |  | 6590 | 25.01 | 52.4523 | 3 | 55.5932
6591 | 34.5 | 57.6966 | 31.9385 | 48.9318 | 0.40744 |  | 6591 | 27.29 | 57.6966 | 4 | 48.9318
6592 | 34.76 | 73.2154 | 47.7342 | 54.1214 | 0.41634 |  | 6592 | 29.18 | 73.2154 | 5 | 54.1214
6593 | 40.47 | 90.081 | 38.8839 | 62.1916 | 0.41974 |  | 6593 | 29.44 | 90.081 | 5.7321 | 62.1916
6594 | 48.01 | 131.1585 | 37.6246 | 82.0156 | 0.41847 |  | 6594 | 34.63 | 131.1585 | 6 | 82.0156
6595 | 51.61 | 160.2393 | 40.9393 | 85.4163 | 0.41952 |  | 6595 | 39.93 | 160.2393 | 5.7321 | 85.4163
6596 | 47.16 | 153.5322 | 25.3038 | 120.297 | 0.40971 |  | 6596 | 45.03 | 153.5322 | 5 | 120.297
6597 | 37.13 | 123.9078 | 29.722 | 75.0451 | 0.40047 |  | 6597 | 39.02 | 123.9078 | 4 | 75.0451
6598 | 34.69 | 108.8135 | 29.0632 | 67.1244 | 0.39759 |  | 6598 | 28.95 | 108.8135 | 3 | 67.1244
6599 | 28.75 | 76.8817 | 26.4501 | 39.7895 | 0.39613 |  | 6599 | 28.84 | 76.8817 | 2.2679 | 39.7895
6600 | 26.21 | 41.031 | 27.53 | 21.8331 | 0.3966 |  | 6600 | 30.05 | 41.031 | 2 | 21.8331
6601 | 26.41 | 32.2397 | 28.6478 | 106.3633 | 0.40233 |  | 6601 | 32.68 | 32.2397 | 2.2679 | 106.3633
6602 | 25.3 | 31.09 | 24.8045 | 146.446 | 0.40544 |  | 6602 | 31.23 | 31.09 | 3 | 146.446
6603 | 25.35 | 29.8986 | 35.1009 | 189.4387 | 0.41144 |  | 6603 | 26.28 | 29.8986 | 4 | 189.4387
6604 | 26.43 | 28.6865 | 102.3566 | 237.6492 | 0.41668 |  | 6604 | 25.13 | 28.6865 | 5 | 237.6492
6605 | 29.31 | 27.8889 | 82.7916 | 284.2075 | 0.42256 |  | 6605 | 24.9 | 27.8889 | 5.7321 | 284.2075
6606 | 35.32 | 27.9074 | 82.6633 | 353.4301 | 0.43481 |  | 6606 | 25.03 | 27.9074 | 6 | 353.4301
6607 | 49 | 43.376 | 80.2528 | 414.956 | 0.45196 |  | 6607 | 25.43 | 43.376 | 5.7321 | 414.956
6608 | 50.5 | 64.1957 | 109.9273 | 394.1123 | 0.46506 |  | 6608 | 26.09 | 64.1957 | 5 | 394.1123
6609 | 55.74 | 44.0785 | 105.5288 | 276.6615 | 0.4632 |  | 6609 | 29.7 | 44.0785 | 4 | 276.6615
6610 | 49.67 | 41.9498 | 102.7223 | 124.5006 | 0.46498 |  | 6610 | 30.99 | 41.9498 | 3 | 124.5006
6611 | 47.57 | 44.5425 | 106.4967 | 62.4306 | 0.46347 |  | 6611 | 29.88 | 44.5425 | 2.2679 | 62.4306
6612 | 42.44 | 44.9071 | 60.0013 | 83.1339 | 0.46421 |  | 6612 | 32.38 | 44.9071 | 2 | 83.1339
6613 | 37.82 | 49.2741 | 30.0683 | 79.3989 | 0.4663 |  | 6613 | 33.01 | 49.2741 | 2.2679 | 79.3989
6614 | 36.74 | 48.6643 | 57.4686 | 74.0557 | 0.46547 |  | 6614 | 26.64 | 48.6643 | 3 | 74.0557
6615 | 36.86 | 56.5454 | 123.7531 | 63.1185 | 0.4698 |  | 6615 | 25.01 | 56.5454 | 4 | 63.1185
6616 | 40.4 | 71.0681 | 61.2967 | 70.1527 | 0.47239 |  | 6616 | 24.65 | 71.0681 | 5 | 70.1527
6617 | 47.93 | 90.0517 | 31.032 | 87.9784 | 0.47428 |  | 6617 | 25.06 | 90.0517 | 5.7321 | 87.9784
6618 | 51.23 | 129.3839 | 55.6354 | 103.6925 | 0.4722 |  | 6618 | 31.65 | 129.3839 | 6 | 103.6925
6619 | 55.06 | 139.0945 | 98.6316 | 89.024 | 0.47286 |  | 6619 | 41.22 | 139.0945 | 5.7321 | 89.024
6620 | 53.53 | 122.7676 | 66.6331 | 103.0513 | 0.47331 |  | 6620 | 49.35 | 122.7676 | 5 | 103.0513
6621 | 48.06 | 112.6393 | 46.5871 | 78.364 | 0.47412 |  | 6621 | 42.4 | 112.6393 | 4 | 78.364
6622 | 45.59 | 102.1993 | 35.5015 | 56.7544 | 0.46711 |  | 6622 | 32.44 | 102.1993 | 3 | 56.7544
6623 | 35.93 | 73.7109 | 224.579 | 43.9681 | 0.46028 |  | 6623 | 29.94 | 73.7109 | 2.2679 | 43.9681
6624 | 37.49 | 37.1489 | 27.1956 | 26.8488 | 0.44678 |  | 6624 | 25.19 | 37.1489 | 2 | 26.8488
6625 | 30.57 | 34.1286 | 57.0243 | 26.985 | 0.44018 |  | 6625 | 30.81 | 34.1286 | 2.2679 | 26.985
6626 | 27.42 | 32.5555 | 109.4374 | 5.9274 | 0.42525 |  | 6626 | 26.11 | 32.5555 | 3 | 5.9274
6627 | 27.42 | 30.9406 | 94.5727 | 37.9991 | 0.42186 |  | 6627 | 25.09 | 30.9406 | 4 | 37.9991
6628 | 25.48 | 29.5166 | 60.0404 | 167.1897 | 0.41747 |  | 6628 | 24.54 | 29.5166 | 5 | 167.1897
6629 | 27.94 | 28.5986 | 80.4637 | 245.4458 | 0.42654 |  | 6629 | 24.59 | 28.5986 | 5.7321 | 245.4458
6630 | 41.5 | 28.4838 | 75.5159 | 281.5186 | 0.43377 |  | 6630 | 25.78 | 28.4838 | 6 | 281.5186
6631 | 48.75 | 42.54 | 71.9523 | 283.9131 | 0.43684 |  | 6631 | 36.12 | 42.54 | 5.7321 | 283.9131
6632 | 50.06 | 68.0775 | 68.7829 | 282.5746 | 0.44073 |  | 6632 | 39.87 | 68.0775 | 5 | 282.5746
6633 | 49.66 | 45.5409 | 100.0419 | 203.0369 | 0.4393 |  | 6633 | 38.19 | 45.5409 | 4 | 203.0369
6634 | 48.48 | 42.2456 | 62.1636 | 147.7394 | 0.44252 |  | 6634 | 39.76 | 42.2456 | 3 | 147.7394
6635 | 48.33 | 44.8045 | 89.9436 | 67.0941 | 0.44419 |  | 6635 | 32.6 | 44.8045 | 2.2679 | 67.0941
6636 | 48.87 | 47.6008 | 97.45 | 67.0129 | 0.45099 |  | 6636 | 33.17 | 47.6008 | 2 | 67.0129
6637 | 46.97 | 50.915 | 88.4198 | 81.191 | 0.44689 |  | 6637 | 26.19 | 50.915 | 2.2679 | 81.191
6638 | 44.2 | 51.7944 | 89.3445 | 55.5932 | 0.44521 |  | 6638 | 26.17 | 51.7944 | 3 | 55.5932
6639 | 46.26 | 58.608 | 66.3591 | 51.0959 | 0.44409 |  | 6639 | 24.59 | 58.608 | 4 | 51.0959
6640 | 46.05 | 71.5358 | 44.3285 | 73.2596 | 0.44336 |  | 6640 | 37.1 | 71.5358 | 5 | 73.2596
6641 | 50.05 | 90.837 | 50.7905 | 86.9166 | 0.44983 |  | 6641 | 37.03 | 90.837 | 5.7321 | 86.9166
6642 | 50.27 | 128.0575 | 56.8575 | 111.8565 | 0.45891 |  | 6642 | 33.37 | 128.0575 | 6 | 111.8565
6643 | 53.52 | 143.0334 | 82.0112 | 102.0752 | 0.45978 |  | 6643 | 37.1 | 143.0334 | 5.7321 | 102.0752
6644 | 49.22 | 142.8267 | 95.6201 | 113.9489 | 0.46153 |  | 6644 | 37.74 | 142.8267 | 5 | 113.9489
6645 | 40.5 | 115.7497 | 100.017 | 96.0651 | 0.46799 |  | 6645 | 32.63 | 115.7497 | 4 | 96.0651
6646 | 35.87 | 104.5641 | 87.8228 | 75.6725 | 0.46247 |  | 6646 | 28.42 | 104.5641 | 3 | 75.6725
6647 | 34.9 | 75.3066 | 58.3385 | 45.7788 | 0.45481 |  | 6647 | 25.74 | 75.3066 | 2.2679 | 45.7788
6648 | 30.5 | 39.4503 | 44.2426 | 25.159 | 0.44165 |  | 6648 | 24.6 | 39.4503 | 2 | 25.159
6649 | 32.76 | 33.9836 | 25.0061 | 28.4352 | 0.43047 |  | 6649 | 28.58 | 33.9836 | 2.2679 | 28.4352
6650 | 29.28 | 32.3421 | 47.4966 | 7.6309 | 0.42132 |  | 6650 | 26.11 | 32.3421 | 3 | 7.6309
6651 | 28.4 | 30.8414 | 86.4489 | 107.6943 | 0.4211 |  | 6651 | 24.85 | 30.8414 | 4 | 107.6943
6652 | 29.6 | 29.4542 | 72.1047 | 217.4212 | 0.42819 |  | 6652 | 22.69 | 29.4542 | 5 | 217.4212
6653 | 29.8 | 28.6224 | 43.5821 | 301.6436 | 0.42875 |  | 6653 | 23.25 | 28.6224 | 5.7321 | 301.6436
6654 | 29.3 | 28.4942 | 99.8189 | 425.2126 | 0.42553 |  | 6654 | 25.54 | 28.4942 | 6 | 425.2126
6655 | 31.51 | 43.7974 | 92.6283 | 397.9833 | 0.42517 |  | 6655 | 30.45 | 43.7974 | 5.7321 | 397.9833
6656 | 37.03 | 65.4164 | 116.0066 | 392.809 | 0.42815 |  | 6656 | 39.72 | 65.4164 | 5 | 392.809
6657 | 43.25 | 45.7867 | 125.6863 | 285.6085 | 0.4305 |  | 6657 | 41.78 | 45.7867 | 4 | 285.6085
6658 | 39.96 | 43.4141 | 126.0469 | 149.9178 | 0.43312 |  | 6658 | 39.42 | 43.4141 | 3 | 149.9178
6659 | 37.7 | 47.1026 | 108.2974 | 77.7749 | 0.4409 |  | 6659 | 35.66 | 47.1026 | 2.2679 | 77.7749
6660 | 37.18 | 47.6852 | 108.0117 | 69.9368 | 0.44983 |  | 6660 | 31.03 | 47.6852 | 2 | 69.9368
6661 | 36.51 | 51.6145 | 99.761 | 75.1913 | 0.45349 |  | 6661 | 32.16 | 51.6145 | 2.2679 | 75.1913
6662 | 35.24 | 52.8942 | 44.2145 | 60.7407 | 0.45564 |  | 6662 | 33.49 | 52.8942 | 3 | 60.7407
6663 | 35.89 | 60.2009 | 46.2553 | 70.0916 | 0.45705 |  | 6663 | 31.99 | 60.2009 | 4 | 70.0916
6664 | 38.05 | 75.7831 | 30.0573 | 63.3176 | 0.45878 |  | 6664 | 32.57 | 75.7831 | 5 | 63.3176
6665 | 43.59 | 96.6042 | 33.4672 | 73.7198 | 0.45992 |  | 6665 | 31.66 | 96.6042 | 5.7321 | 73.7198
6666 | 48.11 | 130.9029 | 49.7108 | 94.027 | 0.46105 |  | 6666 | 36.84 | 130.9029 | 6 | 94.027
6667 | 52.09 | 148.5528 | 59.5954 | 108.4416 | 0.45831 |  | 6667 | 40 | 148.5528 | 5.7321 | 108.4416
6668 | 49.75 | 141.0695 | 22.7898 | 106.6486 | 0.45648 |  | 6668 | 41 | 141.0695 | 5 | 106.6486
6669 | 41 | 117.3055 | 23.2561 | 93.3915 | 0.45317 |  | 6669 | 32.84 | 117.3055 | 4 | 93.3915
6670 | 40 | 109.5458 | 21.7134 | 74.2011 | 0.4385 |  | 6670 | 30.36 | 109.5458 | 3 | 74.2011
6671 | 35.9 | 75.5067 | 31.6697 | 42.9931 | 0.41756 |  | 6671 | 27.23 | 75.5067 | 2.2679 | 42.9931
6672 | 34.22 | 40.0249 | 30.4948 | 27.278 | 0.40187 |  | 6672 | 24.93 | 40.0249 | 2 | 27.278
6673 | 28.94 | 32.2657 | 31.2823 | 60.691 | 0.39173 |  | 6673 | 25.06 | 32.2657 | 2.2679 | 60.691
6674 | 27.43 | 30.9573 | 30.8606 | 94.2997 | 0.38382 |  | 6674 | 23.67 | 30.9573 | 3 | 94.2997
6675 | 28.99 | 29.7134 | 27.7402 | 179.3652 | 0.38348 |  | 6675 | 22.45 | 29.7134 | 4 | 179.3652
6676 | 27 | 28.736 | 27.9693 | 235.2116 | 0.38373 |  | 6676 | 22.23 | 28.736 | 5 | 235.2116
6677 | 27.08 | 28.0272 | 31.1947 | 230.9492 | 0.38372 |  | 6677 | 22.71 | 28.0272 | 5.7321 | 230.9492
6678 | 27.1 | 27.9906 | 28.588 | 256.5302 | 0.38654 |  | 6678 | 24.3 | 27.9906 | 6 | 256.5302
6679 | 28.97 | 42.8521 | 229.5781 | 319.9057 | 0.38189 |  | 6679 | 31.17 | 42.8521 | 5.7321 | 319.9057
6680 | 30 | 64.2957 | 55.1298 | 304.9354 | 0.38222 |  | 6680 | 38.3 | 64.2957 | 5 | 304.9354
6681 | 34.7 | 46.6818 | 47.3007 | 181.8751 | 0.38752 |  | 6681 | 29.38 | 46.6818 | 4 | 181.8751
6682 | 36.55 | 43.9617 | 41.0464 | 95.669 | 0.38795 |  | 6682 | 30.14 | 43.9617 | 3 | 95.669
6683 | 36.52 | 45.2487 | 43.6842 | 81.7615 | 0.38315 |  | 6683 | 27.58 | 45.2487 | 2.2679 | 81.7615
6684 | 36.08 | 47.4978 | 237.2647 | 71.2012 | 0.38075 |  | 6684 | 27.51 | 47.4978 | 2 | 71.2012
6685 | 34.55 | 50.4971 | 66.3617 | 91.2425 | 0.38393 |  | 6685 | 26.33 | 50.4971 | 2.2679 | 91.2425
6686 | 33 | 53.8821 | 99.39 | 55.25 | 0.38487 |  | 6686 | 27.57 | 53.8821 | 3 | 55.25
6687 | 29 | 56.3139 | 107.0056 | 54.6426 | 0.3833 |  | 6687 | 28.28 | 56.3139 | 4 | 54.6426
6688 | 28.92 | 72.0139 | 83.7201 | 51.4495 | 0.37959 |  | 6688 | 28.18 | 72.0139 | 5 | 51.4495
6689 | 35.46 | 91.2028 | 38.7473 | 80.4699 | 0.40166 |  | 6689 | 29.99 | 91.2028 | 5.7321 | 80.4699
6690 | 38.09 | 137.9711 | 41.266 | 102.6603 | 0.41416 |  | 6690 | 35 | 137.9711 | 6 | 102.6603
6691 | 43.35 | 143.8256 | 41.4621 | 121.0684 | 0.42119 |  | 6691 | 38.3 | 143.8256 | 5.7321 | 121.0684
6692 | 38.41 | 124.3585 | 30.5734 | 110.14 | 0.41813 |  | 6692 | 41.08 | 124.3585 | 5 | 110.14
6693 | 34.93 | 112.3139 | 25.8713 | 95.3275 | 0.41968 |  | 6693 | 33.37 | 112.3139 | 4 | 95.3275
6694 | 35.36 | 102.9244 | 28.2415 | 97.5301 | 0.41478 |  | 6694 | 27.67 | 102.9244 | 3 | 97.5301
6695 | 34.06 | 73.5552 | 30.5958 | 166.0291 | 0.40657 |  | 6695 | 27.36 | 73.5552 | 2.2679 | 166.0291
6696 | 28.99 | 37.645 | 25.812 | 165.5456 | 0.39808 |  | 6696 | 26.6 | 37.645 | 2 | 165.5456
6697 | 27.07 | 35.8492 | 35.0601 | 167.3038 | 0.40331 |  | 6697 | 25.96 | 35.8492 | 2.2679 | 167.3038
6698 | 27 | 34.0484 | 31.8153 | 142.0108 | 0.41649 |  | 6698 | 24.54 | 34.0484 | 3 | 142.0108
6699 | 27.19 | 32.1653 | 28.196 | 183.2329 | 0.423 |  | 6699 | 24.34 | 32.1653 | 4 | 183.2329
6700 | 26.28 | 30.4679 | 30.9344 | 182.0735 | 0.42661 |  | 6700 | 24.35 | 30.4679 | 5 | 182.0735
6701 | 30.23 | 29.2827 | 35.4509 | 213.754 | 0.44972 |  | 6701 | 24.73 | 29.2827 | 5.7321 | 213.754
6702 | 47.88 | 28.5106 | 30.9498 | 282.0463 | 0.46063 |  | 6702 | 24.94 | 28.5106 | 6 | 282.0463
6703 | 56.49 | 28.1064 | 39.804 | 276.4041 | 0.46803 |  | 6703 | 29.31 | 28.1064 | 5.7321 | 276.4041
6704 | 59.86 | 30.7287 | 95.9802 | 262.453 | 0.47109 |  | 6704 | 37.49 | 30.7287 | 5 | 262.453
6705 | 56.51 | 49.0624 | 124.1369 | 162.8735 | 0.47645 |  | 6705 | 36.44 | 49.0624 | 4 | 162.8735
6706 | 53.08 | 70.9607 | 106.5384 | 119.5363 | 0.47967 |  | 6706 | 40.66 | 70.9607 | 3 | 119.5363
6707 | 51.75 | 78.1557 | 57.3217 | 97.8423 | 0.47514 |  | 6707 | 40.29 | 78.1557 | 2.2679 | 97.8423
6708 | 49.91 | 78.8136 | 30.3477 | 95.1235 | 0.48064 |  | 6708 | 40 | 78.8136 | 2 | 95.1235
6709 | 48.8 | 82.3133 | 45.1865 | 92.0996 | 0.47664 |  | 6709 | 37.9 | 82.3133 | 2.2679 | 92.0996
6710 | 47.57 | 78.4003 | 41.7967 | 60.6691 | 0.47947 |  | 6710 | 37.9 | 78.4003 | 3 | 60.6691
6711 | 48.04 | 78.5522 | 40.3918 | 77.1319 | 0.48126 |  | 6711 | 37.37 | 78.5522 | 4 | 77.1319
6712 | 48.78 | 77.7863 | 41.561 | 77.5218 | 0.48116 |  | 6712 | 37.01 | 77.7863 | 5 | 77.5218
6713 | 51.5 | 84.9694 | 39.1861 | 90.82 | 0.48016 |  | 6713 | 36.53 | 84.9694 | 5.7321 | 90.82
6714 | 54.91 | 125.8989 | 44.9535 | 166.6007 | 0.47173 |  | 6714 | 42.69 | 125.8989 | 6 | 166.6007
6715 | 61.76 | 144.0126 | 31.2477 | 185.0071 | 0.46908 |  | 6715 | 43.19 | 144.0126 | 5.7321 | 185.0071
6716 | 51.93 | 143.8905 | 29.2607 | 212.7255 | 0.46446 |  | 6716 | 48.19 | 143.8905 | 5 | 212.7255
6717 | 43.03 | 118.8455 | 30.6979 | 181.8998 | 0.45919 |  | 6717 | 42.14 | 118.8455 | 4 | 181.8998
6718 | 38.86 | 107.6943 | 18.6482 | 139.6448 | 0.4503 |  | 6718 | 35.34 | 107.6943 | 3 | 139.6448
6719 | 27.6 | 91.1477 | 23.167 | 138.8384 | 0.43477 |  | 6719 | 32.15 | 91.1477 | 2.2679 | 138.8384
6720 | 30.64 | 43.0508 | 20.6548 | 111.2168 | 0.40863 |  | 6720 | 29.58 | 43.0508 | 2 | 111.2168
6721 | 27.93 | 33.4819 | 32.2396 | 139.2268 | 0.38965 |  | 6721 | 26.06 | 33.4819 | 2.2679 | 139.2268
6722 | 25 | 32.0357 | 24.6803 | 105.7697 | 0.37795 |  | 6722 | 27.99 | 32.0357 | 3 | 105.7697
6723 | 22.98 | 30.5468 | 22.5225 | 139.3868 | 0.37282 |  | 6723 | 27.95 | 30.5468 | 4 | 139.3868
6724 | 21.55 | 29.2169 | 26.2137 | 137.2658 | 0.39144 |  | 6724 | 27.67 | 29.2169 | 5 | 137.2658
6725 | 24.5 | 28.2723 | 45.6169 | 224.4926 | 0.40045 |  | 6725 | 27.96 | 28.2723 | 5.7321 | 224.4926
6726 | 30.52 | 27.6741 | 81.2296 | 263.8735 | 0.42249 |  | 6726 | 28.76 | 27.6741 | 6 | 263.8735
6727 | 42.15 | 27.4165 | 101.9977 | 254.0733 | 0.44469 |  | 6727 | 28.05 | 27.4165 | 5.7321 | 254.0733
6728 | 47.19 | 30.4106 | 127.8031 | 250.216 | 0.45398 |  | 6728 | 47.94 | 30.4106 | 5 | 250.216
6729 | 45.08 | 49.0623 | 97.5473 | 187.5531 | 0.46055 |  | 6729 | 49.62 | 49.0623 | 4 | 187.5531
6730 | 41.49 | 68.8153 | 108.9171 | 127.1018 | 0.45801 |  | 6730 | 50.26 | 68.8153 | 3 | 127.1018
6731 | 39.93 | 76.8197 | 122.5016 | 77.6997 | 0.458 |  | 6731 | 49.36 | 76.8197 | 2.2679 | 77.6997
6732 | 36.34 | 75.4515 | 127.3455 | 85.1885 | 0.45903 |  | 6732 | 54.54 | 75.4515 | 2 | 85.1885
6733 | 35.77 | 78.5166 | 132.034 | 92.3334 | 0.45259 |  | 6733 | 40 | 78.5166 | 2.2679 | 92.3334
6734 | 33 | 79.2396 | 115.0116 | 61.9075 | 0.45127 |  | 6734 | 32.93 | 79.2396 | 3 | 61.9075
6735 | 35.31 | 74.0594 | 90.4393 | 53.0195 | 0.44668 |  | 6735 | 29.2 | 74.0594 | 4 | 53.0195
6736 | 36.2 | 72.1191 | 31.3714 | 61.5157 | 0.44313 |  | 6736 | 31.1 | 72.1191 | 5 | 61.5157
6737 | 40.62 | 71.5189 | 44.3942 | 81.1525 | 0.45309 |  | 6737 | 42.78 | 71.5189 | 5.7321 | 81.1525
6738 | 44.44 | 111.4481 | 58.1999 | 87.5521 | 0.44945 |  | 6738 | 40.35 | 111.4481 | 6 | 87.5521
6739 | 50.15 | 125.5996 | 86.0189 | 114.0653 | 0.44442 |  | 6739 | 45 | 125.5996 | 5.7321 | 114.0653
6740 | 37.5 | 154.5696 | 74.1496 | 105.3789 | 0.43467 |  | 6740 | 46.4 | 154.5696 | 5 | 105.3789
6741 | 33.16 | 118.2422 | 67.8757 | 159.2412 | 0.42163 |  | 6741 | 36.74 | 118.2422 | 4 | 159.2412
6742 | 28.5 | 105.8315 | 78.2206 | 189.4275 | 0.41046 |  | 6742 | 34.04 | 105.8315 | 3 | 189.4275
6743 | 26.3 | 89.2938 | 73.4571 | 192.691 | 0.387 |  | 6743 | 34.38 | 89.2938 | 2.2679 | 192.691
6744 | 24.19 | 39.2952 | 275.0055 | 166.3405 | 0.37112 |  | 6744 | 31.82 | 39.2952 | 2 | 166.3405
6745 | 23.63 | 33.922 | 261.3023 | 191.4005 | 0.36366 |  | 6745 | 32.04 | 33.922 | 2.2679 | 191.4005
6746 | 22.25 | 32.4227 | 68.8372 | 161.75 | 0.36302 |  | 6746 | 29.56 | 32.4227 | 3 | 161.75
6747 | 19.44 | 30.9215 | 87.1692 | 179.1851 | 0.36071 |  | 6747 | 30.52 | 30.9215 | 4 | 179.1851
6748 | 21.92 | 29.5211 | 91.5503 | 230.9111 | 0.3646 |  | 6748 | 30.15 | 29.5211 | 5 | 230.9111
6749 | 25.22 | 28.5193 | 42.3462 | 241.565 | 0.3776 |  | 6749 | 29.99 | 28.5193 | 5.7321 | 241.565
6750 | 31 | 28.0464 | 73.0195 | 333.9054 | 0.39462 |  | 6750 | 29.99 | 28.0464 | 6 | 333.9054
6751 | 43.51 | 43.9878 | 106.8312 | 320.4895 | 0.41125 |  | 6751 | 31.98 | 43.9878 | 5.7321 | 320.4895
6752 | 45.73 | 64.6342 | 109.5161 | 253.9447 | 0.42107 |  | 6752 | 40 | 64.6342 | 5 | 253.9447
6753 | 47.06 | 44.3716 | 101.2825 | 234.898 | 0.42141 |  | 6753 | 41.3 | 44.3716 | 4 | 234.898
6754 | 42.62 | 40.5739 | 112.3302 | 159.191 | 0.42451 |  | 6754 | 47.7 | 40.5739 | 3 | 159.191
6755 | 40.49 | 42.27 | 82.2131 | 137.7705 | 0.42694 |  | 6755 | 46.46 | 42.27 | 2.2679 | 137.7705
6756 | 37.4 | 44.4727 | 97.1877 | 119.7514 | 0.42315 |  | 6756 | 42.08 | 44.4727 | 2 | 119.7514
6757 | 35.7 | 47.4748 | 66.8414 | 74.49 | 0.41325 |  | 6757 | 33.58 | 47.4748 | 2.2679 | 74.49
6758 | 35.49 | 47.0004 | 89.2571 | 63.8979 | 0.40941 |  | 6758 | 32.48 | 47.0004 | 3 | 63.8979
6759 | 35.25 | 54.8337 | 58.6654 | 48.6914 | 0.40963 |  | 6759 | 33.4 | 54.8337 | 4 | 48.6914
6760 | 33.49 | 69.4578 | 29.395 | 55.6126 | 0.41522 |  | 6760 | 32.44 | 69.4578 | 5 | 55.6126
6761 | 40.73 | 92.3545 | 53.166 | 115.8096 | 0.42155 |  | 6761 | 37.25 | 92.3545 | 5.7321 | 115.8096
6762 | 45.1 | 126.3863 | 65.8455 | 175.3516 | 0.42886 |  | 6762 | 42.69 | 126.3863 | 6 | 175.3516
6763 | 51.44 | 149.4257 | 94.4104 | 218.2842 | 0.43015 |  | 6763 | 46 | 149.4257 | 5.7321 | 218.2842
6764 | 43.27 | 150.3926 | 75.2527 | 278.139 | 0.42517 |  | 6764 | 52.75 | 150.3926 | 5 | 278.139
6765 | 38.13 | 119.0492 | 71.5954 | 222.1413 | 0.41105 |  | 6765 | 42.92 | 119.0492 | 4 | 222.1413
6766 | 34.2 | 107.0108 | 85.2848 | 242.8226 | 0.40866 |  | 6766 | 35 | 107.0108 | 3 | 242.8226
6767 | 28.08 | 75.9757 | 73.2673 | 228.4876 | 0.39368 |  | 6767 | 32.44 | 75.9757 | 2.2679 | 228.4876
6768 | 23.88 | 39.339 | 76.5059 | 236.9843 | 0.38909 |  | 6768 | 31.12 | 39.339 | 2 | 236.9843
6769 | 22.93 | 32.2479 | 105.8105 | 228.8906 | 0.37508 |  | 6769 | 30.91 | 32.2479 | 2.2679 | 228.8906
6770 | 21.77 | 30.9773 | 95.4309 | 168.4196 | 0.35382 |  | 6770 | 29.39 | 30.9773 | 3 | 168.4196
6771 | 18.39 | 29.7182 | 47.2498 | 220.9614 | 0.35267 |  | 6771 | 29.26 | 29.7182 | 4 | 220.9614
6772 | 18.95 | 28.6713 | 39.8842 | 252.1827 | 0.35623 |  | 6772 | 29.27 | 28.6713 | 5 | 252.1827
6773 | 22.2 | 27.9756 | 67.5035 | 247.8527 | 0.35611 |  | 6773 | 28.72 | 27.9756 | 5.7321 | 247.8527
6774 | 34.73 | 27.8324 | 102.3006 | 292.872 | 0.37276 |  | 6774 | 28.09 | 27.8324 | 6 | 292.872
6775 | 45.97 | 43.7622 | 98.6476 | 363.5893 | 0.38371 |  | 6775 | 29.27 | 43.7622 | 5.7321 | 363.5893
6776 | 47.65 | 65.0541 | 106.452 | 316.5641 | 0.38966 |  | 6776 | 29.53 | 65.0541 | 5 | 316.5641
6777 | 44.1 | 45.2367 | 76.1539 | 292.5353 | 0.38849 |  | 6777 | 32.81 | 45.2367 | 4 | 292.5353
6778 | 38.5 | 40.84 | 93.7893 | 222.8415 | 0.38264 |  | 6778 | 32.3 | 40.84 | 3 | 222.8415
6779 | 35.7 | 42.8248 | 72.7299 | 229.8929 | 0.37833 |  | 6779 | 32.03 | 42.8248 | 2.2679 | 229.8929
6780 | 31.25 | 44.1928 | 96.2185 | 180.3297 | 0.36827 |  | 6780 | 33.86 | 44.1928 | 2 | 180.3297
6781 | 34.04 | 46.7441 | 116.7383 | 129.2949 | 0.36901 |  | 6781 | 32.77 | 46.7441 | 2.2679 | 129.2949
6782 | 30 | 48.1272 | 108.5786 | 76.8696 | 0.36678 |  | 6782 | 29.61 | 48.1272 | 3 | 76.8696
6783 | 31.89 | 55.1328 | 79.5426 | 60.2932 | 0.36902 |  | 6783 | 28.23 | 55.1328 | 4 | 60.2932
6784 | 29.16 | 68.887 | 39.8207 | 52.3194 | 0.37272 |  | 6784 | 28.21 | 68.887 | 5 | 52.3194
6785 | 36.95 | 88.106 | 49.4039 | 69.6243 | 0.38408 |  | 6785 | 28.8 | 88.106 | 5.7321 | 69.6243
6786 | 43.3 | 117.059 | 53.3114 | 112.138 | 0.39004 |  | 6786 | 32.95 | 117.059 | 6 | 112.138
6787 | 47.79 | 144.6347 | 97.2909 | 144.9641 | 0.39412 |  | 6787 | 41.29 | 144.6347 | 5.7321 | 144.9641
6788 | 41.78 | 135.4186 | 108.4403 | 198.7338 | 0.39212 |  | 6788 | 56.71 | 135.4186 | 5 | 198.7338
6789 | 29 | 113.5407 | 112.8282 | 201.0681 | 0.38581 |  | 6789 | 60 | 113.5407 | 4 | 201.0681
6790 | 28.39 | 103.8531 | 69.8664 | 219.3741 | 0.37468 |  | 6790 | 49 | 103.8531 | 3 | 219.3741
6791 | 25.23 | 75.2694 | 69.6438 | 203.6558 | 0.36505 |  | 6791 | 45.25 | 75.2694 | 2.2679 | 203.6558
6792 | 23.54 | 37.596 | 60.682 | 204.7927 | 0.36331 |  | 6792 | 36.55 | 37.596 | 2 | 204.7927
6793 | 22.34 | 34.2103 | 71.3258 | 243.5384 | 0.351 |  | 6793 | 31.99 | 34.2103 | 2.2679 | 243.5384
6794 | 17.65 | 32.5218 | 88.2817 | 227.0108 | 0.33611 |  | 6794 | 29.98 | 32.5218 | 3 | 227.0108
6795 | 12.57 | 31 | 110.8697 | 209.3259 | 0.32905 |  | 6795 | 29.8 | 31 | 4 | 209.3259
6796 | 14.54 | 29.6746 | 91.3214 | 232.7278 | 0.32726 |  | 6796 | 29.85 | 29.6746 | 5 | 232.7278
6797 | 20.17 | 28.6396 | 47.752 | 264.1577 | 0.3461 |  | 6797 | 29.9 | 28.6396 | 5.7321 | 264.1577
6798 | 25.94 | 28.4277 | 78.234 | 337.9567 | 0.36798 |  | 6798 | 29.61 | 28.4277 | 6 | 337.9567
6799 | 38.66 | 43.5932 | 107.4111 | 372.6316 | 0.37866 |  | 6799 | 30.21 | 43.5932 | 5.7321 | 372.6316
6800 | 40.84 | 66.9578 | 103.0789 | 371.1204 | 0.3852 |  | 6800 | 50 | 66.9578 | 5 | 371.1204
6801 | 37.42 | 45.5397 | 94.1647 | 226.8016 | 0.39099 |  | 6801 | 74.18 | 45.5397 | 4 | 226.8016
6802 | 34.03 | 41.3638 | 92.3414 | 157.4071 | 0.39302 |  | 6802 | 70.16 | 41.3638 | 3 | 157.4071
6803 | 36.13 | 43.5721 | 109.1009 | 96.002 | 0.37999 |  | 6803 | 54.72 | 43.5721 | 2.2679 | 96.002
6804 | 35.9 | 45.5747 | 43.5518 | 124.5949 | 0.37296 |  | 6804 | 49.42 | 45.5747 | 2 | 124.5949
6805 | 33.32 | 48.9333 | 42.0698 | 123.8532 | 0.36901 |  | 6805 | 42.7 | 48.9333 | 2.2679 | 123.8532
6806 | 31.55 | 50.7637 | 256.5299 | 127.9949 | 0.37007 |  | 6806 | 45.79 | 50.7637 | 3 | 127.9949
6807 | 27.94 | 56.3954 | 69.1379 | 113.985 | 0.37174 |  | 6807 | 46.37 | 56.3954 | 4 | 113.985
6808 | 24.9 | 70.1894 | 78.8561 | 113.5033 | 0.36938 |  | 6808 | 48.33 | 70.1894 | 5 | 113.5033
6809 | 30.38 | 91.5069 | 70.059 | 140.5963 | 0.36986 |  | 6809 | 55 | 91.5069 | 5.7321 | 140.5963
6810 | 33.65 | 119.1511 | 53.192 | 228.0819 | 0.36586 |  | 6810 | 57.24 | 119.1511 | 6 | 228.0819
6811 | 34.92 | 158.2024 | 75.068 | 227.0619 | 0.3647 |  | 6811 | 69.94 | 158.2024 | 5.7321 | 227.0619
6812 | 31.19 | 138.4452 | 63.4777 | 214.6151 | 0.36238 |  | 6812 | 81.93 | 138.4452 | 5 | 214.6151
6813 | 24.8 | 114.9881 | 78.0376 | 272.618 | 0.35859 |  | 6813 | 60.11 | 114.9881 | 4 | 272.618
6814 | 24 | 104.7095 | 79.834 | 262.67 | 0.35556 |  | 6814 | 48.59 | 104.7095 | 3 | 262.67
6815 | 23 | 75.8964 | 43.1868 | 199.764 | 0.35416 |  | 6815 | 40.62 | 75.8964 | 2.2679 | 199.764
6816 | 17.8 | 39.6005 | 47.7848 | 229.6084 | 0.35345 |  | 6816 | 34.2 | 39.6005 | 2 | 229.6084
6817 | 21.4 | 34.7318 | 75.4514 | 197.2506 | 0.34968 |  | 6817 | 29.4 | 34.7318 | 2.2679 | 197.2506
6818 | 22 | 33.2463 | 78.9944 | 172.7192 | 0.35784 |  | 6818 | 29.57 | 33.2463 | 3 | 172.7192
6819 | 22.7 | 31.5814 | 58.214 | 197.374 | 0.37328 |  | 6819 | 29.49 | 31.5814 | 4 | 197.374
6820 | 20.8 | 30.0418 | 37.2265 | 266.9534 | 0.39165 |  | 6820 | 29.51 | 30.0418 | 5 | 266.9534
6821 | 24.9 | 28.9668 | 39.203 | 257.6044 | 0.41482 |  | 6821 | 29.74 | 28.9668 | 5.7321 | 257.6044
6822 | 25 | 28.6324 | 73.5 | 329.0606 | 0.42296 |  | 6822 | 30.01 | 28.6324 | 6 | 329.0606
6823 | 32.18 | 43.3109 | 89.3759 | 311.4522 | 0.42536 |  | 6823 | 30.19 | 43.3109 | 5.7321 | 311.4522
6824 | 29.65 | 65.3569 | 93.5237 | 348.5239 | 0.43326 |  | 6824 | 40 | 65.3569 | 5 | 348.5239
6825 | 37.19 | 45.3444 | 101.2757 | 310.3436 | 0.42991 |  | 6825 | 53.88 | 45.3444 | 4 | 310.3436
6826 | 39.9 | 41.6152 | 320.9139 | 180.9411 | 0.43424 |  | 6826 | 52.6 | 41.6152 | 3 | 180.9411
6827 | 37.4 | 45.0794 | 97.761 | 151.9538 | 0.43127 |  | 6827 | 44 | 45.0794 | 2.2679 | 151.9538
6828 | 41 | 47.3557 | 68.0732 | 104.3008 | 0.42886 |  | 6828 | 40 | 47.3557 | 2 | 104.3008
6829 | 36.3 | 46.7668 | 46.8534 | 70.0487 | 0.43154 |  | 6829 | 35 | 46.7668 | 2.2679 | 70.0487
6830 | 34.5 | 50.4318 | 56.0753 | 57.3091 | 0.43138 |  | 6830 | 37.74 | 50.4318 | 3 | 57.3091
6831 | 32.4 | 56.1414 | 38.4401 | 48.5111 | 0.42592 |  | 6831 | 37.06 | 56.1414 | 4 | 48.5111
6832 | 32.43 | 74.059 | 41.7113 | 53.0029 | 0.42206 |  | 6832 | 36.96 | 74.059 | 5 | 53.0029
6833 | 35.82 | 95.761 | 38.0008 | 127.0768 | 0.41952 |  | 6833 | 42.69 | 95.761 | 5.7321 | 127.0768
6834 | 41.98 | 139.2551 | 47.2161 | 212.9141 | 0.4277 |  | 6834 | 43.4 | 139.2551 | 6 | 212.9141
6835 | 44.65 | 149.3574 | 53.4196 | 243.6184 | 0.418 |  | 6835 | 40 | 149.3574 | 5.7321 | 243.6184
6836 | 40.13 | 138.5433 | 79.3618 | 263.9993 | 0.4074 |  | 6836 | 46.25 | 138.5433 | 5 | 263.9993
6837 | 33.15 | 119.0304 | 91.8809 | 284.4134 | 0.41249 |  | 6837 | 32.44 | 119.0304 | 4 | 284.4134
6838 | 33.59 | 109.8599 | 83.3107 | 303.0129 | 0.42099 |  | 6838 | 30.41 | 109.8599 | 3 | 303.0129
6839 | 31.53 | 76.403 | 27.8419 | 305.1117 | 0.42764 |  | 6839 | 29.62 | 76.403 | 2.2679 | 305.1117
6840 | 31.44 | 40.7507 | 27.6311 | 287.1828 | 0.42255 |  | 6840 | 28.05 | 40.7507 | 2 | 287.1828
6841 | 25.66 | 32.5706 | 29.4128 | 273.999 | 0.41531 |  | 6841 | 26.4 | 32.5706 | 2.2679 | 273.999
6842 | 24.05 | 31.1229 | 37.0411 | 242.4815 | 0.41071 |  | 6842 | 27.52 | 31.1229 | 3 | 242.4815
6843 | 21.1 | 29.8165 | 32.5209 | 210.7567 | 0.41081 |  | 6843 | 27.34 | 29.8165 | 4 | 210.7567
6844 | 24.62 | 28.6248 | 19.528 | 278.2568 | 0.41847 |  | 6844 | 27.52 | 28.6248 | 5 | 278.2568
6845 | 22.04 | 27.9718 | 25.4331 | 312.5891 | 0.41798 |  | 6845 | 27.84 | 27.9718 | 5.7321 | 312.5891
6846 | 22.08 | 28.1477 | 25.9187 | 312.9443 | 0.41822 |  | 6846 | 28.04 | 28.1477 | 6 | 312.9443
6847 | 26.22 | 43.239 | 24.9353 | 396.3142 | 0.41607 |  | 6847 | 30.01 | 43.239 | 5.7321 | 396.3142
6848 | 27.85 | 65.5141 | 49.0059 | 332.4409 | 0.40462 |  | 6848 | 33 | 65.5141 | 5 | 332.4409
6849 | 26.58 | 46.8312 | 36.6588 | 317.2809 | 0.39734 |  | 6849 | 58.73 | 46.8312 | 4 | 317.2809
6850 | 25.1 | 43.7806 | 57.383 | 288.0985 | 0.38959 |  | 6850 | 58.41 | 43.7806 | 3 | 288.0985
6851 | 24 | 45.7626 | 50.9432 | 221.4337 | 0.38304 |  | 6851 | 53.91 | 45.7626 | 2.2679 | 221.4337
6852 | 23.08 | 48.2829 | 31.6605 | 133.4267 | 0.38004 |  | 6852 | 54.96 | 48.2829 | 2 | 133.4267
6853 | 21.8 | 50.6351 | 40.3319 | 90.3854 | 0.36634 |  | 6853 | 49.55 | 50.6351 | 2.2679 | 90.3854
6854 | 21.8 | 55.2219 | 48.6643 | 59.2994 | 0.36586 |  | 6854 | 44.92 | 55.2219 | 3 | 59.2994
6855 | 21.8 | 60.6816 | 45.4995 | 60.0527 | 0.36364 |  | 6855 | 40.6 | 60.6816 | 4 | 60.0527
6856 | 21.29 | 75.3344 | 47.4845 | 68.7857 | 0.35727 |  | 6856 | 40.6 | 75.3344 | 5 | 68.7857
6857 | 27.94 | 97.2786 | 38.0533 | 85.6272 | 0.35177 |  | 6857 | 43.21 | 97.2786 | 5.7321 | 85.6272
6858 | 30 | 131.4349 | 33.2022 | 83.1417 | 0.35146 |  | 6858 | 48.37 | 131.4349 | 6 | 83.1417
6859 | 47.5 | 152.7352 | 32.2221 | 156.2796 | 0.36177 |  | 6859 | 50.03 | 152.7352 | 5.7321 | 156.2796
6860 | 32.4 | 150.469 | 27.0654 | 228.0709 | 0.36754 |  | 6860 | 53.31 | 150.469 | 5 | 228.0709
6861 | 25.1 | 117.9625 | 32.2988 | 319.557 | 0.36945 |  | 6861 | 45.34 | 117.9625 | 4 | 319.557
6862 | 21.6 | 107.1493 | 33.5457 | 288.1692 | 0.37337 |  | 6862 | 35 | 107.1493 | 3 | 288.1692
6863 | 20 | 78.0686 | 26.7175 | 304.9188 | 0.3699 |  | 6863 | 33.54 | 78.0686 | 2.2679 | 304.9188
6864 | 26.2 | 37.5937 | 22.2721 | 214.8454 | 0.38245 |  | 6864 | 29.94 | 37.5937 | 2 | 214.8454
6865 | 26.2 | 35.3225 | 24.1269 | 230.9508 | 0.39289 |  | 6865 | 29.8 | 35.3225 | 2.2679 | 230.9508
6866 | 24 | 33.651 | 29.1807 | 194.758 | 0.40196 |  | 6866 | 29.59 | 33.651 | 3 | 194.758
6867 | 15.17 | 31.8884 | 233.2477 | 248.4908 | 0.41013 |  | 6867 | 29.25 | 31.8884 | 4 | 248.4908
6868 | 16 | 30.2653 | 29.4275 | 269.9519 | 0.42428 |  | 6868 | 28.98 | 30.2653 | 5 | 269.9519
6869 | 24.63 | 29.0874 | 22.974 | 287.4291 | 0.45192 |  | 6869 | 28.79 | 29.0874 | 5.7321 | 287.4291
6870 | 36.06 | 28.1644 | 24.9233 | 382.8402 | 0.46838 |  | 6870 | 28.23 | 28.1644 | 6 | 382.8402
6871 | 48.92 | 27.6192 | 27.0545 | 449.9417 | 0.47534 |  | 6871 | 31.7 | 27.6192 | 5.7321 | 449.9417
6872 | 50.24 | 30.6249 | 45.4109 | 428.5424 | 0.47837 |  | 6872 | 44.22 | 30.6249 | 5 | 428.5424
6873 | 56.06 | 49.2031 | 50.7082 | 276.5634 | 0.47865 |  | 6873 | 58.86 | 49.2031 | 4 | 276.5634
6874 | 53.85 | 67.607 | 45.1979 | 187.1998 | 0.47711 |  | 6874 | 55.21 | 67.607 | 3 | 187.1998
6875 | 48 | 75.7218 | 50.1146 | 70.4656 | 0.47331 |  | 6875 | 35.01 | 75.7218 | 2.2679 | 70.4656
6876 | 45.25 | 77.043 | 44.3795 | 86.2949 | 0.47114 |  | 6876 | 31.36 | 77.043 | 2 | 86.2949
6877 | 43 | 75.5594 | 39.979 | 85.5545 | 0.46582 |  | 6877 | 35.45 | 75.5594 | 2.2679 | 85.5545
6878 | 39.5 | 75.6706 | 44.5485 | 69.0454 | 0.46083 |  | 6878 | 35.1 | 75.6706 | 3 | 69.0454
6879 | 43.18 | 72.6536 | 33.6414 | 62.4572 | 0.45634 |  | 6879 | 32.92 | 72.6536 | 4 | 62.4572
6880 | 46.34 | 76.0951 | 40.3088 | 68.6614 | 0.45816 |  | 6880 | 33.79 | 76.0951 | 5 | 68.6614
6881 | 48.39 | 78.0527 | 38.3995 | 77.2086 | 0.4544 |  | 6881 | 33.52 | 78.0527 | 5.7321 | 77.2086
6882 | 50.09 | 117.7931 | 51.1125 | 86.8952 | 0.44201 |  | 6882 | 41.5 | 117.7931 | 6 | 86.8952
6883 | 52.79 | 147.1905 | 48.7622 | 107.5928 | 0.44078 |  | 6883 | 31.65 | 147.1905 | 5.7321 | 107.5928
6884 | 48.93 | 141.4675 | 22.0641 | 171.9649 | 0.43032 |  | 6884 | 35.01 | 141.4675 | 5 | 171.9649
6885 | 37.01 | 113.003 | 26.4867 | 208.3117 | 0.42388 |  | 6885 | 30.92 | 113.003 | 4 | 208.3117
6886 | 35 | 102.571 | 28.6705 | 226.9249 | 0.41883 |  | 6886 | 38.95 | 102.571 | 3 | 226.9249
6887 | 25.18 | 91.4214 | 26.0404 | 247.6297 | 0.4209 |  | 6887 | 37.76 | 91.4214 | 2.2679 | 247.6297
6888 | 26 | 42.0123 | 29.8253 | 237.2416 | 0.42293 |  | 6888 | 29.79 | 42.0123 | 2 | 237.2416
6889 | 25.72 | 32.6082 | 30.3024 | 184.231 | 0.41174 |  | 6889 | 28.44 | 32.6082 | 2.2679 | 184.231
6890 | 25 | 31.2533 | 36.0228 | 169.0728 | 0.40538 |  | 6890 | 23.09 | 31.2533 | 3 | 169.0728
6891 | 24.27 | 29.9833 | 24.7591 | 231.0331 | 0.40601 |  | 6891 | 18 | 29.9833 | 4 | 231.0331
6892 | 25 | 28.8441 | 40.7969 | 256.1286 | 0.4151 |  | 6892 | 22.34 | 28.8441 | 5 | 256.1286
6893 | 29.99 | 28.0382 | 111.3337 | 302.6322 | 0.42205 |  | 6893 | 24.85 | 28.0382 | 5.7321 | 302.6322
6894 | 40.61 | 27.5343 | 69.6671 | 290.2049 | 0.43671 |  | 6894 | 28.69 | 27.5343 | 6 | 290.2049
6895 | 52.64 | 27.3587 | 37.127 | 372.7785 | 0.45334 |  | 6895 | 30.47 | 27.3587 | 5.7321 | 372.7785
6896 | 55.21 | 30.8602 | 67.6624 | 288.7006 | 0.46641 |  | 6896 | 42.44 | 30.8602 | 5 | 288.7006
6897 | 54.8 | 50.7711 | 40.881 | 302.116 | 0.46546 |  | 6897 | 42.86 | 50.7711 | 4 | 302.116
6898 | 51.76 | 67.3551 | 45.3446 | 254.9179 | 0.47205 |  | 6898 | 50.89 | 67.3551 | 3 | 254.9179
6899 | 50.62 | 71.7035 | 62.3046 | 324.3313 | 0.47257 |  | 6899 | 46.38 | 71.7035 | 2.2679 | 324.3313
6900 | 47.9 | 75.5288 | 104.4882 | 306.0092 | 0.47665 |  | 6900 | 43 | 75.5288 | 2 | 306.0092
6901 | 46.64 | 80.9523 | 51.13 | 272.0774 | 0.47869 |  | 6901 | 35.55 | 80.9523 | 2.2679 | 272.0774
6902 | 44.58 | 77.9773 | 45.1363 | 273.3464 | 0.47786 |  | 6902 | 35.15 | 77.9773 | 3 | 273.3464
6903 | 45.19 | 75.5141 | 47.2666 | 234.267 | 0.4835 |  | 6903 | 40.52 | 75.5141 | 4 | 234.267
6904 | 46.98 | 71.7586 | 37.2904 | 282.3403 | 0.48344 |  | 6904 | 35 | 71.7586 | 5 | 282.3403
6905 | 52.37 | 73.2237 | 45.044 | 281.0047 | 0.48123 |  | 6905 | 32.29 | 73.2237 | 5.7321 | 281.0047
6906 | 58.33 | 110.407 | 82.7858 | 318.516 | 0.4839 |  | 6906 | 31.36 | 110.407 | 6 | 318.516
6907 | 67.95 | 135.7161 | 100.2412 | 279.5644 | 0.48821 |  | 6907 | 31.41 | 135.7161 | 5.7321 | 279.5644
6908 | 55.29 | 160.5448 | 67.248 | 286.1117 | 0.48196 |  | 6908 | 38.52 | 160.5448 | 5 | 286.1117
6909 | 45.97 | 120.4878 | 90.3573 | 220.8796 | 0.48516 |  | 6909 | 31.5 | 120.4878 | 4 | 220.8796
6910 | 39.5 | 101.877 | 86.7187 | 257.5341 | 0.47956 |  | 6910 | 30.8 | 101.877 | 3 | 257.5341
6911 | 29.85 | 88.5756 | 74.6858 | 187.0522 | 0.4754 |  | 6911 | 35 | 88.5756 | 2.2679 | 187.0522
6912 | 34.81 | 39.6952 | 63.3195 | 193.5198 | 0.4724 |  | 6912 | 32 | 39.6952 | 2 | 193.5198
6913 | 33.02 | 34.4619 | 107.4662 | 217.7161 | 0.46652 |  | 6913 | 27.2 | 34.4619 | 2.2679 | 217.7161
6914 | 29.25 | 32.7544 | 92.3769 | 152.0621 | 0.45815 |  | 6914 | 26.86 | 32.7544 | 3 | 152.0621
6915 | 28.4 | 31.1234 | 63.0677 | 215.3362 | 0.4552 |  | 6915 | 26.61 | 31.1234 | 4 | 215.3362
6916 | 28.7 | 29.7062 | 26.9963 | 202.4762 | 0.45889 |  | 6916 | 26.4 | 29.7062 | 5 | 202.4762
6917 | 30.3 | 28.7762 | 33.4624 | 278.2937 | 0.46965 |  | 6917 | 26.28 | 28.7762 | 5.7321 | 278.2937
6918 | 38.68 | 28.4496 | 62.8829 | 331.0746 | 0.48294 |  | 6918 | 27.13 | 28.4496 | 6 | 331.0746
6919 | 49.97 | 44.2921 | 108.0447 | 285.4083 | 0.48355 |  | 6919 | 26.7 | 44.2921 | 5.7321 | 285.4083
6920 | 51.3 | 65.8302 | 82.6931 | 335.6304 | 0.47768 |  | 6920 | 31.3 | 65.8302 | 5 | 335.6304
6921 | 50.14 | 46.7303 | 37.1581 | 248.2809 | 0.47389 |  | 6921 | 30.66 | 46.7303 | 4 | 248.2809
6922 | 46.99 | 40.8581 | 42.2265 | 238.3332 | 0.47225 |  | 6922 | 40.01 | 40.8581 | 3 | 238.3332
6923 | 42.59 | 42.7624 | 77.7593 | 180.6823 | 0.46808 |  | 6923 | 31.89 | 42.7624 | 2.2679 | 180.6823
6924 | 36 | 47.7946 | 96.5712 | 229.3288 | 0.46583 |  | 6924 | 33.34 | 47.7946 | 2 | 229.3288
6925 | 36 | 46.6678 | 43.4895 | 191.3703 | 0.46494 |  | 6925 | 31.39 | 46.6678 | 2.2679 | 191.3703
6926 | 36.09 | 50.6286 | 38.9228 | 179.9294 | 0.4669 |  | 6926 | 31.36 | 50.6286 | 3 | 179.9294
6927 | 36.98 | 56.3349 | 40.964 | 184.9804 | 0.46782 |  | 6927 | 32.24 | 56.3349 | 4 | 184.9804
6928 | 38.03 | 72.4225 | 236.2797 | 162.5108 | 0.47613 |  | 6928 | 33.24 | 72.4225 | 5 | 162.5108
6929 | 46.99 | 89.7679 | 275.3281 | 151.4432 | 0.47404 |  | 6929 | 37.87 | 89.7679 | 5.7321 | 151.4432
6930 | 50.07 | 130.6818 | 109.9525 | 187.8994 | 0.46946 |  | 6930 | 42.86 | 130.6818 | 6 | 187.8994
6931 | 47.43 | 152.5522 | 92.2558 | 234.5517 | 0.46646 |  | 6931 | 49.92 | 152.5522 | 5.7321 | 234.5517
6932 | 40 | 141.4497 | 90.4645 | 222.0201 | 0.46049 |  | 6932 | 57.05 | 141.4497 | 5 | 222.0201
6933 | 33.06 | 121.2696 | 85.8277 | 227.3855 | 0.44919 |  | 6933 | 47 | 121.2696 | 4 | 227.3855
6934 | 33.86 | 112.1552 | 66.5479 | 183.5298 | 0.4394 |  | 6934 | 43.22 | 112.1552 | 3 | 183.5298
6935 | 30.87 | 77.3699 | 57.905 | 207.6912 | 0.43405 |  | 6935 | 34.3 | 77.3699 | 2.2679 | 207.6912
6936 | 27.65 | 40.3845 | 96.4796 | 206.413 | 0.43957 |  | 6936 | 32.96 | 40.3845 | 2 | 206.413
6937 | 28.1 | 34.3461 | 113.5725 | 219.49 | 0.44735 |  | 6937 | 33.08 | 34.3461 | 2.2679 | 219.49
6938 | 26.6 | 32.6991 | 52.2683 | 176.2968 | 0.45274 |  | 6938 | 30.84 | 32.6991 | 3 | 176.2968
6939 | 26.34 | 30.9996 | 37.4909 | 186.0178 | 0.46045 |  | 6939 | 35.69 | 30.9996 | 4 | 186.0178
6940 | 28.43 | 29.5589 | 31.1444 | 251.8444 | 0.47361 |  | 6940 | 30.59 | 29.5589 | 5 | 251.8444
6941 | 31.29 | 28.6708 | 29.3703 | 270.9597 | 0.49094 |  | 6941 | 30.66 | 28.6708 | 5.7321 | 270.9597
6942 | 39.74 | 28.478 | 29.4322 | 311.746 | 0.50206 |  | 6942 | 30.61 | 28.478 | 6 | 311.746
6943 | 52.13 | 43.7767 | 71.8366 | 345.3285 | 0.50356 |  | 6943 | 30.91 | 43.7767 | 5.7321 | 345.3285
6944 | 54.42 | 64.6682 | 93.7782 | 281.7504 | 0.50661 |  | 6944 | 31.79 | 64.6682 | 5 | 281.7504
6945 | 54.03 | 48.2709 | 110.9527 | 234.8347 | 0.50595 |  | 6945 | 36.63 | 48.2709 | 4 | 234.8347
6946 | 51.43 | 43.4093 | 82.8986 | 178.1251 | 0.50509 |  | 6946 | 38.31 | 43.4093 | 3 | 178.1251
6947 | 50.43 | 48.0994 | 41.8344 | 162.2305 | 0.50198 |  | 6947 | 40.77 | 48.0994 | 2.2679 | 162.2305
6948 | 48.7 | 49.5026 | 56.6674 | 141.2886 | 0.49949 |  | 6948 | 40.52 | 49.5026 | 2 | 141.2886
6949 | 43 | 50.3329 | 44.9013 | 127.934 | 0.49937 |  | 6949 | 40.53 | 50.3329 | 2.2679 | 127.934
6950 | 41.45 | 52.6879 | 36.5082 | 77.0755 | 0.50479 |  | 6950 | 32.14 | 52.6879 | 3 | 77.0755
6951 | 44.77 | 58.635 | 43.7947 | 65.2825 | 0.50631 |  | 6951 | 30.08 | 58.635 | 4 | 65.2825
6952 | 48.53 | 77.0795 | 48.6596 | 73.1974 | 0.51123 |  | 6952 | 30.44 | 77.0795 | 5 | 73.1974
6953 | 51.83 | 91.6178 | 79.0277 | 81.4436 | 0.51271 |  | 6953 | 31.05 | 91.6178 | 5.7321 | 81.4436
6954 | 56.62 | 140.4659 | 93.4729 | 173.8835 | 0.5057 |  | 6954 | 36.7 | 140.4659 | 6 | 173.8835
6955 | 63.96 | 159.6199 | 127.0397 | 209.4885 | 0.5018 |  | 6955 | 46.47 | 159.6199 | 5.7321 | 209.4885
6956 | 54.34 | 136.9667 | 103.3304 | 248.0061 | 0.50038 |  | 6956 | 49.88 | 136.9667 | 5 | 248.0061
6957 | 45.53 | 117.158 | 97.3051 | 256.67 | 0.49294 |  | 6957 | 37.29 | 117.158 | 4 | 256.67
6958 | 38.6 | 105.9708 | 84.0085 | 263.1999 | 0.48371 |  | 6958 | 33.42 | 105.9708 | 3 | 263.1999
6959 | 34.44 | 77.2629 | 84.0885 | 244.1431 | 0.47879 |  | 6959 | 33.27 | 77.2629 | 2.2679 | 244.1431
6960 | 33.15 | 40.1206 | 97.001 | 173.0916 | 0.464 |  | 6960 | 32.46 | 40.1206 | 2 | 173.0916
6961 | 31.05 | 33.6787 | 129.0499 | 241.5091 | 0.46019 |  | 6961 | 32.35 | 33.6787 | 2.2679 | 241.5091
6962 | 28.31 | 32.275 | 104.092 | 226.6236 | 0.45878 |  | 6962 | 29.44 | 32.275 | 3 | 226.6236
6963 | 27.5 | 30.8698 | 73.1131 | 204.4114 | 0.45286 |  | 6963 | 29.05 | 30.8698 | 4 | 204.4114
6964 | 26.4 | 29.4794 | 30.3901 | 267.401 | 0.45466 |  | 6964 | 28.44 | 29.4794 | 5 | 267.401
6965 | 29.58 | 28.5423 | 36.4985 | 339.6079 | 0.45713 |  | 6965 | 28.53 | 28.5423 | 5.7321 | 339.6079
6966 | 38.2 | 28.5081 | 59.4287 | 321.5228 | 0.46124 |  | 6966 | 30.46 | 28.5081 | 6 | 321.5228
6967 | 47.04 | 43.8468 | 89.893 | 384.7131 | 0.46393 |  | 6967 | 35 | 43.8468 | 5.7321 | 384.7131
6968 | 51.46 | 67.7126 | 96.1366 | 428.5732 | 0.46215 |  | 6968 | 42.44 | 67.7126 | 5 | 428.5732
6969 | 47 | 45.2829 | 57.9906 | 273.9385 | 0.46014 |  | 6969 | 48.34 | 45.2829 | 4 | 273.9385
6970 | 38.7 | 39.9622 | 59.4976 | 164.6659 | 0.45094 |  | 6970 | 47.25 | 39.9622 | 3 | 164.6659
6971 | 36 | 41.4142 | 127.7656 | 72.5849 | 0.44192 |  | 6971 | 57.39 | 41.4142 | 2.2679 | 72.5849
6972 | 27.76 | 43.1978 | 110.1458 | 82.8178 | 0.42846 |  | 6972 | 50.88 | 43.1978 | 2 | 82.8178
6973 | 26.6 | 44.9229 | 71.6136 | 81.1131 | 0.41811 |  | 6973 | 50.23 | 44.9229 | 2.2679 | 81.1131
6974 | 27.26 | 50.2701 | 36.8127 | 60.7407 | 0.41565 |  | 6974 | 43.22 | 50.2701 | 3 | 60.7407
6975 | 28.1 | 53.3075 | 40.2571 | 59.5117 | 0.41103 |  | 6975 | 40.03 | 53.3075 | 4 | 59.5117
6976 | 28.78 | 73.895 | 41.9283 | 60.0865 | 0.4068 |  | 6976 | 41.89 | 73.895 | 5 | 60.0865
6977 | 36.42 | 91.5677 | 80.144 | 71.0653 | 0.41432 |  | 6977 | 47.26 | 91.5677 | 5.7321 | 71.0653
6978 | 36.79 | 134.9472 | 99.8417 | 99.0005 | 0.41273 |  | 6978 | 50.48 | 134.9472 | 6 | 99.0005
6979 | 37.03 | 155.808 | 118.3985 | 112.4737 | 0.40886 |  | 6979 | 64.05 | 155.808 | 5.7321 | 112.4737
6980 | 29.9 | 144.2406 | 86.9874 | 124.3678 | 0.40843 |  | 6980 | 58.12 | 144.2406 | 5 | 124.3678
6981 | 29 | 114.1716 | 97.7075 | 192.3185 | 0.40829 |  | 6981 | 50.87 | 114.1716 | 4 | 192.3185
6982 | 27.8 | 104.5541 | 88.2325 | 258.2798 | 0.40812 |  | 6982 | 40.89 | 104.5541 | 3 | 258.2798
6983 | 27.9 | 74.6455 | 92.1281 | 228.4419 | 0.40704 |  | 6983 | 31.93 | 74.6455 | 2.2679 | 228.4419
6984 | 27.04 | 38.9727 | 73.2527 | 213.5855 | 0.39716 |  | 6984 | 30.37 | 38.9727 | 2 | 213.5855
6985 | 27.56 | 35.5336 | 111.8526 | 275.0187 | 0.39452 |  | 6985 | 32.13 | 35.5336 | 2.2679 | 275.0187
6986 | 25.4 | 33.6798 | 104.9194 | 216.2827 | 0.40002 |  | 6986 | 31.53 | 33.6798 | 3 | 216.2827
6987 | 23.9 | 31.8918 | 77.4857 | 239.2538 | 0.39918 |  | 6987 | 30.46 | 31.8918 | 4 | 239.2538
6988 | 24.2 | 30.4006 | 26.6706 | 272.4117 | 0.39895 |  | 6988 | 30.5 | 30.4006 | 5 | 272.4117
6989 | 25.09 | 29.1904 | 32.9224 | 314.9176 | 0.3984 |  | 6989 | 31.11 | 29.1904 | 5.7321 | 314.9176
6990 | 26.89 | 28.817 | 58.0467 | 371.9709 | 0.40952 |  | 6990 | 29.95 | 28.817 | 6 | 371.9709
6991 | 29.7 | 43.5159 | 256.3952 | 456.1203 | 0.42286 |  | 6991 | 34.78 | 43.5159 | 5.7321 | 456.1203
6992 | 32.97 | 67.3831 | 61.3403 | 420.4874 | 0.43012 |  | 6992 | 51.33 | 67.3831 | 5 | 420.4874
6993 | 35.14 | 47.7328 | 92.2685 | 387.6399 | 0.43313 |  | 6993 | 59.24 | 47.7328 | 4 | 387.6399
6994 | 36 | 42.4818 | 77.8759 | 278.0721 | 0.4303 |  | 6994 | 59 | 42.4818 | 3 | 278.0721
6995 | 36.53 | 44.6753 | 43.2943 | 87.3095 | 0.4301 |  | 6995 | 50.35 | 44.6753 | 2.2679 | 87.3095
6996 | 35.2 | 47.4641 | 50.5996 | 76.0857 | 0.42979 |  | 6996 | 42.44 | 47.4641 | 2 | 76.0857
6997 | 34.08 | 50.2409 | 233.5323 | 71.634 | 0.42633 |  | 6997 | 41.65 | 50.2409 | 2.2679 | 71.634
6998 | 33.3 | 52.3724 | 35.6299 | 80.3013 | 0.4268 |  | 6998 | 41.16 | 52.3724 | 3 | 80.3013
6999 | 33.07 | 58.0362 | 41.9257 | 67.9876 | 0.42582 |  | 6999 | 37.59 | 58.0362 | 4 | 67.9876
7000 | 35.04 | 75.4303 | 42.7631 | 70.7119 | 0.43203 |  | 7000 | 39.09 | 75.4303 | 5 | 70.7119
7001 | 38.48 | 97.8546 | 43.9162 | 64.4669 | 0.4489 |  | 7001 | 39.91 | 97.8546 | 5.7321 | 64.4669
7002 | 44.08 | 135.976 | 48.4675 | 91.0242 | 0.46048 |  | 7002 | 49.4 | 135.976 | 6 | 91.0242
7003 | 47.9 | 148.3971 | 48.302 | 175.3255 | 0.45786 |  | 7003 | 53.76 | 148.3971 | 5.7321 | 175.3255
7004 | 39.19 | 146.533 | 22.3415 | 296.5468 | 0.45251 |  | 7004 | 59.67 | 146.533 | 5 | 296.5468
7005 | 35.06 | 120.9138 | 28.8539 | 299.6978 | 0.44734 |  | 7005 | 45.74 | 120.9138 | 4 | 299.6978
7006 | 35.05 | 109.2822 | 26.0853 | 292.2154 | 0.44407 |  | 7006 | 40.39 | 109.2822 | 3 | 292.2154
7007 | 33.18 | 77.3991 | 32.3885 | 344.0541 | 0.44957 |  | 7007 | 38.17 | 77.3991 | 2.2679 | 344.0541
7008 | 29.99 | 41.5376 | 30.9539 | 348.3301 | 0.44428 |  | 7008 | 31.56 | 41.5376 | 2 | 348.3301
7009 | 26.01 | 34.471 | 29.4739 | 296.882 | 0.44616 |  | 7009 | 30.15 | 34.471 | 2.2679 | 296.882
7010 | 27.01 | 32.9704 | 24.9906 | 359.5927 | 0.4485 |  | 7010 | 29.5 | 32.9704 | 3 | 359.5927
7011 | 26.9 | 31.3472 | 24.1783 | 303.3163 | 0.45354 |  | 7011 | 29.82 | 31.3472 | 4 | 303.3163
7012 | 26.51 | 29.7935 | 32.9888 | 392.5946 | 0.46063 |  | 7012 | 30.01 | 29.7935 | 5 | 392.5946
7013 | 26.3 | 28.7041 | 59.8491 | 383.5412 | 0.46406 |  | 7013 | 30.32 | 28.7041 | 5.7321 | 383.5412
7014 | 27.03 | 28.3643 | 78.448 | 442.6083 | 0.46699 |  | 7014 | 30.85 | 28.3643 | 6 | 442.6083
7015 | 29.94 | 42.9433 | 59.1858 | 533.8904 | 0.46712 |  | 7015 | 31.72 | 42.9433 | 5.7321 | 533.8904
7016 | 31.74 | 66.516 | 36.5546 | 394.966 | 0.46855 |  | 7016 | 48.52 | 66.516 | 5 | 394.966
7017 | 36.37 | 48.6953 | 42.2579 | 349.573 | 0.47162 |  | 7017 | 50.25 | 48.6953 | 4 | 349.573
7018 | 37.47 | 43.5312 | 37.6022 | 249.2851 | 0.48062 |  | 7018 | 57.65 | 43.5312 | 3 | 249.2851
7019 | 38.32 | 45.7551 | 37.8842 | 139.9194 | 0.48443 |  | 7019 | 57.86 | 45.7551 | 2.2679 | 139.9194
7020 | 37.9 | 49.2533 | 44.2301 | 65.4324 | 0.48441 |  | 7020 | 53.48 | 49.2533 | 2 | 65.4324
7021 | 35.02 | 51.1833 | 37.3519 | 65.919 | 0.4828 |  | 7021 | 50.86 | 51.1833 | 2.2679 | 65.919
7022 | 31.04 | 50.5853 | 42.28 | 65.2019 | 0.48066 |  | 7022 | 48.55 | 50.5853 | 3 | 65.2019
7023 | 32.8 | 60.6072 | 40.7745 | 60.7741 | 0.4809 |  | 7023 | 45.31 | 60.6072 | 4 | 60.7741
7024 | 35.73 | 73.7643 | 38.834 | 74.378 | 0.48401 |  | 7024 | 44.77 | 73.7643 | 5 | 74.378
7025 | 40.38 | 92.3792 | 36.2922 | 84.7171 | 0.49236 |  | 7025 | 43.11 | 92.3792 | 5.7321 | 84.7171
7026 | 47.58 | 145.1559 | 32.8364 | 112.138 | 0.49306 |  | 7026 | 52.54 | 145.1559 | 6 | 112.138
7027 | 51.06 | 155.9058 | 50.3601 | 87.5385 | 0.4936 |  | 7027 | 54.57 | 155.9058 | 5.7321 | 87.5385
7028 | 47.1 | 139.3207 | 31.0844 | 155.9697 | 0.4938 |  | 7028 | 60.37 | 139.3207 | 5 | 155.9697
7029 | 39.62 | 116.2252 | 31.0859 | 226.3162 | 0.49286 |  | 7029 | 54.43 | 116.2252 | 4 | 226.3162
7030 | 38.09 | 105.3056 | 28.0035 | 256.0631 | 0.48692 |  | 7030 | 41.5 | 105.3056 | 3 | 256.0631
7031 | 36 | 75.8931 | 24.2706 | 302.4239 | 0.47532 |  | 7031 | 42.28 | 75.8931 | 2.2679 | 302.4239
7032 | 30.34 | 39.8439 | 24.0249 | 347.741 | 0.46576 |  | 7032 | 33.73 | 39.8439 | 2 | 347.741
7033 | 27.11 | 36.2147 | 24.115 | 303.4298 | 0.46271 |  | 7033 | 31.77 | 36.2147 | 2.2679 | 303.4298
7034 | 26.28 | 34.2948 | 26.6407 | 269.111 | 0.45566 |  | 7034 | 32.56 | 34.2948 | 3 | 269.111
7035 | 25.79 | 32.285 | 26.0407 | 242.1588 | 0.4525 |  | 7035 | 29.97 | 32.285 | 4 | 242.1588
7036 | 25.7 | 30.6227 | 32.6589 | 297.1685 | 0.45015 |  | 7036 | 30.03 | 30.6227 | 5 | 297.1685
7037 | 26.39 | 29.3116 | 27.2326 | 390.4114 | 0.45254 |  | 7037 | 30.56 | 29.3116 | 5.7321 | 390.4114
7038 | 38.01 | 28.5332 | 26.1635 | 435.3043 | 0.46014 |  | 7038 | 31.31 | 28.5332 | 6 | 435.3043
7039 | 51.93 | 28.156 | 29.5122 | 463.9782 | 0.4632 |  | 7039 | 34.13 | 28.156 | 5.7321 | 463.9782
7040 | 52.43 | 31.2351 | 47.5376 | 382.3276 | 0.46446 |  | 7040 | 43.59 | 31.2351 | 5 | 382.3276
7041 | 51.84 | 52.6217 | 37.5792 | 369.2028 | 0.46983 |  | 7041 | 47.05 | 52.6217 | 4 | 369.2028
7042 | 49.6 | 68.2196 | 41.5015 | 306.9094 | 0.47393 |  | 7042 | 66.35 | 68.2196 | 3 | 306.9094
7043 | 49.43 | 72.108 | 44.5524 | 304.5203 | 0.4795 |  | 7043 | 60.98 | 72.108 | 2.2679 | 304.5203
7044 | 44.75 | 73.8486 | 44.2604 | 262.5885 | 0.48104 |  | 7044 | 49.32 | 73.8486 | 2 | 262.5885
7045 | 43.73 | 80.4453 | 43.2611 | 231.4687 | 0.48289 |  | 7045 | 46.34 | 80.4453 | 2.2679 | 231.4687
7046 | 45.16 | 73.3694 | 49.197 | 216.4955 | 0.48225 |  | 7046 | 50.03 | 73.3694 | 3 | 216.4955
7047 | 47.71 | 73.2595 | 37.2394 | 200.67 | 0.48928 |  | 7047 | 48.7 | 73.2595 | 4 | 200.67
7048 | 50.03 | 79.2138 | 38.9525 | 217.426 | 0.49144 |  | 7048 | 48.7 | 79.2138 | 5 | 217.426
7049 | 54.11 | 80.3383 | 35.2611 | 239.8576 | 0.49447 |  | 7049 | 53.64 | 80.3383 | 5.7321 | 239.8576
7050 | 58.02 | 112.8795 | 31.2298 | 283.0794 | 0.49353 |  | 7050 | 55.07 | 112.8795 | 6 | 283.0794
7051 | 66.51 | 156.0453 | 41.8899 | 253.1503 | 0.49184 |  | 7051 | 51.62 | 156.0453 | 5.7321 | 253.1503
7052 | 52.2 | 161.7109 | 223.2946 | 298.3863 | 0.48861 |  | 7052 | 59.35 | 161.7109 | 5 | 298.3863
7053 | 48.9 | 118.8856 | 26.9843 | 288.4612 | 0.48551 |  | 7053 | 50.04 | 118.8856 | 4 | 288.4612
7054 | 40.92 | 108.2952 | 22.5587 | 228.4062 | 0.47982 |  | 7054 | 36.78 | 108.2952 | 3 | 228.4062
7055 | 35.68 | 92.7907 | 30.7523 | 242.1954 | 0.46956 |  | 7055 | 41.81 | 92.7907 | 2.2679 | 242.1954
7056 | 38.82 | 43.4903 | 36.2401 | 176.0187 | 0.46902 |  | 7056 | 33.96 | 43.4903 | 2 | 176.0187
7057 | 35.88 | 33.1716 | 34.5315 | 203.3204 | 0.46924 |  | 7057 | 34.04 | 33.1716 | 2.2679 | 203.3204
7058 | 34.64 | 31.6852 | 41.1613 | 186.0112 | 0.46729 |  | 7058 | 32.94 | 31.6852 | 3 | 186.0112
7059 | 31.84 | 30.2402 | 77.0778 | 196.9455 | 0.46669 |  | 7059 | 31.8 | 30.2402 | 4 | 196.9455
7060 | 33.55 | 28.9747 | 115.3156 | 214.735 | 0.46686 |  | 7060 | 31.78 | 28.9747 | 5 | 214.735
7061 | 36.2 | 28.3443 | 120.2782 | 264.4335 | 0.47743 |  | 7061 | 33.4 | 28.3443 | 5.7321 | 264.4335
7062 | 46.99 | 27.8799 | 117.6863 | 313.7824 | 0.49135 |  | 7062 | 34.12 | 27.8799 | 6 | 313.7824
7063 | 56.43 | 27.5719 | 90.3953 | 290.0332 | 0.49729 |  | 7063 | 36.51 | 27.5719 | 5.7321 | 290.0332
7064 | 61.3 | 30.2106 | 100.0508 | 318.1457 | 0.49756 |  | 7064 | 37.69 | 30.2106 | 5 | 318.1457
7065 | 60 | 51.9781 | 275.8789 | 219.5397 | 0.49952 |  | 7065 | 48.98 | 51.9781 | 4 | 219.5397
7066 | 55.49 | 67.3568 | 79.562 | 183.8798 | 0.50216 |  | 7066 | 59.99 | 67.3568 | 3 | 183.8798
7067 | 52.72 | 74.124 | 80.0349 | 106.7331 | 0.50432 |  | 7067 | 50 | 74.124 | 2.2679 | 106.7331
7068 | 44.82 | 75.7555 | 56.3781 | 67.8031 | 0.50719 |  | 7068 | 53.71 | 75.7555 | 2 | 67.8031
7069 | 40 | 79.6858 | 53.7609 | 78.5418 | 0.50779 |  | 7069 | 45 | 79.6858 | 2.2679 | 78.5418
7070 | 42 | 81.2083 | 40.3442 | 65.6137 | 0.5072 |  | 7070 | 51.3 | 81.2083 | 3 | 65.6137
7071 | 42.88 | 75.0233 | 39.426 | 62.0966 | 0.50648 |  | 7071 | 50.03 | 75.0233 | 4 | 62.0966
7072 | 46.24 | 69.942 | 44.965 | 59.4651 | 0.50732 |  | 7072 | 47.99 | 69.942 | 5 | 59.4651
7073 | 51.93 | 74.6193 | 66.983 | 113.3207 | 0.50834 |  | 7073 | 48.92 | 74.6193 | 5.7321 | 113.3207
7074 | 60 | 103.5752 | 96.2913 | 202.7095 | 0.50885 |  | 7074 | 45 | 103.5752 | 6 | 202.7095
7075 | 65.47 | 129.4732 | 83.3952 | 218.1642 | 0.50324 |  | 7075 | 49.8 | 129.4732 | 5.7321 | 218.1642
7076 | 51.97 | 165.1287 | 106.9137 | 211.7917 | 0.50396 |  | 7076 | 34.83 | 165.1287 | 5 | 211.7917
7077 | 45.15 | 120.1623 | 104.7247 | 252.014 | 0.50512 |  | 7077 | 34.46 | 120.1623 | 4 | 252.014
7078 | 39.5 | 104.761 | 92.9951 | 199.1674 | 0.50453 |  | 7078 | 38 | 104.761 | 3 | 199.1674
7079 | 36.48 | 88.5522 | 110.4703 | 192.0809 | 0.49552 |  | 7079 | 38.41 | 88.5522 | 2.2679 | 192.0809
7080 | 35.52 | 39.5577 | 109.7133 | 152.6443 | 0.48128 |  | 7080 | 35.97 | 39.5577 | 2 | 152.6443
7081 | 32.31 | 33.7243 | 100.5691 | 182.2388 | 0.47529 |  | 7081 | 34.31 | 33.7243 | 2.2679 | 182.2388
7082 | 31.36 | 32.0905 | 58.4109 | 123.3376 | 0.47725 |  | 7082 | 34.55 | 32.0905 | 3 | 123.3376
7083 | 30.09 | 30.5871 | 24.2775 | 159.3088 | 0.4739 |  | 7083 | 34 | 30.5871 | 4 | 159.3088
7084 | 30.39 | 29.276 | 29.237 | 200.0675 | 0.48078 |  | 7084 | 34.35 | 29.276 | 5 | 200.0675
7085 | 34.4 | 28.4451 | 42.0361 | 249.1461 | 0.49029 |  | 7085 | 35.36 | 28.4451 | 5.7321 | 249.1461
7086 | 40.7 | 28.2502 | 107.4987 | 290.7839 | 0.5054 |  | 7086 | 35.61 | 28.2502 | 6 | 290.7839
7087 | 52.4 | 43.9192 | 125.1582 | 302.9787 | 0.51839 |  | 7087 | 34.55 | 43.9192 | 5.7321 | 302.9787
7088 | 59.77 | 66.8302 | 126.2127 | 313.8925 | 0.51832 |  | 7088 | 38.06 | 66.8302 | 5 | 313.8925
7089 | 57.12 | 48.339 | 128.41 | 317.723 | 0.51602 |  | 7089 | 37.68 | 48.339 | 4 | 317.723
7090 | 54.11 | 41.2569 | 113.0826 | 247.6018 | 0.51664 |  | 7090 | 39.72 | 41.2569 | 3 | 247.6018
7091 | 51.23 | 43.2339 | 113.9671 | 307.8981 | 0.51915 |  | 7091 | 39.59 | 43.2339 | 2.2679 | 307.8981
7092 | 42.01 | 46.7266 | 93.8515 | 286.6966 | 0.5212 |  | 7092 | 39.22 | 46.7266 | 2 | 286.6966
7093 | 39.46 | 49.8526 | 63.9301 | 191.7926 | 0.52166 |  | 7093 | 41.33 | 49.8526 | 2.2679 | 191.7926
7094 | 38.87 | 52.4894 | 52.4764 | 227.5249 | 0.52019 |  | 7094 | 36.65 | 52.4894 | 3 | 227.5249
7095 | 41.8 | 57.9206 | 33.3966 | 260.6425 | 0.51814 |  | 7095 | 35.41 | 57.9206 | 4 | 260.6425
7096 | 45.87 | 74.8939 | 52.1502 | 210.175 | 0.51664 |  | 7096 | 35.28 | 74.8939 | 5 | 210.175
7097 | 50.67 | 97.7848 | 72.5284 | 225.5399 | 0.51649 |  | 7097 | 36.21 | 97.7848 | 5.7321 | 225.5399
7098 | 53.49 | 132.7569 | 110.0269 | 305.5739 | 0.51268 |  | 7098 | 47.19 | 132.7569 | 6 | 305.5739
7099 | 55.1 | 156.7784 | 112.8699 | 267.2114 | 0.50966 |  | 7099 | 51.48 | 156.7784 | 5.7321 | 267.2114
7100 | 40.45 | 146.2396 | 106.5424 | 349.9522 | 0.50873 |  | 7100 | 52.27 | 146.2396 | 5 | 349.9522
7101 | 38.17 | 117.1288 | 101.1638 | 290.0887 | 0.50607 |  | 7101 | 46.74 | 117.1288 | 4 | 290.0887
7102 | 37.38 | 104.9169 | 90.0524 | 287.6237 | 0.50624 |  | 7102 | 37.47 | 104.9169 | 3 | 287.6237
7103 | 33.75 | 74.8151 | 91.3523 | 286.5907 | 0.49733 |  | 7103 | 35.86 | 74.8151 | 2.2679 | 286.5907
7104 | 33.55 | 38.6305 | 117.7389 | 242.1928 | 0.48874 |  | 7104 | 36.29 | 38.6305 | 2 | 242.1928
7105 | 31.04 | 35.561 | 111.8269 | 287.785 | 0.49137 |  | 7105 | 35.64 | 35.561 | 2.2679 | 287.785
7106 | 30.02 | 33.8535 | 59.5244 | 228.2996 | 0.49126 |  | 7106 | 35.02 | 33.8535 | 3 | 228.2996
7107 | 29.41 | 32.1431 | 23.2677 | 285.4947 | 0.48737 |  | 7107 | 34.56 | 32.1431 | 4 | 285.4947
7108 | 30.06 | 30.5222 | 27.7044 | 307.6736 | 0.49614 |  | 7108 | 32.41 | 30.5222 | 5 | 307.6736
7109 | 32.89 | 29.1946 | 46.1264 | 365.6287 | 0.50031 |  | 7109 | 32.03 | 29.1946 | 5.7321 | 365.6287
7110 | 39.55 | 28.8393 | 71.1711 | 443.8183 | 0.52136 |  | 7110 | 31.94 | 28.8393 | 6 | 443.8183
7111 | 48.98 | 42.6858 | 97.5824 | 370.8763 | 0.52242 |  | 7111 | 32.63 | 42.6858 | 5.7321 | 370.8763
7112 | 54.11 | 64.2784 | 101.8322 | 361.5059 | 0.51767 |  | 7112 | 33.48 | 64.2784 | 5 | 361.5059
7113 | 54.11 | 49.0327 | 313.8741 | 308.6796 | 0.51681 |  | 7113 | 34.27 | 49.0327 | 4 | 308.6796
7114 | 51.08 | 42.8744 | 99.4261 | 166.547 | 0.51687 |  | 7114 | 35.85 | 42.8744 | 3 | 166.547
7115 | 46.93 | 45.8396 | 103.5716 | 109.259 | 0.51468 |  | 7115 | 35.21 | 45.8396 | 2.2679 | 109.259
7116 | 43.66 | 48.5653 | 101.9813 | 132.61 | 0.50247 |  | 7116 | 34.66 | 48.5653 | 2 | 132.61
7117 | 40.39 | 48.2607 | 76.7545 | 127.5348 | 0.49611 |  | 7117 | 33.31 | 48.2607 | 2.2679 | 127.5348
7118 | 37.97 | 51.8469 | 76.1049 | 71.7221 | 0.4832 |  | 7118 | 35.08 | 51.8469 | 3 | 71.7221
7119 | 36.78 | 56.8706 | 52.166 | 66.064 | 0.47338 |  | 7119 | 34.94 | 56.8706 | 4 | 66.064
7120 | 37.81 | 75.3169 | 43.1708 | 81.7686 | 0.471 |  | 7120 | 32.66 | 75.3169 | 5 | 81.7686
7121 | 39.9 | 94.8705 | 75.1744 | 156.3335 | 0.47167 |  | 7121 | 34.44 | 94.8705 | 5.7321 | 156.3335
7122 | 43.41 | 139.6966 | 114.7315 | 231.7903 | 0.46605 |  | 7122 | 37.24 | 139.6966 | 6 | 231.7903
7123 | 38.13 | 164.5585 | 83.9702 | 294.7777 | 0.46106 |  | 7123 | 42.01 | 164.5585 | 5.7321 | 294.7777
7124 | 35.67 | 135.1974 | 100.0058 | 333.7759 | 0.45272 |  | 7124 | 52.44 | 135.1974 | 5 | 333.7759
7125 | 30.07 | 116.5756 | 103.6693 | 357.149 | 0.44012 |  | 7125 | 43 | 116.5756 | 4 | 357.149
7126 | 30.21 | 109.4478 | 105.0101 | 326.6109 | 0.42845 |  | 7126 | 36.86 | 109.4478 | 3 | 326.6109
7127 | 26.03 | 78.9133 | 105.4692 | 273.8588 | 0.42463 |  | 7127 | 34.75 | 78.9133 | 2.2679 | 273.8588
7128 | 27 | 40.8232 | 116.8436 | 256.6623 | 0.41518 |  | 7128 | 34.71 | 40.8232 | 2 | 256.6623
7129 | 25.27 | 34.5614 | 106.9096 | 242.0252 | 0.41099 |  | 7129 | 32.63 | 34.5614 | 2.2679 | 242.0252
7130 | 25.2 | 33.0197 | 63.1901 | 213.1339 | 0.41151 |  | 7130 | 32.29 | 33.0197 | 3 | 213.1339
7131 | 24.42 | 31.3596 | 33.81 | 255.2969 | 0.41103 |  | 7131 | 32.25 | 31.3596 | 4 | 255.2969
7132 | 25.2 | 29.9024 | 35.8182 | 300.9452 | 0.41275 |  | 7132 | 31.62 | 29.9024 | 5 | 300.9452
7133 | 28.22 | 28.9003 | 40.564 | 355.6247 | 0.41819 |  | 7133 | 31.44 | 28.9003 | 5.7321 | 355.6247
7134 | 36.06 | 28.4372 | 107.2209 | 344.8996 | 0.42916 |  | 7134 | 31.68 | 28.4372 | 6 | 344.8996
7135 | 47.9 | 42.8963 | 281.4391 | 413.4987 | 0.43684 |  | 7135 | 40.76 | 42.8963 | 5.7321 | 413.4987
7136 | 51.52 | 67.8381 | 79.9946 | 374.5112 | 0.44104 |  | 7136 | 40.01 | 67.8381 | 5 | 374.5112
7137 | 46.68 | 48.216 | 117.2658 | 392.7463 | 0.43956 |  | 7137 | 50 | 48.216 | 4 | 392.7463
7138 | 44.49 | 40.56 | 88.4963 | 269.6046 | 0.43546 |  | 7138 | 59.22 | 40.56 | 3 | 269.6046
7139 | 39.76 | 43.7343 | 95.4759 | 261.5655 | 0.42932 |  | 7139 | 40.36 | 43.7343 | 2.2679 | 261.5655
7140 | 35.65 | 43.7251 | 45.9221 | 169.3041 | 0.42375 |  | 7140 | 43.7 | 43.7251 | 2 | 169.3041
7141 | 36.07 | 45.9622 | 53.1132 | 157.6517 | 0.42629 |  | 7141 | 37.07 | 45.9622 | 2.2679 | 157.6517
7142 | 34.78 | 47.2573 | 51.7072 | 160.4794 | 0.42701 |  | 7142 | 46.7 | 47.2573 | 3 | 160.4794
7143 | 35.33 | 56.9331 | 45.0031 | 197.8636 | 0.42825 |  | 7143 | 45.49 | 56.9331 | 4 | 197.8636
7144 | 36.92 | 73.138 | 42.9198 | 202.4554 | 0.4325 |  | 7144 | 51.83 | 73.138 | 5 | 202.4554
7145 | 43.83 | 98.0436 | 57.1109 | 280.167 | 0.43603 |  | 7145 | 57.68 | 98.0436 | 5.7321 | 280.167
7146 | 48.11 | 131.7756 | 126.3343 | 304.4797 | 0.43396 |  | 7146 | 53.43 | 131.7756 | 6 | 304.4797
7147 | 46.69 | 167.7352 | 116.3737 | 342.5564 | 0.42898 |  | 7147 | 37 | 167.7352 | 5.7321 | 342.5564
7148 | 36.05 | 138.5655 | 96.0694 | 309.0537 | 0.41607 |  | 7148 | 36.6 | 138.5655 | 5 | 309.0537
7149 | 33.21 | 116.9389 | 104.0003 | 303.4269 | 0.40578 |  | 7149 | 36.41 | 116.9389 | 4 | 303.4269
7150 | 30.35 | 108.37 | 95.6537 | 225.4263 | 0.40064 |  | 7150 | 42 | 108.37 | 3 | 225.4263
7151 | 25.51 | 77.4549 | 114.0766 | 273.0083 | 0.3918 |  | 7151 | 37.44 | 77.4549 | 2.2679 | 273.0083
7152 | 25.8 | 39.9536 | 96.9344 | 248.0699 | 0.37958 |  | 7152 | 37.1 | 39.9536 | 2 | 248.0699
7153 | 26 | 32.5845 | 99.0131 | 213.6842 | 0.36531 |  | 7153 | 30.31 | 32.5845 | 2.2679 | 213.6842
7154 | 23.9 | 31.1626 | 116.5272 | 218.9255 | 0.35953 |  | 7154 | 31.6 | 31.1626 | 3 | 218.9255
7155 | 20 | 29.8751 | 110.9908 | 222.4881 | 0.36085 |  | 7155 | 32.49 | 29.8751 | 4 | 222.4881
7156 | 17 | 28.6671 | 54.0644 | 216.9383 | 0.35816 |  | 7156 | 32.57 | 28.6671 | 5 | 216.9383
7157 | 23.9 | 27.9213 | 47.3788 | 251.39 | 0.36405 |  | 7157 | 35.26 | 27.9213 | 5.7321 | 251.39
7158 | 25.2 | 27.8239 | 99.3221 | 371.7395 | 0.36922 |  | 7158 | 36.65 | 27.8239 | 6 | 371.7395
7159 | 26.8 | 43.3718 | 77.4945 | 392.3348 | 0.37609 |  | 7159 | 42.27 | 43.3718 | 5.7321 | 392.3348
7160 | 31.5 | 61.635 | 95.1363 | 297.8543 | 0.38406 |  | 7160 | 37 | 61.635 | 5 | 297.8543
7161 | 36.13 | 43.9139 | 100.2717 | 296.5381 | 0.3863 |  | 7161 | 36.82 | 43.9139 | 4 | 296.5381
7162 | 29.32 | 42.609 | 87.9393 | 261.7958 | 0.383 |  | 7162 | 44.94 | 42.609 | 3 | 261.7958
7163 | 29 | 46.9282 | 55.0155 | 212.5143 | 0.37843 |  | 7163 | 41.88 | 46.9282 | 2.2679 | 212.5143
7164 | 26.8 | 47.0207 | 38.1132 | 190.3303 | 0.37558 |  | 7164 | 46.28 | 47.0207 | 2 | 190.3303
7165 | 31.8 | 49.412 | 38.0873 | 197.6092 | 0.37679 |  | 7165 | 41.88 | 49.412 | 2.2679 | 197.6092
7166 | 31.8 | 50.3726 | 39.402 | 122.7739 | 0.37814 |  | 7166 | 36.26 | 50.3726 | 3 | 122.7739
7167 | 27 | 57.744 | 35.8612 | 58.9788 | 0.38066 |  | 7167 | 37.08 | 57.744 | 4 | 58.9788
7168 | 30.54 | 72.289 | 45.7346 | 57.7253 | 0.39168 |  | 7168 | 65.55 | 72.289 | 5 | 57.7253
7169 | 36.22 | 92.2047 | 34.6347 | 113.7694 | 0.39753 |  | 7169 | 65.84 | 92.2047 | 5.7321 | 113.7694
7170 | 37.97 | 154.3816 | 49.8154 | 224.5466 | 0.3995 |  | 7170 | 76.69 | 154.3816 | 6 | 224.5466
7171 | 37.37 | 147.4635 | 42.5464 | 266.0425 | 0.39415 |  | 7171 | 59.61 | 147.4635 | 5.7321 | 266.0425
7172 | 35.77 | 132.0963 | 34.5287 | 272.1986 | 0.39137 |  | 7172 | 46.28 | 132.0963 | 5 | 272.1986
7173 | 35.05 | 114.0782 | 29.3466 | 315.1994 | 0.39057 |  | 7173 | 38.97 | 114.0782 | 4 | 315.1994
7174 | 31.82 | 105.8812 | 233.1363 | 281.9055 | 0.38797 |  | 7174 | 48.68 | 105.8812 | 3 | 281.9055
7175 | 26.81 | 75.0694 | 28.9788 | 316.7967 | 0.381 |  | 7175 | 40 | 75.0694 | 2.2679 | 316.7967
7176 | 32.21 | 37.622 | 26.4533 | 251.5233 | 0.38844 |  | 7176 | 37.88 | 37.622 | 2 | 251.5233
7177 | 27.11 | 33.8116 | 32.4034 | 278.3411 | 0.39395 |  | 7177 | 35.81 | 33.8116 | 2.2679 | 278.3411
7178 | 25 | 32.3793 | 26.0941 | 262.3151 | 0.41613 |  | 7178 | 34.6 | 32.3793 | 3 | 262.3151
7179 | 25.7 | 30.8433 | 29.3239 | 253.4529 | 0.39147 |  | 7179 | 34.6 | 30.8433 | 4 | 253.4529
7180 | 22.86 | 29.4943 | 26.43 | 381.247 | 0.38719 |  | 7180 | 34.6 | 29.4943 | 5 | 381.247
7181 | 16.47 | 28.5566 | 28.7398 | 367.8512 | 0.38047 |  | 7181 | 35 | 28.5566 | 5.7321 | 367.8512
7182 | 19.39 | 28.3356 | 22.2975 | 385.5613 | 0.38322 |  | 7182 | 33.66 | 28.3356 | 6 | 385.5613
7183 | 21.04 | 43.2464 | 31.2356 | 472.2253 | 0.39936 |  | 7183 | 36.45 | 43.2464 | 5.7321 | 472.2253
7184 | 26.7 | 62.2071 | 40.6398 | 446.4628 | 0.41584 |  | 7184 | 50.68 | 62.2071 | 5 | 446.4628
7185 | 28.98 | 43.1137 | 48.5771 | 339.2533 | 0.42225 |  | 7185 | 64.5 | 43.1137 | 4 | 339.2533
7186 | 33.7 | 42.0567 | 42.1429 | 321.3541 | 0.4194 |  | 7186 | 66.6 | 42.0567 | 3 | 321.3541
7187 | 36.07 | 43.5937 | 24.6166 | 185.6481 | 0.4189 |  | 7187 | 66.91 | 43.5937 | 2.2679 | 185.6481
7188 | 30 | 45.1173 | 43.3395 | 80.0094 | 0.41638 |  | 7188 | 59.63 | 45.1173 | 2 | 80.0094
7189 | 28.44 | 49.3007 | 37.3828 | 75.8926 | 0.41807 |  | 7189 | 52.75 | 49.3007 | 2.2679 | 75.8926
7190 | 28 | 51.437 | 52.6353 | 61.4271 | 0.41477 |  | 7190 | 50.01 | 51.437 | 3 | 61.4271
7191 | 28 | 58.1369 | 34.5462 | 71.5944 | 0.41542 |  | 7191 | 45.9 | 58.1369 | 4 | 71.5944
7192 | 31.1 | 74.2687 | 33.8554 | 56.4204 | 0.42786 |  | 7192 | 43.62 | 74.2687 | 5 | 56.4204
7193 | 36.3 | 99.1417 | 49.1857 | 73.5681 | 0.43985 |  | 7193 | 50.73 | 99.1417 | 5.7321 | 73.5681
7194 | 44.44 | 146.3587 | 247.8575 | 120.3481 | 0.45455 |  | 7194 | 54.83 | 146.3587 | 6 | 120.3481
7195 | 42.53 | 157.6457 | 33.678 | 196.4381 | 0.4552 |  | 7195 | 41.26 | 157.6457 | 5.7321 | 196.4381
7196 | 41.32 | 134.7552 | 25.3151 | 258.2017 | 0.45356 |  | 7196 | 37.11 | 134.7552 | 5 | 258.2017
7197 | 36.06 | 112.1064 | 23.8891 | 266.5042 | 0.44695 |  | 7197 | 40.01 | 112.1064 | 4 | 266.5042
7198 | 34.06 | 106.6295 | 29.1804 | 245.9254 | 0.43701 |  | 7198 | 42.44 | 106.6295 | 3 | 245.9254
7199 | 29.85 | 78.1634 | 28.3537 | 274.4137 | 0.43768 |  | 7199 | 35.58 | 78.1634 | 2.2679 | 274.4137
7200 | 25.82 | 39.3427 | 18.9772 | 259.9114 | 0.43406 |  | 7200 | 34.1 | 39.3427 | 2 | 259.9114
7201 | 26.4 | 35.2304 | 25.7376 | 216.9241 | 0.439 |  | 7201 | 32.84 | 35.2304 | 2.2679 | 216.9241
7202 | 26.6 | 33.4417 | 26.595 | 216.6478 | 0.44086 |  | 7202 | 32.98 | 33.4417 | 3 | 216.6478
7203 | 26.9 | 31.7406 | 37.069 | 268.6458 | 0.4434 |  | 7203 | 32.83 | 31.7406 | 4 | 268.6458
7204 | 27.64 | 30.1562 | 28.1545 | 293.4421 | 0.45 |  | 7204 | 32.05 | 30.1562 | 5 | 293.4421
7205 | 27.93 | 29.0745 | 34.6607 | 318.3295 | 0.4638 |  | 7205 | 33.08 | 29.0745 | 5.7321 | 318.3295
7206 | 30.97 | 28.3715 | 78.9795 | 365.4785 | 0.47501 |  | 7206 | 33.95 | 28.3715 | 6 | 365.4785
7207 | 39.27 | 28.0174 | 124.9615 | 320.1145 | 0.48635 |  | 7207 | 39.08 | 28.0174 | 5.7321 | 320.1145
7208 | 48.47 | 30.5725 | 126.881 | 364.6821 | 0.49573 |  | 7208 | 50.39 | 30.5725 | 5 | 364.6821
7209 | 45.93 | 49.7114 | 134.353 | 291.6938 | 0.49839 |  | 7209 | 56.62 | 49.7114 | 4 | 291.6938
7210 | 44.01 | 68.4383 | 94.5451 | 290.4429 | 0.50167 |  | 7210 | 54.74 | 68.4383 | 3 | 290.4429
7211 | 43.06 | 74.612 | 53.5131 | 300.7991 | 0.50853 |  | 7211 | 53.95 | 74.612 | 2.2679 | 300.7991
7212 | 42.33 | 74.6055 | 38.9138 | 256.0768 | 0.50252 |  | 7212 | 52 | 74.6055 | 2 | 256.0768
7213 | 40.58 | 77.7456 | 66.1475 | 225.0448 | 0.50852 |  | 7213 | 45.58 | 77.7456 | 2.2679 | 225.0448
7214 | 42.27 | 75.1578 | 128.2643 | 248.5944 | 0.51203 |  | 7214 | 43.24 | 75.1578 | 3 | 248.5944
7215 | 48.83 | 71.5647 | 41.3978 | 239.3153 | 0.51777 |  | 7215 | 40.67 | 71.5647 | 4 | 239.3153
7216 | 50.55 | 75.3625 | 71.427 | 259.2861 | 0.51898 |  | 7216 | 39.91 | 75.3625 | 5 | 259.2861
7217 | 54.99 | 80.1111 | 123.5952 | 222.8176 | 0.52021 |  | 7217 | 42.28 | 80.1111 | 5.7321 | 222.8176
7218 | 61.23 | 135.5416 | 106.2819 | 311.684 | 0.51665 |  | 7218 | 45 | 135.5416 | 6 | 311.684
7219 | 63.62 | 156.1511 | 33.5464 | 250.1745 | 0.51505 |  | 7219 | 50.01 | 156.1511 | 5.7321 | 250.1745
7220 | 57.39 | 154.1095 | 28.3862 | 265.3418 | 0.51491 |  | 7220 | 42.28 | 154.1095 | 5 | 265.3418
7221 | 48.69 | 117.993 | 29.5488 | 258.5352 | 0.52133 |  | 7221 | 38.35 | 117.993 | 4 | 258.5352
7222 | 41.52 | 105.3477 | 39.9719 | 275.1358 | 0.524 |  | 7222 | 38.45 | 105.3477 | 3 | 275.1358
7223 | 39.66 | 91.3782 | 30.5866 | 244.3129 | 0.52854 |  | 7223 | 37.76 | 91.3782 | 2.2679 | 244.3129
7224 | 35.85 | 42.135 | 219.792 | 236.7017 | 0.52433 |  | 7224 | 32.07 | 42.135 | 2 | 236.7017
7225 | 36.92 | 34.484 | 29.838 | 246.6854 | 0.52225 |  | 7225 | 30.51 | 34.484 | 2.2679 | 246.6854
7226 | 36.5 | 32.8307 | 27.1719 | 172.164 | 0.51853 |  | 7226 | 26.93 | 32.8307 | 3 | 172.164
7227 | 35.83 | 31.1752 | 21.755 | 217.3968 | 0.50997 |  | 7227 | 26.45 | 31.1752 | 4 | 217.3968
7228 | 35.2 | 29.7215 | 29.5593 | 243.7203 | 0.50732 |  | 7228 | 26.65 | 29.7215 | 5 | 243.7203
7229 | 35.17 | 28.7005 | 31.4505 | 247.6905 | 0.51313 |  | 7229 | 26.31 | 28.7005 | 5.7321 | 247.6905
7230 | 36 | 28.0921 | 32.4684 | 291.0773 | 0.51946 |  | 7230 | 30.22 | 28.0921 | 6 | 291.0773
7231 | 43.26 | 27.8664 | 18.938 | 316.9741 | 0.52081 |  | 7231 | 32.76 | 27.8664 | 5.7321 | 316.9741
7232 | 53.5 | 30.012 | 41.863 | 264.1934 | 0.52085 |  | 7232 | 44.94 | 30.012 | 5 | 264.1934
7233 | 55.81 | 48.3186 | 49.5587 | 259.2453 | 0.51598 |  | 7233 | 43.52 | 48.3186 | 4 | 259.2453
7234 | 55.01 | 64.6094 | 69.0118 | 254.6367 | 0.51419 |  | 7234 | 41.4 | 64.6094 | 3 | 254.6367
7235 | 50.37 | 72.7124 | 56.4516 | 242.868 | 0.51037 |  | 7235 | 46.52 | 72.7124 | 2.2679 | 242.868
7236 | 50.27 | 74.3085 | 311.1843 | 220.2366 | 0.50926 |  | 7236 | 47.1 | 74.3085 | 2 | 220.2366
7237 | 45.1 | 79.3881 | 91.4743 | 207.4715 | 0.51107 |  | 7237 | 43.07 | 79.3881 | 2.2679 | 207.4715
7238 | 46.64 | 75.865 | 60.0321 | 225.3302 | 0.51292 |  | 7238 | 42.69 | 75.865 | 3 | 225.3302
7239 | 52.3 | 72.2927 | 50.1345 | 231.3343 | 0.51481 |  | 7239 | 41.34 | 72.2927 | 4 | 231.3343
7240 | 55.01 | 69.682 | 29.1904 | 217.872 | 0.51594 |  | 7240 | 41.66 | 69.682 | 5 | 217.872
7241 | 57.2 | 76.7201 | 41.4236 | 248.3848 | 0.51766 |  | 7241 | 42.25 | 76.7201 | 5.7321 | 248.3848
7242 | 62.44 | 122.9515 | 35.9983 | 271.9991 | 0.50996 |  | 7242 | 50 | 122.9515 | 6 | 271.9991
7243 | 66.18 | 143.7964 | 38.3253 | 303.3902 | 0.49964 |  | 7243 | 58.35 | 143.7964 | 5.7321 | 303.3902
7244 | 60.75 | 149.3692 | 35.4851 | 264.3025 | 0.49692 |  | 7244 | 56.64 | 149.3692 | 5 | 264.3025
7245 | 53.85 | 115.9606 | 34.1003 | 211.4103 | 0.50041 |  | 7245 | 49.99 | 115.9606 | 4 | 211.4103
7246 | 45.76 | 102.41 | 21.3491 | 199.2071 | 0.50249 |  | 7246 | 45.92 | 102.41 | 3 | 199.2071
7247 | 40.12 | 88.9763 | 26.8991 | 238.003 | 0.50232 |  | 7247 | 36.03 | 88.9763 | 2.2679 | 238.003
7248 | 37.34 | 41.5995 | 20.7257 | 199.6622 | 0.50347 |  | 7248 | 33.01 | 41.5995 | 2 | 199.6622
7249 | 37.45 | 33.3664 | 35.9204 | 179.0124 | 0.49636 |  | 7249 | 31.05 | 33.3664 | 2.2679 | 179.0124
7250 | 36.39 | 31.9 | 19.5208 | 145.4995 | 0.49059 |  | 7250 | 29.85 | 31.9 | 3 | 145.4995
7251 | 36.14 | 30.5295 | 18.6993 | 178.3563 | 0.49123 |  | 7251 | 29.04 | 30.5295 | 4 | 178.3563
7252 | 35.58 | 29.229 | 28.5435 | 216.8108 | 0.48899 |  | 7252 | 28.65 | 29.229 | 5 | 216.8108
7253 | 36.15 | 28.3683 | 229.0389 | 229.1155 | 0.49316 |  | 7253 | 28.77 | 28.3683 | 5.7321 | 229.1155
7254 | 37.72 | 28.0913 | 51.7201 | 305.5251 | 0.50302 |  | 7254 | 28.84 | 28.0913 | 6 | 305.5251
7255 | 44.9 | 44.7283 | 119.9693 | 274.6805 | 0.50862 |  | 7255 | 30.77 | 44.7283 | 5.7321 | 274.6805
7256 | 54.12 | 62.8924 | 109.5874 | 297.3003 | 0.51141 |  | 7256 | 32.5 | 62.8924 | 5 | 297.3003
7257 | 57.6 | 44.4725 | 105.1054 | 320.0548 | 0.51011 |  | 7257 | 35.06 | 44.4725 | 4 | 320.0548
7258 | 53.92 | 42.0003 | 133.5301 | 266.9946 | 0.50968 |  | 7258 | 41.76 | 42.0003 | 3 | 266.9946
7259 | 45.5 | 44.3838 | 123.8531 | 240.1553 | 0.51139 |  | 7259 | 55 | 44.3838 | 2.2679 | 240.1553
7260 | 42.48 | 46.014 | 111.7745 | 243.8688 | 0.50967 |  | 7260 | 49.94 | 46.014 | 2 | 243.8688
7261 | 39.21 | 49.9867 | 86.2821 | 202.974 | 0.50726 |  | 7261 | 34.94 | 49.9867 | 2.2679 | 202.974
7262 | 39.2 | 50.6624 | 109.019 | 225.5823 | 0.50488 |  | 7262 | 35 | 50.6624 | 3 | 225.5823
7263 | 41.88 | 59.0847 | 103.2956 | 194.5316 | 0.50736 |  | 7263 | 34.94 | 59.0847 | 4 | 194.5316
7264 | 52.31 | 73.5565 | 75.9642 | 194.9855 | 0.50986 |  | 7264 | 31.41 | 73.5565 | 5 | 194.9855
7265 | 56.17 | 97.6138 | 43.0179 | 255.49 | 0.50816 |  | 7265 | 32.7 | 97.6138 | 5.7321 | 255.49
7266 | 61.57 | 149.9697 | 42.3062 | 277.2738 | 0.49979 |  | 7266 | 39.54 | 149.9697 | 6 | 277.2738
7267 | 66.7 | 163.2467 | 37.3745 | 294.9953 | 0.48965 |  | 7267 | 45.92 | 163.2467 | 5.7321 | 294.9953
7268 | 60 | 141.6548 | 27.3937 | 282.9012 | 0.48489 |  | 7268 | 45.01 | 141.6548 | 5 | 282.9012
7269 | 52.12 | 121.6305 | 30.8161 | 267.0265 | 0.48612 |  | 7269 | 39.44 | 121.6305 | 4 | 267.0265
7270 | 43.42 | 105.2945 | 33.1834 | 253.4429 | 0.48799 |  | 7270 | 35.24 | 105.2945 | 3 | 253.4429
7271 | 39.76 | 74.5412 | 27.3514 | 203.3721 | 0.49208 |  | 7271 | 35.12 | 74.5412 | 2.2679 | 203.3721
7272 | 32.9 | 38.8191 | 31.4089 | 184.7986 | 0.48616 |  | 7272 | 46.17 | 38.8191 | 2 | 184.7986
7273 | 34.25 | 33.1273 | 25.3325 | 183.9999 | 0.48526 |  | 7273 | 45 | 33.1273 | 2.2679 | 183.9999
7274 | 34.23 | 31.8226 | 25.6153 | 176.8734 | 0.47981 |  | 7274 | 42.87 | 31.8226 | 3 | 176.8734
7275 | 33.92 | 30.408 | 24.1831 | 165.5602 | 0.477 |  | 7275 | 33.11 | 30.408 | 4 | 165.5602
7276 | 33.16 | 29.1883 | 25.0701 | 257.933 | 0.47961 |  | 7276 | 32.93 | 29.1883 | 5 | 257.933
7277 | 33.37 | 28.3562 | 31.063 | 255.2667 | 0.48692 |  | 7277 | 31.4 | 28.3562 | 5.7321 | 255.2667
7278 | 35.23 | 28.0832 | 41.6125 | 300.7382 | 0.49818 |  | 7278 | 31.45 | 28.0832 | 6 | 300.7382
7279 | 39.9 | 42.6731 | 107.4451 | 325.9424 | 0.51024 |  | 7279 | 32.03 | 42.6731 | 5.7321 | 325.9424
7280 | 45.19 | 62.9361 | 132.3404 | 289.2619 | 0.51255 |  | 7280 | 32.55 | 62.9361 | 5 | 289.2619
7281 | 44.56 | 43.0624 | 90.1291 | 265.0202 | 0.50951 |  | 7281 | 33.35 | 43.0624 | 4 | 265.0202
7282 | 45.21 | 41.6922 | 48.8946 | 230.8618 | 0.50631 |  | 7282 | 35.02 | 41.6922 | 3 | 230.8618
7283 | 40.52 | 44.746 | 57.7205 | 280.6413 | 0.50371 |  | 7283 | 36.49 | 44.746 | 2.2679 | 280.6413
7284 | 38.82 | 45.3567 | 80.4198 | 273.1448 | 0.50373 |  | 7284 | 36.99 | 45.3567 | 2 | 273.1448
7285 | 37.04 | 48.8011 | 105.9132 | 188.3439 | 0.49961 |  | 7285 | 38.33 | 48.8011 | 2.2679 | 188.3439
7286 | 38.09 | 48.2649 | 125.4248 | 191.4023 | 0.49853 |  | 7286 | 37.2 | 48.2649 | 3 | 191.4023
7287 | 42.71 | 56.1437 | 71.7002 | 191.979 | 0.50197 |  | 7287 | 33.9 | 56.1437 | 4 | 191.979
7288 | 46.7 | 70.2122 | 37.8236 | 225.6832 | 0.50519 |  | 7288 | 32.48 | 70.2122 | 5 | 225.6832
7289 | 51.08 | 91.3036 | 44.1697 | 194.7566 | 0.50727 |  | 7289 | 33.09 | 91.3036 | 5.7321 | 194.7566
7290 | 56.01 | 146.7356 | 44.1381 | 245.9552 | 0.50087 |  | 7290 | 34.64 | 146.7356 | 6 | 245.9552
7291 | 55.44 | 159.8162 | 49.9644 | 263.2994 | 0.49047 |  | 7291 | 49.2 | 159.8162 | 5.7321 | 263.2994
7292 | 46.97 | 151.1564 | 27.544 | 275.3378 | 0.48292 |  | 7292 | 57.56 | 151.1564 | 5 | 275.3378
7293 | 44.9 | 111.3832 | 25.7924 | 244.1646 | 0.47763 |  | 7293 | 56.65 | 111.3832 | 4 | 244.1646
7294 | 42.08 | 104.3424 | 32.8468 | 255.5471 | 0.47271 |  | 7294 | 40.3 | 104.3424 | 3 | 255.5471
7295 | 38.93 | 75.1974 | 28.7697 | 189.2745 | 0.46918 |  | 7295 | 39 | 75.1974 | 2.2679 | 189.2745
7296 | 36.04 | 38.6713 | 235.2303 | 178.4816 | 0.46191 |  | 7296 | 39 | 38.6713 | 2 | 178.4816
7297 | 35.94 | 35.0326 | 29.9476 | 174.0391 | 0.46267 |  | 7297 | 37.87 | 35.0326 | 2.2679 | 174.0391
7298 | 33.49 | 33.1443 | 29.5769 | 173.3681 | 0.46401 |  | 7298 | 35.36 | 33.1443 | 3 | 173.3681
7299 | 28.99 | 31.3896 | 36.1266 | 192.1814 | 0.46195 |  | 7299 | 34.94 | 31.3896 | 4 | 192.1814
7300 | 27.12 | 29.9012 | 230.7362 | 195.8382 | 0.46344 |  | 7300 | 34.66 | 29.9012 | 5 | 195.8382
7301 | 26.17 | 28.8777 | 26.5849 | 271.993 | 0.4616 |  | 7301 | 33.92 | 28.8777 | 5.7321 | 271.993
7302 | 26.14 | 28.7126 | 37.2112 | 267.8314 | 0.46032 |  | 7302 | 34.39 | 28.7126 | 6 | 267.8314
7303 | 29.1 | 43.6341 | 70.2345 | 285.7231 | 0.45758 |  | 7303 | 38.4 | 43.6341 | 5.7321 | 285.7231
7304 | 34.92 | 65.2923 | 118.9942 | 292.7017 | 0.45653 |  | 7304 | 39.94 | 65.2923 | 5 | 292.7017
7305 | 34.27 | 44.0947 | 100.6356 | 308.2146 | 0.459 |  | 7305 | 51.68 | 44.0947 | 4 | 308.2146
7306 | 35.07 | 42.4294 | 97.6741 | 266.1026 | 0.46072 |  | 7306 | 50.47 | 42.4294 | 3 | 266.1026
7307 | 38.46 | 44.6596 | 48.7099 | 218.4169 | 0.46259 |  | 7307 | 47.38 | 44.6596 | 2.2679 | 218.4169
7308 | 34.04 | 49.9917 | 50.4119 | 217.1923 | 0.4582 |  | 7308 | 45.1 | 49.9917 | 2 | 217.1923
7309 | 35.9 | 49.7476 | 38.5563 | 209.5765 | 0.46118 |  | 7309 | 44 | 49.7476 | 2.2679 | 209.5765
7310 | 33.43 | 51.1132 | 49.4493 | 235.2856 | 0.45904 |  | 7310 | 39 | 51.1132 | 3 | 235.2856
7311 | 31.5 | 58.4785 | 52.7903 | 163.6597 | 0.45906 |  | 7311 | 44.98 | 58.4785 | 4 | 163.6597
7312 | 31.52 | 75.5946 | 39.0602 | 179.9278 | 0.46207 |  | 7312 | 44.05 | 75.5946 | 5 | 179.9278
7313 | 31.59 | 100.4104 | 20.7648 | 218.0508 | 0.46551 |  | 7313 | 46.48 | 100.4104 | 5.7321 | 218.0508
7314 | 38 | 152.7431 | 55.943 | 285.4668 | 0.46459 |  | 7314 | 49.73 | 152.7431 | 6 | 285.4668
7315 | 38.08 | 165.205 | 59.9599 | 249.6583 | 0.45813 |  | 7315 | 59.69 | 165.205 | 5.7321 | 249.6583
7316 | 37.01 | 136.4575 | 32.9781 | 263.6516 | 0.44795 |  | 7316 | 63.5 | 136.4575 | 5 | 263.6516
7317 | 31.98 | 114.563 | 34.1425 | 251.7543 | 0.43837 |  | 7317 | 48.96 | 114.563 | 4 | 251.7543
7318 | 30.11 | 110.9961 | 30.2502 | 205.0869 | 0.43922 |  | 7318 | 44.13 | 110.9961 | 3 | 205.0869
7319 | 30.49 | 78.1462 | 32.3278 | 218.231 | 0.44108 |  | 7319 | 40.26 | 78.1462 | 2.2679 | 218.231
7320 | 28.06 | 40.5682 | 32.5252 | 177.1768 | 0.44377 |  | 7320 | 38.62 | 40.5682 | 2 | 177.1768
7321 | 31.5 | 33.6721 | 27.5971 | 167.6381 | 0.44244 |  | 7321 | 33.47 | 33.6721 | 2.2679 | 167.6381
7322 | 30.07 | 32.2015 | 37.5691 | 174.1976 | 0.43714 |  | 7322 | 33.31 | 32.2015 | 3 | 174.1976
7323 | 26.1 | 30.6616 | 25.5084 | 192.3484 | 0.43451 |  | 7323 | 33.68 | 30.6616 | 4 | 192.3484
7324 | 25 | 29.2442 | 33.4642 | 251.6077 | 0.43396 |  | 7324 | 33.31 | 29.2442 | 5 | 251.6077
7325 | 18.99 | 28.4089 | 26.7852 | 245.6614 | 0.43023 |  | 7325 | 32.52 | 28.4089 | 5.7321 | 245.6614
7326 | 21.86 | 28.4146 | 28.9048 | 327.8603 | 0.42076 |  | 7326 | 32.99 | 28.4146 | 6 | 327.8603
7327 | 25.98 | 43.7315 | 24.8524 | 300.272 | 0.41348 |  | 7327 | 33.31 | 43.7315 | 5.7321 | 300.272
7328 | 35.7 | 64.4095 | 55.2962 | 286.2096 | 0.41176 |  | 7328 | 36.98 | 64.4095 | 5 | 286.2096
7329 | 36.59 | 45.0798 | 61.4029 | 276.2187 | 0.41727 |  | 7329 | 41.93 | 45.0798 | 4 | 276.2187
7330 | 37.95 | 43.7165 | 71.0691 | 246.7167 | 0.42233 |  | 7330 | 41.09 | 43.7165 | 3 | 246.7167
7331 | 38.43 | 46.349 | 44.8909 | 193.15 | 0.43506 |  | 7331 | 40 | 46.349 | 2.2679 | 193.15
7332 | 37.1 | 49.8178 | 41.7023 | 219.3572 | 0.42518 |  | 7332 | 39.94 | 49.8178 | 2 | 219.3572
7333 | 30.3 | 51.1349 | 51.443 | 236.4595 | 0.4203 |  | 7333 | 42.3 | 51.1349 | 2.2679 | 236.4595
7334 | 30 | 54.0347 | 44.8028 | 129.2291 | 0.41804 |  | 7334 | 40.01 | 54.0347 | 3 | 129.2291
7335 | 27.6 | 61.516 | 40.2523 | 127.3835 | 0.42052 |  | 7335 | 38.9 | 61.516 | 4 | 127.3835
7336 | 27.94 | 74.7201 | 53.8849 | 127.9993 | 0.42399 |  | 7336 | 35.63 | 74.7201 | 5 | 127.9993
7337 | 30 | 98.5698 | 43.1972 | 158.7379 | 0.42406 |  | 7337 | 35.41 | 98.5698 | 5.7321 | 158.7379
7338 | 33.91 | 147.3563 | 36.1383 | 260.8678 | 0.42229 |  | 7338 | 39.34 | 147.3563 | 6 | 260.8678
7339 | 39.44 | 164.08 | 50.4902 | 262.0112 | 0.41929 |  | 7339 | 54.02 | 164.08 | 5.7321 | 262.0112
7340 | 37.31 | 137.5894 | 29.4296 | 268.0791 | 0.41285 |  | 7340 | 49.99 | 137.5894 | 5 | 268.0791
7341 | 36.88 | 113.5187 | 21.3992 | 220.998 | 0.40815 |  | 7341 | 39.94 | 113.5187 | 4 | 220.998
7342 | 27.85 | 106.5557 | 33.3301 | 224.3535 | 0.40672 |  | 7342 | 37.7 | 106.5557 | 3 | 224.3535
7343 | 28.81 | 76.2938 | 232.3984 | 246.5507 | 0.40411 |  | 7343 | 35.64 | 76.2938 | 2.2679 | 246.5507
7344 | 29 | 39.4273 | 36.7762 | 251.5271 | 0.40927 |  | 7344 | 37.09 | 39.4273 | 2 | 251.5271
7345 | 21 | 32.5743 | 35.9334 | 222.6048 | 0.41439 |  | 7345 | 34.14 | 32.5743 | 2.2679 | 222.6048
7346 | 25.7 | 31.2931 | 35.6906 | 212.7065 | 0.4184 |  | 7346 | 32.17 | 31.2931 | 3 | 212.7065
7347 | 26.7 | 29.9324 | 43.1616 | 258.0051 | 0.42221 |  | 7347 | 32.28 | 29.9324 | 4 | 258.0051
7348 | 26.7 | 28.8237 | 79.9973 | 276.9984 | 0.42928 |  | 7348 | 31.4 | 28.8237 | 5 | 276.9984
7349 | 25 | 27.9925 | 99.3603 | 347.9851 | 0.43279 |  | 7349 | 31.25 | 27.9925 | 5.7321 | 347.9851
7350 | 25.86 | 27.8741 | 115.1287 | 343.0202 | 0.43821 |  | 7350 | 31.6 | 27.8741 | 6 | 343.0202
7351 | 28.35 | 43.9544 | 92.8322 | 385.8964 | 0.44539 |  | 7351 | 32.17 | 43.9544 | 5.7321 | 385.8964
7352 | 25.4 | 63.8614 | 105.9819 | 437.8715 | 0.44846 |  | 7352 | 37.44 | 63.8614 | 5 | 437.8715
7353 | 24.2 | 44.0698 | 96.6991 | 408.0984 | 0.45353 |  | 7353 | 40.33 | 44.0698 | 4 | 408.0984
7354 | 29.11 | 43.4723 | 111.1949 | 314.3778 | 0.46062 |  | 7354 | 44.94 | 43.4723 | 3 | 314.3778
7355 | 29.73 | 46.0595 | 114.4151 | 313.246 | 0.46999 |  | 7355 | 47.3 | 46.0595 | 2.2679 | 313.246
7356 | 34.11 | 49.6803 | 307.8058 | 300.2497 | 0.48843 |  | 7356 | 47.3 | 49.6803 | 2 | 300.2497
7357 | 37.76 | 49.52 | 97.2875 | 230.0815 | 0.49759 |  | 7357 | 39.94 | 49.52 | 2.2679 | 230.0815
7358 | 36.26 | 52.3808 | 69.3694 | 257.8878 | 0.50205 |  | 7358 | 39.49 | 52.3808 | 3 | 257.8878
7359 | 35.92 | 57.0711 | 54.5613 | 210.5041 | 0.50389 |  | 7359 | 39.61 | 57.0711 | 4 | 210.5041
7360 | 35.98 | 73.9565 | 53.6418 | 202.9649 | 0.50667 |  | 7360 | 39.94 | 73.9565 | 5 | 202.9649
7361 | 38.19 | 96.8723 | 36.9867 | 213.2063 | 0.50913 |  | 7361 | 40.01 | 96.8723 | 5.7321 | 213.2063
7362 | 41.22 | 148.2395 | 42.0269 | 264.1724 | 0.50812 |  | 7362 | 55 | 148.2395 | 6 | 264.1724
7363 | 42.83 | 156.2133 | 44.4824 | 278.2998 | 0.50416 |  | 7363 | 57.89 | 156.2133 | 5.7321 | 278.2998
7364 | 41.04 | 144.2266 | 34.6967 | 304.7419 | 0.50434 |  | 7364 | 52.46 | 144.2266 | 5 | 304.7419
7365 | 38.29 | 113.7986 | 31.3369 | 291.5086 | 0.49868 |  | 7365 | 47.3 | 113.7986 | 4 | 291.5086
7366 | 34.3 | 104.9803 | 27.2075 | 277.7659 | 0.49005 |  | 7366 | 40.19 | 104.9803 | 3 | 277.7659
7367 | 31.37 | 75.2566 | 27.8101 | 316.3431 | 0.48293 |  | 7367 | 37.52 | 75.2566 | 2.2679 | 316.3431
7368 | 26.46 | 37.7156 | 24.8407 | 258.0053 | 0.48255 |  | 7368 | 39.1 | 37.7156 | 2 | 258.0053
7369 | 26.68 | 34.2206 | 28.5969 | 337.4348 | 0.48091 |  | 7369 | 35.67 | 34.2206 | 2.2679 | 337.4348
7370 | 24.94 | 32.5863 | 39.9679 | 281.8737 | 0.48479 |  | 7370 | 35.05 | 32.5863 | 3 | 281.8737
7371 | 22.51 | 30.9959 | 27.8145 | 266.6866 | 0.48202 |  | 7371 | 35.07 | 30.9959 | 4 | 266.6866
7372 | 18.82 | 29.6209 | 31.063 | 245.2387 | 0.48501 |  | 7372 | 34.74 | 29.6209 | 5 | 245.2387
7373 | 18.26 | 28.7775 | 23.0629 | 356.1589 | 0.47948 |  | 7373 | 35.87 | 28.7775 | 5.7321 | 356.1589
7374 | 23.81 | 28.078 | 243.9404 | 338.3839 | 0.47517 |  | 7374 | 36.74 | 28.078 | 6 | 338.3839
7375 | 35.5 | 27.6968 | 78.0076 | 412.7682 | 0.48458 |  | 7375 | 39.78 | 27.6968 | 5.7321 | 412.7682
7376 | 43.56 | 30.4485 | 126.5806 | 433.2901 | 0.5005 |  | 7376 | 35.92 | 30.4485 | 5 | 433.2901
7377 | 45.35 | 47.6879 | 113.7419 | 363.8157 | 0.50825 |  | 7377 | 50.01 | 47.6879 | 4 | 363.8157
7378 | 45.07 | 67.1216 | 132.5291 | 348.053 | 0.50974 |  | 7378 | 56.06 | 67.1216 | 3 | 348.053
7379 | 43.97 | 74.4088 | 117.7604 | 334.199 | 0.50833 |  | 7379 | 65.49 | 74.4088 | 2.2679 | 334.199
7380 | 43.33 | 77.9276 | 116.3513 | 266.4521 | 0.51195 |  | 7380 | 54.99 | 77.9276 | 2 | 266.4521
7381 | 41.71 | 80.4159 | 110.5307 | 185.312 | 0.51673 |  | 7381 | 62.43 | 80.4159 | 2.2679 | 185.312
7382 | 43.65 | 75.5238 | 34.5977 | 103.0151 | 0.51927 |  | 7382 | 42.4 | 75.5238 | 3 | 103.0151
7383 | 44.39 | 72.1359 | 40.6678 | 85.2382 | 0.52321 |  | 7383 | 50.79 | 72.1359 | 4 | 85.2382
7384 | 46.38 | 76.0266 | 34.4673 | 99.8602 | 0.52567 |  | 7384 | 50.66 | 76.0266 | 5 | 99.8602
7385 | 47.89 | 83.881 | 40.7859 | 203.9325 | 0.52431 |  | 7385 | 50.34 | 83.881 | 5.7321 | 203.9325
7386 | 52.89 | 136.0413 | 54.7552 | 248.4995 | 0.52221 |  | 7386 | 57.7 | 136.0413 | 6 | 248.4995
7387 | 52.92 | 150.3726 | 41.2777 | 284.063 | 0.51829 |  | 7387 | 65.56 | 150.3726 | 5.7321 | 284.063
7388 | 48.91 | 150.0625 | 30.9184 | 345.5626 | 0.51934 |  | 7388 | 66.57 | 150.0625 | 5 | 345.5626
7389 | 44.21 | 118.3901 | 31.7379 | 268.7829 | 0.52497 |  | 7389 | 51.54 | 118.3901 | 4 | 268.7829
7390 | 37.95 | 103.639 | 25.9366 | 277.1118 | 0.51927 |  | 7390 | 42.41 | 103.639 | 3 | 277.1118
7391 | 35.5 | 89.942 | 33.9189 | 284.7535 | 0.50544 |  | 7391 | 40.14 | 89.942 | 2.2679 | 284.7535
7392 | 30 | 41.5153 | 29.7543 | 302.9987 | 0.49705 |  | 7392 | 40.01 | 41.5153 | 2 | 302.9987
7393 | 26.5 | 33.1124 | 32.8132 | 254.9432 | 0.50315 |  | 7393 | 33.55 | 33.1124 | 2.2679 | 254.9432
7394 | 25.64 | 31.6104 | 28.3296 | 285.6169 | 0.50184 |  | 7394 | 32.4 | 31.6104 | 3 | 285.6169
7395 | 25.97 | 30.2473 | 26.132 | 273.4101 | 0.50095 |  | 7395 | 32.42 | 30.2473 | 4 | 273.4101
7396 | 24.99 | 29.0682 | 40.3223 | 360.9886 | 0.50243 |  | 7396 | 30.96 | 29.0682 | 5 | 360.9886
7397 | 26.04 | 28.2469 | 35.5741 | 411.5704 | 0.50153 |  | 7397 | 30.8 | 28.2469 | 5.7321 | 411.5704
7398 | 27.94 | 27.7467 | 60.2364 | 378.7624 | 0.50288 |  | 7398 | 31.98 | 27.7467 | 6 | 378.7624
7399 | 38.92 | 27.5409 | 112.2448 | 485.7757 | 0.51912 |  | 7399 | 34.43 | 27.5409 | 5.7321 | 485.7757
7400 | 45.52 | 30.8728 | 137.3911 | 341.6783 | 0.52953 |  | 7400 | 37.2 | 30.8728 | 5 | 341.6783
7401 | 47.97 | 49.223 | 89.6171 | 370.1207 | 0.52806 |  | 7401 | 41.72 | 49.223 | 4 | 370.1207
7402 | 47.43 | 67.97 | 56.2558 | 340.1845 | 0.52911 |  | 7402 | 41.39 | 67.97 | 3 | 340.1845
7403 | 47.98 | 76.2045 | 45.7266 | 277.719 | 0.5299 |  | 7403 | 41.96 | 76.2045 | 2.2679 | 277.719
7404 | 48.43 | 78.4999 | 78.6419 | 219.3934 | 0.52714 |  | 7404 | 40.86 | 78.4999 | 2 | 219.3934
7405 | 46.96 | 81.3525 | 87.8541 | 175.8272 | 0.52302 |  | 7405 | 41.44 | 81.3525 | 2.2679 | 175.8272
7406 | 48.34 | 77.1502 | 88.9724 | 72.3398 | 0.52112 |  | 7406 | 38.05 | 77.1502 | 3 | 72.3398
7407 | 49.91 | 75.8183 | 70.4713 | 70.2719 | 0.52429 |  | 7407 | 40.49 | 75.8183 | 4 | 70.2719
7408 | 50 | 75.3802 | 56.7838 | 88.9524 | 0.52246 |  | 7408 | 43.15 | 75.3802 | 5 | 88.9524
7409 | 50.04 | 78.8732 | 25.824 | 175.227 | 0.51964 |  | 7409 | 49.91 | 78.8732 | 5.7321 | 175.227
7410 | 60.71 | 116.1063 | 38.3654 | 283.6661 | 0.51455 |  | 7410 | 52.98 | 116.1063 | 6 | 283.6661
7411 | 62.89 | 135.5005 | 40.2906 | 351.0059 | 0.51123 |  | 7411 | 55.63 | 135.5005 | 5.7321 | 351.0059
7412 | 52.3 | 159.484 | 25.9044 | 312.1013 | 0.50933 |  | 7412 | 49.6 | 159.484 | 5 | 312.1013
7413 | 47.56 | 119.3908 | 35.9118 | 282.8839 | 0.51234 |  | 7413 | 49.73 | 119.3908 | 4 | 282.8839
7414 | 43.3 | 100.3613 | 28.0375 | 297.0968 | 0.51197 |  | 7414 | 39.23 | 100.3613 | 3 | 297.0968
7415 | 41.21 | 85.9781 | 237.2405 | 279.9489 | 0.50839 |  | 7415 | 41.84 | 85.9781 | 2.2679 | 279.9489
7416 | 38.3 | 39.3749 | 226.8056 | 270.8583 | 0.50813 |  | 7416 | 39.99 | 39.3749 | 2 | 270.8583
7417 | 36.97 | 32.9735 | 36.1666 | 215.1984 | 0.50648 |  | 7417 | 34.9 | 32.9735 | 2.2679 | 215.1984
7418 | 35.75 | 31.5577 | 20.8905 | 217.4706 | 0.50125 |  | 7418 | 37.05 | 31.5577 | 3 | 217.4706
7419 | 34.27 | 30.2356 | 33.822 | 269.9949 | 0.49475 |  | 7419 | 37.07 | 30.2356 | 4 | 269.9949
7420 | 33.79 | 28.9247 | 35.9867 | 279.3906 | 0.49337 |  | 7420 | 37.99 | 28.9247 | 5 | 279.3906
7421 | 34.45 | 28.2087 | 28.8914 | 404.1219 | 0.49787 |  | 7421 | 35.97 | 28.2087 | 5.7321 | 404.1219
7422 | 37.74 | 28.2738 | 45.2386 | 466.874 | 0.5106 |  | 7422 | 35.54 | 28.2738 | 6 | 466.874
7423 | 45.63 | 43.322 | 71.3303 | 367.3018 | 0.51883 |  | 7423 | 35.93 | 43.322 | 5.7321 | 367.3018
7424 | 55.77 | 65.772 | 114.8545 | 391.9715 | 0.5209 |  | 7424 | 38.4 | 65.772 | 5 | 391.9715
7425 | 57.77 | 45.0085 | 140.9758 | 382.5237 | 0.5225 |  | 7425 | 37.02 | 45.0085 | 4 | 382.5237
7426 | 56.92 | 41.7164 | 92.1104 | 331.8411 | 0.52634 |  | 7426 | 38.96 | 41.7164 | 3 | 331.8411
7427 | 56.8 | 43.9294 | 92.6324 | 326.0282 | 0.525 |  | 7427 | 39.89 | 43.9294 | 2.2679 | 326.0282
7428 | 56.44 | 47.3382 | 125.1983 | 339.8981 | 0.524 |  | 7428 | 44.72 | 47.3382 | 2 | 339.8981
7429 | 54.42 | 50.1895 | 119.2577 | 294.949 | 0.5258 |  | 7429 | 44.79 | 50.1895 | 2.2679 | 294.949
7430 | 55.8 | 50.6064 | 87.6379 | 260.318 | 0.52818 |  | 7430 | 46.54 | 50.6064 | 3 | 260.318
7431 | 57.28 | 57.7772 | 51.6345 | 297.3202 | 0.52945 |  | 7431 | 41.14 | 57.7772 | 4 | 297.3202
7432 | 57.39 | 74.3031 | 33.2032 | 267.0416 | 0.53178 |  | 7432 | 44.94 | 74.3031 | 5 | 267.0416
7433 | 60.71 | 99.4434 | 44.6317 | 309.3117 | 0.53384 |  | 7433 | 38.88 | 99.4434 | 5.7321 | 309.3117
7434 | 76.08 | 143.1965 | 51.2537 | 345.811 | 0.531 |  | 7434 | 42.65 | 143.1965 | 6 | 345.811
7435 | 87.12 | 157.4645 | 46.0675 | 299.3911 | 0.52816 |  | 7435 | 48.1 | 157.4645 | 5.7321 | 299.3911
7436 | 65 | 144.6755 | 33.7508 | 335.8622 | 0.52778 |  | 7436 | 44.78 | 144.6755 | 5 | 335.8622
7437 | 54.47 | 120.7608 | 21.9828 | 351.8262 | 0.531 |  | 7437 | 40.91 | 120.7608 | 4 | 351.8262
7438 | 47.52 | 107.8334 | 29.2315 | 298.6991 | 0.53171 |  | 7438 | 37.07 | 107.8334 | 3 | 298.6991
7439 | 44.59 | 76.5572 | 37.9827 | 325.8831 | 0.53159 |  | 7439 | 35.9 | 76.5572 | 2.2679 | 325.8831
7440 | 40.3 | 38.334 | 29.7178 | 316.8458 | 0.525 |  | 7440 | 35.5 | 38.334 | 2 | 316.8458
7441 | 39.07 | 35.3172 | 25.1595 | 306.9569 | 0.51893 |  | 7441 | 34.94 | 35.3172 | 2.2679 | 306.9569
7442 | 35.95 | 33.5949 | 19.3781 | 368.7952 | 0.50482 |  | 7442 | 34.44 | 33.5949 | 3 | 368.7952
7443 | 33.4 | 31.7759 | 34.3279 | 336.2184 | 0.4941 |  | 7443 | 33.32 | 31.7759 | 4 | 336.2184
7444 | 32.67 | 30.1655 | 37.2497 | 325.5846 | 0.48922 |  | 7444 | 34.69 | 30.1655 | 5 | 325.5846
7445 | 32.9 | 28.9844 | 34.5213 | 390.1654 | 0.49502 |  | 7445 | 33.05 | 28.9844 | 5.7321 | 390.1654
7446 | 35.25 | 28.4827 | 64.7443 | 495.6854 | 0.5112 |  | 7446 | 30.1 | 28.4827 | 6 | 495.6854
7447 | 42.49 | 43.1173 | 118.423 | 527.9719 | 0.51541 |  | 7447 | 29.82 | 43.1173 | 5.7321 | 527.9719
7448 | 48.12 | 66.0343 | 111.3641 | 405.5911 | 0.5122 |  | 7448 | 30.89 | 66.0343 | 5 | 405.5911
7449 | 51.29 | 43.5864 | 118.5702 | 460.4035 | 0.50836 |  | 7449 | 30.89 | 43.5864 | 4 | 460.4035
7450 | 48.56 | 41.214 | 125.274 | 420.0247 | 0.50318 |  | 7450 | 33.81 | 41.214 | 3 | 420.0247
7451 | 47.54 | 44.8686 | 149.2696 | 306.4956 | 0.49632 |  | 7451 | 37.66 | 44.8686 | 2.2679 | 306.4956
7452 | 46.36 | 45.7735 | 89.4029 | 279.4941 | 0.49306 |  | 7452 | 37.93 | 45.7735 | 2 | 279.4941
7453 | 43.91 | 49.4642 | 94.3251 | 154.7634 | 0.49289 |  | 7453 | 41.68 | 49.4642 | 2.2679 | 154.7634
7454 | 44.57 | 50.274 | 94.7548 | 105.034 | 0.48995 |  | 7454 | 42.55 | 50.274 | 3 | 105.034
7455 | 45.61 | 54.5658 | 70.0352 | 86.5058 | 0.48615 |  | 7455 | 41.86 | 54.5658 | 4 | 86.5058
7456 | 46.83 | 70.1291 | 54.8673 | 103.5748 | 0.48245 |  | 7456 | 37.33 | 70.1291 | 5 | 103.5748
7457 | 48.68 | 90.3432 | 38.9165 | 182.2286 | 0.47801 |  | 7457 | 37 | 90.3432 | 5.7321 | 182.2286
7458 | 51.17 | 149.4428 | 44.0999 | 241.5022 | 0.47517 |  | 7458 | 39.5 | 149.4428 | 6 | 241.5022
7459 | 48.19 | 158.5763 | 46.6819 | 319.4722 | 0.47252 |  | 7459 | 52.34 | 158.5763 | 5.7321 | 319.4722
7460 | 46.72 | 133.6198 | 37.9768 | 361.8864 | 0.46936 |  | 7460 | 58.95 | 133.6198 | 5 | 361.8864
7461 | 44.98 | 111.2031 | 27.7712 | 369.8436 | 0.47382 |  | 7461 | 53.12 | 111.2031 | 4 | 369.8436
7462 | 37.8 | 108.2973 | 25.4629 | 288.2985 | 0.47275 |  | 7462 | 37.78 | 108.2973 | 3 | 288.2985
7463 | 37.3 | 76.0333 | 24.926 | 259.5489 | 0.46367 |  | 7463 | 40 | 76.0333 | 2.2679 | 259.5489
7464 | 34.1 | 40.4814 | 30.2592 | 319.5092 | 0.45884 |  | 7464 | 37.44 | 40.4814 | 2 | 319.5092
7465 | 30.82 | 32.7827 | 25.7509 | 377.5827 | 0.45722 |  | 7465 | 37.09 | 32.7827 | 2.2679 | 377.5827
7466 | 31.6 | 31.3977 | 31.6884 | 293.1104 | 0.45336 |  | 7466 | 10.72 | 31.3977 | 3 | 293.1104
7467 | 32.07 | 30.0257 | 26.2972 | 351.5357 | 0.45441 |  | 7467 | 32.48 | 30.0257 | 4 | 351.5357
7468 | 31.82 | 28.8388 | 31.6963 | 389.0331 | 0.45674 |  | 7468 | 32.79 | 28.8388 | 5 | 389.0331
7469 | 33.19 | 28.0942 | 35.2749 | 371.827 | 0.46681 |  | 7469 | 30.8 | 28.0942 | 5.7321 | 371.827
7470 | 35.22 | 28.1138 | 62.4036 | 424.9519 | 0.48189 |  | 7470 | 30.24 | 28.1138 | 6 | 424.9519
7471 | 44.9 | 43.6349 | 40.6545 | 511.3652 | 0.495 |  | 7471 | 18.03 | 43.6349 | 5.7321 | 511.3652
7472 | 51.49 | 66.2004 | 248.5891 | 410.0668 | 0.5016 |  | 7472 | 34.36 | 66.2004 | 5 | 410.0668
7473 | 54.32 | 44.135 | 41.9814 | 404.7369 | 0.50442 |  | 7473 | 40.81 | 44.135 | 4 | 404.7369
7474 | 55.41 | 41.1916 | 49.1528 | 455.5301 | 0.50698 |  | 7474 | 38.25 | 41.1916 | 3 | 455.5301
7475 | 54.81 | 42.9486 | 70.2473 | 312.6111 | 0.50966 |  | 7475 | 39.14 | 42.9486 | 2.2679 | 312.6111
7476 | 53.82 | 44.3326 | 108.1633 | 293.6447 | 0.51196 |  | 7476 | 39.93 | 44.3326 | 2 | 293.6447
7477 | 52.44 | 47.8983 | 79.0823 | 292.3801 | 0.51056 |  | 7477 | 40.15 | 47.8983 | 2.2679 | 292.3801
7478 | 52.52 | 49.2762 | 51.6903 | 115.5382 | 0.51301 |  | 7478 | 41.76 | 49.2762 | 3 | 115.5382
7479 | 53.01 | 57.7694 | 70.8776 | 114.8645 | 0.51404 |  | 7479 | 42.67 | 57.7694 | 4 | 114.8645
7480 | 52.19 | 73.4794 | 252.838 | 107.5606 | 0.51691 |  | 7480 | 47 | 73.4794 | 5 | 107.5606
7481 | 54.3 | 98.4492 | 39.2255 | 179.8489 | 0.51207 |  | 7481 | 53.28 | 98.4492 | 5.7321 | 179.8489
7482 | 66.47 | 144.8203 | 37.2467 | 263.0521 | 0.50177 |  | 7482 | 59.18 | 144.8203 | 6 | 263.0521
7483 | 59.98 | 158.0621 | 46.5471 | 299.0289 | 0.49966 |  | 7483 | 69.83 | 158.0621 | 5.7321 | 299.0289
7484 | 51.97 | 142.3044 | 35.6358 | 310.5834 | 0.49614 |  | 7484 | 65.94 | 142.3044 | 5 | 310.5834
7485 | 46.41 | 112.3367 | 31.0768 | 407.9438 | 0.49233 |  | 7485 | 59.93 | 112.3367 | 4 | 407.9438
7486 | 43.69 | 107.6662 | 27.6618 | 368.5038 | 0.4975 |  | 7486 | 49.99 | 107.6662 | 3 | 368.5038
7487 | 43.8 | 75.6754 | 33.8777 | 277.9623 | 0.50242 |  | 7487 | 37.85 | 75.6754 | 2.2679 | 277.9623
7488 | 39.34 | 38.1317 | 34.4261 | 305.8788 | 0.50713 |  | 7488 | 39.7 | 38.1317 | 2 | 305.8788
7489 | 42.63 | 34.5595 | 28.6679 | 370.5851 | 0.51246 |  | 7489 | 34.78 | 34.5595 | 2.2679 | 370.5851
7490 | 39.78 | 32.8426 | 39.3313 | 262.8203 | 0.5072 |  | 7490 | 37.47 | 32.8426 | 3 | 262.8203
7491 | 38.81 | 31.2573 | 31.6504 | 399.2895 | 0.50672 |  | 7491 | 36.65 | 31.2573 | 4 | 399.2895
7492 | 36.94 | 29.7615 | 30.6089 | 381.8361 | 0.50371 |  | 7492 | 36.09 | 29.7615 | 5 | 381.8361
7493 | 36.2 | 28.8838 | 31.7271 | 372.6475 | 0.50017 |  | 7493 | 36.17 | 28.8838 | 5.7321 | 372.6475
7494 | 36.13 | 28.6458 | 43.5231 | 402.1824 | 0.49494 |  | 7494 | 37.13 | 28.6458 | 6 | 402.1824
7495 | 39.57 | 44.9606 | 93.9625 | 394.6502 | 0.4946 |  | 7495 | 35.3 | 44.9606 | 5.7321 | 394.6502
7496 | 41.56 | 66.6899 | 120.2883 | 478.6939 | 0.49275 |  | 7496 | 35.3 | 66.6899 | 5 | 478.6939
7497 | 42.02 | 46.2383 | 104.4503 | 357.3906 | 0.48955 |  | 7497 | 44.99 | 46.2383 | 4 | 357.3906
7498 | 44.57 | 43.9178 | 115.7888 | 317.7884 | 0.48247 |  | 7498 | 57.44 | 43.9178 | 3 | 317.7884
7499 | 44.15 | 47.5372 | 81.9605 | 227.7473 | 0.47677 |  | 7499 | 60.12 | 47.5372 | 2.2679 | 227.7473
7500 | 42.55 | 47.9666 | 57.4004 | 106.735 | 0.47331 |  | 7500 | 61.89 | 47.9666 | 2 | 106.735
7501 | 41.42 | 52.8743 | 46.9771 | 79.2431 | 0.47101 |  | 7501 | 60.01 | 52.8743 | 2.2679 | 79.2431
7502 | 40.01 | 54.1839 | 52.2101 | 78.7914 | 0.47285 |  | 7502 | 50.03 | 54.1839 | 3 | 78.7914
7503 | 39.96 | 61.9382 | 59.4576 | 70.2118 | 0.47761 |  | 7503 | 55 | 61.9382 | 4 | 70.2118
7504 | 41.67 | 75.7668 | 68.8837 | 62.0749 | 0.47661 |  | 7504 | 65 | 75.7668 | 5 | 62.0749
7505 | 43.81 | 102.7091 | 91.8739 | 70.1552 | 0.47768 |  | 7505 | 67.09 | 102.7091 | 5.7321 | 70.1552
7506 | 49.95 | 145.8069 | 45.6798 | 91.0242 | 0.47952 |  | 7506 | 84.55 | 145.8069 | 6 | 91.0242
7507 | 51 | 172.3181 | 45.3623 | 203.1533 | 0.48786 |  | 7507 | 121.31 | 172.3181 | 5.7321 | 203.1533
7508 | 48.45 | 142.2743 | 24.8606 | 301.1384 | 0.49396 |  | 7508 | 70.03 | 142.2743 | 5 | 301.1384
7509 | 42.75 | 119.192 | 30.9704 | 363.7384 | 0.4922 |  | 7509 | 56.43 | 119.192 | 4 | 363.7384
7510 | 40.36 | 109.332 | 29.8339 | 364.5169 | 0.49815 |  | 7510 | 44.15 | 109.332 | 3 | 364.5169
7511 | 39.66 | 76.2511 | 21.1899 | 348.8752 | 0.49947 |  | 7511 | 37.45 | 76.2511 | 2.2679 | 348.8752
7512 | 36.67 | 40.2534 | 33.0359 | 290.1238 | 0.50224 |  | 7512 | 40 | 40.2534 | 2 | 290.1238
7513 | 37.57 | 35.0865 | 32.692 | 312.6006 | 0.50695 |  | 7513 | 35.98 | 35.0865 | 2.2679 | 312.6006
7514 | 35.3 | 33.2074 | 34.4012 | 280.1882 | 0.49529 |  | 7514 | 34.98 | 33.2074 | 3 | 280.1882
7515 | 35.13 | 31.5189 | 27.8654 | 290.5216 | 0.49326 |  | 7515 | 34.66 | 31.5189 | 4 | 290.5216
7516 | 34.22 | 30.0225 | 33.547 | 382.7121 | 0.49714 |  | 7516 | 33.45 | 30.0225 | 5 | 382.7121
7517 | 33.86 | 29.005 | 31.7972 | 418.6605 | 0.49228 |  | 7517 | 32.68 | 29.005 | 5.7321 | 418.6605
7518 | 35.01 | 28.827 | 29.4134 | 468.1069 | 0.49574 |  | 7518 | 34.11 | 28.827 | 6 | 468.1069
7519 | 35.6 | 43.3363 | 36.1598 | 570.6558 | 0.50168 |  | 7519 | 33.6 | 43.3363 | 5.7321 | 570.6558
7520 | 37.52 | 64.9463 | 60.78 | 418.2567 | 0.50722 |  | 7520 | 32.75 | 64.9463 | 5 | 418.2567
7521 | 37.52 | 45.8151 | 143.5386 | 418.6787 | 0.50819 |  | 7521 | 51.89 | 45.8151 | 4 | 418.6787
7522 | 39.12 | 43.3439 | 126.0388 | 437.0589 | 0.50909 |  | 7522 | 55.2 | 43.3439 | 3 | 437.0589
7523 | 38.4 | 46.5954 | 53.7213 | 297.2784 | 0.50383 |  | 7523 | 54.96 | 46.5954 | 2.2679 | 297.2784
7524 | 38.84 | 47.0525 | 49.1809 | 185.4415 | 0.49858 |  | 7524 | 49.72 | 47.0525 | 2 | 185.4415
7525 | 40.1 | 51.1447 | 56.9321 | 193.7793 | 0.49672 |  | 7525 | 56.92 | 51.1447 | 2.2679 | 193.7793
7526 | 37.8 | 52.963 | 48.8614 | 189.6138 | 0.5005 |  | 7526 | 55.82 | 52.963 | 3 | 189.6138
7527 | 39.68 | 59.537 | 45.7273 | 143.435 | 0.50362 |  | 7527 | 55.58 | 59.537 | 4 | 143.435
7528 | 41.35 | 76.0341 | 52.5011 | 181.2128 | 0.50448 |  | 7528 | 54.28 | 76.0341 | 5 | 181.2128
7529 | 46.41 | 104.5303 | 60.6622 | 241.2651 | 0.5085 |  | 7529 | 55.08 | 104.5303 | 5.7321 | 241.2651
7530 | 52.17 | 154.1239 | 38.2643 | 340.7628 | 0.5019 |  | 7530 | 62.21 | 154.1239 | 6 | 340.7628
7531 | 53.09 | 167.0915 | 60.1314 | 443.2085 | 0.49562 |  | 7531 | 78.44 | 167.0915 | 5.7321 | 443.2085
7532 | 52.51 | 135.7771 | 229.6055 | 425.5816 | 0.49824 |  | 7532 | 60.93 | 135.7771 | 5 | 425.5816
7533 | 51.01 | 114.0923 | 36.5487 | 405.4125 | 0.49999 |  | 7533 | 56.96 | 114.0923 | 4 | 405.4125
7534 | 47 | 105.9131 | 32.3256 | 419.04 | 0.50014 |  | 7534 | 38.04 | 105.9131 | 3 | 419.04
7535 | 44.08 | 75.8085 | 24.8793 | 435.4606 | 0.49871 |  | 7535 | 40.85 | 75.8085 | 2.2679 | 435.4606
7536 | 39 | 40.6732 | 28.6356 | 408.5938 | 0.49454 |  | 7536 | 39.5 | 40.6732 | 2 | 408.5938
7537 | 35.66 | 32.1726 | 32.4244 | 376.7218 | 0.48831 |  | 7537 | 35.91 | 32.1726 | 2.2679 | 376.7218
7538 | 35.8 | 31.019 | 25.7623 | 400.9994 | 0.46984 |  | 7538 | 33.53 | 31.019 | 3 | 400.9994
7539 | 35.94 | 29.7209 | 28.4187 | 321.2339 | 0.46122 |  | 7539 | 33.25 | 29.7209 | 4 | 321.2339
7540 | 34.75 | 28.6785 | 30.9751 | 416.7645 | 0.4538 |  | 7540 | 31.69 | 28.6785 | 5 | 416.7645
7541 | 34.8 | 27.9165 | 35.4105 | 400.0682 | 0.45592 |  | 7541 | 33.2 | 27.9165 | 5.7321 | 400.0682
7542 | 36.58 | 27.4321 | 47.7419 | 513.272 | 0.46228 |  | 7542 | 33.53 | 27.4321 | 6 | 513.272
7543 | 43 | 27.283 | 98.6856 | 498.2105 | 0.46192 |  | 7543 | 35 | 27.283 | 5.7321 | 498.2105
7544 | 47.43 | 30.1432 | 121.8375 | 521.9749 | 0.46018 |  | 7544 | 44.32 | 30.1432 | 5 | 521.9749
7545 | 51 | 50.0024 | 98.4054 | 422.9596 | 0.46063 |  | 7545 | 59.05 | 50.0024 | 4 | 422.9596
7546 | 49.85 | 69.0187 | 54.116 | 446.1142 | 0.45923 |  | 7546 | 68.25 | 69.0187 | 3 | 446.1142
7547 | 48 | 73.7037 | 45.9238 | 368.1016 | 0.45387 |  | 7547 | 66.05 | 73.7037 | 2.2679 | 368.1016
7548 | 47.29 | 72.564 | 59.0882 | 303.7693 | 0.45462 |  | 7548 | 67.81 | 72.564 | 2 | 303.7693
7549 | 45 | 76.9659 | 35.5762 | 206.3422 | 0.45243 |  | 7549 | 67.91 | 76.9659 | 2.2679 | 206.3422
7550 | 45.6 | 71.6303 | 46.5687 | 162.5229 | 0.45335 |  | 7550 | 65.44 | 71.6303 | 3 | 162.5229
7551 | 43.77 | 64.5719 | 57.3224 | 194.7701 | 0.45668 |  | 7551 | 67.97 | 64.5719 | 4 | 194.7701
7552 | 43.92 | 68.4759 | 49.5976 | 204.3183 | 0.45442 |  | 7552 | 65.75 | 68.4759 | 5 | 204.3183
7553 | 44.37 | 78.5205 | 252.0698 | 261.0388 | 0.45151 |  | 7553 | 65.37 | 78.5205 | 5.7321 | 261.0388
7554 | 48.39 | 134.4342 | 52.48 | 329.8025 | 0.44801 |  | 7554 | 66.11 | 134.4342 | 6 | 329.8025
7555 | 45.39 | 150.3445 | 41.4256 | 346.911 | 0.4498 |  | 7555 | 98.15 | 150.3445 | 5.7321 | 346.911
7556 | 40.36 | 147.2633 | 31.9894 | 373.5739 | 0.45309 |  | 7556 | 73.57 | 147.2633 | 5 | 373.5739
7557 | 35.26 | 116.3267 | 24.7666 | 344.1637 | 0.46134 |  | 7557 | 61.03 | 116.3267 | 4 | 344.1637
7558 | 35.4 | 101.0193 | 23.195 | 286.5342 | 0.45455 |  | 7558 | 50.01 | 101.0193 | 3 | 286.5342
7559 | 34.5 | 86.1542 | 27.2583 | 258.8196 | 0.44407 |  | 7559 | 41.86 | 86.1542 | 2.2679 | 258.8196
7560 | 34.6 | 38.6388 | 30.0595 | 273.5154 | 0.44267 |  | 7560 | 39.94 | 38.6388 | 2 | 273.5154
7561 | 37.3 | 33.826 | 26.9289 | 229.3727 | 0.43621 |  | 7561 | 36.03 | 33.826 | 2.2679 | 229.3727
7562 | 36 | 32.3622 | 29.8086 | 217.3692 | 0.42566 |  | 7562 | 33.91 | 32.3622 | 3 | 217.3692
7563 | 34.3 | 30.9182 | 32.087 | 251.877 | 0.42102 |  | 7563 | 33 | 30.9182 | 4 | 251.877
7564 | 32.6 | 29.4449 | 31.0886 | 281.8269 | 0.41636 |  | 7564 | 34 | 29.4449 | 5 | 281.8269
7565 | 32.3 | 28.4301 | 45.1117 | 294.5907 | 0.41696 |  | 7565 | 34 | 28.4301 | 5.7321 | 294.5907
7566 | 35.3 | 27.871 | 87.3167 | 322.812 | 0.4336 |  | 7566 | 34 | 27.871 | 6 | 322.812
7567 | 40.42 | 27.4208 | 86.2395 | 345.3473 | 0.46008 |  | 7567 | 35.45 | 27.4208 | 5.7321 | 345.3473
7568 | 43.87 | 30.2894 | 38.842 | 283.1815 | 0.47768 |  | 7568 | 36.78 | 30.2894 | 5 | 283.1815
7569 | 43.99 | 48.9444 | 65.0956 | 264.452 | 0.48813 |  | 7569 | 47.96 | 48.9444 | 4 | 264.452
7570 | 43 | 67.2334 | 103.1454 | 271.0435 | 0.49412 |  | 7570 | 55.45 | 67.2334 | 3 | 271.0435
7571 | 42.42 | 71.9079 | 83.9511 | 231.0579 | 0.4874 |  | 7571 | 55.44 | 71.9079 | 2.2679 | 231.0579
7572 | 42.03 | 72.3526 | 39.3919 | 261.7549 | 0.48763 |  | 7572 | 56.42 | 72.3526 | 2 | 261.7549
7573 | 40.5 | 76.6111 | 47.1515 | 266.3881 | 0.48218 |  | 7573 | 56.41 | 76.6111 | 2.2679 | 266.3881
7574 | 41.01 | 76.7562 | 56.7169 | 250.5806 | 0.48004 |  | 7574 | 55.69 | 76.7562 | 3 | 250.5806
7575 | 44.74 | 71.2107 | 44.2901 | 229.683 | 0.48102 |  | 7575 | 54.7 | 71.2107 | 4 | 229.683
7576 | 51.04 | 69.421 | 35.7805 | 189.7788 | 0.4859 |  | 7576 | 51.84 | 69.421 | 5 | 189.7788
7577 | 51.04 | 77.733 | 43.0155 | 209.9258 | 0.48235 |  | 7577 | 52 | 77.733 | 5.7321 | 209.9258
7578 | 59.05 | 122.321 | 50.9854 | 282.911 | 0.47515 |  | 7578 | 58.46 | 122.321 | 6 | 282.911
7579 | 50 | 132.8261 | 38.8429 | 268.2455 | 0.46428 |  | 7579 | 64.92 | 132.8261 | 5.7321 | 268.2455
7580 | 43 | 165.8321 | 36.5223 | 271.6741 | 0.46167 |  | 7580 | 56.94 | 165.8321 | 5 | 271.6741
7581 | 41.38 | 114.797 | 27.2675 | 263.8425 | 0.46273 |  | 7581 | 55 | 114.797 | 4 | 263.8425
7582 | 39.64 | 103.8549 | 29.1051 | 252.6619 | 0.46626 |  | 7582 | 42.56 | 103.8549 | 3 | 252.6619
7583 | 39.26 | 87.351 | 26.8262 | 209.8569 | 0.46302 |  | 7583 | 41.54 | 87.351 | 2.2679 | 209.8569
7584 | 34.6 | 40.7167 | 36.6188 | 246.244 | 0.45783 |  | 7584 | 40.92 | 40.7167 | 2 | 246.244
7585 | 34 | 36.1991 | 28.6884 | 193.8529 | 0.45044 |  | 7585 | 34.4 | 36.1991 | 2.2679 | 193.8529
7586 | 33.9 | 34.2376 | 32.9564 | 201.7055 | 0.43993 |  | 7586 | 40.21 | 34.2376 | 3 | 201.7055
7587 | 34.3 | 32.191 | 31.2248 | 227.707 | 0.43882 |  | 7587 | 37.08 | 32.191 | 4 | 227.707
7588 | 34.68 | 30.5311 | 33.7269 | 281.2557 | 0.442 |  | 7588 | 35.6 | 30.5311 | 5 | 281.2557
7589 | 34.72 | 29.3958 | 33.1125 | 287.8001 | 0.44479 |  | 7589 | 34.94 | 29.3958 | 5.7321 | 287.8001
7590 | 34.9 | 28.9685 | 26.2036 | 386.1299 | 0.47034 |  | 7590 | 34.89 | 28.9685 | 6 | 386.1299
7591 | 40.71 | 44.1416 | 28.9945 | 414.6884 | 0.48836 |  | 7591 | 34.94 | 44.1416 | 5.7321 | 414.6884
7592 | 47.7 | 69.2021 | 233.3785 | 378.8559 | 0.49195 |  | 7592 | 35.21 | 69.2021 | 5 | 378.8559
7593 | 52.08 | 46.5618 | 35.1557 | 362.8944 | 0.49331 |  | 7593 | 34.94 | 46.5618 | 4 | 362.8944
7594 | 51.56 | 42.431 | 57.1766 | 245.755 | 0.50367 |  | 7594 | 41.74 | 42.431 | 3 | 245.755
7595 | 50.12 | 45.9932 | 33.4304 | 260.8347 | 0.50835 |  | 7595 | 45.77 | 45.9932 | 2.2679 | 260.8347
7596 | 50.59 | 48.7949 | 35.7367 | 207.5083 | 0.50616 |  | 7596 | 46.52 | 48.7949 | 2 | 207.5083
7597 | 48.97 | 52.4013 | 40.8494 | 206.8915 | 0.50004 |  | 7597 | 43.34 | 52.4013 | 2.2679 | 206.8915
7598 | 55.12 | 51.8541 | 49.2613 | 203.5833 | 0.50571 |  | 7598 | 39.94 | 51.8541 | 3 | 203.5833
7599 | 55.98 | 58.706 | 54.0157 | 189.7879 | 0.51362 |  | 7599 | 35.84 | 58.706 | 4 | 189.7879
7600 | 58.42 | 76.8853 | 47.6742 | 219.8032 | 0.51778 |  | 7600 | 36.09 | 76.8853 | 5 | 219.8032
7601 | 63.51 | 108.72 | 30.0754 | 232.7607 | 0.52318 |  | 7601 | 38.06 | 108.72 | 5.7321 | 232.7607
7602 | 80.59 | 154.3201 | 53.5964 | 274.024 | 0.51603 |  | 7602 | 45.9 | 154.3201 | 6 | 274.024
7603 | 56.09 | 165.9249 | 42.3611 | 262.5401 | 0.51107 |  | 7603 | 51.17 | 165.9249 | 5.7321 | 262.5401
7604 | 52.94 | 155.9299 | 23.5152 | 286.605 | 0.51373 |  | 7604 | 48.32 | 155.9299 | 5 | 286.605
7605 | 46.22 | 120.8031 | 29.9571 | 270.6275 | 0.51424 |  | 7605 | 38.89 | 120.8031 | 4 | 270.6275
7606 | 42.91 | 110.3258 | 35.9772 | 191.9907 | 0.51491 |  | 7606 | 36.1 | 110.3258 | 3 | 191.9907
7607 | 40.14 | 81.0707 | 19.0507 | 183.7818 | 0.50684 |  | 7607 | 34.77 | 81.0707 | 2.2679 | 183.7818
7608 | 38 | 42.0896 | 29.209 | 123.5371 | 0.50796 |  | 7608 | 34.99 | 42.0896 | 2 | 123.5371
7609 | 37.02 | 35.3383 | 32.0449 | 136.5456 | 0.51128 |  | 7609 | 34.34 | 35.3383 | 2.2679 | 136.5456
7610 | 37.85 | 33.4813 | 30.5209 | 106.7816 | 0.51493 |  | 7610 | 36.59 | 33.4813 | 3 | 106.7816
7611 | 36.51 | 31.7725 | 31.2207 | 117.4775 | 0.50818 |  | 7611 | 36.33 | 31.7725 | 4 | 117.4775
7612 | 35.37 | 30.1732 | 30.7258 | 139.8122 | 0.50548 |  | 7612 | 34.45 | 30.1732 | 5 | 139.8122
7613 | 35.77 | 29.087 | 41.1546 | 195.1576 | 0.50541 |  | 7613 | 36.33 | 29.087 | 5.7321 | 195.1576
7614 | 38.14 | 28.957 | 303.4612 | 204.2783 | 0.50838 |  | 7614 | 36.39 | 28.957 | 6 | 204.2783
7615 | 44.42 | 44.0891 | 103.0137 | 220.4828 | 0.50893 |  | 7615 | 36.44 | 44.0891 | 5.7321 | 220.4828
7616 | 51.22 | 66.1843 | 115.6031 | 237.4371 | 0.50309 |  | 7616 | 36.77 | 66.1843 | 5 | 237.4371
7617 | 52.32 | 47.1322 | 90.2998 | 189.8418 | 0.50134 |  | 7617 | 35 | 47.1322 | 4 | 189.8418
7618 | 49.1 | 43.3679 | 58.492 | 154.0511 | 0.50032 |  | 7618 | 40.24 | 43.3679 | 3 | 154.0511
7619 | 47.24 | 45.377 | 66.7731 | 153.3219 | 0.50566 |  | 7619 | 42.39 | 45.377 | 2.2679 | 153.3219
7620 | 47.95 | 49.0031 | 37.7022 | 159.6025 | 0.50788 |  | 7620 | 37.05 | 49.0031 | 2 | 159.6025
7621 | 48.64 | 51.3695 | 39.4028 | 149.363 | 0.5098 |  | 7621 | 37.57 | 51.3695 | 2.2679 | 149.363
7622 | 50.62 | 53.2389 | 46.1118 | 126.6417 | 0.51486 |  | 7622 | 40 | 53.2389 | 3 | 126.6417
7623 | 53.7 | 58.7119 | 39.7949 | 132.0774 | 0.52116 |  | 7623 | 37.65 | 58.7119 | 4 | 132.0774
7624 | 54.12 | 76.138 | 41.7663 | 164.2872 | 0.52199 |  | 7624 | 37.98 | 76.138 | 5 | 164.2872
7625 | 56.15 | 101.3247 | 56.4393 | 197.6197 | 0.5169 |  | 7625 | 39.76 | 101.3247 | 5.7321 | 197.6197
7626 | 61.14 | 153.1758 | 36.7871 | 191.1326 | 0.50524 |  | 7626 | 44.74 | 153.1758 | 6 | 191.1326
7627 | 49.8 | 160.1305 | 50.3662 | 216.3136 | 0.50662 |  | 7627 | 69.37 | 160.1305 | 5.7321 | 216.3136
7628 | 45.1 | 135.7911 | 39.3826 | 248.6862 | 0.51067 |  | 7628 | 70.01 | 135.7911 | 5 | 248.6862
7629 | 42.69 | 119.6394 | 38.0705 | 195.4003 | 0.51311 |  | 7629 | 50 | 119.6394 | 4 | 195.4003
7630 | 42.05 | 108.5184 | 19.2964 | 188.7883 | 0.51297 |  | 7630 | 54 | 108.5184 | 3 | 188.7883
7631 | 38.65 | 77.8618 | 24.1137 | 153.9379 | 0.51088 |  | 7631 | 39.32 | 77.8618 | 2.2679 | 153.9379
7632 | 35.38 | 41.1647 | 32.51 | 163.5953 | 0.50791 |  | 7632 | 37.44 | 41.1647 | 2 | 163.5953
7633 | 32.4 | 35.7975 | 24.575 | 128.9896 | 0.49816 |  | 7633 | 37.54 | 35.7975 | 2.2679 | 128.9896
7634 | 32.1 | 33.9939 | 28.0736 | 107.4972 | 0.49283 |  | 7634 | 36.19 | 33.9939 | 3 | 107.4972
7635 | 30 | 32.0813 | 29.2988 | 129.8157 | 0.47324 |  | 7635 | 33.12 | 32.0813 | 4 | 129.8157
7636 | 33 | 30.4617 | 37.505 | 172.6307 | 0.46997 |  | 7636 | 33.4 | 30.4617 | 5 | 172.6307
7637 | 33 | 29.2731 | 36.632 | 243.4714 | 0.46193 |  | 7637 | 33.85 | 29.2731 | 5.7321 | 243.4714
7638 | 33 | 28.9925 | 57.8522 | 280.0214 | 0.46339 |  | 7638 | 34.08 | 28.9925 | 6 | 280.0214
7639 | 36.1 | 44.0106 | 85.9333 | 269.0853 | 0.48164 |  | 7639 | 34.65 | 44.0106 | 5.7321 | 269.0853
7640 | 39.73 | 67.4384 | 55.3683 | 290.2529 | 0.48687 |  | 7640 | 42.94 | 67.4384 | 5 | 290.2529
7641 | 40.86 | 45.5755 | 55.445 | 249.5392 | 0.49102 |  | 7641 | 60.39 | 45.5755 | 4 | 249.5392
7642 | 40.61 | 40.8215 | 66.4433 | 204.9609 | 0.4962 |  | 7642 | 64.18 | 40.8215 | 3 | 204.9609
7643 | 40.38 | 42.6384 | 123.3241 | 255.1605 | 0.50234 |  | 7643 | 74.94 | 42.6384 | 2.2679 | 255.1605
7644 | 40.5 | 44.3894 | 119.4514 | 251.0945 | 0.49914 |  | 7644 | 80.01 | 44.3894 | 2 | 251.0945
7645 | 40.02 | 49.1313 | 66.7282 | 158.1913 | 0.49744 |  | 7645 | 89.54 | 49.1313 | 2.2679 | 158.1913
7646 | 40.12 | 49.3843 | 50.1831 | 118.5288 | 0.49949 |  | 7646 | 77.5 | 49.3843 | 3 | 118.5288
7647 | 42.14 | 56.1522 | 254.6943 | 133.8814 | 0.50404 |  | 7647 | 88.78 | 56.1522 | 4 | 133.8814
7648 | 45.41 | 75.4077 | 42.5458 | 162.2677 | 0.50618 |  | 7648 | 62.53 | 75.4077 | 5 | 162.2677
7649 | 49 | 104.3272 | 45.8326 | 164.0303 | 0.50463 |  | 7649 | 56.28 | 104.3272 | 5.7321 | 164.0303
7650 | 61 | 152.4761 | 57.4727 | 191.4561 | 0.50798 |  | 7650 | 60.54 | 152.4761 | 6 | 191.4561
7651 | 45.91 | 157.6556 | 258.2685 | 261.7749 | 0.51138 |  | 7651 | 61.58 | 157.6556 | 5.7321 | 261.7749
7652 | 43.8 | 144.3372 | 26.9247 | 254.9962 | 0.51733 |  | 7652 | 80.01 | 144.3372 | 5 | 254.9962
7653 | 42.92 | 122.0685 | 30.7728 | 254.6146 | 0.52429 |  | 7653 | 48.19 | 122.0685 | 4 | 254.6146
7654 | 41.35 | 109.3037 | 28.2423 | 225.0679 | 0.53336 |  | 7654 | 42.44 | 109.3037 | 3 | 225.0679
7655 | 40.04 | 79.1171 | 30.9308 | 233.7638 | 0.5411 |  | 7655 | 37.41 | 79.1171 | 2.2679 | 233.7638
7656 | 38.46 | 41.2636 | 29.5766 | 173.723 | 0.54558 |  | 7656 | 40 | 41.2636 | 2 | 173.723
7657 | 36.98 | 34.2004 | 25.9963 | 234.34 | 0.54922 |  | 7657 | 31.72 | 34.2004 | 2.2679 | 234.34
7658 | 37.07 | 32.515 | 20.7816 | 166.5729 | 0.5461 |  | 7658 | 32.37 | 32.515 | 3 | 166.5729
7659 | 36.53 | 30.8631 | 33.7249 | 216.5103 | 0.54558 |  | 7659 | 32.07 | 30.8631 | 4 | 216.5103
7660 | 37.19 | 29.5088 | 31.8284 | 190.079 | 0.55031 |  | 7660 | 30.94 | 29.5088 | 5 | 190.079
7661 | 37.32 | 28.6254 | 35.2388 | 269.5609 | 0.55133 |  | 7661 | 29.2 | 28.6254 | 5.7321 | 269.5609
7662 | 37.49 | 28.6899 | 38.6 | 256.1614 | 0.55103 |  | 7662 | 30.07 | 28.6899 | 6 | 256.1614
7663 | 38.42 | 43.8658 | 70.2341 | 316.1059 | 0.54923 |  | 7663 | 32.18 | 43.8658 | 5.7321 | 316.1059
7664 | 39.01 | 66.2433 | 85.4308 | 284.5539 | 0.54687 |  | 7664 | 36.6 | 66.2433 | 5 | 284.5539
7665 | 42.47 | 47.1113 | 46.2153 | 278.3298 | 0.54627 |  | 7665 | 44.65 | 47.1113 | 4 | 278.3298
7666 | 43.13 | 42.9836 | 50.1238 | 209.8737 | 0.53853 |  | 7666 | 58.63 | 42.9836 | 3 | 209.8737
7667 | 41.51 | 46.4609 | 266.6524 | 171.534 | 0.53159 |  | 7667 | 60.74 | 46.4609 | 2.2679 | 171.534
7668 | 41.9 | 49.1581 | 96.1377 | 187.2059 | 0.52367 |  | 7668 | 58.24 | 49.1581 | 2 | 187.2059
7669 | 38.97 | 51.2913 | 136.0064 | 143.4488 | 0.51806 |  | 7669 | 52.2 | 51.2913 | 2.2679 | 143.4488
7670 | 38.94 | 51.5677 | 76.9518 | 130.1298 | 0.51446 |  | 7670 | 55.02 | 51.5677 | 3 | 130.1298
7671 | 40.12 | 61.4029 | 44.7119 | 150.2799 | 0.51273 |  | 7671 | 55.4 | 61.4029 | 4 | 150.2799
7672 | 40.19 | 76.4327 | 44.453 | 165.4376 | 0.5155 |  | 7672 | 57.08 | 76.4327 | 5 | 165.4376
7673 | 42.61 | 110.3779 | 44.4818 | 200.5866 | 0.51724 |  | 7673 | 58.1 | 110.3779 | 5.7321 | 200.5866
7674 | 43.87 | 156.4776 | 60.069 | 211.2169 | 0.50996 |  | 7674 | 74.94 | 156.4776 | 6 | 211.2169
7675 | 42.2 | 167.6934 | 34.6083 | 282.5426 | 0.50243 |  | 7675 | 119.16 | 167.6934 | 5.7321 | 282.5426
7676 | 39.32 | 138.2625 | 24.7697 | 241.7325 | 0.49943 |  | 7676 | 94.41 | 138.2625 | 5 | 241.7325
7677 | 37 | 120.7917 | 25.8281 | 243.3196 | 0.4937 |  | 7677 | 67.13 | 120.7917 | 4 | 243.3196
7678 | 34.23 | 110.6076 | 26.386 | 175.3078 | 0.48777 |  | 7678 | 54.29 | 110.6076 | 3 | 175.3078
7679 | 34.3 | 78.01 | 33.3159 | 170.0012 | 0.48837 |  | 7679 | 39.84 | 78.01 | 2.2679 | 170.0012
7680 | 34.7 | 39.2555 | 28.5631 | 142.7081 | 0.50122 |  | 7680 | 38.42 | 39.2555 | 2 | 142.7081
7681 | 32.9 | 33.224 | 36.0936 | 177.4772 | 0.4997 |  | 7681 | 37.29 | 33.224 | 2.2679 | 177.4772
7682 | 32.5 | 31.8278 | 31.5521 | 145.892 | 0.48547 |  | 7682 | 35.55 | 31.8278 | 3 | 145.892
7683 | 34.7 | 30.4259 | 27.6437 | 211.9595 | 0.4717 |  | 7683 | 34.14 | 30.4259 | 4 | 211.9595
7684 | 32.23 | 29.1128 | 31.0488 | 211.9984 | 0.47791 |  | 7684 | 33.4 | 29.1128 | 5 | 211.9984
7685 | 32.86 | 28.359 | 31.8122 | 305.096 | 0.47988 |  | 7685 | 33.45 | 28.359 | 5.7321 | 305.096
7686 | 33.75 | 28.2677 | 31.4294 | 306.2838 | 0.4841 |  | 7686 | 33.05 | 28.2677 | 6 | 306.2838
7687 | 32.49 | 43.2004 | 31.04 | 281.5887 | 0.50157 |  | 7687 | 34.19 | 43.2004 | 5.7321 | 281.5887
7688 | 33.88 | 67.44 | 31.4515 | 339.6617 | 0.51581 |  | 7688 | 42.13 | 67.44 | 5 | 339.6617
7689 | 36.85 | 48.6819 | 39.3074 | 293.866 | 0.53528 |  | 7689 | 51.92 | 48.6819 | 4 | 293.866
7690 | 38.81 | 44.4608 | 45.3059 | 275.7151 | 0.53797 |  | 7690 | 56.36 | 44.4608 | 3 | 275.7151
7691 | 39.72 | 46.4083 | 42.0826 | 250.0455 | 0.53952 |  | 7691 | 58.06 | 46.4083 | 2.2679 | 250.0455
7692 | 40.76 | 49.636 | 31.4685 | 220.3216 | 0.54175 |  | 7692 | 56.36 | 49.636 | 2 | 220.3216
7693 | 40.15 | 51.8246 | 45.546 | 165.9481 | 0.54483 |  | 7693 | 53.96 | 51.8246 | 2.2679 | 165.9481
7694 | 39.25 | 52.4284 | 63.7221 | 192.3743 | 0.54911 |  | 7694 | 46.79 | 52.4284 | 3 | 192.3743
7695 | 39.06 | 60.0046 | 35.2826 | 233.693 | 0.55029 |  | 7695 | 45.63 | 60.0046 | 4 | 233.693
7696 | 39.83 | 76.3146 | 248.191 | 269.5297 | 0.55241 |  | 7696 | 41.25 | 76.3146 | 5 | 269.5297
7697 | 41.15 | 100.1766 | 43.15 | 217.6734 | 0.55167 |  | 7697 | 41.6 | 100.1766 | 5.7321 | 217.6734
7698 | 45.44 | 144.1701 | 33.5766 | 282.7663 | 0.5438 |  | 7698 | 44.89 | 144.1701 | 6 | 282.7663
7699 | 43.67 | 166.0778 | 47.0915 | 302.4037 | 0.53819 |  | 7699 | 53.05 | 166.0778 | 5.7321 | 302.4037
7700 | 42.6 | 137.0975 | 39.7662 | 271.2642 | 0.53841 |  | 7700 | 51.81 | 137.0975 | 5 | 271.2642
7701 | 40.18 | 118.3713 | 39.8557 | 295.5828 | 0.53682 |  | 7701 | 46.94 | 118.3713 | 4 | 295.5828
7702 | 38.6 | 106.0988 | 84.661 | 268.7212 | 0.53478 |  | 7702 | 39.62 | 106.0988 | 3 | 268.7212
7703 | 35.06 | 77.0831 | 109.2149 | 228.8876 | 0.52531 |  | 7703 | 37.44 | 77.0831 | 2.2679 | 228.8876
7704 | 32.3 | 39.2567 | 98.1766 | 243.1117 | 0.51816 |  | 7704 | 37 | 39.2567 | 2 | 243.1117
7705 | 24.76 | 33.0618 | 58.6321 | 209.721 | 0.51279 |  | 7705 | 31.83 | 33.0618 | 2.2679 | 209.721
7706 | 27.83 | 31.659 | 35.0815 | 225.591 | 0.49901 |  | 7706 | 30.57 | 31.659 | 3 | 225.591
7707 | 26.5 | 30.3264 | 28.1672 | 212.7262 | 0.49027 |  | 7707 | 30.01 | 30.3264 | 4 | 212.7262
7708 | 28.16 | 29.1612 | 27.4681 | 273.2491 | 0.48827 |  | 7708 | 29.85 | 29.1612 | 5 | 273.2491
7709 | 29.9 | 28.1954 | 26.002 | 311.1067 | 0.49049 |  | 7709 | 30.73 | 28.1954 | 5.7321 | 311.1067
7710 | 34 | 27.6003 | 44.6933 | 311.1618 | 0.49901 |  | 7710 | 30.86 | 27.6003 | 6 | 311.1618
7711 | 40.02 | 27.3253 | 257.5457 | 335.8546 | 0.50017 |  | 7711 | 30.85 | 27.3253 | 5.7321 | 335.8546
7712 | 41.76 | 30.4589 | 61.3251 | 343.6308 | 0.50155 |  | 7712 | 38.54 | 30.4589 | 5 | 343.6308
7713 | 45.87 | 49.227 | 48.8612 | 290.6619 | 0.50478 |  | 7713 | 48.92 | 49.227 | 4 | 290.6619
7714 | 46.37 | 66.7193 | 45.6877 | 257.0669 | 0.50915 |  | 7714 | 51.79 | 66.7193 | 3 | 257.0669
7715 | 48.38 | 72.5643 | 52.1863 | 250.4343 | 0.50756 |  | 7715 | 46.09 | 72.5643 | 2.2679 | 250.4343
7716 | 49.79 | 74.6942 | 47.2096 | 193.8883 | 0.5104 |  | 7716 | 45.6 | 74.6942 | 2 | 193.8883
7717 | 48.81 | 76.7943 | 48.903 | 171.3913 | 0.51009 |  | 7717 | 46.37 | 76.7943 | 2.2679 | 171.3913
7718 | 51.58 | 74.7434 | 42.6739 | 144.0155 | 0.49993 |  | 7718 | 45.66 | 74.7434 | 3 | 144.0155
7719 | 49.8 | 69.6267 | 47.0891 | 128.332 | 0.49557 |  | 7719 | 44.71 | 69.6267 | 4 | 128.332
7720 | 52.87 | 72.3006 | 49.5706 | 189.7076 | 0.48821 |  | 7720 | 40.91 | 72.3006 | 5 | 189.7076
7721 | 55 | 88.3816 | 39.811 | 244.0267 | 0.4822 |  | 7721 | 38.27 | 88.3816 | 5.7321 | 244.0267
7722 | 54.94 | 138.9886 | 41.4073 | 284.3569 | 0.47532 |  | 7722 | 41.73 | 138.9886 | 6 | 284.3569
7723 | 43.67 | 160.4108 | 243.3041 | 259.2135 | 0.46651 |  | 7723 | 46.51 | 160.4108 | 5.7321 | 259.2135
7724 | 41.62 | 143.1125 | 30.1671 | 285.9737 | 0.4652 |  | 7724 | 37.76 | 143.1125 | 5 | 285.9737
7725 | 39.39 | 114.5479 | 25.1202 | 290.8449 | 0.46475 |  | 7725 | 36.02 | 114.5479 | 4 | 290.8449
7726 | 35.3 | 98.9483 | 24.6219 | 266.7508 | 0.46293 |  | 7726 | 35.64 | 98.9483 | 3 | 266.7508
7727 | 33.89 | 86.5472 | 28.6463 | 202.8928 | 0.45539 |  | 7727 | 35.62 | 86.5472 | 2.2679 | 202.8928
7728 | 32.8 | 39.3928 | 34.8741 | 208.887 | 0.45 |  | 7728 | 33.6 | 39.3928 | 2 | 208.887
7729 | 32.3 | 32.9089 | 26.0877 | 190.4939 | 0.44367 |  | 7729 | 34.01 | 32.9089 | 2.2679 | 190.4939
7730 | 32.8 | 31.5754 | 30.9787 | 165.6444 | 0.44221 |  | 7730 | 32.95 | 31.5754 | 3 | 165.6444
7731 | 32.2 | 30.3032 | 31.8299 | 204.9909 | 0.44153 |  | 7731 | 31.02 | 30.3032 | 4 | 204.9909
7732 | 32 | 28.9646 | 32.2773 | 207.7015 | 0.44235 |  | 7732 | 29.75 | 28.9646 | 5 | 207.7015
7733 | 32 | 28.1319 | 41.4936 | 291.6353 | 0.45237 |  | 7733 | 30.35 | 28.1319 | 5.7321 | 291.6353
7734 | 35.2 | 27.4874 | 44.9198 | 366.619 | 0.4594 |  | 7734 | 31.4 | 27.4874 | 6 | 366.619
7735 | 38.36 | 27.1946 | 70.6285 | 302.4359 | 0.48499 |  | 7735 | 31.5 | 27.1946 | 5.7321 | 302.4359
7736 | 43.32 | 30.5059 | 90.1098 | 304.317 | 0.50333 |  | 7736 | 35 | 30.5059 | 5 | 304.317
7737 | 44.86 | 51.0575 | 72.4189 | 248.4435 | 0.50541 |  | 7737 | 45.6 | 51.0575 | 4 | 248.4435
7738 | 43.38 | 69.5081 | 43.2534 | 233.9877 | 0.4933 |  | 7738 | 45.6 | 69.5081 | 3 | 233.9877
7739 | 43.08 | 75.1426 | 43.8925 | 176.1229 | 0.49626 |  | 7739 | 45.99 | 75.1426 | 2.2679 | 176.1229
7740 | 43.15 | 76.467 | 38.2879 | 188.0957 | 0.49079 |  | 7740 | 45.6 | 76.467 | 2 | 188.0957
7741 | 43.35 | 78.5076 | 51.0693 | 159.6632 | 0.49387 |  | 7741 | 45 | 78.5076 | 2.2679 | 159.6632
7742 | 47.97 | 79.2871 | 33.9756 | 166.2681 | 0.49665 |  | 7742 | 45.6 | 79.2871 | 3 | 166.2681
7743 | 54.9 | 76.2275 | 52.3471 | 137.8893 | 0.50681 |  | 7743 | 45.6 | 76.2275 | 4 | 137.8893
7744 | 61.81 | 75.9432 | 51.2766 | 176.7469 | 0.50623 |  | 7744 | 44.99 | 75.9432 | 5 | 176.7469
7745 | 70.43 | 84.4026 | 41.4369 | 199.4747 | 0.50468 |  | 7745 | 37.44 | 84.4026 | 5.7321 | 199.4747
7746 | 80.1 | 134.7285 | 53.8859 | 177.9123 | 0.50567 |  | 7746 | 51.32 | 134.7285 | 6 | 177.9123
7747 | 76.09 | 155.6116 | 49.368 | 211.6014 | 0.50679 |  | 7747 | 56 | 155.6116 | 5.7321 | 211.6014
7748 | 71.53 | 147.7003 | 37.9111 | 202.7844 | 0.50717 |  | 7748 | 41.71 | 147.7003 | 5 | 202.7844
7749 | 58.97 | 119.6738 | 35.122 | 218.3822 | 0.51336 |  | 7749 | 44.99 | 119.6738 | 4 | 218.3822
7750 | 46.95 | 102.1003 | 72.3424 | 198.0047 | 0.52037 |  | 7750 | 53.4 | 102.1003 | 3 | 198.0047
7751 | 40.63 | 87.8493 | 97.9363 | 146.9672 | 0.52257 |  | 7751 | 38 | 87.8493 | 2.2679 | 146.9672
7752 | 38.03 | 39.3715 | 97.7321 | 123.0686 | 0.52253 |  | 7752 | 34.94 | 39.3715 | 2 | 123.0686
7753 | 35.5 | 33.1781 | 307.6152 | 150.9511 | 0.51978 |  | 7753 | 31.44 | 33.1781 | 2.2679 | 150.9511
7754 | 33.4 | 31.6927 | 87.1579 | 112.0009 | 0.51896 |  | 7754 | 32.56 | 31.6927 | 3 | 112.0009
7755 | 33.7 | 30.2644 | 101.5163 | 124.9359 | 0.51789 |  | 7755 | 31.28 | 30.2644 | 4 | 124.9359
7756 | 35.28 | 29.0243 | 77.2517 | 166.7426 | 0.52258 |  | 7756 | 31.23 | 29.0243 | 5 | 166.7426
7757 | 36.1 | 28.2315 | 37.3121 | 215.8333 | 0.52513 |  | 7757 | 30.95 | 28.2315 | 5.7321 | 215.8333
7758 | 38 | 28.1347 | 32.9336 | 260.7872 | 0.52455 |  | 7758 | 30.77 | 28.1347 | 6 | 260.7872
7759 | 50.05 | 43.6573 | 31.2511 | 300.8024 | 0.52353 |  | 7759 | 30.76 | 43.6573 | 5.7321 | 300.8024
7760 | 59 | 67.7972 | 40.8721 | 306.5619 | 0.52181 |  | 7760 | 33.63 | 67.7972 | 5 | 306.5619
7761 | 65.1 | 48.2976 | 44.382 | 234.3364 | 0.52195 |  | 7761 | 44.88 | 48.2976 | 4 | 234.3364
7762 | 64.45 | 42.6458 | 36.5557 | 210.8811 | 0.5206 |  | 7762 | 39.94 | 42.6458 | 3 | 210.8811
7763 | 60.07 | 46.2667 | 46.3674 | 180.5927 | 0.52146 |  | 7763 | 42 | 46.2667 | 2.2679 | 180.5927
7764 | 59.27 | 47.0508 | 35.7402 | 211.9925 | 0.51976 |  | 7764 | 41 | 47.0508 | 2 | 211.9925
7765 | 57.23 | 49.4871 | 57.4677 | 150.2355 | 0.52159 |  | 7765 | 40.1 | 49.4871 | 2.2679 | 150.2355
7766 | 57.61 | 51.3806 | 51.8107 | 172.1434 | 0.5262 |  | 7766 | 39.24 | 51.3806 | 3 | 172.1434
7767 | 59.82 | 57.5387 | 48.981 | 170.9207 | 0.5266 |  | 7767 | 40.1 | 57.5387 | 4 | 170.9207
7768 | 60.69 | 72.6871 | 34.839 | 193.434 | 0.52559 |  | 7768 | 36.97 | 72.6871 | 5 | 193.434
7769 | 62.64 | 101.0071 | 55.8336 | 211.6576 | 0.51953 |  | 7769 | 45.7 | 101.0071 | 5.7321 | 211.6576
7770 | 71.05 | 155.6539 | 45.3868 | 228.4875 | 0.51449 |  | 7770 | 47.07 | 155.6539 | 6 | 228.4875
7771 | 61.06 | 164.0745 | 243.2164 | 210.9447 | 0.51321 |  | 7771 | 63.63 | 164.0745 | 5.7321 | 210.9447
7772 | 50.1 | 133.4414 | 25.9534 | 241.2635 | 0.5135 |  | 7772 | 52.16 | 133.4414 | 5 | 241.2635
7773 | 48.66 | 119.1905 | 35.1038 | 251.1115 | 0.51288 |  | 7773 | 40 | 119.1905 | 4 | 251.1115
7774 | 41.62 | 106.3212 | 77.4934 | 199.8331 | 0.51689 |  | 7774 | 35.75 | 106.3212 | 3 | 199.8331
7775 | 35.4 | 75.3097 | 101.8464 | 207.6242 | 0.51986 |  | 7775 | 35.39 | 75.3097 | 2.2679 | 207.6242
7776 | 36.6 | 38.7955 | 262.9308 | 168.3534 | 0.52196 |  | 7776 | 34.86 | 38.7955 | 2 | 168.3534
7777 | 35 | 34.922 | 27.0296 | 175.1262 | 0.51623 |  | 7777 | 31.99 | 34.922 | 2.2679 | 175.1262
7778 | 35 | 33.1079 | 40.8405 | 146.3452 | 0.50363 |  | 7778 | 31.93 | 33.1079 | 3 | 146.3452
7779 | 35.86 | 31.2767 | 87.1819 | 151.7587 | 0.49879 |  | 7779 | 25.37 | 31.2767 | 4 | 151.7587
7780 | 33.5 | 29.8166 | 99.4111 | 169.8826 | 0.49944 |  | 7780 | 31.16 | 29.8166 | 5 | 169.8826
7781 | 36.21 | 29.0035 | 91.7714 | 192.9112 | 0.50551 |  | 7781 | 23.99 | 29.0035 | 5.7321 | 192.9112
7782 | 38.57 | 28.943 | 54.1309 | 258.3526 | 0.51263 |  | 7782 | 13.64 | 28.943 | 6 | 258.3526
7783 | 43.51 | 43.6405 | 23.3644 | 308.1795 | 0.51612 |  | 7783 | 14.9 | 43.6405 | 5.7321 | 308.1795
7784 | 55.44 | 66.7186 | 57.1819 | 249.7466 | 0.51477 |  | 7784 | 24.91 | 66.7186 | 5 | 249.7466
7785 | 51.72 | 48.6824 | 39.4637 | 272.9244 | 0.51081 |  | 7785 | 25.9 | 48.6824 | 4 | 272.9244
7786 | 54.29 | 42.8421 | 65.3546 | 215.9552 | 0.50652 |  | 7786 | 23.55 | 42.8421 | 3 | 215.9552
7787 | 57.24 | 47.4237 | 102.816 | 212.5441 | 0.50702 |  | 7787 | 32.31 | 47.4237 | 2.2679 | 212.5441
7788 | 57.39 | 49.9833 | 83.9074 | 204.0906 | 0.51048 |  | 7788 | 33.59 | 49.9833 | 2 | 204.0906
7789 | 53.33 | 51.6611 | 46.8974 | 215.5281 | 0.51 |  | 7789 | 33.55 | 51.6611 | 2.2679 | 215.5281
7790 | 56.92 | 52.6098 | 39.2666 | 174.6833 | 0.51273 |  | 7790 | 43.53 | 52.6098 | 3 | 174.6833
7791 | 56.22 | 58.0416 | 46.5223 | 174.5253 | 0.50885 |  | 7791 | 44.09 | 58.0416 | 4 | 174.5253
7792 | 56.51 | 73.3796 | 49.2335 | 197.8879 | 0.50716 |  | 7792 | 35.32 | 73.3796 | 5 | 197.8879
7793 | 58.7 | 105.2701 | 48.4298 | 214.0545 | 0.5053 |  | 7793 | 32.7 | 105.2701 | 5.7321 | 214.0545
7794 | 63.38 | 156.3209 | 42.1568 | 238.7808 | 0.49964 |  | 7794 | 34.99 | 156.3209 | 6 | 238.7808
7795 | 53.11 | 168.2637 | 37.523 | 280.4983 | 0.4869 |  | 7795 | 44.09 | 168.2637 | 5.7321 | 280.4983
7796 | 49.78 | 142.427 | 45.8686 | 220.3645 | 0.48637 |  | 7796 | 50 | 142.427 | 5 | 220.3645
7797 | 43.55 | 116.848 | 108.767 | 267.0821 | 0.49892 |  | 7797 | 50.03 | 116.848 | 4 | 267.0821
7798 | 40.19 | 104.9752 | 106.6305 | 237.6332 | 0.50521 |  | 7798 | 51.67 | 104.9752 | 3 | 237.6332
7799 | 37.92 | 75.9634 | 268.7163 | 193.5905 | 0.50384 |  | 7799 | 39.99 | 75.9634 | 2.2679 | 193.5905
7800 | 36.5 | 40.3639 | 26.291 | 178.1259 | 0.50396 |  | 7800 | 39.94 | 40.3639 | 2 | 178.1259
7801 | 33.5 | 36.0642 | 63.2486 | 210.0693 | 0.50482 |  | 7801 | 34.51 | 36.0642 | 2.2679 | 210.0693
7802 | 34.5 | 34.0655 | 89.2934 | 152.9311 | 0.49794 |  | 7802 | 34.68 | 34.0655 | 3 | 152.9311
7803 | 34.2 | 32.2131 | 57.1706 | 183.103 | 0.4946 |  | 7803 | 32.12 | 32.2131 | 4 | 183.103
7804 | 34.5 | 30.4944 | 35.8144 | 181.9266 | 0.49783 |  | 7804 | 32.69 | 30.4944 | 5 | 181.9266
7805 | 35.4 | 29.3402 | 35.3185 | 202.9122 | 0.50094 |  | 7805 | 31.05 | 29.3402 | 5.7321 | 202.9122
7806 | 36.83 | 28.7833 | 27.2263 | 257.4754 | 0.50648 |  | 7806 | 10.88 | 28.7833 | 6 | 257.4754
7807 | 35.41 | 44.4031 | 27.5208 | 247.1146 | 0.50186 |  | 7807 | 20 | 44.4031 | 5.7321 | 247.1146
7808 | 50.77 | 67.6823 | 49.7684 | 275.407 | 0.50302 |  | 7808 | 38.71 | 67.6823 | 5 | 275.407
7809 | 51.58 | 46.4194 | 36.9307 | 248.0921 | 0.50667 |  | 7809 | 49.86 | 46.4194 | 4 | 248.0921
7810 | 49.9 | 40.4996 | 52.0194 | 229.6935 | 0.50289 |  | 7810 | 49.4 | 40.4996 | 3 | 229.6935
7811 | 48.69 | 42.9467 | 44.2276 | 193.8542 | 0.50044 |  | 7811 | 48.04 | 42.9467 | 2.2679 | 193.8542
7812 | 47.23 | 44.0842 | 33.2576 | 233.2691 | 0.49595 |  | 7812 | 48.7 | 44.0842 | 2 | 233.2691
7813 | 45.1 | 47.8 | 34.6031 | 229.8052 | 0.48751 |  | 7813 | 48.7 | 47.8 | 2.2679 | 229.8052
7814 | 45.91 | 51.1663 | 50.8065 | 156.7711 | 0.49346 |  | 7814 | 48.29 | 51.1663 | 3 | 156.7711
7815 | 49.03 | 57.3041 | 52.7072 | 165.6056 | 0.50015 |  | 7815 | 48.5 | 57.3041 | 4 | 165.6056
7816 | 49.5 | 73.2195 | 41.294 | 169.7505 | 0.49868 |  | 7816 | 48.7 | 73.2195 | 5 | 169.7505
7817 | 49.04 | 108.5442 | 34.7065 | 167.34 | 0.48863 |  | 7817 | 48.1 | 108.5442 | 5.7321 | 167.34
7818 | 51.91 | 150.0807 | 36.4124 | 222.4491 | 0.47728 |  | 7818 | 50.05 | 150.0807 | 6 | 222.4491
7819 | 43.45 | 170.8388 | 44.0608 | 232.1942 | 0.47489 |  | 7819 | 59.94 | 170.8388 | 5.7321 | 232.1942
7820 | 38.5 | 139.7347 | 27.889 | 242.63 | 0.48138 |  | 7820 | 39.99 | 139.7347 | 5 | 242.63
7821 | 39.56 | 116.7062 | 21.448 | 210.8549 | 0.48044 |  | 7821 | 36.3 | 116.7062 | 4 | 210.8549
7822 | 39.27 | 108.0825 | 229.2915 | 184.3495 | 0.47903 |  | 7822 | 35.75 | 108.0825 | 3 | 184.3495
7823 | 38.32 | 79.5756 | 27.3676 | 174.5898 | 0.48692 |  | 7823 | 35.1 | 79.5756 | 2.2679 | 174.5898
7824 | 35.49 | 41.7064 | 26.7612 | 136.85 | 0.49239 |  | 7824 | 32.53 | 41.7064 | 2 | 136.85
7825 | 34.36 | 35.5809 | 29.8994 | 177.6187 | 0.48694 |  | 7825 | 32.36 | 35.5809 | 2.2679 | 177.6187
7826 | 35.5 | 33.8468 | 26.1769 | 143.4872 | 0.49106 |  | 7826 | 31.89 | 33.8468 | 3 | 143.4872
7827 | 35.5 | 32.0809 | 34.1428 | 156.4373 | 0.48342 |  | 7827 | 31.21 | 32.0809 | 4 | 156.4373
7828 | 33.17 | 30.3909 | 34.6804 | 202.5099 | 0.47224 |  | 7828 | 29.28 | 30.3909 | 5 | 202.5099
7829 | 30.03 | 29.2185 | 31.6646 | 262.5615 | 0.4539 |  | 7829 | 27.16 | 29.2185 | 5.7321 | 262.5615
7830 | 28.22 | 28.6779 | 227.634 | 294.2218 | 0.4486 |  | 7830 | 19.99 | 28.6779 | 6 | 294.2218
7831 | 32.39 | 43.0707 | 30.2594 | 306.8906 | 0.46043 |  | 7831 | 29.38 | 43.0707 | 5.7321 | 306.8906
7832 | 36.14 | 66.1998 | 35.6897 | 301.497 | 0.48591 |  | 7832 | 33.89 | 66.1998 | 5 | 301.497
7833 | 37.45 | 48.4164 | 36.3388 | 255.3073 | 0.49493 |  | 7833 | 40.89 | 48.4164 | 4 | 255.3073
7834 | 44.98 | 42.9228 | 39.9169 | 255.7976 | 0.47843 |  | 7834 | 39.43 | 42.9228 | 3 | 255.7976
7835 | 52.09 | 46.7442 | 52.3062 | 251.455 | 0.47198 |  | 7835 | 37.16 | 46.7442 | 2.2679 | 251.455
7836 | 52.63 | 49.3238 | 45.7819 | 242.8537 | 0.46879 |  | 7836 | 35.85 | 49.3238 | 2 | 242.8537
7837 | 57.8 | 52.1283 | 42.5619 | 207.6994 | 0.4677 |  | 7837 | 36.35 | 52.1283 | 2.2679 | 207.6994
7838 | 50 | 53.1361 | 53.1192 | 176.618 | 0.46366 |  | 7838 | 37 | 53.1361 | 3 | 176.618
7839 | 49.42 | 59.9793 | 43.0474 | 206.9293 | 0.4662 |  | 7839 | 38.46 | 59.9793 | 4 | 206.9293
7840 | 48.23 | 76.2546 | 44.8514 | 173.0563 | 0.46236 |  | 7840 | 46.02 | 76.2546 | 5 | 173.0563
7841 | 51.12 | 107.7542 | 38.6824 | 219.4482 | 0.45811 |  | 7841 | 50.92 | 107.7542 | 5.7321 | 219.4482
7842 | 61.43 | 170.5994 | 35.0889 | 214.8431 | 0.44885 |  | 7842 | 51.51 | 170.5994 | 6 | 214.8431
7843 | 54 | 165.7496 | 42.9227 | 272.1302 | 0.44894 |  | 7843 | 68.96 | 165.7496 | 5.7321 | 272.1302
7844 | 39.9 | 138.8447 | 226.8924 | 287.5397 | 0.45072 |  | 7844 | 55.54 | 138.8447 | 5 | 287.5397
7845 | 37.54 | 122.1023 | 27.729 | 191.3198 | 0.45961 |  | 7845 | 52.81 | 122.1023 | 4 | 191.3198
7846 | 39.9 | 113.2299 | 33.866 | 236.1883 | 0.46473 |  | 7846 | 47.59 | 113.2299 | 3 | 236.1883
7847 | 36.94 | 81.0685 | 34.9543 | 197.4914 | 0.46897 |  | 7847 | 37.15 | 81.0685 | 2.2679 | 197.4914
7848 | 36.1 | 41.5914 | 22.8426 | 147.4851 | 0.4738 |  | 7848 | 37.48 | 41.5914 | 2 | 147.4851
7849 | 36.6 | 33.5377 | 33.1975 | 187.2426 | 0.48858 |  | 7849 | 39.94 | 33.5377 | 2.2679 | 187.2426
7850 | 38 | 31.9943 | 38.8726 | 145.0841 | 0.49679 |  | 7850 | 34.9 | 31.9943 | 3 | 145.0841
7851 | 36.74 | 30.5046 | 32.9414 | 172.567 | 0.5028 |  | 7851 | 34.21 | 30.5046 | 4 | 172.567
7852 | 35.4 | 29.2483 | 36.7806 | 187.6204 | 0.50982 |  | 7852 | 33.46 | 29.2483 | 5 | 187.6204
7853 | 39.6 | 28.3827 | 30.9469 | 231.3928 | 0.51675 |  | 7853 | 32.08 | 28.3827 | 5.7321 | 231.3928
7854 | 38.3 | 28.1235 | 30.6113 | 244.6621 | 0.51638 |  | 7854 | 33.54 | 28.1235 | 6 | 244.6621
7855 | 36.43 | 42.4436 | 30.7641 | 257.6889 | 0.51355 |  | 7855 | 35.38 | 42.4436 | 5.7321 | 257.6889
7856 | 48.31 | 66.5065 | 49.5769 | 285.5346 | 0.51356 |  | 7856 | 46.1 | 66.5065 | 5 | 285.5346
7857 | 45.12 | 48.7681 | 54.1933 | 223.0298 | 0.51904 |  | 7857 | 48.81 | 48.7681 | 4 | 223.0298
7858 | 51.85 | 42.4669 | 46.7958 | 261.8253 | 0.51829 |  | 7858 | 51.58 | 42.4669 | 3 | 261.8253
7859 | 37.55 | 44.6955 | 42.1222 | 232.0209 | 0.52367 |  | 7859 | 57.66 | 44.6955 | 2.2679 | 232.0209
7860 | 39.81 | 47.6668 | 45.0494 | 252.1412 | 0.5288 |  | 7860 | 57.66 | 47.6668 | 2 | 252.1412
7861 | 39.81 | 49.2085 | 36.5013 | 232.5037 | 0.53422 |  | 7861 | 57.66 | 49.2085 | 2.2679 | 232.5037
7862 | 39.76 | 51.4516 | 41.0888 | 186.7666 | 0.53434 |  | 7862 | 50.76 | 51.4516 | 3 | 186.7666
7863 | 40.05 | 57.6718 | 61.1831 | 202.2719 | 0.54131 |  | 7863 | 52.51 | 57.6718 | 4 | 202.2719
7864 | 41.68 | 72.3704 | 33.6377 | 208.6281 | 0.54727 |  | 7864 | 55.04 | 72.3704 | 5 | 208.6281
7865 | 45.01 | 101.9237 | 38.3498 | 213.2202 | 0.5456 |  | 7865 | 58.52 | 101.9237 | 5.7321 | 213.2202
7866 | 50 | 148.0762 | 49.6059 | 226.3754 | 0.54032 |  | 7866 | 55.38 | 148.0762 | 6 | 226.3754
7867 | 51.77 | 162.038 | 28.0957 | 250.3636 | 0.54321 |  | 7867 | 62.11 | 162.038 | 5.7321 | 250.3636
7868 | 50.11 | 138.9088 | 38.6519 | 209.233 | 0.54785 |  | 7868 | 53.65 | 138.9088 | 5 | 209.233
7869 | 49.96 | 116.9288 | 36.7002 | 209.9988 | 0.54837 |  | 7869 | 51.08 | 116.9288 | 4 | 209.9988
7870 | 45.7 | 105.0298 | 31.31 | 148.6332 | 0.55447 |  | 7870 | 39.22 | 105.0298 | 3 | 148.6332
7871 | 44.64 | 76.3237 | 29.9526 | 150.6065 | 0.55432 |  | 7871 | 38.21 | 76.3237 | 2.2679 | 150.6065
7872 | 39.8 | 39.0771 | 38.3635 | 128.9341 | 0.55347 |  | 7872 | 37.88 | 39.0771 | 2 | 128.9341
7873 | 38.19 | 33.7366 | 28.0026 | 140.4335 | 0.55917 |  | 7873 | 33.99 | 33.7366 | 2.2679 | 140.4335
7874 | 36.3 | 32.1748 | 28.5372 | 86.8748 | 0.55049 |  | 7874 | 32.66 | 32.1748 | 3 | 86.8748
7875 | 36.02 | 30.63 | 238.1225 | 90.681 | 0.54317 |  | 7875 | 31.61 | 30.63 | 4 | 90.681
7876 | 35.4 | 29.2551 | 33.8072 | 133.9378 | 0.53682 |  | 7876 | 30.8 | 29.2551 | 5 | 133.9378
7877 | 35.38 | 28.3781 | 34.899 | 188.4397 | 0.53276 |  | 7877 | 29.58 | 28.3781 | 5.7321 | 188.4397
7878 | 37.84 | 27.9513 | 28.6953 | 253.2197 | 0.53542 |  | 7878 | 29.76 | 27.9513 | 6 | 253.2197
7879 | 50 | 27.6581 | 31.7043 | 227.3495 | 0.53459 |  | 7879 | 32.44 | 27.6581 | 5.7321 | 227.3495
7880 | 60.42 | 31.1889 | 37.7427 | 230.0298 | 0.52961 |  | 7880 | 35.59 | 31.1889 | 5 | 230.0298
7881 | 58.37 | 52.7416 | 51.7849 | 175.1804 | 0.52727 |  | 7881 | 43.9 | 52.7416 | 4 | 175.1804
7882 | 58.42 | 70.3734 | 42.0773 | 174.0151 | 0.52812 |  | 7882 | 46.27 | 70.3734 | 3 | 174.0151
7883 | 57.3 | 82.2765 | 42.3079 | 165.0412 | 0.53151 |  | 7883 | 45.5 | 82.2765 | 2.2679 | 165.0412
7884 | 58.26 | 77.0865 | 46.4353 | 127.4339 | 0.53152 |  | 7884 | 44.25 | 77.0865 | 2 | 127.4339
7885 | 58.77 | 82.9699 | 40.6664 | 129.9477 | 0.5314 |  | 7885 | 44.14 | 82.9699 | 2.2679 | 129.9477
7886 | 58.6 | 81.4954 | 45.4039 | 128.4149 | 0.52845 |  | 7886 | 43.1 | 81.4954 | 3 | 128.4149
7887 | 57.05 | 73.2042 | 22.7957 | 92.5236 | 0.52224 |  | 7887 | 43.14 | 73.2042 | 4 | 92.5236
7888 | 59.23 | 79.7043 | 35.4015 | 132.7859 | 0.51843 |  | 7888 | 42.82 | 79.7043 | 5 | 132.7859
7889 | 58.4 | 88.5233 | 40.4563 | 178.8589 | 0.51225 |  | 7889 | 44.85 | 88.5233 | 5.7321 | 178.8589
7890 | 63.45 | 131.7971 | 233.8382 | 194.6986 | 0.50025 |  | 7890 | 49.73 | 131.7971 | 6 | 194.6986
7891 | 59.36 | 154.6512 | 36.9531 | 206.1073 | 0.49451 |  | 7891 | 51.27 | 154.6512 | 5.7321 | 206.1073
7892 | 58.07 | 150.9713 | 29.643 | 182.9478 | 0.49584 |  | 7892 | 45.23 | 150.9713 | 5 | 182.9478
7893 | 53.93 | 117.4626 | 31.0298 | 190.7099 | 0.49772 |  | 7893 | 44.01 | 117.4626 | 4 | 190.7099
7894 | 50.17 | 110.9257 | 33.9101 | 217.3647 | 0.49764 |  | 7894 | 38.2 | 110.9257 | 3 | 217.3647
7895 | 45.28 | 91.1363 | 32.9192 | 189.6938 | 0.49677 |  | 7895 | 37.92 | 91.1363 | 2.2679 | 189.6938
7896 | 39.45 | 40.3875 | 26.615 | 201.6044 | 0.49585 |  | 7896 | 36.4 | 40.3875 | 2 | 201.6044
7897 | 39.07 | 33.3916 | 31.599 | 242.4577 | 0.49788 |  | 7897 | 33.33 | 33.3916 | 2.2679 | 242.4577
7898 | 38.43 | 31.9061 | 23.6654 | 183.5216 | 0.49466 |  | 7898 | 35.23 | 31.9061 | 3 | 183.5216
7899 | 36.2 | 30.3481 | 35.2585 | 268.3476 | 0.48861 |  | 7899 | 32.99 | 30.3481 | 4 | 268.3476
7900 | 35.91 | 29.1329 | 29.261 | 254.5501 | 0.48852 |  | 7900 | 32.02 | 29.1329 | 5 | 254.5501
7901 | 35.98 | 28.3922 | 38.9636 | 332.5378 | 0.4899 |  | 7901 | 31.05 | 28.3922 | 5.7321 | 332.5378
7902 | 38.01 | 27.8748 | 80.078 | 475.7411 | 0.4937 |  | 7902 | 31.18 | 27.8748 | 6 | 475.7411
7903 | 45.21 | 27.8695 | 103.7026 | 432.0637 | 0.4942 |  | 7903 | 34.85 | 27.8695 | 5.7321 | 432.0637
7904 | 53.39 | 31.4285 | 316.9899 | 404.4747 | 0.49042 |  | 7904 | 35.75 | 31.4285 | 5 | 404.4747
7905 | 54.79 | 52.3048 | 110.4754 | 397.5786 | 0.48293 |  | 7905 | 47.1 | 52.3048 | 4 | 397.5786
7906 | 54.58 | 68.3038 | 123.8039 | 354.1089 | 0.47692 |  | 7906 | 50.01 | 68.3038 | 3 | 354.1089
7907 | 54.79 | 73.5201 | 100.84 | 278.7522 | 0.4788 |  | 7907 | 49.62 | 73.5201 | 2.2679 | 278.7522
7908 | 54.05 | 75.6116 | 103.4701 | 274.5476 | 0.47338 |  | 7908 | 47.66 | 75.6116 | 2 | 274.5476
7909 | 52.91 | 79.485 | 111.4677 | 244.802 | 0.47459 |  | 7909 | 48.82 | 79.485 | 2.2679 | 244.802
7910 | 52.59 | 80.3228 | 80.4832 | 222.9059 | 0.4754 |  | 7910 | 47.44 | 80.3228 | 3 | 222.9059
7911 | 52.99 | 75.5986 | 60.7471 | 234.555 | 0.47402 |  | 7911 | 47.52 | 75.5986 | 4 | 234.555
7912 | 52.34 | 73.977 | 39.6906 | 197.1944 | 0.47357 |  | 7912 | 47.4 | 73.977 | 5 | 197.1944
7913 | 52.43 | 86.1009 | 49.1222 | 213.6967 | 0.46619 |  | 7913 | 48.33 | 86.1009 | 5.7321 | 213.6967
7914 | 54.55 | 122.55 | 39.8737 | 243.5398 | 0.46166 |  | 7914 | 50.04 | 122.55 | 6 | 243.5398
7915 | 54.52 | 149.3239 | 46.6794 | 223.5695 | 0.45994 |  | 7915 | 54.94 | 149.3239 | 5.7321 | 223.5695
7916 | 52.9 | 154.5016 | 25.0972 | 219.6887 | 0.45939 |  | 7916 | 48.33 | 154.5016 | 5 | 219.6887
7917 | 47.51 | 121.8404 | 40.8663 | 216.8082 | 0.46236 |  | 7917 | 49.44 | 121.8404 | 4 | 216.8082
7918 | 43.53 | 107.5948 | 35.8207 | 210.1167 | 0.46401 |  | 7918 | 43.52 | 107.5948 | 3 | 210.1167
7919 | 42.28 | 90.0756 | 27.2684 | 178.5536 | 0.46541 |  | 7919 | 39.12 | 90.0756 | 2.2679 | 178.5536
7920 | 37.74 | 39.9923 | 25.8486 | 122.9419 | 0.47287 |  | 7920 | 38.61 | 39.9923 | 2 | 122.9419
7921 | 36.2 | 32.2313 | 24.9965 | 174.415 | 0.46991 |  | 7921 | 34.68 | 32.2313 | 2.2679 | 174.415
7922 | 35.32 | 30.9322 | 31.1324 | 133.1619 | 0.46247 |  | 7922 | 42.44 | 30.9322 | 3 | 133.1619
7923 | 32.84 | 29.8087 | 25.0338 | 142.6557 | 0.45302 |  | 7923 | 32.79 | 29.8087 | 4 | 142.6557
7924 | 30.23 | 28.6871 | 31.3079 | 167.9662 | 0.45379 |  | 7924 | 34.56 | 28.6871 | 5 | 167.9662
7925 | 31.65 | 28.016 | 33.5983 | 226.9677 | 0.45761 |  | 7925 | 34.7 | 28.016 | 5.7321 | 226.9677
7926 | 34.8 | 27.7521 | 22.4201 | 298.2166 | 0.4728 |  | 7926 | 33 | 27.7521 | 6 | 298.2166
7927 | 41.94 | 44.2265 | 244.2084 | 245.7306 | 0.48208 |  | 7927 | 33.25 | 44.2265 | 5.7321 | 245.7306
7928 | 50.68 | 66.563 | 110.6002 | 251.2061 | 0.4675 |  | 7928 | 38.29 | 66.563 | 5 | 251.2061
7929 | 50.54 | 48.263 | 90.4532 | 264.2808 | 0.46578 |  | 7929 | 42.22 | 48.263 | 4 | 264.2808
7930 | 53.21 | 40.3529 | 84.7859 | 260.1877 | 0.45887 |  | 7930 | 44.1 | 40.3529 | 3 | 260.1877
7931 | 48.26 | 42.7211 | 94.7171 | 233.1318 | 0.45422 |  | 7931 | 46.76 | 42.7211 | 2.2679 | 233.1318
7932 | 45.38 | 45.0403 | 62.3411 | 274.903 | 0.4563 |  | 7932 | 48.92 | 45.0403 | 2 | 274.903
7933 | 44.12 | 49.4684 | 44.7534 | 210.2356 | 0.45292 |  | 7933 | 48.56 | 49.4684 | 2.2679 | 210.2356
7934 | 43.87 | 48.0867 | 42.2736 | 240.0033 | 0.45692 |  | 7934 | 47.91 | 48.0867 | 3 | 240.0033
7935 | 43.67 | 54.3696 | 47.1691 | 202.7025 | 0.45742 |  | 7935 | 43.97 | 54.3696 | 4 | 202.7025
7936 | 43.9 | 68.4171 | 43.3254 | 212.1374 | 0.453 |  | 7936 | 42.89 | 68.4171 | 5 | 212.1374
7937 | 44.88 | 101.1452 | 54.1189 | 247.5304 | 0.44328 |  | 7937 | 40.44 | 101.1452 | 5.7321 | 247.5304
7938 | 47.19 | 148.0229 | 59.6648 | 289.3472 | 0.44905 |  | 7938 | 45.3 | 148.0229 | 6 | 289.3472
7939 | 47.72 | 156.9198 | 62.7277 | 325.283 | 0.44359 |  | 7939 | 53.69 | 156.9198 | 5.7321 | 325.283
7940 | 44 | 144.0427 | 27.6988 | 331.9065 | 0.44159 |  | 7940 | 42.44 | 144.0427 | 5 | 331.9065
7941 | 42.55 | 118.5811 | 27.0133 | 278.1872 | 0.44309 |  | 7941 | 39.94 | 118.5811 | 4 | 278.1872
7942 | 39.4 | 103.5374 | 24.853 | 270.4997 | 0.44671 |  | 7942 | 34 | 103.5374 | 3 | 270.4997
7943 | 39 | 75.0315 | 32.3343 | 277.3621 | 0.44353 |  | 7943 | 34.53 | 75.0315 | 2.2679 | 277.3621
7944 | 38.58 | 37.2432 | 29.0225 | 294.0665 | 0.43962 |  | 7944 | 38 | 37.2432 | 2 | 294.0665
7945 | 40.34 | 34.3806 | 29.0298 | 289.4058 | 0.44176 |  | 7945 | 33.7 | 34.3806 | 2.2679 | 289.4058
7946 | 36.31 | 32.8161 | 29.3035 | 272.4486 | 0.43295 |  | 7946 | 32.58 | 32.8161 | 3 | 272.4486
7947 | 34 | 31.1138 | 27.619 | 271.9442 | 0.42046 |  | 7947 | 35 | 31.1138 | 4 | 271.9442
7948 | 31.95 | 29.6595 | 238.7478 | 327.0875 | 0.41084 |  | 7948 | 32.3 | 29.6595 | 5 | 327.0875
7949 | 28 | 28.6452 | 35.7435 | 320.3678 | 0.40193 |  | 7949 | 29.59 | 28.6452 | 5.7321 | 320.3678
7950 | 28.54 | 28.4624 | 229.089 | 366.5218 | 0.40483 |  | 7950 | 28.84 | 28.4624 | 6 | 366.5218
7951 | 38.02 | 43.9911 | 29.8057 | 397.8674 | 0.43646 |  | 7951 | 28.58 | 43.9911 | 5.7321 | 397.8674
7952 | 50 | 66.9685 | 58.3936 | 354.6846 | 0.44802 |  | 7952 | 30.41 | 66.9685 | 5 | 354.6846
7953 | 50.95 | 48.9878 | 40.0255 | 381.8083 | 0.44338 |  | 7953 | 32.99 | 48.9878 | 4 | 381.8083
7954 | 51.93 | 42.8509 | 62.4043 | 312.4163 | 0.44545 |  | 7954 | 39.41 | 42.8509 | 3 | 312.4163
7955 | 49.05 | 45.1818 | 91.4524 | 311.0863 | 0.44779 |  | 7955 | 37.48 | 45.1818 | 2.2679 | 311.0863
7956 | 49.27 | 46.547 | 108.5687 | 255.6235 | 0.4483 |  | 7956 | 35.37 | 46.547 | 2 | 255.6235
7957 | 47.2 | 51.1343 | 81.9836 | 154.372 | 0.45182 |  | 7957 | 38.13 | 51.1343 | 2.2679 | 154.372
7958 | 45.88 | 51.0237 | 53.8297 | 175.2142 | 0.45061 |  | 7958 | 39.75 | 51.0237 | 3 | 175.2142
7959 | 44.3 | 59.2843 | 42.6396 | 212.2614 | 0.44877 |  | 7959 | 40.77 | 59.2843 | 4 | 212.2614
7960 | 47.39 | 75.5818 | 41.3381 | 231.8412 | 0.45192 |  | 7960 | 34.64 | 75.5818 | 5 | 231.8412
7961 | 47.7 | 105.2495 | 35.5733 | 251.8034 | 0.45286 |  | 7961 | 34.2 | 105.2495 | 5.7321 | 251.8034
7962 | 60 | 154.0533 | 38.0915 | 320.6881 | 0.45027 |  | 7962 | 37.48 | 154.0533 | 6 | 320.6881
7963 | 56.1 | 164.5424 | 33.079 | 338.8283 | 0.44917 |  | 7963 | 49.93 | 164.5424 | 5.7321 | 338.8283
7964 | 54.5 | 136.0308 | 32.106 | 349.6917 | 0.4506 |  | 7964 | 51 | 136.0308 | 5 | 349.6917
7965 | 59.64 | 113.1281 | 28.0532 | 303.4334 | 0.45181 |  | 7965 | 51.3 | 113.1281 | 4 | 303.4334
7966 | 49.9 | 106.7131 | 25.8465 | 335.4939 | 0.45245 |  | 7966 | 47 | 106.7131 | 3 | 335.4939
7967 | 44.49 | 77.6335 | 30.5977 | 304.9382 | 0.45346 |  | 7967 | 42.77 | 77.6335 | 2.2679 | 304.9382
7968 | 40.72 | 39.9046 | 33.8666 | 283.0085 | 0.44957 |  | 7968 | 43.32 | 39.9046 | 2 | 283.0085
7969 | 41.57 | 34.4583 | 22.6988 | 314.277 | 0.45586 |  | 7969 | 34 | 34.4583 | 2.2679 | 314.277
7970 | 37.74 | 32.7698 | 28.3818 | 271.9505 | 0.46027 |  | 7970 | 27.06 | 32.7698 | 3 | 271.9505
7971 | 37.39 | 31.2135 | 26.5517 | 240.3543 | 0.45836 |  | 7971 | 29.6 | 31.2135 | 4 | 240.3543
7972 | 37.49 | 29.7869 | 25.3069 | 257.5725 | 0.45709 |  | 7972 | 25.12 | 29.7869 | 5 | 257.5725
7973 | 37.3 | 28.7647 | 32.1122 | 358.8595 | 0.44994 |  | 7973 | 29.6 | 28.7647 | 5.7321 | 358.8595
7974 | 36.5 | 28.533 | 34.6043 | 416.58 | 0.445 |  | 7974 | 26.81 | 28.533 | 6 | 416.58
7975 | 44.35 | 43.1634 | 36.7169 | 441.768 | 0.4534 |  | 7975 | 31.96 | 43.1634 | 5.7321 | 441.768
7976 | 54.71 | 68.2455 | 46.9833 | 398.1676 | 0.45238 |  | 7976 | 37.94 | 68.2455 | 5 | 398.1676
7977 | 56.49 | 49.8201 | 60.0715 | 357.4879 | 0.44943 |  | 7977 | 49 | 49.8201 | 4 | 357.4879
7978 | 59.43 | 42.0328 | 99.5774 | 382.2542 | 0.45314 |  | 7978 | 48.96 | 42.0328 | 3 | 382.2542
7979 | 57.94 | 44.3284 | 72.4534 | 325.6167 | 0.45699 |  | 7979 | 46.5 | 44.3284 | 2.2679 | 325.6167
7980 | 50 | 45.9581 | 43.0479 | 320.8881 | 0.45372 |  | 7980 | 40.51 | 45.9581 | 2 | 320.8881
7981 | 41.65 | 50.1592 | 46.2468 | 320.381 | 0.45159 |  | 7981 | 45.01 | 50.1592 | 2.2679 | 320.381
7982 | 43.62 | 51.024 | 37.1769 | 279.9088 | 0.45318 |  | 7982 | 38.8 | 51.024 | 3 | 279.9088
7983 | 47.91 | 58.6564 | 46.3824 | 279.7187 | 0.44585 |  | 7983 | 45.61 | 58.6564 | 4 | 279.7187
7984 | 51.04 | 75.6473 | 39.6724 | 231.4083 | 0.45715 |  | 7984 | 47.06 | 75.6473 | 5 | 231.4083
7985 | 52.14 | 107.998 | 49.4594 | 269.439 | 0.45857 |  | 7985 | 52.16 | 107.998 | 5.7321 | 269.439
7986 | 54.13 | 147.8537 | 42.2761 | 347.2832 | 0.45116 |  | 7986 | 59.7 | 147.8537 | 6 | 347.2832
7987 | 54.03 | 170.7883 | 45.0568 | 337.8347 | 0.45576 |  | 7987 | 66.42 | 170.7883 | 5.7321 | 337.8347
7988 | 49.13 | 144.5337 | 29.4885 | 486.6239 | 0.46086 |  | 7988 | 57.4 | 144.5337 | 5 | 486.6239
7989 | 50.61 | 116.7199 | 31.2603 | 361.2178 | 0.46661 |  | 7989 | 54.13 | 116.7199 | 4 | 361.2178
7990 | 42.78 | 108.7763 | 31.954 | 457.1421 | 0.47555 |  | 7990 | 51.4 | 108.7763 | 3 | 457.1421
7991 | 42.24 | 78.0757 | 28.1556 | 351.3028 | 0.47838 |  | 7991 | 39.94 | 78.0757 | 2.2679 | 351.3028
7992 | 39.28 | 40.554 | 30.5478 | 308.839 | 0.47837 |  | 7992 | 37.44 | 40.554 | 2 | 308.839
7993 | 36.29 | 33.5848 | 38.8641 | 360.0699 | 0.48038 |  | 7993 | 34.59 | 33.5848 | 2.2679 | 360.0699
7994 | 38.79 | 32.0363 | 35.1662 | 396.4711 | 0.48754 |  | 7994 | 36.92 | 32.0363 | 3 | 396.4711
7995 | 36.44 | 30.4731 | 30.6817 | 323.1752 | 0.48655 |  | 7995 | 42.2 | 30.4731 | 4 | 323.1752
7996 | 35.39 | 29.2269 | 23.762 | 366.0933 | 0.49037 |  | 7996 | 34.81 | 29.2269 | 5 | 366.0933
7997 | 35.39 | 28.5075 | 34.5546 | 493.4039 | 0.48953 |  | 7997 | 34.43 | 28.5075 | 5.7321 | 493.4039
7998 | 36.03 | 28.4973 | 57.3131 | 545.6436 | 0.49192 |  | 7998 | 34.89 | 28.4973 | 6 | 545.6436
7999 | 36.56 | 43.3318 | 92.921 | 553.2904 | 0.49034 |  | 7999 | 35 | 43.3318 | 5.7321 | 553.2904
8000 | 44.08 | 66.5712 | 294.2266 | 558.2592 | 0.49516 |  | 8000 | 33.45 | 66.5712 | 5 | 558.2592
8001 | 42.29 | 50.9813 | 55.2979 | 452.9326 | 0.4883 |  | 8001 | 45 | 50.9813 | 4 | 452.9326
8002 | 45.35 | 44.2895 | 60.6396 | 364.3668 | 0.48894 |  | 8002 | 55.21 | 44.2895 | 3 | 364.3668
8003 | 44 | 48.3981 | 43.8652 | 428.1142 | 0.48867 |  | 8003 | 50.45 | 48.3981 | 2.2679 | 428.1142
8004 | 42.7 | 47.5768 | 36.663 | 371.6915 | 0.48876 |  | 8004 | 46.01 | 47.5768 | 2 | 371.6915
8005 | 41.5 | 51.6097 | 52.0332 | 406.3613 | 0.48854 |  | 8005 | 45.94 | 51.6097 | 2.2679 | 406.3613
8006 | 40.77 | 52.1779 | 42.0041 | 346.6457 | 0.48512 |  | 8006 | 44.05 | 52.1779 | 3 | 346.6457
8007 | 41.14 | 60.5893 | 41.6567 | 425.4815 | 0.48814 |  | 8007 | 44.76 | 60.5893 | 4 | 425.4815
8008 | 43.02 | 77.8666 | 249.8187 | 318.9774 | 0.4874 |  | 8008 | 46.53 | 77.8666 | 5 | 318.9774
8009 | 48.76 | 107.7546 | 53.3247 | 369.8148 | 0.48893 |  | 8009 | 53.91 | 107.7546 | 5.7321 | 369.8148
8010 | 52.9 | 145.056 | 38.0254 | 470.0086 | 0.48719 |  | 8010 | 57.26 | 145.056 | 6 | 470.0086
8011 | 53.1 | 165.1126 | 47.9217 | 394.7018 | 0.49033 |  | 8011 | 59.05 | 165.1126 | 5.7321 | 394.7018
8012 | 50.01 | 145.5415 | 34.2123 | 375.837 | 0.49642 |  | 8012 | 67.61 | 145.5415 | 5 | 375.837
8013 | 47.35 | 115.6869 | 31.2418 | 437.1377 | 0.49909 |  | 8013 | 57.97 | 115.6869 | 4 | 437.1377
8014 | 42.42 | 108.8063 | 29.7912 | 320.4085 | 0.50149 |  | 8014 | 44.49 | 108.8063 | 3 | 320.4085
8015 | 41.94 | 77.1541 | 30.3659 | 329.4746 | 0.50245 |  | 8015 | 35.9 | 77.1541 | 2.2679 | 329.4746
8016 | 40.13 | 39.066 | 29.6777 | 330.7697 | 0.50367 |  | 8016 | 34.34 | 39.066 | 2 | 330.7697
8017 | 38.55 | 34.6821 | 28.2908 | 378.8749 | 0.50973 |  | 8017 | 30.38 | 34.6821 | 2.2679 | 378.8749
8018 | 37.07 | 32.9401 | 24.5351 | 322.0455 | 0.51221 |  | 8018 | 33.04 | 32.9401 | 3 | 322.0455
8019 | 36.26 | 31.2479 | 33.687 | 320.1858 | 0.51978 |  | 8019 | 30.53 | 31.2479 | 4 | 320.1858
8020 | 35.93 | 29.7224 | 24.7622 | 296.4497 | 0.51625 |  | 8020 | 31.72 | 29.7224 | 5 | 296.4497
8021 | 35.86 | 28.7194 | 27.1313 | 384.353 | 0.51055 |  | 8021 | 30.33 | 28.7194 | 5.7321 | 384.353
8022 | 35.92 | 28.5471 | 28.1201 | 407.9974 | 0.51318 |  | 8022 | 30.23 | 28.5471 | 6 | 407.9974
8023 | 36.13 | 43.7359 | 27.1903 | 451.0631 | 0.51534 |  | 8023 | 29.93 | 43.7359 | 5.7321 | 451.0631
8024 | 37.04 | 66.8927 | 51.2714 | 525.3976 | 0.51234 |  | 8024 | 40.59 | 66.8927 | 5 | 525.3976
8025 | 38.74 | 51.1169 | 48.916 | 383.2957 | 0.51254 |  | 8025 | 35 | 51.1169 | 4 | 383.2957
8026 | 42.12 | 43.9599 | 46.3907 | 395.8109 | 0.51409 |  | 8026 | 46.9 | 43.9599 | 3 | 395.8109
8027 | 44.77 | 46.4622 | 31.4223 | 308.1904 | 0.50989 |  | 8027 | 52.07 | 46.4622 | 2.2679 | 308.1904
8028 | 48 | 47.7086 | 39.6988 | 322.2257 | 0.51093 |  | 8028 | 52.36 | 47.7086 | 2 | 322.2257
8029 | 48.15 | 52.6315 | 42.6225 | 314.6473 | 0.51534 |  | 8029 | 44.46 | 52.6315 | 2.2679 | 314.6473
8030 | 45.76 | 55.0074 | 43.2301 | 209.6865 | 0.51883 |  | 8030 | 47.3 | 55.0074 | 3 | 209.6865
8031 | 44.7 | 60.3414 | 40.0618 | 155.3729 | 0.51888 |  | 8031 | 46.9 | 60.3414 | 4 | 155.3729
8032 | 44.98 | 75.9211 | 47.6455 | 236.0907 | 0.51865 |  | 8032 | 48.3 | 75.9211 | 5 | 236.0907
8033 | 47.79 | 102.6116 | 56.1782 | 315.7098 | 0.51526 |  | 8033 | 43.48 | 102.6116 | 5.7321 | 315.7098
8034 | 50.45 | 151.743 | 38.245 | 415.8762 | 0.5099 |  | 8034 | 51.3 | 151.743 | 6 | 415.8762
8035 | 52.4 | 170.6538 | 52.1455 | 344.8499 | 0.50525 |  | 8035 | 54.74 | 170.6538 | 5.7321 | 344.8499
8036 | 50.1 | 138.6692 | 30.3934 | 462.0134 | 0.50458 |  | 8036 | 46.9 | 138.6692 | 5 | 462.0134
8037 | 43.5 | 116.2633 | 33.0622 | 384.0212 | 0.50912 |  | 8037 | 48 | 116.2633 | 4 | 384.0212
8038 | 42.07 | 106.7495 | 22.7403 | 420.3589 | 0.50931 |  | 8038 | 36.12 | 106.7495 | 3 | 420.3589
8039 | 39.9 | 77.926 | 27.8354 | 433.4588 | 0.51053 |  | 8039 | 34.94 | 77.926 | 2.2679 | 433.4588
8040 | 37.83 | 39.978 | 31.6087 | 347.8734 | 0.51161 |  | 8040 | 31.95 | 39.978 | 2 | 347.8734
8041 | 36.03 | 32.7358 | 22.9288 | 421.336 | 0.51227 |  | 8041 | 30.19 | 32.7358 | 2.2679 | 421.336
8042 | 36.93 | 31.3489 | 31.6874 | 405.9562 | 0.5017 |  | 8042 | 32.42 | 31.3489 | 3 | 405.9562
8043 | 35.4 | 30.1099 | 29.4703 | 397.3044 | 0.49471 |  | 8043 | 29.76 | 30.1099 | 4 | 397.3044
8044 | 34.46 | 28.8855 | 28.5082 | 377.7208 | 0.48604 |  | 8044 | 29.76 | 28.8855 | 5 | 377.7208
8045 | 35.4 | 28.0824 | 28.4166 | 487.856 | 0.48354 |  | 8045 | 29.88 | 28.0824 | 5.7321 | 487.856
8046 | 36.3 | 27.6213 | 27.2532 | 569.5812 | 0.4858 |  | 8046 | 30.69 | 27.6213 | 6 | 569.5812
8047 | 44.72 | 27.4275 | 27.8336 | 562.5557 | 0.48074 |  | 8047 | 30.66 | 27.4275 | 5.7321 | 562.5557
8048 | 52.97 | 30.6021 | 41.3769 | 464.2598 | 0.48882 |  | 8048 | 32.44 | 30.6021 | 5 | 464.2598
8049 | 55 | 54.6993 | 36.4575 | 410.4932 | 0.48923 |  | 8049 | 35.39 | 54.6993 | 4 | 410.4932
8050 | 54.09 | 69.138 | 43.6981 | 449.318 | 0.4897 |  | 8050 | 58.49 | 69.138 | 3 | 449.318
8051 | 46.81 | 76.9283 | 39.581 | 374.5341 | 0.48901 |  | 8051 | 62.29 | 76.9283 | 2.2679 | 374.5341
8052 | 45.03 | 75.9532 | 54.0255 | 404.9016 | 0.49368 |  | 8052 | 59.1 | 75.9532 | 2 | 404.9016
8053 | 41.96 | 80.2759 | 49.4244 | 416.0943 | 0.49232 |  | 8053 | 60.28 | 80.2759 | 2.2679 | 416.0943
8054 | 44.28 | 77.3813 | 40.4802 | 431.455 | 0.50048 |  | 8054 | 33.99 | 77.3813 | 3 | 431.455
8055 | 49.71 | 71.7333 | 41.9061 | 458.0278 | 0.51104 |  | 8055 | 45.83 | 71.7333 | 4 | 458.0278
8056 | 52.95 | 75.3506 | 48.7207 | 378.2101 | 0.51357 |  | 8056 | 33.54 | 75.3506 | 5 | 378.2101
8057 | 59.05 | 89.6129 | 51.9698 | 495.2406 | 0.50756 |  | 8057 | 33.62 | 89.6129 | 5.7321 | 495.2406
8058 | 73.93 | 134.3323 | 43.2024 | 442.1736 | 0.51035 |  | 8058 | 47 | 134.3323 | 6 | 442.1736
8059 | 66.22 | 158.4123 | 45.3357 | 397.5867 | 0.51425 |  | 8059 | 50 | 158.4123 | 5.7321 | 397.5867
8060 | 60 | 139.0543 | 32.606 | 522.6904 | 0.5124 |  | 8060 | 34.03 | 139.0543 | 5 | 522.6904
8061 | 54.43 | 110.5227 | 27.6226 | 523.275 | 0.51405 |  | 8061 | 34.03 | 110.5227 | 4 | 523.275
8062 | 49.33 | 99.5631 | 27.8942 | 471.0716 | 0.51229 |  | 8062 | 39.94 | 99.5631 | 3 | 471.0716
8063 | 42.99 | 86.8539 | 31.9871 | 383.1067 | 0.51368 |  | 8063 | 40.1 | 86.8539 | 2.2679 | 383.1067
8064 | 40.58 | 39.2409 | 19.9958 | 321.9437 | 0.5147 |  | 8064 | 33.5 | 39.2409 | 2 | 321.9437
8065 | 40.04 | 35.2673 | 32.9392 | 383.5832 | 0.5142 |  | 8065 | 32.07 | 35.2673 | 2.2679 | 383.5832
8066 | 37.32 | 33.5542 | 31.1069 | 276.594 | 0.51461 |  | 8066 | 32.39 | 33.5542 | 3 | 276.594
8067 | 38.24 | 31.7673 | 33.9164 | 292.5026 | 0.51687 |  | 8067 | 31.71 | 31.7673 | 4 | 292.5026
8068 | 38.16 | 30.1691 | 23.4937 | 300.8572 | 0.52048 |  | 8068 | 30.15 | 30.1691 | 5 | 300.8572
8069 | 39.42 | 29.064 | 45.5594 | 410.3298 | 0.52173 |  | 8069 | 29.94 | 29.064 | 5.7321 | 410.3298
8070 | 42.81 | 28.3709 | 101.3945 | 429.5739 | 0.52225 |  | 8070 | 29.99 | 28.3709 | 6 | 429.5739
8071 | 55.07 | 27.9095 | 316.6724 | 339.2521 | 0.51616 |  | 8071 | 31.44 | 27.9095 | 5.7321 | 339.2521
8072 | 67.28 | 30.9519 | 126.1754 | 426.7965 | 0.51844 |  | 8072 | 31.87 | 30.9519 | 5 | 426.7965
8073 | 76.47 | 55.2535 | 123.3389 | 383.91 | 0.51457 |  | 8073 | 46.06 | 55.2535 | 4 | 383.91
8074 | 71 | 67.9018 | 86.6956 | 397.5648 | 0.51078 |  | 8074 | 63.75 | 67.9018 | 3 | 397.5648
8075 | 60.49 | 75.4753 | 51.6597 | 376.0817 | 0.50746 |  | 8075 | 79.66 | 75.4753 | 2.2679 | 376.0817
8076 | 59.31 | 78.3008 | 102.8882 | 238.988 | 0.50466 |  | 8076 | 74.51 | 78.3008 | 2 | 238.988
8077 | 55.24 | 80.4497 | 136.1415 | 190.5547 | 0.50786 |  | 8077 | 69.94 | 80.4497 | 2.2679 | 190.5547
8078 | 53.3 | 80.7574 | 111.9721 | 239.0788 | 0.50873 |  | 8078 | 68.11 | 80.7574 | 3 | 239.0788
8079 | 56.63 | 76.5323 | 82.732 | 241.8808 | 0.50967 |  | 8079 | 68.26 | 76.5323 | 4 | 241.8808
8080 | 57.59 | 75.6163 | 43.4655 | 255.4307 | 0.51307 |  | 8080 | 67.17 | 75.6163 | 5 | 255.4307
8081 | 60 | 85.3118 | 31.3706 | 351.8163 | 0.50996 |  | 8081 | 56 | 85.3118 | 5.7321 | 351.8163
8082 | 71.84 | 123.8255 | 50.3219 | 383.1433 | 0.50591 |  | 8082 | 65 | 123.8255 | 6 | 383.1433
8083 | 49.9 | 141.7764 | 246.5801 | 337.7086 | 0.50192 |  | 8083 | 135 | 141.7764 | 5.7321 | 337.7086
8084 | 47.32 | 153.1138 | 34.3077 | 423.8596 | 0.49974 |  | 8084 | 80 | 153.1138 | 5 | 423.8596
8085 | 42.67 | 118.0022 | 36.6758 | 396.6176 | 0.49883 |  | 8085 | 42.44 | 118.0022 | 4 | 396.6176
8086 | 41.48 | 104.7299 | 32.0411 | 342.0058 | 0.50025 |  | 8086 | 36.84 | 104.7299 | 3 | 342.0058
8087 | 38.47 | 89.629 | 27.3272 | 316.5607 | 0.49539 |  | 8087 | 47.91 | 89.629 | 2.2679 | 316.5607
8088 | 37.05 | 42.0074 | 24.5054 | 296.0223 | 0.49604 |  | 8088 | 40.1 | 42.0074 | 2 | 296.0223
8089 | 35 | 34.9526 | 30.1717 | 324.45 | 0.49784 |  | 8089 | 36.03 | 34.9526 | 2.2679 | 324.45
8090 | 35 | 33.1615 | 33.3525 | 286.7818 | 0.49087 |  | 8090 | 32.9 | 33.1615 | 3 | 286.7818
8091 | 35.24 | 31.4075 | 29.8805 | 280.7125 | 0.49125 |  | 8091 | 33.11 | 31.4075 | 4 | 280.7125
8092 | 35.58 | 29.9397 | 26.9201 | 305.9715 | 0.49764 |  | 8092 | 33.22 | 29.9397 | 5 | 305.9715
8093 | 36.29 | 28.9933 | 33.6598 | 438.499 | 0.5048 |  | 8093 | 33.05 | 28.9933 | 5.7321 | 438.499
8094 | 36.94 | 28.5169 | 49.3436 | 463.0276 | 0.50699 |  | 8094 | 33.14 | 28.5169 | 6 | 463.0276
8095 | 43.26 | 44.6419 | 99.2338 | 432.0859 | 0.50832 |  | 8095 | 32.7 | 44.6419 | 5.7321 | 432.0859
8096 | 53.4 | 66.1708 | 92.4654 | 473.6187 | 0.5139 |  | 8096 | 33.48 | 66.1708 | 5 | 473.6187
8097 | 54.76 | 49.7188 | 66.6108 | 447.3234 | 0.51693 |  | 8097 | 35.23 | 49.7188 | 4 | 447.3234
8098 | 58.01 | 41.9887 | 77.5106 | 412.4877 | 0.52113 |  | 8098 | 36.26 | 41.9887 | 3 | 412.4877
8099 | 57.4 | 44.6637 | 123.8684 | 312.7393 | 0.52304 |  | 8099 | 36.86 | 44.6637 | 2.2679 | 312.7393
8100 | 52.07 | 45.0836 | 79.9666 | 376.6766 | 0.51698 |  | 8100 | 36.83 | 45.0836 | 2 | 376.6766
8101 | 49.9 | 48.8513 | 41.6356 | 337.2846 | 0.51317 |  | 8101 | 36.81 | 48.8513 | 2.2679 | 337.2846
8102 | 51.49 | 52.1296 | 67.1768 | 277.1735 | 0.52261 |  | 8102 | 36.23 | 52.1296 | 3 | 277.1735
8103 | 56.11 | 57.9156 | 44.7313 | 328.466 | 0.52659 |  | 8103 | 34.94 | 57.9156 | 4 | 328.466
8104 | 58.3 | 72.4429 | 249.364 | 298.4899 | 0.52389 |  | 8104 | 34.8 | 72.4429 | 5 | 298.4899
8105 | 62.69 | 107.1668 | 62.6523 | 298.3452 | 0.5224 |  | 8105 | 36.9 | 107.1668 | 5.7321 | 298.3452
8106 | 77.83 | 150.1549 | 78.4977 | 371.7042 | 0.5196 |  | 8106 | 52 | 150.1549 | 6 | 371.7042
8107 | 77.51 | 162.0142 | 32.0589 | 416.4652 | 0.51598 |  | 8107 | 64.6 | 162.0142 | 5.7321 | 416.4652
8108 | 60.1 | 156.4503 | 33.1959 | 408.2254 | 0.51499 |  | 8108 | 58.94 | 156.4503 | 5 | 408.2254
8109 | 52.93 | 123.3086 | 31.5501 | 370.7621 | 0.51411 |  | 8109 | 44.94 | 123.3086 | 4 | 370.7621
8110 | 45 | 110.7549 | 30.6926 | 309.9838 | 0.52177 |  | 8110 | 40 | 110.7549 | 3 | 309.9838
8111 | 40.63 | 79.8978 | 29.1855 | 334.0215 | 0.52244 |  | 8111 | 36.17 | 79.8978 | 2.2679 | 334.0215
8112 | 37.57 | 41.0343 | 32.5775 | 249.246 | 0.52337 |  | 8112 | 36.12 | 41.0343 | 2 | 249.246
8113 | 36.16 | 34.3646 | 29.318 | 305.1581 | 0.52526 |  | 8113 | 35.31 | 34.3646 | 2.2679 | 305.1581
8114 | 35.73 | 32.7747 | 34.4811 | 310.6638 | 0.51854 |  | 8114 | 35.6 | 32.7747 | 3 | 310.6638
8115 | 35.86 | 31.287 | 31.2504 | 250.6838 | 0.51605 |  | 8115 | 35.02 | 31.287 | 4 | 250.6838
8116 | 35.75 | 29.8862 | 29.9184 | 353.2886 | 0.51383 |  | 8116 | 35.35 | 29.8862 | 5 | 353.2886
8117 | 35.56 | 28.7495 | 26.1197 | 413.229 | 0.50878 |  | 8117 | 35.42 | 28.7495 | 5.7321 | 413.229
8118 | 36 | 28.2708 | 30.329 | 453.4238 | 0.50655 |  | 8118 | 34.58 | 28.2708 | 6 | 453.4238
8119 | 37.14 | 43.2522 | 27.0454 | 426.1647 | 0.50756 |  | 8119 | 34.87 | 43.2522 | 5.7321 | 426.1647
8120 | 48.3 | 66.0103 | 38.3166 | 363.8294 | 0.50747 |  | 8120 | 34.97 | 66.0103 | 5 | 363.8294
8121 | 58.29 | 50.2686 | 52.0312 | 377.5458 | 0.50787 |  | 8121 | 37.44 | 50.2686 | 4 | 377.5458
8122 | 61.66 | 42.73 | 53.5876 | 354.7224 | 0.50663 |  | 8122 | 35.4 | 42.73 | 3 | 354.7224
8123 | 57.15 | 44.5322 | 55.2992 | 335.38 | 0.50274 |  | 8123 | 39.94 | 44.5322 | 2.2679 | 335.38
8124 | 45.72 | 47.1458 | 105.9109 | 355.1568 | 0.50249 |  | 8124 | 35.88 | 47.1458 | 2 | 355.1568
8125 | 41.95 | 50.3009 | 130.2401 | 313.7155 | 0.49627 |  | 8125 | 35.78 | 50.3009 | 2.2679 | 313.7155
8126 | 41.86 | 52.2721 | 122.6961 | 276.7497 | 0.49626 |  | 8126 | 35.56 | 52.2721 | 3 | 276.7497
8127 | 40.38 | 57.1167 | 71.3182 | 276.2069 | 0.49326 |  | 8127 | 35.14 | 57.1167 | 4 | 276.2069
8128 | 42.74 | 73.7767 | 37.3672 | 261.153 | 0.48864 |  | 8128 | 34.2 | 73.7767 | 5 | 261.153
8129 | 44.9 | 105.7952 | 38.1744 | 274.2236 | 0.4792 |  | 8129 | 35.68 | 105.7952 | 5.7321 | 274.2236
8130 | 44.9 | 143.2133 | 47.2404 | 353.5708 | 0.47215 |  | 8130 | 44 | 143.2133 | 6 | 353.5708
8131 | 40.41 | 157.2483 | 39.0389 | 305.7233 | 0.46484 |  | 8131 | 50.1 | 157.2483 | 5.7321 | 305.7233
8132 | 39.9 | 137.8169 | 31.5322 | 373.2999 | 0.46557 |  | 8132 | 53.01 | 137.8169 | 5 | 373.2999
8133 | 39.35 | 117.3166 | 30.3893 | 341.4119 | 0.46362 |  | 8133 | 50 | 117.3166 | 4 | 341.4119
8134 | 36.45 | 110.2981 | 33.1121 | 287.1282 | 0.4567 |  | 8134 | 50.1 | 110.2981 | 3 | 287.1282
8135 | 35.23 | 78.5236 | 31.7411 | 352.6451 | 0.44164 |  | 8135 | 44 | 78.5236 | 2.2679 | 352.6451
8136 | 32 | 39.804 | 29.3927 | 314.4242 | 0.42507 |  | 8136 | 39.94 | 39.804 | 2 | 314.4242
8137 | 33.55 | 32.8348 | 232.2018 | 246.9992 | 0.42534 |  | 8137 | 35.72 | 32.8348 | 2.2679 | 246.9992
8138 | 31.2 | 31.6033 | 23.0173 | 294.6588 | 0.41358 |  | 8138 | 32.84 | 31.6033 | 3 | 294.6588
8139 | 22 | 30.217 | 33.434 | 274.7257 | 0.40898 |  | 8139 | 32.26 | 30.217 | 4 | 274.7257
8140 | 15.4 | 28.9358 | 30.2474 | 280.9312 | 0.40805 |  | 8140 | 31.98 | 28.9358 | 5 | 280.9312
8141 | 21.14 | 28.2027 | 34.2763 | 301.9042 | 0.40757 |  | 8141 | 31.96 | 28.2027 | 5.7321 | 301.9042
8142 | 27.67 | 28.0279 | 64.3302 | 333.4937 | 0.41573 |  | 8142 | 31.7 | 28.0279 | 6 | 333.4937
8143 | 32.9 | 43.3864 | 56.9391 | 458.2199 | 0.44048 |  | 8143 | 33.85 | 43.3864 | 5.7321 | 458.2199
8144 | 40.7 | 64.8961 | 68.0157 | 403.2838 | 0.45945 |  | 8144 | 41.59 | 64.8961 | 5 | 403.2838
8145 | 41.31 | 48.6734 | 110.0333 | 283.0343 | 0.46538 |  | 8145 | 62.67 | 48.6734 | 4 | 283.0343
8146 | 49.9 | 40.7692 | 103.4863 | 288.0864 | 0.46414 |  | 8146 | 65 | 40.7692 | 3 | 288.0864
8147 | 50.8 | 41.288 | 89.6663 | 232.7462 | 0.46264 |  | 8147 | 59.26 | 41.288 | 2.2679 | 232.7462
8148 | 48.5 | 42.8251 | 49.7329 | 260.8144 | 0.46198 |  | 8148 | 51.69 | 42.8251 | 2 | 260.8144
8149 | 44.55 | 47.1542 | 73.1657 | 184.098 | 0.46021 |  | 8149 | 48.71 | 47.1542 | 2.2679 | 184.098
8150 | 43.6 | 46.5439 | 114.8281 | 156.4188 | 0.45852 |  | 8150 | 41.83 | 46.5439 | 3 | 156.4188
8151 | 40.48 | 53.1494 | 82.3935 | 172.3933 | 0.45687 |  | 8151 | 41.1 | 53.1494 | 4 | 172.3933
8152 | 42.25 | 69.5352 | 40.7098 | 188.5022 | 0.45598 |  | 8152 | 60.33 | 69.5352 | 5 | 188.5022
8153 | 44.66 | 102.7148 | 36.5845 | 237.2349 | 0.45425 |  | 8153 | 62.54 | 102.7148 | 5.7321 | 237.2349
8154 | 44.1 | 142.6326 | 35.5267 | 256.5038 | 0.45138 |  | 8154 | 63.55 | 142.6326 | 6 | 256.5038
8155 | 38.99 | 155.1254 | 40.5244 | 244.8606 | 0.45216 |  | 8155 | 78.61 | 155.1254 | 5.7321 | 244.8606
8156 | 37.18 | 140.4171 | 33.7389 | 242.1227 | 0.45026 |  | 8156 | 59.5 | 140.4171 | 5 | 242.1227
8157 | 35.1 | 113.1846 | 29.2295 | 209.8073 | 0.45312 |  | 8157 | 57.52 | 113.1846 | 4 | 209.8073
8158 | 35.98 | 105.7411 | 31.4255 | 202.4722 | 0.4573 |  | 8158 | 49.4 | 105.7411 | 3 | 202.4722
8159 | 36 | 75.3372 | 28.8397 | 188.1365 | 0.44848 |  | 8159 | 42.23 | 75.3372 | 2.2679 | 188.1365
8160 | 33.3 | 38.2124 | 22.4818 | 157.1013 | 0.43872 |  | 8160 | 34.99 | 38.2124 | 2 | 157.1013
8161 | 30.7 | 35.9175 | 228.4167 | 177.0696 | 0.42957 |  | 8161 | 33.51 | 35.9175 | 2.2679 | 177.0696
8162 | 33.9 | 33.8497 | 24.629 | 155.3027 | 0.43717 |  | 8162 | 33.05 | 33.8497 | 3 | 155.3027
8163 | 30 | 31.9291 | 31.2314 | 159.7739 | 0.43569 |  | 8163 | 31.3 | 31.9291 | 4 | 159.7739
8164 | 27.86 | 30.2724 | 28.3642 | 158.4124 | 0.43538 |  | 8164 | 31.53 | 30.2724 | 5 | 158.4124
8165 | 25.5 | 29.1128 | 25.9622 | 234.5511 | 0.43276 |  | 8165 | 31.39 | 29.1128 | 5.7321 | 234.5511
8166 | 31.5 | 28.858 | 56.1556 | 244.0999 | 0.43665 |  | 8166 | 31.2 | 28.858 | 6 | 244.0999
8167 | 32.5 | 44.8143 | 68.781 | 283.3958 | 0.44033 |  | 8167 | 31.39 | 44.8143 | 5.7321 | 283.3958
8168 | 33.9 | 65.2896 | 40.6777 | 235.9694 | 0.45423 |  | 8168 | 34.05 | 65.2896 | 5 | 235.9694
8169 | 33 | 50.7625 | 76.9439 | 253.1323 | 0.47045 |  | 8169 | 53.07 | 50.7625 | 4 | 253.1323
8170 | 41.95 | 43.1066 | 98.7766 | 225.6413 | 0.48542 |  | 8170 | 80.09 | 43.1066 | 3 | 225.6413
8171 | 39.29 | 45.0749 | 73.1009 | 189.3798 | 0.489 |  | 8171 | 76 | 45.0749 | 2.2679 | 189.3798
8172 | 39.16 | 47.4525 | 44.4203 | 155.4462 | 0.49105 |  | 8172 | 67.21 | 47.4525 | 2 | 155.4462
8173 | 37.5 | 53.9074 | 45.9892 | 165.0616 | 0.49666 |  | 8173 | 58.99 | 53.9074 | 2.2679 | 165.0616
8174 | 36.26 | 54.3628 | 49.6195 | 181.5686 | 0.4923 |  | 8174 | 56.77 | 54.3628 | 3 | 181.5686
8175 | 39.08 | 60.0002 | 47.3053 | 194.3432 | 0.48942 |  | 8175 | 58.12 | 60.0002 | 4 | 194.3432
8176 | 39.41 | 77.8695 | 45.3752 | 211.5763 | 0.49201 |  | 8176 | 60.12 | 77.8695 | 5 | 211.5763
8177 | 44.72 | 108.7516 | 32.2655 | 201.7005 | 0.49132 |  | 8177 | 65.38 | 108.7516 | 5.7321 | 201.7005
8178 | 48.46 | 153.0149 | 47.1129 | 239.3295 | 0.48359 |  | 8178 | 72.97 | 153.0149 | 6 | 239.3295
8179 | 51.4 | 171.7824 | 45.766 | 255.2802 | 0.48299 |  | 8179 | 89.25 | 171.7824 | 5.7321 | 255.2802
8180 | 43.13 | 142.5086 | 27.1511 | 243.9206 | 0.47892 |  | 8180 | 82.71 | 142.5086 | 5 | 243.9206
8181 | 35.17 | 119.7935 | 29.3748 | 233.6401 | 0.47176 |  | 8181 | 75 | 119.7935 | 4 | 233.6401
8182 | 35.05 | 110.9369 | 29.2252 | 191.6036 | 0.46288 |  | 8182 | 55.86 | 110.9369 | 3 | 191.6036
8183 | 36.07 | 78.359 | 24.4113 | 204.7476 | 0.45211 |  | 8183 | 39.82 | 78.359 | 2.2679 | 204.7476
8184 | 30.48 | 41.322 | 32.989 | 195.7041 | 0.4415 |  | 8184 | 35 | 41.322 | 2 | 195.7041
8185 | 21.97 | 35.3264 | 33.56 | 230.4794 | 0.42727 |  | 8185 | 34.08 | 35.3264 | 2.2679 | 230.4794
8186 | 20.76 | 33.6828 | 28.4302 | 160.5545 | 0.40932 |  | 8186 | 32.54 | 33.6828 | 3 | 160.5545
8187 | 7.09 | 31.9248 | 28.8917 | 252.6859 | 0.40181 |  | 8187 | 32.2 | 31.9248 | 4 | 252.6859
8188 | 1.14 | 30.29 | 28.4869 | 209.6758 | 0.39986 |  | 8188 | 31.4 | 30.29 | 5 | 209.6758
8189 | 0.01 | 29.0864 | 36.3331 | 300.9389 | 0.41228 |  | 8189 | 30.05 | 29.0864 | 5.7321 | 300.9389
8190 | 0 | 28.6862 | 23.9321 | 318.1129 | 0.40713 |  | 8190 | 30.57 | 28.6862 | 6 | 318.1129
8191 | 0.01 | 43.1905 | 29.2262 | 309.6209 | 0.40074 |  | 8191 | 31.53 | 43.1905 | 5.7321 | 309.6209
8192 | 2.22 | 64.0687 | 51.1169 | 301.4517 | 0.40207 |  | 8192 | 32.96 | 64.0687 | 5 | 301.4517
8193 | 29.9 | 49.85 | 50.6221 | 240.4104 | 0.40799 |  | 8193 | 45.28 | 49.85 | 4 | 240.4104
8194 | 31.75 | 42.3512 | 33.1795 | 226.1991 | 0.42491 |  | 8194 | 47.96 | 42.3512 | 3 | 226.1991
8195 | 36.79 | 45.5139 | 34.3774 | 178.0201 | 0.44356 |  | 8195 | 46.95 | 45.5139 | 2.2679 | 178.0201
8196 | 36.91 | 45.8591 | 46.2181 | 212.3472 | 0.4569 |  | 8196 | 46.98 | 45.8591 | 2 | 212.3472
8197 | 36.66 | 48.3283 | 229.0288 | 167.134 | 0.46044 |  | 8197 | 44.89 | 48.3283 | 2.2679 | 167.134
8198 | 36.67 | 50.2453 | 40.9918 | 187.9813 | 0.45966 |  | 8198 | 43.94 | 50.2453 | 3 | 187.9813
8199 | 36.83 | 55.1474 | 41.3867 | 161.3013 | 0.46216 |  | 8199 | 43.06 | 55.1474 | 4 | 161.3013
8200 | 39.43 | 75.401 | 46.5739 | 186.0383 | 0.46313 |  | 8200 | 43.54 | 75.401 | 5 | 186.0383
8201 | 38.73 | 103.6131 | 38.8844 | 235.5394 | 0.46339 |  | 8201 | 41.12 | 103.6131 | 5.7321 | 235.5394
8202 | 59.16 | 143.1344 | 36.9608 | 287.7043 | 0.46008 |  | 8202 | 44.47 | 143.1344 | 6 | 287.7043
8203 | 45 | 159.2612 | 42.7004 | 269.463 | 0.45699 |  | 8203 | 45.28 | 159.2612 | 5.7321 | 269.463
8204 | 43 | 151.7384 | 21.037 | 277.021 | 0.45962 |  | 8204 | 37.6 | 151.7384 | 5 | 277.021
8205 | 36.2 | 113.7332 | 24.9416 | 228.6687 | 0.45701 |  | 8205 | 36.03 | 113.7332 | 4 | 228.6687
8206 | 35 | 106.0079 | 27.6453 | 223.8391 | 0.43548 |  | 8206 | 34.14 | 106.0079 | 3 | 223.8391
8207 | 34.9 | 76.6304 | 24.7286 | 219.5761 | 0.42648 |  | 8207 | 32.18 | 76.6304 | 2.2679 | 219.5761
8208 | 30.6 | 40.8093 | 28.167 | 180.5977 | 0.41983 |  | 8208 | 31.05 | 40.8093 | 2 | 180.5977
8209 | 22.1 | 33.2666 | 26.1845 | 174.8713 | 0.41527 |  | 8209 | 28.32 | 33.2666 | 2.2679 | 174.8713
8210 | 18.08 | 31.7571 | 23.5792 | 105.0994 | 0.41147 |  | 8210 | 27.55 | 31.7571 | 3 | 105.0994
8211 | 13.54 | 30.3113 | 33.0241 | 118.3733 | 0.40956 |  | 8211 | 26.35 | 30.3113 | 4 | 118.3733
8212 | 0 | 29.1246 | 30.2973 | 146.8967 | 0.41559 |  | 8212 | 26.08 | 29.1246 | 5 | 146.8967
8213 | -3.47 | 28.4076 | 31.6869 | 198.6882 | 0.42028 |  | 8213 | 26.25 | 28.4076 | 5.7321 | 198.6882
8214 | 0.1 | 27.9174 | 31.3366 | 213.9348 | 0.43518 |  | 8214 | 26.92 | 27.9174 | 6 | 213.9348
8215 | 30 | 27.7382 | 25.2587 | 283.0883 | 0.46809 |  | 8215 | 28.2 | 27.7382 | 5.7321 | 283.0883
8216 | 41.9 | 30.245 | 42.1952 | 255.5851 | 0.49438 |  | 8216 | 30 | 30.245 | 5 | 255.5851
8217 | 43.33 | 55.5153 | 42.2931 | 210.4309 | 0.50328 |  | 8217 | 35.98 | 55.5153 | 4 | 210.4309
8218 | 46.15 | 69.1663 | 44.5054 | 173.7353 | 0.50262 |  | 8218 | 38.37 | 69.1663 | 3 | 173.7353
8219 | 46.27 | 76.244 | 38.962 | 152.4783 | 0.50073 |  | 8219 | 39.22 | 76.244 | 2.2679 | 152.4783
8220 | 44.2 | 78.0745 | 29.1008 | 104.4181 | 0.499 |  | 8220 | 36.59 | 78.0745 | 2 | 104.4181
8221 | 41.23 | 83.2 | 51.4698 | 109.1183 | 0.49487 |  | 8221 | 34.09 | 83.2 | 2.2679 | 109.1183
8222 | 41.25 | 76.5333 | 45.8119 | 124.97 | 0.48584 |  | 8222 | 35 | 76.5333 | 3 | 124.97
8223 | 41.29 | 73.7492 | 35.4448 | 129.1957 | 0.4639 |  | 8223 | 35.19 | 73.7492 | 4 | 129.1957
8224 | 40.89 | 73.7114 | 29.1325 | 140.1173 | 0.45323 |  | 8224 | 37.96 | 73.7114 | 5 | 140.1173
8225 | 41.49 | 91.5845 | 35.9972 | 168.7888 | 0.45493 |  | 8225 | 43.21 | 91.5845 | 5.7321 | 168.7888
8226 | 47.34 | 130.7299 | 34.3837 | 177.3678 | 0.4524 |  | 8226 | 45.11 | 130.7299 | 6 | 177.3678
8227 | 39.84 | 159.4933 | 43.9461 | 223.2955 | 0.45008 |  | 8227 | 48.86 | 159.4933 | 5.7321 | 223.2955
8228 | 38.62 | 141.6264 | 29.23 | 198.9189 | 0.45603 |  | 8228 | 48.58 | 141.6264 | 5 | 198.9189
8229 | 34.12 | 114.4496 | 27.0872 | 165.0907 | 0.46198 |  | 8229 | 44.69 | 114.4496 | 4 | 165.0907
8230 | 32.6 | 101.0987 | 31.7995 | 183.2698 | 0.45591 |  | 8230 | 35 | 101.0987 | 3 | 183.2698
8231 | 31.95 | 86.4004 | 27.4459 | 160.2013 | 0.46235 |  | 8231 | 34.94 | 86.4004 | 2.2679 | 160.2013
8232 | 30.4 | 39.515 | 27.9838 | 152.9536 | 0.45877 |  | 8232 | 31 | 39.515 | 2 | 152.9536
8233 | 30.6 | 35.7401 | 32.9931 | 190.7897 | 0.45908 |  | 8233 | 28.99 | 35.7401 | 2.2679 | 190.7897
8234 | 31 | 33.8111 | 31.492 | 159.587 | 0.46075 |  | 8234 | 27.59 | 33.8111 | 3 | 159.587
8235 | 31 | 32.0271 | 24.0464 | 157.3138 | 0.46608 |  | 8235 | 27.21 | 32.0271 | 4 | 157.3138
8236 | 31.45 | 30.3736 | 26.1831 | 169.7117 | 0.48465 |  | 8236 | 27.02 | 30.3736 | 5 | 169.7117
8237 | 32.09 | 29.2502 | 46.7822 | 251.0795 | 0.50726 |  | 8237 | 27.03 | 29.2502 | 5.7321 | 251.0795
8238 | 34.93 | 28.4627 | 75.6236 | 310.2436 | 0.51599 |  | 8238 | 27.46 | 28.4627 | 6 | 310.2436
8239 | 46.11 | 27.9367 | 123.9454 | 355.6387 | 0.51563 |  | 8239 | 28.46 | 27.9367 | 5.7321 | 355.6387
8240 | 53.1 | 30.9337 | 507.4551 | 329.8493 | 0.50945 |  | 8240 | 31.57 | 30.9337 | 5 | 329.8493
8241 | 56.38 | 56.2643 | 111.8511 | 316.3678 | 0.49543 |  | 8241 | 44.47 | 56.2643 | 4 | 316.3678
8242 | 54.93 | 71.121 | 80.9954 | 276.2414 | 0.47802 |  | 8242 | 49.94 | 71.121 | 3 | 276.2414
8243 | 51 | 77.0896 | 128.7525 | 298.9322 | 0.46543 |  | 8243 | 50.04 | 77.0896 | 2.2679 | 298.9322
8244 | 49.9 | 79.8925 | 76.1561 | 228.1876 | 0.46159 |  | 8244 | 49.01 | 79.8925 | 2 | 228.1876
8245 | 47.34 | 87.2325 | 61.2088 | 224.9099 | 0.45803 |  | 8245 | 47.01 | 87.2325 | 2.2679 | 224.9099
8246 | 46.99 | 81.4393 | 118.3478 | 232.5036 | 0.45467 |  | 8246 | 39.94 | 81.4393 | 3 | 232.5036
8247 | 46.83 | 80.0191 | 83.9583 | 195.1871 | 0.45547 |  | 8247 | 39.94 | 80.0191 | 4 | 195.1871
8248 | 46.22 | 79.9202 | 40.7168 | 211.7585 | 0.45383 |  | 8248 | 37.44 | 79.9202 | 5 | 211.7585
8249 | 45.41 | 93.2487 | 44.1286 | 258.9233 | 0.45086 |  | 8249 | 40.82 | 93.2487 | 5.7321 | 258.9233
8250 | 47.21 | 129.1951 | 55.6957 | 286.0229 | 0.44831 |  | 8250 | 50 | 129.1951 | 6 | 286.0229
8251 | 32.9 | 162.6938 | 34.3015 | 274.4712 | 0.43619 |  | 8251 | 41.96 | 162.6938 | 5.7321 | 274.4712
8252 | 31.3 | 150.8906 | 35.6065 | 320.6436 | 0.42241 |  | 8252 | 32.6 | 150.8906 | 5 | 320.6436
8253 | 33.24 | 120.8858 | 26.5942 | 265.4942 | 0.41112 |  | 8253 | 35 | 120.8858 | 4 | 265.4942
8254 | 35 | 104.2896 | 30.761 | 236.7731 | 0.40508 |  | 8254 | 35 | 104.2896 | 3 | 236.7731
8255 | 30.1 | 90.7407 | 23.7392 | 186.8794 | 0.40153 |  | 8255 | 32.46 | 90.7407 | 2.2679 | 186.8794
8256 | 24.94 | 42.7245 | 26.0438 | 168.8883 | 0.40332 |  | 8256 | 30.02 | 42.7245 | 2 | 168.8883
8257 | 30 | 36.0056 | 23.3794 | 166.0932 | 0.40138 |  | 8257 | 27.62 | 36.0056 | 2.2679 | 166.0932
8258 | 15.1 | 34.1998 | 27.8011 | 199.0197 | 0.4015 |  | 8258 | 26.42 | 34.1998 | 3 | 199.0197
8259 | 21 | 32.231 | 27.7697 | 188.451 | 0.40741 |  | 8259 | 25.99 | 32.231 | 4 | 188.451
8260 | 30.27 | 30.5029 | 32.0897 | 232.9681 | 0.42424 |  | 8260 | 25.7 | 30.5029 | 5 | 232.9681
8261 | 30.31 | 29.2905 | 32.5094 | 255.5326 | 0.43924 |  | 8261 | 25.8 | 29.2905 | 5.7321 | 255.5326
8262 | 34.11 | 28.68 | 35.7483 | 287.2362 | 0.4516 |  | 8262 | 21 | 28.68 | 6 | 287.2362
8263 | 37.14 | 43.9332 | 94.7816 | 306.5207 | 0.48053 |  | 8263 | 26.59 | 43.9332 | 5.7321 | 306.5207
8264 | 39.17 | 66.5158 | 104.2469 | 328.9112 | 0.50183 |  | 8264 | 27.52 | 66.5158 | 5 | 328.9112
8265 | 51.64 | 51.2062 | 72.3961 | 293.6653 | 0.50973 |  | 8265 | 24.72 | 51.2062 | 4 | 293.6653
8266 | 53.03 | 41.7075 | 68.5425 | 222.7011 | 0.51203 |  | 8266 | 30.9 | 41.7075 | 3 | 222.7011
8267 | 53.03 | 46.3972 | 92.6883 | 254.1789 | 0.50257 |  | 8267 | 31.08 | 46.3972 | 2.2679 | 254.1789
8268 | 49.38 | 46.8912 | 59.5459 | 239.9296 | 0.50671 |  | 8268 | 31.86 | 46.8912 | 2 | 239.9296
8269 | 49.64 | 51.3272 | 299.3321 | 246.7022 | 0.50275 |  | 8269 | 34.94 | 51.3272 | 2.2679 | 246.7022
8270 | 51.82 | 53.4504 | 47.2646 | 254.3636 | 0.5007 |  | 8270 | 33.99 | 53.4504 | 3 | 254.3636
8271 | 51.29 | 58.3461 | 47.8032 | 260.3314 | 0.49196 |  | 8271 | 34.94 | 58.3461 | 4 | 260.3314
8272 | 51.79 | 72.8043 | 60.1917 | 276.4241 | 0.4911 |  | 8272 | 35.02 | 72.8043 | 5 | 276.4241
8273 | 52.86 | 111.3689 | 50.6268 | 296.5757 | 0.48782 |  | 8273 | 45.7 | 111.3689 | 5.7321 | 296.5757
8274 | 60.23 | 164.0264 | 44.5687 | 308.923 | 0.48767 |  | 8274 | 51.76 | 164.0264 | 6 | 308.923
8275 | 56.36 | 168.5359 | 38.5096 | 372.5453 | 0.48083 |  | 8275 | 54.94 | 168.5359 | 5.7321 | 372.5453
8276 | 53.46 | 136.4578 | 25.3493 | 334.641 | 0.48136 |  | 8276 | 45.12 | 136.4578 | 5 | 334.641
8277 | 47.22 | 122.718 | 32.606 | 324.4714 | 0.48778 |  | 8277 | 40.17 | 122.718 | 4 | 324.4714
8278 | 44.7 | 112.4434 | 23.6054 | 247.0591 | 0.49201 |  | 8278 | 37.6 | 112.4434 | 3 | 247.0591
8279 | 37.63 | 79.1247 | 29.3469 | 307.9282 | 0.48916 |  | 8279 | 34.72 | 79.1247 | 2.2679 | 307.9282
8280 | 37.17 | 42.0926 | 24.3486 | 251.0607 | 0.48245 |  | 8280 | 34.94 | 42.0926 | 2 | 251.0607
8281 | 37 | 35.71 | 22.4066 | 275.2141 | 0.48878 |  | 8281 | 31.4 | 35.71 | 2.2679 | 275.2141
8282 | 35.83 | 33.8975 | 30.7442 | 209.4736 | 0.49298 |  | 8282 | 30.58 | 33.8975 | 3 | 209.4736
8283 | 35.02 | 32.0887 | 26.9075 | 226.4489 | 0.49209 |  | 8283 | 28.44 | 32.0887 | 4 | 226.4489
8284 | 34.65 | 30.354 | 26.7397 | 224.5242 | 0.48484 |  | 8284 | 29.41 | 30.354 | 5 | 224.5242
8285 | 35.18 | 29.1809 | 25.3055 | 252.2601 | 0.48853 |  | 8285 | 28.66 | 29.1809 | 5.7321 | 252.2601
8286 | 36.98 | 28.9085 | 29.818 | 335.9765 | 0.49983 |  | 8286 | 27.56 | 28.9085 | 6 | 335.9765
8287 | 49 | 44.0391 | 24.0943 | 399.3283 | 0.50459 |  | 8287 | 27.94 | 44.0391 | 5.7321 | 399.3283
8288 | 57.64 | 66.3431 | 39.8028 | 356.9994 | 0.50051 |  | 8288 | 29.41 | 66.3431 | 5 | 356.9994
8289 | 61.6 | 50.1219 | 248.47 | 328.6183 | 0.49192 |  | 8289 | 28.02 | 50.1219 | 4 | 328.6183
8290 | 60.1 | 41.6541 | 42.2085 | 325.9028 | 0.486 |  | 8290 | 30.34 | 41.6541 | 3 | 325.9028
8291 | 54 | 42.9019 | 34.8017 | 303.5953 | 0.48036 |  | 8291 | 32.02 | 42.9019 | 2.2679 | 303.5953
8292 | 49.69 | 44.8701 | 54.5515 | 257.0158 | 0.47694 |  | 8292 | 36 | 44.8701 | 2 | 257.0158
8293 | 49 | 49.5885 | 47.7432 | 228.1055 | 0.47509 |  | 8293 | 40.1 | 49.5885 | 2.2679 | 228.1055
8294 | 46.87 | 50.0023 | 38.006 | 240.8984 | 0.47107 |  | 8294 | 37.44 | 50.0023 | 3 | 240.8984
8295 | 47.15 | 54.9073 | 49.7609 | 267.3663 | 0.46914 |  | 8295 | 34.94 | 54.9073 | 4 | 267.3663
8296 | 48.75 | 71.1559 | 45.9172 | 278.945 | 0.4648 |  | 8296 | 33 | 71.1559 | 5 | 278.945
8297 | 47.69 | 108.4869 | 37.8507 | 269.716 | 0.46031 |  | 8297 | 32.4 | 108.4869 | 5.7321 | 269.716
8298 | 52.13 | 150.7679 | 56.7122 | 282.3676 | 0.45316 |  | 8298 | 35.99 | 150.7679 | 6 | 282.3676
8299 | 47.05 | 169.5046 | 71.7553 | 301.9886 | 0.44794 |  | 8299 | 52.26 | 169.5046 | 5.7321 | 301.9886
8300 | 40.36 | 139.323 | 46.9771 | 266.6313 | 0.44257 |  | 8300 | 52.72 | 139.323 | 5 | 266.6313
8301 | 38.04 | 116.041 | 92.5952 | 249.7668 | 0.4447 |  | 8301 | 45 | 116.041 | 4 | 249.7668
8302 | 36.13 | 105.0499 | 67.7786 | 225.9114 | 0.45248 |  | 8302 | 35 | 105.0499 | 3 | 225.9114
8303 | 35.07 | 75.3598 | 78.4219 | 197.0821 | 0.45081 |  | 8303 | 32.44 | 75.3598 | 2.2679 | 197.0821
8304 | 34.27 | 41.0035 | 92.6617 | 163.0117 | 0.43668 |  | 8304 | 31.1 | 41.0035 | 2 | 163.0117
8305 | 30.1 | 34.3721 | 70.1312 | 169.7362 | 0.428 |  | 8305 | 30.56 | 34.3721 | 2.2679 | 169.7362
8306 | 28.42 | 32.6461 | 41.5008 | 163.5651 | 0.41675 |  | 8306 | 23.98 | 32.6461 | 3 | 163.5651
8307 | 29 | 30.9283 | 22.3141 | 152.7232 | 0.40388 |  | 8307 | 29.77 | 30.9283 | 4 | 152.7232
8308 | 19.9 | 29.6376 | 234.6422 | 169.1522 | 0.40525 |  | 8308 | 28.24 | 29.6376 | 5 | 169.1522
8309 | 21 | 28.6797 | 35.9158 | 221.7793 | 0.41585 |  | 8309 | 27.49 | 28.6797 | 5.7321 | 221.7793
8310 | 27.6 | 28.6685 | 56.3058 | 275.7875 | 0.43585 |  | 8310 | 26.6 | 28.6685 | 6 | 275.7875
8311 | 32.83 | 43.1037 | 74.0464 | 249.4708 | 0.46684 |  | 8311 | 28.78 | 43.1037 | 5.7321 | 249.4708
8312 | 39.77 | 68.2331 | 92.1459 | 273.6779 | 0.48587 |  | 8312 | 41.08 | 68.2331 | 5 | 273.6779
8313 | 45 | 51.8049 | 89.8072 | 247.3565 | 0.4997 |  | 8313 | 60 | 51.8049 | 4 | 247.3565
8314 | 43.9 | 42.86 | 47.7123 | 205.7687 | 0.5095 |  | 8314 | 56.6 | 42.86 | 3 | 205.7687
8315 | 40.82 | 44.663 | 29.5372 | 185.9066 | 0.51548 |  | 8315 | 57.33 | 44.663 | 2.2679 | 185.9066
8316 | 41.65 | 47.5585 | 48.6551 | 202.0062 | 0.52145 |  | 8316 | 58.42 | 47.5585 | 2 | 202.0062
8317 | 43.27 | 50.7451 | 246.1481 | 231.491 | 0.52399 |  | 8317 | 62.74 | 50.7451 | 2.2679 | 231.491
8318 | 40.8 | 51.0736 | 38.5047 | 211.5775 | 0.51604 |  | 8318 | 59.3 | 51.0736 | 3 | 211.5775
8319 | 38.08 | 59.3549 | 42.1089 | 178.9166 | 0.5094 |  | 8319 | 65.35 | 59.3549 | 4 | 178.9166
8320 | 38.74 | 75.4014 | 38.0305 | 231.109 | 0.50552 |  | 8320 | 65.26 | 75.4014 | 5 | 231.109
8321 | 40.55 | 107.4596 | 42.1431 | 225.81 | 0.49974 |  | 8321 | 61.18 | 107.4596 | 5.7321 | 225.81
8322 | 50.56 | 155.9346 | 33.3574 | 240.5582 | 0.49531 |  | 8322 | 70.25 | 155.9346 | 6 | 240.5582
8323 | 46.59 | 162.3032 | 60.5675 | 233.4253 | 0.48528 |  | 8323 | 80.62 | 162.3032 | 5.7321 | 233.4253
8324 | 42.79 | 138.4428 | 75.353 | 284.257 | 0.47713 |  | 8324 | 71.18 | 138.4428 | 5 | 284.257
8325 | 38.64 | 118.4826 | 45.4028 | 267.2608 | 0.47798 |  | 8325 | 61.18 | 118.4826 | 4 | 267.2608
8326 | 36.51 | 111.5064 | 92.3505 | 217.3158 | 0.48381 |  | 8326 | 46.96 | 111.5064 | 3 | 217.3158
8327 | 35.04 | 78.4537 | 40.9489 | 245.4536 | 0.48389 |  | 8327 | 37.73 | 78.4537 | 2.2679 | 245.4536
8328 | 33.96 | 39.7461 | 104.9472 | 238.5496 | 0.48451 |  | 8328 | 38 | 39.7461 | 2 | 238.5496
8329 | 34.39 | 33.7198 | 76.5014 | 184.0684 | 0.47847 |  | 8329 | 32 | 33.7198 | 2.2679 | 184.0684
8330 | 32.62 | 32.2977 | 296.2401 | 177.5021 | 0.46316 |  | 8330 | 34.24 | 32.2977 | 3 | 177.5021
8331 | 31.83 | 30.8718 | 66.5857 | 194.3153 | 0.44906 |  | 8331 | 31.6 | 30.8718 | 4 | 194.3153
8332 | 25.5 | 29.5153 | 20.859 | 260.0026 | 0.45451 |  | 8332 | 31.82 | 29.5153 | 5 | 260.0026
8333 | 21.92 | 28.5121 | 22.7528 | 339.8841 | 0.44979 |  | 8333 | 31.89 | 28.5121 | 5.7321 | 339.8841
8334 | 19.92 | 28.2206 | 34.4105 | 357.0138 | 0.44039 |  | 8334 | 32.32 | 28.2206 | 6 | 357.0138
8335 | 22.25 | 43.3463 | 70.8516 | 422.0064 | 0.43011 |  | 8335 | 32.41 | 43.3463 | 5.7321 | 422.0064
8336 | 28.15 | 66.0354 | 45.1337 | 336.9782 | 0.42171 |  | 8336 | 32.81 | 66.0354 | 5 | 336.9782
8337 | 33.89 | 51.4568 | 69.3587 | 317.5561 | 0.44083 |  | 8337 | 49.9 | 51.4568 | 4 | 317.5561
8338 | 35.56 | 43.429 | 92.436 | 357.0882 | 0.44967 |  | 8338 | 57.63 | 43.429 | 3 | 357.0882
8339 | 35.3 | 44.3783 | 59.1146 | 292.2103 | 0.45139 |  | 8339 | 61.26 | 44.3783 | 2.2679 | 292.2103
8340 | 35.06 | 44.7362 | 47.9237 | 261.4955 | 0.45106 |  | 8340 | 65.08 | 44.7362 | 2 | 261.4955
8341 | 35.48 | 47.6745 | 47.8645 | 210.4032 | 0.45295 |  | 8341 | 63.1 | 47.6745 | 2.2679 | 210.4032
8342 | 35.98 | 49.7726 | 46.0715 | 246.7512 | 0.46271 |  | 8342 | 60.32 | 49.7726 | 3 | 246.7512
8343 | 35.84 | 55.9181 | 49.7895 | 258.3512 | 0.47103 |  | 8343 | 61.73 | 55.9181 | 4 | 258.3512
8344 | 36.02 | 71.561 | 45.333 | 231.0055 | 0.47099 |  | 8344 | 62.23 | 71.561 | 5 | 231.0055
8345 | 36.35 | 106.2121 | 31.6848 | 296.2057 | 0.4726 |  | 8345 | 64.02 | 106.2121 | 5.7321 | 296.2057
8346 | 40.67 | 141.9051 | 51.8175 | 286.8291 | 0.46251 |  | 8346 | 64.63 | 141.9051 | 6 | 286.8291
8347 | 40.01 | 160.3525 | 34.8412 | 296.6554 | 0.45723 |  | 8347 | 71.9 | 160.3525 | 5.7321 | 296.6554
8348 | 39 | 145.2247 | 34.0304 | 385.9953 | 0.46134 |  | 8348 | 65.48 | 145.2247 | 5 | 385.9953
8349 | 39.3 | 119.5512 | 28.7348 | 322.6513 | 0.46641 |  | 8349 | 58.04 | 119.5512 | 4 | 322.6513
8350 | 35.02 | 108.795 | 221.4133 | 313.6643 | 0.46649 |  | 8350 | 46.68 | 108.795 | 3 | 313.6643
8351 | 34 | 76.447 | 29.0594 | 281.3792 | 0.46427 |  | 8351 | 39.89 | 76.447 | 2.2679 | 281.3792
8352 | 35 | 38.7559 | 34.0048 | 243.311 | 0.45945 |  | 8352 | 36.45 | 38.7559 | 2 | 243.311
8353 | 34.9 | 32.6686 | 24.2617 | 300.0629 | 0.45745 |  | 8353 | 32.23 | 32.6686 | 2.2679 | 300.0629
8354 | 35 | 31.3195 | 27.2138 | 269.4076 | 0.44496 |  | 8354 | 32.44 | 31.3195 | 3 | 269.4076
8355 | 29.9 | 30.0495 | 30.0893 | 224.3308 | 0.42282 |  | 8355 | 31.74 | 30.0495 | 4 | 224.3308
8356 | 16.54 | 28.8824 | 25.1933 | 277.7047 | 0.40365 |  | 8356 | 31.27 | 28.8824 | 5 | 277.7047
8357 | 11.91 | 28.0863 | 35.9141 | 327.797 | 0.396 |  | 8357 | 31.91 | 28.0863 | 5.7321 | 327.797
8358 | 15.7 | 28.0221 | 24.8427 | 397.4385 | 0.39486 |  | 8358 | 32.34 | 28.0221 | 6 | 397.4385
8359 | 26.94 | 42.679 | 35.7937 | 356.0705 | 0.39857 |  | 8359 | 35.99 | 42.679 | 5.7321 | 356.0705
8360 | 31.58 | 66.8881 | 32.3465 | 353.8558 | 0.40438 |  | 8360 | 43.93 | 66.8881 | 5 | 353.8558
8361 | 29.1 | 51.4678 | 36.1303 | 328.8625 | 0.41619 |  | 8361 | 68.08 | 51.4678 | 4 | 328.8625
8362 | 34.15 | 43.2348 | 44.1971 | 307.2468 | 0.43372 |  | 8362 | 82.26 | 43.2348 | 3 | 307.2468
8363 | 35.46 | 45.7498 | 60.3616 | 403.9625 | 0.44445 |  | 8363 | 78.58 | 45.7498 | 2.2679 | 403.9625
8364 | 35.45 | 46.8483 | 43.367 | 307.0721 | 0.44373 |  | 8364 | 77.17 | 46.8483 | 2 | 307.0721
8365 | 35.45 | 49.9214 | 33.8472 | 293.2941 | 0.44195 |  | 8365 | 75.94 | 49.9214 | 2.2679 | 293.2941
8366 | 35.48 | 49.9097 | 29.8309 | 339.628 | 0.43984 |  | 8366 | 70.55 | 49.9097 | 3 | 339.628
8367 | 38.06 | 57.2301 | 49.0767 | 266.8657 | 0.44006 |  | 8367 | 69.91 | 57.2301 | 4 | 266.8657
8368 | 43.56 | 73.3122 | 31.9156 | 307.7913 | 0.44767 |  | 8368 | 69.69 | 73.3122 | 5 | 307.7913
8369 | 34.5 | 104.1459 | 48.3795 | 301.9788 | 0.45164 |  | 8369 | 72.52 | 104.1459 | 5.7321 | 301.9788
8370 | 39.1 | 148.5791 | 39.0937 | 317.3546 | 0.45923 |  | 8370 | 75.15 | 148.5791 | 6 | 317.3546
8371 | 42.01 | 155.0026 | 35.8524 | 326.9801 | 0.4619 |  | 8371 | 91.81 | 155.0026 | 5.7321 | 326.9801
8372 | 42.4 | 124.4651 | 230.2328 | 359.7674 | 0.46622 |  | 8372 | 81.94 | 124.4651 | 5 | 359.7674
8373 | 37.49 | 112.0593 | 36.0743 | 379.0932 | 0.46977 |  | 8373 | 78.61 | 112.0593 | 4 | 379.0932
8374 | 35.32 | 105.1339 | 32.9147 | 295.087 | 0.46598 |  | 8374 | 67.47 | 105.1339 | 3 | 295.087
8375 | 33.4 | 73.7324 | 31.3635 | 286.3838 | 0.45987 |  | 8375 | 47.92 | 73.7324 | 2.2679 | 286.3838
8376 | 35.1 | 37.5154 | 27.0581 | 271.1397 | 0.46097 |  | 8376 | 39.57 | 37.5154 | 2 | 271.1397
8377 | 35.23 | 32.2604 | 23.002 | 321.0449 | 0.46126 |  | 8377 | 33.08 | 32.2604 | 2.2679 | 321.0449
8378 | 33.68 | 30.9637 | 31.3266 | 246.9984 | 0.4559 |  | 8378 | 32.78 | 30.9637 | 3 | 246.9984
8379 | 30.91 | 29.7102 | 33.0835 | 292.8468 | 0.44225 |  | 8379 | 32.63 | 29.7102 | 4 | 292.8468
8380 | 29.49 | 28.6108 | 39.5893 | 307.1076 | 0.43374 |  | 8380 | 32.8 | 28.6108 | 5 | 307.1076
8381 | 29.19 | 27.9645 | 31.1118 | 282.3026 | 0.43308 |  | 8381 | 33.45 | 27.9645 | 5.7321 | 282.3026
8382 | 31.77 | 27.5201 | 24.6647 | 360.7423 | 0.44052 |  | 8382 | 34.19 | 27.5201 | 6 | 360.7423
8383 | 38.87 | 27.2066 | 26.877 | 398.6725 | 0.46596 |  | 8383 | 33.6 | 27.2066 | 5.7321 | 398.6725
8384 | 50.01 | 30.4003 | 44.5563 | 398.0698 | 0.47308 |  | 8384 | 40.47 | 30.4003 | 5 | 398.0698
8385 | 44.43 | 55.2307 | 41.9036 | 370.0412 | 0.47405 |  | 8385 | 48.94 | 55.2307 | 4 | 370.0412
8386 | 46.1 | 70.57 | 56.3217 | 384.3785 | 0.47741 |  | 8386 | 60 | 70.57 | 3 | 384.3785
8387 | 42.56 | 74.0478 | 47.2389 | 311.9346 | 0.48076 |  | 8387 | 62.27 | 74.0478 | 2.2679 | 311.9346
8388 | 48 | 77.9228 | 42.7711 | 325.6659 | 0.47924 |  | 8388 | 59.13 | 77.9228 | 2 | 325.6659
8389 | 44.24 | 80.4633 | 50.0367 | 261.817 | 0.47747 |  | 8389 | 57.69 | 80.4633 | 2.2679 | 261.817
8390 | 44.72 | 76.7751 | 55.0605 | 222.582 | 0.4833 |  | 8390 | 53.72 | 76.7751 | 3 | 222.582
8391 | 46.03 | 71.1835 | 30.9086 | 234.925 | 0.48548 |  | 8391 | 54.95 | 71.1835 | 4 | 234.925
8392 | 47.34 | 77.5288 | 42.1939 | 216.1685 | 0.48586 |  | 8392 | 54.61 | 77.5288 | 5 | 216.1685
8393 | 50 | 88.2568 | 44.5434 | 285.779 | 0.48588 |  | 8393 | 59.94 | 88.2568 | 5.7321 | 285.779
8394 | 52.01 | 124.8518 | 44.5631 | 263.48 | 0.48738 |  | 8394 | 62.05 | 124.8518 | 6 | 263.48
8395 | 51.96 | 148.7891 | 249.9315 | 274.3875 | 0.48656 |  | 8395 | 74.94 | 148.7891 | 5.7321 | 274.3875
8396 | 47.55 | 144.3651 | 225.6579 | 315.4346 | 0.49367 |  | 8396 | 62.6 | 144.3651 | 5 | 315.4346
8397 | 42.17 | 112.3844 | 24.3545 | 292.203 | 0.50754 |  | 8397 | 56.32 | 112.3844 | 4 | 292.203
8398 | 40.1 | 99.4641 | 27.479 | 215.8102 | 0.51379 |  | 8398 | 45.72 | 99.4641 | 3 | 215.8102
8399 | 38.08 | 85.116 | 32.3054 | 224.1396 | 0.52085 |  | 8399 | 39.64 | 85.116 | 2.2679 | 224.1396
8400 | 36 | 39.0169 | 22.1729 | 211.1747 | 0.52317 |  | 8400 | 38.12 | 39.0169 | 2 | 211.1747
8401 | 32.71 | 35.6205 | 33.5682 | 226.8438 | 0.51622 |  | 8401 | 33.98 | 35.6205 | 2.2679 | 226.8438
8402 | 31.9 | 33.815 | 31.6343 | 247.406 | 0.50408 |  | 8402 | 33.33 | 33.815 | 3 | 247.406
8403 | 30.5 | 31.9406 | 27.7329 | 270.2873 | 0.50061 |  | 8403 | 33.12 | 31.9406 | 4 | 270.2873
8404 | 29.19 | 30.3088 | 29.0675 | 308.5763 | 0.4899 |  | 8404 | 32.15 | 30.3088 | 5 | 308.5763
8405 | 29.4 | 29.1764 | 24.8192 | 268.5945 | 0.48518 |  | 8405 | 32.11 | 29.1764 | 5.7321 | 268.5945
8406 | 31.27 | 28.4078 | 18.7299 | 353.8189 | 0.48936 |  | 8406 | 33.15 | 28.4078 | 6 | 353.8189
8407 | 35.74 | 27.9978 | 34.2367 | 317.3014 | 0.5019 |  | 8407 | 33.19 | 27.9978 | 5.7321 | 317.3014
8408 | 44.17 | 31.064 | 39.7738 | 364.3925 | 0.4981 |  | 8408 | 41.82 | 31.064 | 5 | 364.3925
8409 | 49.5 | 54.3437 | 47.8207 | 364.0617 | 0.49278 |  | 8409 | 54.94 | 54.3437 | 4 | 364.0617
8410 | 42.53 | 68.6516 | 46.8767 | 312.4379 | 0.48557 |  | 8410 | 66.73 | 68.6516 | 3 | 312.4379
8411 | 39.98 | 72.2126 | 46.8111 | 304.405 | 0.47494 |  | 8411 | 64.07 | 72.2126 | 2.2679 | 304.405
8412 | 37.92 | 74.3323 | 44.9998 | 297.3391 | 0.47297 |  | 8412 | 63.15 | 74.3323 | 2 | 297.3391
8413 | 34.7 | 80.8782 | 42.3736 | 231.8131 | 0.47065 |  | 8413 | 63.03 | 80.8782 | 2.2679 | 231.8131
8414 | 35.36 | 77.8454 | 36.4147 | 179.8461 | 0.46496 |  | 8414 | 56.96 | 77.8454 | 3 | 179.8461
8415 | 38 | 77.8341 | 44.8942 | 205.5392 | 0.46492 |  | 8415 | 57 | 77.8341 | 4 | 205.5392
8416 | 42.52 | 80.4173 | 41.7302 | 211.7961 | 0.4666 |  | 8416 | 64.88 | 80.4173 | 5 | 211.7961
8417 | 42.57 | 86.1122 | 42.064 | 226.1271 | 0.468 |  | 8417 | 65.1 | 86.1122 | 5.7321 | 226.1271
8418 | 42.83 | 126.4675 | 36.5816 | 258.2662 | 0.4723 |  | 8418 | 69.46 | 126.4675 | 6 | 258.2662
8419 | 38.79 | 143.4942 | 46.6379 | 253.8295 | 0.48032 |  | 8419 | 84.94 | 143.4942 | 5.7321 | 253.8295
8420 | 36.74 | 163.7915 | 25.4059 | 283.2246 | 0.48685 |  | 8420 | 79.07 | 163.7915 | 5 | 283.2246
8421 | 34.2 | 119.0654 | 28.2553 | 256.1535 | 0.48964 |  | 8421 | 71.71 | 119.0654 | 4 | 256.1535
8422 | 33.39 | 104.5308 | 27.3932 | 287.4398 | 0.48713 |  | 8422 | 63.63 | 104.5308 | 3 | 287.4398
8423 | 31.9 | 88.6935 | 22.0562 | 272.8169 | 0.47014 |  | 8423 | 49.76 | 88.6935 | 2.2679 | 272.8169
8424 | 30.1 | 42.8451 | 28.5045 | 251.2264 | 0.45202 |  | 8424 | 42.49 | 42.8451 | 2 | 251.2264
8425 | 33.93 | 34.9163 | 30.391 | 191.9583 | 0.45941 |  | 8425 | 36.32 | 34.9163 | 2.2679 | 191.9583
8426 | 30.5 | 33.1902 | 25.2601 | 190.6883 | 0.44523 |  | 8426 | 32.06 | 33.1902 | 3 | 190.6883
8427 | 30 | 31.5313 | 34.7213 | 235.2491 | 0.4426 |  | 8427 | 30.95 | 31.5313 | 4 | 235.2491
8428 | 26.83 | 29.9645 | 229.1656 | 251.184 | 0.44015 |  | 8428 | 32.42 | 29.9645 | 5 | 251.184
8429 | 28.39 | 28.898 | 31.2092 | 311.2109 | 0.44187 |  | 8429 | 35.99 | 28.898 | 5.7321 | 311.2109
8430 | 30.22 | 28.4495 | 22.4246 | 323.1529 | 0.44335 |  | 8430 | 38.91 | 28.4495 | 6 | 323.1529
8431 | 36.19 | 43.7741 | 25.3983 | 329.9853 | 0.45824 |  | 8431 | 38.74 | 43.7741 | 5.7321 | 329.9853
8432 | 42.05 | 67.4607 | 42.3557 | 340.8238 | 0.47066 |  | 8432 | 35.25 | 67.4607 | 5 | 340.8238
8433 | 52.1 | 53.5125 | 43.7652 | 340.0721 | 0.47584 |  | 8433 | 38.23 | 53.5125 | 4 | 340.0721
8434 | 51.97 | 43.4139 | 51.1337 | 335.5418 | 0.47875 |  | 8434 | 42.12 | 43.4139 | 3 | 335.5418
8435 | 44.48 | 44.9448 | 36.5882 | 230.3351 | 0.47834 |  | 8435 | 53.41 | 44.9448 | 2.2679 | 230.3351
8436 | 48.03 | 49.5917 | 41.8076 | 314.7621 | 0.48672 |  | 8436 | 51.13 | 49.5917 | 2 | 314.7621
8437 | 46.31 | 52.3774 | 36.7775 | 252.7291 | 0.49802 |  | 8437 | 56.81 | 52.3774 | 2.2679 | 252.7291
8438 | 46.69 | 52.1928 | 36.3739 | 243.9553 | 0.50644 |  | 8438 | 52.44 | 52.1928 | 3 | 243.9553
8439 | 47.65 | 59.9959 | 48.6655 | 251.4508 | 0.50657 |  | 8439 | 43.64 | 59.9959 | 4 | 251.4508
8440 | 46.75 | 77.4962 | 39.8838 | 288.6533 | 0.50729 |  | 8440 | 49.68 | 77.4962 | 5 | 288.6533
8441 | 50.39 | 107.2691 | 50.4673 | 343.5647 | 0.49964 |  | 8441 | 50.68 | 107.2691 | 5.7321 | 343.5647
8442 | 54.19 | 150.3546 | 50.7687 | 330.6175 | 0.4865 |  | 8442 | 54.8 | 150.3546 | 6 | 330.6175
8443 | 51 | 163.0519 | 54.9389 | 340.9343 | 0.47573 |  | 8443 | 61.01 | 163.0519 | 5.7321 | 340.9343
8444 | 46.3 | 148.9087 | 28.1306 | 381.4349 | 0.47596 |  | 8444 | 60 | 148.9087 | 5 | 381.4349
8445 | 43.85 | 123.0057 | 32.5704 | 409.8264 | 0.46424 |  | 8445 | 43.98 | 123.0057 | 4 | 409.8264
8446 | 39.15 | 109.4603 | 24.8277 | 403.0961 | 0.45111 |  | 8446 | 35 | 109.4603 | 3 | 403.0961
8447 | 35.9 | 80.7997 | 31.2916 | 377.2965 | 0.43852 |  | 8447 | 31.28 | 80.7997 | 2.2679 | 377.2965
8448 | 31.97 | 40.7201 | 22.9259 | 348.9466 | 0.43211 |  | 8448 | 31.21 | 40.7201 | 2 | 348.9466
8449 | 27.38 | 32.8376 | 23.5626 | 290.247 | 0.42888 |  | 8449 | 31.55 | 32.8376 | 2.2679 | 290.247
8450 | 24.36 | 31.4644 | 20.4631 | 342.7428 | 0.4278 |  | 8450 | 29.99 | 31.4644 | 3 | 342.7428
8451 | 24.36 | 30.0593 | 16.6457 | 351.3417 | 0.4171 |  | 8451 | 29.75 | 30.0593 | 4 | 351.3417
8452 | 22.4 | 28.8336 | 28.1539 | 392.1571 | 0.41162 |  | 8452 | 32.04 | 28.8336 | 5 | 392.1571
8453 | 15.66 | 28.1898 | 29.6454 | 439.0694 | 0.41318 |  | 8453 | 31.9 | 28.1898 | 5.7321 | 439.0694
8454 | 18.27 | 27.7447 | 30.6985 | 405.4408 | 0.41646 |  | 8454 | 32.99 | 27.7447 | 6 | 405.4408
8455 | 30.84 | 42.9224 | 28.7949 | 525.4368 | 0.42811 |  | 8455 | 39.34 | 42.9224 | 5.7321 | 525.4368
8456 | 40 | 66.3444 | 50.6918 | 405.9449 | 0.44423 |  | 8456 | 40.12 | 66.3444 | 5 | 405.9449
8457 | 42.95 | 52.0184 | 33.1516 | 364.1071 | 0.44796 |  | 8457 | 35.31 | 52.0184 | 4 | 364.1071
8458 | 39.62 | 44.5629 | 39.9027 | 445.5854 | 0.45592 |  | 8458 | 36.88 | 44.5629 | 3 | 445.5854
8459 | 37.86 | 46.0928 | 46.0946 | 353.9894 | 0.45712 |  | 8459 | 43.71 | 46.0928 | 2.2679 | 353.9894
8460 | 37.69 | 46.1272 | 42.3205 | 267.717 | 0.45172 |  | 8460 | 41.94 | 46.1272 | 2 | 267.717
8461 | 36.87 | 52.6475 | 44.2668 | 241.1847 | 0.45306 |  | 8461 | 51.92 | 52.6475 | 2.2679 | 241.1847
8462 | 37.11 | 51.673 | 37.0788 | 241.1973 | 0.45709 |  | 8462 | 52 | 51.673 | 3 | 241.1973
8463 | 36.8 | 57.1976 | 31.7223 | 321.5418 | 0.46271 |  | 8463 | 49.78 | 57.1976 | 4 | 321.5418
8464 | 38.72 | 74.8097 | 36.4735 | 245.7544 | 0.46539 |  | 8464 | 45.82 | 74.8097 | 5 | 245.7544
8465 | 39.49 | 106.5542 | 36.6568 | 345.9977 | 0.45906 |  | 8465 | 47.43 | 106.5542 | 5.7321 | 345.9977
8466 | 40.31 | 162.9261 | 250.1009 | 403.3021 | 0.44752 |  | 8466 | 49.98 | 162.9261 | 6 | 403.3021
8467 | 39.91 | 166.9061 | 55.969 | 447.9448 | 0.44094 |  | 8467 | 57.44 | 166.9061 | 5.7321 | 447.9448
8468 | 38.97 | 133.2755 | 28.5456 | 452.36 | 0.44519 |  | 8468 | 43.58 | 133.2755 | 5 | 452.36
8469 | 35.68 | 111.8104 | 28.9498 | 419.8066 | 0.44214 |  | 8469 | 35.21 | 111.8104 | 4 | 419.8066
8470 | 35.09 | 99.663 | 30.2361 | 377.8671 | 0.43448 |  | 8470 | 37.52 | 99.663 | 3 | 377.8671
8471 | 34.14 | 72.6972 | 24.6219 | 375.6521 | 0.42865 |  | 8471 | 42.6 | 72.6972 | 2.2679 | 375.6521
8472 | 30.4 | 37.7003 | 34.991 | 410.4065 | 0.42473 |  | 8472 | 40.1 | 37.7003 | 2 | 410.4065
8473 | 26.56 | 35.4343 | 31.5389 | 381.6455 | 0.41261 |  | 8473 | 32.56 | 35.4343 | 2.2679 | 381.6455
8474 | 25.95 | 33.4731 | 220.376 | 310.6501 | 0.41155 |  | 8474 | 31.42 | 33.4731 | 3 | 310.6501
8475 | 25.78 | 31.7279 | 37.4758 | 302.7108 | 0.4159 |  | 8475 | 31.78 | 31.7279 | 4 | 302.7108
8476 | 16.54 | 30.1616 | 28.1803 | 333.5161 | 0.41815 |  | 8476 | 33.16 | 30.1616 | 5 | 333.5161
8477 | 21.22 | 29.0405 | 29.4713 | 383.439 | 0.41989 |  | 8477 | 32.44 | 29.0405 | 5.7321 | 383.439
8478 | 29.21 | 28.8953 | 30.8986 | 505.9276 | 0.42416 |  | 8478 | 34.28 | 28.8953 | 6 | 505.9276
8479 | 34.1 | 42.8294 | 31.3883 | 488.2401 | 0.43076 |  | 8479 | 32.95 | 42.8294 | 5.7321 | 488.2401
8480 | 37.56 | 67.2595 | 41.8055 | 435.1407 | 0.44486 |  | 8480 | 40.1 | 67.2595 | 5 | 435.1407
8481 | 39.39 | 51.3398 | 45.9715 | 509.8799 | 0.44577 |  | 8481 | 55.3 | 51.3398 | 4 | 509.8799
8482 | 44.9 | 42.9743 | 49.1325 | 490.3937 | 0.44558 |  | 8482 | 67.44 | 42.9743 | 3 | 490.3937
8483 | 39.19 | 43.6492 | 40.9107 | 369.8836 | 0.43964 |  | 8483 | 75.1 | 43.6492 | 2.2679 | 369.8836
8484 | 47 | 46.7822 | 45.2558 | 306.6639 | 0.42845 |  | 8484 | 74.99 | 46.7822 | 2 | 306.6639
8485 | 39.02 | 50.7148 | 40.4082 | 281.6189 | 0.42003 |  | 8485 | 73.03 | 50.7148 | 2.2679 | 281.6189
8486 | 54 | 52.0644 | 42.4241 | 302.1523 | 0.42305 |  | 8486 | 71.56 | 52.0644 | 3 | 302.1523
8487 | 44.9 | 57.6145 | 41.3167 | 285.3419 | 0.42133 |  | 8487 | 71.48 | 57.6145 | 4 | 285.3419
8488 | 38.66 | 73.2434 | 35.3661 | 297.9112 | 0.42805 |  | 8488 | 71.26 | 73.2434 | 5 | 297.9112
8489 | 38.69 | 103.7813 | 38.1434 | 373.8129 | 0.44023 |  | 8489 | 72.99 | 103.7813 | 5.7321 | 373.8129
8490 | 49.9 | 150.389 | 39.7012 | 393.1642 | 0.4361 |  | 8490 | 69.24 | 150.389 | 6 | 393.1642
8491 | 38.71 | 159.2683 | 24.2799 | 470.7945 | 0.427 |  | 8491 | 79.86 | 159.2683 | 5.7321 | 470.7945
8492 | 37 | 133.1121 | 26.1027 | 384.5198 | 0.42486 |  | 8492 | 66 | 133.1121 | 5 | 384.5198
8493 | 34.01 | 118.5081 | 35.8309 | 367.9881 | 0.41579 |  | 8493 | 60.53 | 118.5081 | 4 | 367.9881
8494 | 34.96 | 110.7303 | 25.6945 | 336.2328 | 0.41022 |  | 8494 | 46.5 | 110.7303 | 3 | 336.2328
8495 | 32 | 79.4493 | 35.7209 | 425.0118 | 0.40145 |  | 8495 | 46.17 | 79.4493 | 2.2679 | 425.0118
8496 | 29.9 | 41.2308 | 24.6707 | 346.2969 | 0.39964 |  | 8496 | 40.1 | 41.2308 | 2 | 346.2969
8497 | 27.4 | 35.7099 | 35.8777 | 421.0747 | 0.40546 |  | 8497 | 35.19 | 35.7099 | 2.2679 | 421.0747
8498 | 27.5 | 33.855 | 22.2563 | 395.12 | 0.41095 |  | 8498 | 32.9 | 33.855 | 3 | 395.12
8499 | 10 | 31.9173 | 23.4637 | 303.6988 | 0.4117 |  | 8499 | 34.6 | 31.9173 | 4 | 303.6988
8500 | 30.83 | 30.2568 | 30.9654 | 394.2373 | 0.42299 |  | 8500 | 34.26 | 30.2568 | 5 | 394.2373
8501 | 31.67 | 29.2784 | 29.2584 | 370.9127 | 0.42252 |  | 8501 | 32.05 | 29.2784 | 5.7321 | 370.9127
8502 | 30.6 | 29.0018 | 30.9499 | 427.2545 | 0.43052 |  | 8502 | 34.76 | 29.0018 | 6 | 427.2545
8503 | 29.9 | 44.9652 | 31.3643 | 474.5372 | 0.43393 |  | 8503 | 38.34 | 44.9652 | 5.7321 | 474.5372
8504 | 34.18 | 67.3188 | 47.931 | 523.4795 | 0.43467 |  | 8504 | 43.27 | 67.3188 | 5 | 523.4795
8505 | 30.98 | 52.2344 | 38.9205 | 399.8299 | 0.443 |  | 8505 | 55.34 | 52.2344 | 4 | 399.8299
8506 | 34.76 | 44.7792 | 51.9111 | 342.9212 | 0.44966 |  | 8506 | 60.93 | 44.7792 | 3 | 342.9212
8507 | 36 | 47.7701 | 41.3684 | 383.7439 | 0.45871 |  | 8507 | 64.82 | 47.7701 | 2.2679 | 383.7439
8508 | 36.32 | 48.8882 | 45.0167 | 309.4873 | 0.4594 |  | 8508 | 63.75 | 48.8882 | 2 | 309.4873
8509 | 36.23 | 51.9319 | 38.3206 | 417.7115 | 0.45836 |  | 8509 | 58.92 | 51.9319 | 2.2679 | 417.7115
8510 | 35 | 54.3977 | 42.7647 | 333.2003 | 0.46152 |  | 8510 | 54.49 | 54.3977 | 3 | 333.2003
8511 | 35.6 | 61.3662 | 42.2361 | 351.5517 | 0.4642 |  | 8511 | 47.6 | 61.3662 | 4 | 351.5517
8512 | 36.99 | 79.8089 | 34.5109 | 278.2253 | 0.4664 |  | 8512 | 47.95 | 79.8089 | 5 | 278.2253
8513 | 36.95 | 109.0242 | 48.5598 | 413.0974 | 0.46309 |  | 8513 | 59.89 | 109.0242 | 5.7321 | 413.0974
8514 | 39.93 | 158.5505 | 42.5681 | 357.4237 | 0.4585 |  | 8514 | 61.86 | 158.5505 | 6 | 357.4237
8515 | 37.76 | 172.7295 | 53.7892 | 444.478 | 0.45258 |  | 8515 | 75.55 | 172.7295 | 5.7321 | 444.478
8516 | 36.92 | 147.2881 | 227.2957 | 459.2936 | 0.44535 |  | 8516 | 74.52 | 147.2881 | 5 | 459.2936
8517 | 31 | 121.0866 | 23.9718 | 466.8384 | 0.437 |  | 8517 | 62.53 | 121.0866 | 4 | 466.8384
8518 | 30.2 | 109.365 | 31.336 | 393.2123 | 0.43164 |  | 8518 | 53.43 | 109.365 | 3 | 393.2123
8519 | 29 | 78.111 | 33.1202 | 392.8887 | 0.42317 |  | 8519 | 43.25 | 78.111 | 2.2679 | 392.8887
8520 | 29 | 41.6195 | 22.7966 | 404.4433 | 0.41915 |  | 8520 | 43.2 | 41.6195 | 2 | 404.4433
8521 | 18.43 | 34.2425 | 32.804 | 386.2194 | 0.40435 |  | 8521 | 36.28 | 34.2425 | 2.2679 | 386.2194
8522 | 24 | 32.5389 | 34.0441 | 328.2421 | 0.4059 |  | 8522 | 31.7 | 32.5389 | 3 | 328.2421
8523 | 18.1 | 30.9487 | 25.5485 | 327.347 | 0.41102 |  | 8523 | 31.35 | 30.9487 | 4 | 327.347
8524 | 28.5 | 29.5776 | 34.7565 | 355.0357 | 0.41226 |  | 8524 | 31.74 | 29.5776 | 5 | 355.0357
8525 | 27.5 | 28.6593 | 32.7634 | 491.5883 | 0.42044 |  | 8525 | 31.35 | 28.6593 | 5.7321 | 491.5883
8526 | 23 | 28.5406 | 31.8909 | 395.5115 | 0.43351 |  | 8526 | 30.56 | 28.5406 | 6 | 395.5115
8527 | 29 | 42.9498 | 35.1234 | 493.2344 | 0.44213 |  | 8527 | 31.34 | 42.9498 | 5.7321 | 493.2344
8528 | 26.5 | 66.9646 | 42.681 | 543.5006 | 0.45072 |  | 8528 | 35.63 | 66.9646 | 5 | 543.5006
8529 | 31 | 53.7728 | 54.7089 | 465.8525 | 0.46367 |  | 8529 | 46.97 | 53.7728 | 4 | 465.8525
8530 | 35 | 46.6933 | 46.1754 | 430.4471 | 0.48541 |  | 8530 | 38.88 | 46.6933 | 3 | 430.4471
8531 | 38.71 | 48.75 | 42.0573 | 389.3928 | 0.50102 |  | 8531 | 46.27 | 48.75 | 2.2679 | 389.3928
8532 | 40.14 | 49.8695 | 41.8355 | 389.3711 | 0.51193 |  | 8532 | 46.9 | 49.8695 | 2 | 389.3711
8533 | 35 | 54.3134 | 37.9495 | 315.8964 | 0.51769 |  | 8533 | 40.68 | 54.3134 | 2.2679 | 315.8964
8534 | 35.89 | 54.8106 | 37.6448 | 305.1382 | 0.51348 |  | 8534 | 35 | 54.8106 | 3 | 305.1382
8535 | 36.14 | 63.2277 | 37.3127 | 374.6594 | 0.50655 |  | 8535 | 35.35 | 63.2277 | 4 | 374.6594
8536 | 38.28 | 78.094 | 44.4715 | 349.3837 | 0.50559 |  | 8536 | 35.82 | 78.094 | 5 | 349.3837
8537 | 37.52 | 113.6969 | 50.7947 | 430.1008 | 0.50526 |  | 8537 | 46.65 | 113.6969 | 5.7321 | 430.1008
8538 | 41.49 | 149.2139 | 37.594 | 432.3469 | 0.50005 |  | 8538 | 47.95 | 149.2139 | 6 | 432.3469
8539 | 38.68 | 160.1863 | 38.9118 | 496.0149 | 0.48008 |  | 8539 | 49.94 | 160.1863 | 5.7321 | 496.0149
8540 | 37 | 148.3539 | 24.9614 | 495.8314 | 0.46581 |  | 8540 | 47 | 148.3539 | 5 | 495.8314
8541 | 34.77 | 118.9446 | 29.2321 | 440.2856 | 0.45367 |  | 8541 | 46.65 | 118.9446 | 4 | 440.2856
8542 | 32 | 108.0683 | 28.2424 | 469.8568 | 0.43117 |  | 8542 | 40.1 | 108.0683 | 3 | 469.8568
8543 | 32.62 | 78.1619 | 23.2191 | 446.1269 | 0.41137 |  | 8543 | 37.22 | 78.1619 | 2.2679 | 446.1269
8544 | 18.67 | 40.3022 | 39.1023 | 443.388 | 0.41025 |  | 8544 | 37.58 | 40.3022 | 2 | 443.388
8545 | 24 | 33.7925 | 41.3942 | 421.2511 | 0.4138 |  | 8545 | 33.94 | 33.7925 | 2.2679 | 421.2511
8546 | 30.81 | 32.4322 | 29.3625 | 357.0793 | 0.41987 |  | 8546 | 34.34 | 32.4322 | 3 | 357.0793
8547 | 30 | 30.997 | 32.2566 | 368.7629 | 0.42313 |  | 8547 | 32.72 | 30.997 | 4 | 368.7629
8548 | 30.16 | 29.5889 | 35.0146 | 440.4628 | 0.41863 |  | 8548 | 31.7 | 29.5889 | 5 | 440.4628
8549 | 25 | 28.5337 | 28.9906 | 518.0458 | 0.41148 |  | 8549 | 32.07 | 28.5337 | 5.7321 | 518.0458
8550 | 2.59 | 27.8409 | 31.9485 | 494.2222 | 0.41463 |  | 8550 | 34.9 | 27.8409 | 6 | 494.2222
8551 | 24.5 | 27.4452 | 25.4984 | 492.2415 | 0.42606 |  | 8551 | 33.33 | 27.4452 | 5.7321 | 492.2415
8552 | 30.6 | 30.4454 | 48.2724 | 483.6246 | 0.43885 |  | 8552 | 39.24 | 30.4454 | 5 | 483.6246
8553 | 37.58 | 54.2473 | 241.7839 | 455.7909 | 0.45163 |  | 8553 | 51.84 | 54.2473 | 4 | 455.7909
8554 | 37.56 | 68.1759 | 49.8417 | 516.1841 | 0.45729 |  | 8554 | 50.15 | 68.1759 | 3 | 516.1841
8555 | 37.4 | 74.6101 | 42.173 | 456.1415 | 0.45629 |  | 8555 | 52.67 | 74.6101 | 2.2679 | 456.1415
8556 | 37.3 | 76.0133 | 34.1835 | 394.3459 | 0.44519 |  | 8556 | 57.77 | 76.0133 | 2 | 394.3459
8557 | 35.94 | 77.8785 | 50.3572 | 264.8858 | 0.44092 |  | 8557 | 56.5 | 77.8785 | 2.2679 | 264.8858
8558 | 34.9 | 73.9652 | 29.2151 | 180.9913 | 0.44264 |  | 8558 | 55.24 | 73.9652 | 3 | 180.9913
8559 | 35.9 | 70.1673 | 44.9509 | 149.1906 | 0.44399 |  | 8559 | 53.7 | 70.1673 | 4 | 149.1906
8560 | 37.42 | 73.6414 | 36.2958 | 212.6756 | 0.4413 |  | 8560 | 52.78 | 73.6414 | 5 | 212.6756
8561 | 37.18 | 89.5523 | 52.6594 | 342.6976 | 0.44093 |  | 8561 | 55.6 | 89.5523 | 5.7321 | 342.6976
8562 | 40 | 129.6857 | 29.0572 | 391.3263 | 0.44108 |  | 8562 | 58.19 | 129.6857 | 6 | 391.3263
8563 | 40.93 | 155.6748 | 38.6096 | 405.4047 | 0.43901 |  | 8563 | 55.7 | 155.6748 | 5.7321 | 405.4047
8564 | 39.22 | 145.2905 | 25.8059 | 487.8139 | 0.43975 |  | 8564 | 59.02 | 145.2905 | 5 | 487.8139
8565 | 35.98 | 112.7803 | 32.2146 | 366.5972 | 0.43527 |  | 8565 | 45 | 112.7803 | 4 | 366.5972
8566 | 34.63 | 102.1485 | 26.827 | 418.9363 | 0.42903 |  | 8566 | 39.94 | 102.1485 | 3 | 418.9363
8567 | 33.14 | 87.8464 | 28.7483 | 434.4292 | 0.41799 |  | 8567 | 37.66 | 87.8464 | 2.2679 | 434.4292
8568 | 32.4 | 40.743 | 32.1541 | 360.4737 | 0.41416 |  | 8568 | 38.62 | 40.743 | 2 | 360.4737
8569 | 35.18 | 32.8582 | 225.5404 | 350.499 | 0.41626 |  | 8569 | 34.95 | 32.8582 | 2.2679 | 350.499
8570 | 35.05 | 31.5374 | 27.5207 | 400.4324 | 0.41523 |  | 8570 | 29.02 | 31.5374 | 3 | 400.4324
8571 | 32.32 | 30.1777 | 22.594 | 395.8016 | 0.41743 |  | 8571 | 29.58 | 30.1777 | 4 | 395.8016
8572 | 27.09 | 28.9321 | 30.6044 | 446.0812 | 0.40055 |  | 8572 | 31.2 | 28.9321 | 5 | 446.0812
8573 | 10.87 | 28.0971 | 23.3474 | 578.4182 | 0.40091 |  | 8573 | 29.94 | 28.0971 | 5.7321 | 578.4182
8574 | 12.52 | 27.5455 | 25.9066 | 624.8756 | 0.40486 |  | 8574 | 29.72 | 27.5455 | 6 | 624.8756
8575 | 30.01 | 27.2103 | 23.1477 | 658.6452 | 0.41231 |  | 8575 | 30 | 27.2103 | 5.7321 | 658.6452
8576 | 35.24 | 30.3311 | 39.4357 | 516.8211 | 0.43223 |  | 8576 | 36.3 | 30.3311 | 5 | 516.8211
8577 | 35.22 | 54.6745 | 51.011 | 564.1307 | 0.44835 |  | 8577 | 44.86 | 54.6745 | 4 | 564.1307
8578 | 37 | 69.2902 | 39.8325 | 464.414 | 0.45494 |  | 8578 | 50.91 | 69.2902 | 3 | 464.414
8579 | 33.55 | 75.3277 | 46.9201 | 473.4134 | 0.45284 |  | 8579 | 51.1 | 75.3277 | 2.2679 | 473.4134
8580 | 37 | 73.4174 | 36.4446 | 444.2737 | 0.45617 |  | 8580 | 50.87 | 73.4174 | 2 | 444.2737
8581 | 35.93 | 73.8166 | 49.6177 | 304.8058 | 0.45126 |  | 8581 | 48.89 | 73.8166 | 2.2679 | 304.8058
8582 | 36.8 | 77.9884 | 40.9403 | 373.4474 | 0.44419 |  | 8582 | 45.09 | 77.9884 | 3 | 373.4474
8583 | 36.85 | 71.0007 | 53.2815 | 330.1486 | 0.44477 |  | 8583 | 44.31 | 71.0007 | 4 | 330.1486
8584 | 36.31 | 71.0885 | 37.2602 | 450.325 | 0.4477 |  | 8584 | 40.42 | 71.0885 | 5 | 450.325
8585 | 39.53 | 84.165 | 37.1557 | 475.6997 | 0.45272 |  | 8585 | 38.62 | 84.165 | 5.7321 | 475.6997
8586 | 41.63 | 116.2959 | 53.7084 | 459.6884 | 0.45566 |  | 8586 | 46.53 | 116.2959 | 6 | 459.6884
8587 | 36.51 | 148.0386 | 30.7933 | 469.5585 | 0.44979 |  | 8587 | 48.39 | 148.0386 | 5.7321 | 469.5585
8588 | 34.03 | 166.9899 | 33.0721 | 517.0806 | 0.44257 |  | 8588 | 40.84 | 166.9899 | 5 | 517.0806
8589 | 35.41 | 116.9072 | 18.7849 | 480.0061 | 0.43619 |  | 8589 | 38.15 | 116.9072 | 4 | 480.0061
8590 | 31.5 | 100.8258 | 27.6093 | 357.3655 | 0.43674 |  | 8590 | 36.28 | 100.8258 | 3 | 357.3655
8591 | 34.9 | 86.32 | 25.6449 | 453.6162 | 0.43995 |  | 8591 | 33 | 86.32 | 2.2679 | 453.6162
8592 | 30.5 | 39.1392 | 27.8111 | 417.8866 | 0.4472 |  | 8592 | 35 | 39.1392 | 2 | 417.8866
8593 | 26 | 34.4688 | 20.5884 | 346.2416 | 0.45136 |  | 8593 | 34.38 | 34.4688 | 2.2679 | 346.2416
8594 | 26 | 32.6668 | 25.4483 | 298.2021 | 0.43864 |  | 8594 | 31.99 | 32.6668 | 3 | 298.2021
8595 | 15.34 | 30.9909 | 26.1744 | 282.4665 | 0.42691 |  | 8595 | 32.6 | 30.9909 | 4 | 282.4665
8596 | 11.46 | 29.6041 | 24.7669 | 392.7114 | 0.42073 |  | 8596 | 31.99 | 29.6041 | 5 | 392.7114
8597 | 9.62 | 28.7192 | 31.3287 | 381.7687 | 0.41551 |  | 8597 | 29.94 | 28.7192 | 5.7321 | 381.7687
8598 | 15.71 | 28.6185 | 30.7598 | 448.6901 | 0.41648 |  | 8598 | 30.13 | 28.6185 | 6 | 448.6901
8599 | 9.56 | 43.3123 | 32.7575 | 515.6065 | 0.41434 |  | 8599 | 30.29 | 43.3123 | 5.7321 | 515.6065
8600 | 16.55 | 66.1047 | 49.9593 | 485.7165 | 0.41567 |  | 8600 | 32.15 | 66.1047 | 5 | 485.7165
8601 | 27.85 | 51.5705 | 231.5336 | 419.0192 | 0.42115 |  | 8601 | 34.93 | 51.5705 | 4 | 419.0192
8602 | 33.1 | 43.2446 | 51.5644 | 388.3184 | 0.43149 |  | 8602 | 39.41 | 43.2446 | 3 | 388.3184
8603 | 34.6 | 44.8567 | 50.0929 | 461.6495 | 0.43905 |  | 8603 | 49.73 | 44.8567 | 2.2679 | 461.6495
8604 | 34.81 | 47.1828 | 35.1169 | 347.809 | 0.45087 |  | 8604 | 51.23 | 47.1828 | 2 | 347.809
8605 | 32.5 | 51.9184 | 52.7803 | 397.7205 | 0.45181 |  | 8605 | 50.1 | 51.9184 | 2.2679 | 397.7205
8606 | 34.4 | 51.1859 | 30.0918 | 356.9125 | 0.45671 |  | 8606 | 50 | 51.1859 | 3 | 356.9125
8607 | 34.96 | 58.5494 | 53.5516 | 318.7316 | 0.46729 |  | 8607 | 50.18 | 58.5494 | 4 | 318.7316
8608 | 35.28 | 73.2774 | 32.5194 | 340.9599 | 0.47479 |  | 8608 | 38.01 | 73.2774 | 5 | 340.9599
8609 | 38.42 | 106.826 | 48.276 | 368.4013 | 0.46426 |  | 8609 | 37.82 | 106.826 | 5.7321 | 368.4013
8610 | 47.3 | 151.6348 | 42.812 | 397.5359 | 0.46549 |  | 8610 | 42 | 151.6348 | 6 | 397.5359
8611 | 42.46 | 173.0314 | 44.5571 | 498.4751 | 0.46866 |  | 8611 | 58.75 | 173.0314 | 5.7321 | 498.4751
8612 | 38.53 | 134.8886 | 31.7671 | 483.9217 | 0.48089 |  | 8612 | 55.32 | 134.8886 | 5 | 483.9217
8613 | 34.85 | 116.9583 | 31.0298 | 513.384 | 0.48098 |  | 8613 | 55 | 116.9583 | 4 | 513.384
8614 | 34.63 | 107.6298 | 30.604 | 578.6473 | 0.47873 |  | 8614 | 39.94 | 107.6298 | 3 | 578.6473
8615 | 34.94 | 75.5447 | 24.9789 | 488.6748 | 0.47762 |  | 8615 | 39.94 | 75.5447 | 2.2679 | 488.6748
8616 | 32.09 | 40.0079 | 28.7148 | 471.788 | 0.46603 |  | 8616 | 50.14 | 40.0079 | 2 | 471.788
8617 | 34.42 | 32.9368 | 28.4794 | 591.8995 | 0.46839 |  | 8617 | 37.44 | 32.9368 | 2.2679 | 591.8995
8618 | 34.01 | 31.5854 | 25.4953 | 611.0652 | 0.47174 |  | 8618 | 34 | 31.5854 | 3 | 611.0652
8619 | 31.87 | 30.1583 | 30.4608 | 534.0422 | 0.46915 |  | 8619 | 29.49 | 30.1583 | 4 | 534.0422
8620 | 31.56 | 29.0179 | 22.3577 | 622.0349 | 0.47162 |  | 8620 | 28.8 | 29.0179 | 5 | 622.0349
8621 | 32.01 | 28.2183 | 30.5587 | 533.2498 | 0.47246 |  | 8621 | 26.7 | 28.2183 | 5.7321 | 533.2498
8622 | 26.16 | 28.1331 | 33.2031 | 554.0443 | 0.47185 |  | 8622 | 19.78 | 28.1331 | 6 | 554.0443
8623 | 26.11 | 43.4966 | 26.4644 | 567.197 | 0.46817 |  | 8623 | 16.12 | 43.4966 | 5.7321 | 567.197
8624 | 26.3 | 66.2445 | 29.0861 | 452.5827 | 0.46699 |  | 8624 | 17.1 | 66.2445 | 5 | 452.5827
8625 | 29.75 | 51.8199 | 40.4249 | 489.5826 | 0.46576 |  | 8625 | 22.24 | 51.8199 | 4 | 489.5826
8626 | 34.31 | 43.766 | 50.6101 | 561.2587 | 0.46264 |  | 8626 | 20.98 | 43.766 | 3 | 561.2587
8627 | 34.95 | 44.2168 | 46.0935 | 348.0914 | 0.45628 |  | 8627 | 35.04 | 44.2168 | 2.2679 | 348.0914
8628 | 35.71 | 46.274 | 46.6295 | 309.7354 | 0.45238 |  | 8628 | 39.94 | 46.274 | 2 | 309.7354
8629 | 35.5 | 50.3482 | 38.7559 | 257.7516 | 0.45248 |  | 8629 | 42.39 | 50.3482 | 2.2679 | 257.7516
8630 | 34.96 | 52.4657 | 37.3425 | 290.1978 | 0.44938 |  | 8630 | 44.74 | 52.4657 | 3 | 290.1978
8631 | 36.11 | 57.6769 | 46.0966 | 245.7726 | 0.44734 |  | 8631 | 38.65 | 57.6769 | 4 | 245.7726
8632 | 37.49 | 74.7608 | 230.5542 | 263.7426 | 0.45027 |  | 8632 | 32 | 74.7608 | 5 | 263.7426
8633 | 39.06 | 108.6117 | 33.5357 | 378.1828 | 0.45187 |  | 8633 | 31 | 108.6117 | 5.7321 | 378.1828
8634 | 42.55 | 154.9597 | 248.1083 | 480.2208 | 0.44786 |  | 8634 | 35 | 154.9597 | 6 | 480.2208
8635 | 42.64 | 161.8585 | 39.267 | 455.7379 | 0.44026 |  | 8635 | 44.75 | 161.8585 | 5.7321 | 455.7379
8636 | 40.92 | 137.0379 | 30.535 | 482.5456 | 0.43401 |  | 8636 | 44.99 | 137.0379 | 5 | 482.5456
8637 | 37.24 | 113.2148 | 20.609 | 613.7798 | 0.42885 |  | 8637 | 42 | 113.2148 | 4 | 613.7798
8638 | 36.42 | 106.8699 | 29.7363 | 560.1632 | 0.42875 |  | 8638 | 38 | 106.8699 | 3 | 560.1632
8639 | 35.96 | 76.0338 | 27.6914 | 471.9819 | 0.43778 |  | 8639 | 34.39 | 76.0338 | 2.2679 | 471.9819
8640 | 34.25 | 37.9606 | 24.8046 | 424.21 | 0.43694 |  | 8640 | 35 | 37.9606 | 2 | 424.21
8641 | 30.81 | 33.9887 | 34.4501 | 460.4528 | 0.43787 |  | 8641 | 32.7 | 33.9887 | 2.2679 | 460.4528
8642 | 29.51 | 32.3459 | 32.4558 | 374.3981 | 0.43706 |  | 8642 | 29.55 | 32.3459 | 3 | 374.3981
8643 | 27.8 | 30.7703 | 31.4839 | 338.8521 | 0.43604 |  | 8643 | 25.7 | 30.7703 | 4 | 338.8521
8644 | 27.8 | 29.3766 | 32.5246 | 461.4305 | 0.4322 |  | 8644 | 26.31 | 29.3766 | 5 | 461.4305
8645 | 27.92 | 28.5879 | 23.0222 | 395.8889 | 0.43588 |  | 8645 | 21.97 | 28.5879 | 5.7321 | 395.8889
8646 | 29.76 | 28.6166 | 25.2573 | 536.3374 | 0.44064 |  | 8646 | 15.35 | 28.6166 | 6 | 536.3374
8647 | 31.98 | 44.0371 | 37.344 | 444.8518 | 0.44372 |  | 8647 | 22.66 | 44.0371 | 5.7321 | 444.8518
8648 | 37.48 | 66.5954 | 45.6916 | 500.7686 | 0.44839 |  | 8648 | 25.54 | 66.5954 | 5 | 500.7686
8649 | 38 | 50.5106 | 47.6431 | 489.1501 | 0.44886 |  | 8649 | 30.44 | 50.5106 | 4 | 489.1501
8650 | 39.77 | 42.4288 | 41.3124 | 445.4281 | 0.44924 |  | 8650 | 31.94 | 42.4288 | 3 | 445.4281
8651 | 39.83 | 43.1354 | 37.6975 | 435.9211 | 0.45126 |  | 8651 | 37.44 | 43.1354 | 2.2679 | 435.9211
8652 | 40.17 | 45.2847 | 37.8299 | 436.5803 | 0.45269 |  | 8652 | 45.67 | 45.2847 | 2 | 436.5803
8653 | 40 | 49.842 | 32.1998 | 313.9786 | 0.46066 |  | 8653 | 47.83 | 49.842 | 2.2679 | 313.9786
8654 | 40.04 | 51.5003 | 45.6294 | 359.3698 | 0.46724 |  | 8654 | 45.73 | 51.5003 | 3 | 359.3698
8655 | 41.27 | 57.8936 | 49.3057 | 374.652 | 0.47136 |  | 8655 | 35.99 | 57.8936 | 4 | 374.652
8656 | 43.52 | 71.7561 | 40.1594 | 380.7143 | 0.47317 |  | 8656 | 34.94 | 71.7561 | 5 | 380.7143
8657 | 45.06 | 104.3268 | 242.956 | 454.7418 | 0.46964 |  | 8657 | 35 | 104.3268 | 5.7321 | 454.7418
8658 | 48.19 | 151.7853 | 39.2208 | 446.4378 | 0.45858 |  | 8658 | 49.02 | 151.7853 | 6 | 446.4378
8659 | 44.88 | 162.8951 | 47.6326 | 509.0957 | 0.45649 |  | 8659 | 56.12 | 162.8951 | 5.7321 | 509.0957
8660 | 43.99 | 142.9085 | 25.6242 | 479.9262 | 0.45733 |  | 8660 | 56.19 | 142.9085 | 5 | 479.9262
8661 | 39.52 | 112.6829 | 24.2632 | 541.2487 | 0.45508 |  | 8661 | 50.03 | 112.6829 | 4 | 541.2487
8662 | 36.67 | 104.059 | 31.9416 | 582.7606 | 0.45204 |  | 8662 | 44.72 | 104.059 | 3 | 582.7606
8663 | 35.38 | 76.273 | 27.5865 | 495.2326 | 0.45217 |  | 8663 | 37.99 | 76.273 | 2.2679 | 495.2326
8664 | 33.57 | 39.6459 | 33.0859 | 494.4264 | 0.4509 |  | 8664 | 35 | 39.6459 | 2 | 494.4264
8665 | 30.17 | 34.481 | 29.74 | 410.8265 | 0.44555 |  | 8665 | 32.6 | 34.481 | 2.2679 | 410.8265
8666 | 29.5 | 32.8168 | 23.0083 | 472.9074 | 0.44974 |  | 8666 | 31.8 | 32.8168 | 3 | 472.9074
8667 | 29.13 | 31.206 | 33.7736 | 596.5684 | 0.45717 |  | 8667 | 28.76 | 31.206 | 4 | 596.5684
8668 | 27.92 | 29.7666 | 34.8254 | 475.1462 | 0.45394 |  | 8668 | 29.94 | 29.7666 | 5 | 475.1462
8669 | 27.9 | 28.6844 | 32.4075 | 583.2134 | 0.44585 |  | 8669 | 31.99 | 28.6844 | 5.7321 | 583.2134
8670 | 27.05 | 28.4573 | 22.4871 | 528.1482 | 0.4471 |  | 8670 | 29.69 | 28.4573 | 6 | 528.1482
8671 | 28.57 | 43.1335 | 31.6149 | 563.8048 | 0.45181 |  | 8671 | 28.35 | 43.1335 | 5.7321 | 563.8048
8672 | 30.86 | 66.6738 | 48.8657 | 732.4934 | 0.45858 |  | 8672 | 30.99 | 66.6738 | 5 | 732.4934
8673 | 33.93 | 52.3342 | 45.7068 | 599.907 | 0.47069 |  | 8673 | 42.08 | 52.3342 | 4 | 599.907
8674 | 36.6 | 44.8937 | 47.0028 | 642.6296 | 0.47414 |  | 8674 | 33.63 | 44.8937 | 3 | 642.6296
8675 | 35.61 | 46.2052 | 60.5665 | 477.8763 | 0.46777 |  | 8675 | 42.44 | 46.2052 | 2.2679 | 477.8763
8676 | 35.05 | 48.9339 | 38.982 | 380.1909 | 0.46083 |  | 8676 | 44.43 | 48.9339 | 2 | 380.1909
8677 | 34.7 | 52.2939 | 45.0252 | 461.3361 | 0.46465 |  | 8677 | 35.12 | 52.2939 | 2.2679 | 461.3361
8678 | 33.65 | 51.5294 | 40.8714 | 355.6631 | 0.47311 |  | 8678 | 34.94 | 51.5294 | 3 | 355.6631
8679 | 35.2 | 60.8194 | 38.5422 | 446.2977 | 0.47496 |  | 8679 | 39.94 | 60.8194 | 4 | 446.2977
8680 | 36.48 | 76.5252 | 43.5233 | 368.1622 | 0.47778 |  | 8680 | 39.99 | 76.5252 | 5 | 368.1622
8681 | 39.19 | 107.3918 | 34.7729 | 504.9067 | 0.47971 |  | 8681 | 44.94 | 107.3918 | 5.7321 | 504.9067
8682 | 40.79 | 162.677 | 41.3215 | 585.6066 | 0.47369 |  | 8682 | 49.06 | 162.677 | 6 | 585.6066
8683 | 43.75 | 155.6482 | 241.6028 | 474.0334 | 0.46572 |  | 8683 | 43.41 | 155.6482 | 5.7321 | 474.0334
8684 | 43.29 | 136.76 | 31.5194 | 535.6736 | 0.45743 |  | 8684 | 40.91 | 136.76 | 5 | 535.6736
8685 | 39.62 | 121.2604 | 24.3489 | 613.7776 | 0.4578 |  | 8685 | 41.99 | 121.2604 | 4 | 613.7776
8686 | 35.39 | 111.1491 | 25.1146 | 569.5083 | 0.45547 |  | 8686 | 40.1 | 111.1491 | 3 | 569.5083
8687 | 34.75 | 77.5965 | 21.4543 | 431.2997 | 0.44422 |  | 8687 | 44 | 77.5965 | 2.2679 | 431.2997
8688 | 30.17 | 40.0774 | 25.3157 | 510.4424 | 0.44028 |  | 8688 | 42.44 | 40.0774 | 2 | 510.4424
8689 | 30.6 | 35.2262 | 31.854 | 508.7241 | 0.43632 |  | 8689 | 40.84 | 35.2262 | 2.2679 | 508.7241
8690 | 28.1 | 33.4714 | 35.0358 | 436.4711 | 0.42377 |  | 8690 | 31.94 | 33.4714 | 3 | 436.4711
8691 | 26.92 | 31.7853 | 34.1222 | 561.3652 | 0.42371 |  | 8691 | 32.6 | 31.7853 | 4 | 561.3652
8692 | 22.85 | 30.0792 | 28.3253 | 480.2741 | 0.42994 |  | 8692 | 29.98 | 30.0792 | 5 | 480.2741
8693 | 20.97 | 29.0825 | 37.0006 | 668.3866 | 0.43162 |  | 8693 | 28.7 | 29.0825 | 5.7321 | 668.3866
8694 | 21.31 | 28.8266 | 27.1322 | 709.9958 | 0.42603 |  | 8694 | 30.94 | 28.8266 | 6 | 709.9958
8695 | 22.72 | 44.2326 | 37.2157 | 722.7188 | 0.4225 |  | 8695 | 30.96 | 44.2326 | 5.7321 | 722.7188
8696 | 25.1 | 65.7513 | 41.19 | 606.7802 | 0.42348 |  | 8696 | 34.03 | 65.7513 | 5 | 606.7802
8697 | 27.52 | 51.7461 | 36.754 | 629.5592 | 0.41933 |  | 8697 | 47.6 | 51.7461 | 4 | 629.5592
8698 | 30.04 | 44.74 | 47.7355 | 605.4557 | 0.4166 |  | 8698 | 47.25 | 44.74 | 3 | 605.4557
8699 | 36.05 | 45.0251 | 37.778 | 498.6064 | 0.42772 |  | 8699 | 56.5 | 45.0251 | 2.2679 | 498.6064
8700 | 35.45 | 47.9079 | 32.4288 | 417.5172 | 0.42513 |  | 8700 | 57.95 | 47.9079 | 2 | 417.5172
8701 | 32.03 | 50.8884 | 52.2685 | 326.671 | 0.4179 |  | 8701 | 59.13 | 50.8884 | 2.2679 | 326.671
8702 | 30.61 | 55.2192 | 33.0305 | 336.0396 | 0.41554 |  | 8702 | 59.2 | 55.2192 | 3 | 336.0396
8703 | 30.8 | 62.6859 | 42.3914 | 280.0605 | 0.42497 |  | 8703 | 55.82 | 62.6859 | 4 | 280.0605
8704 | 32.89 | 75.82 | 36.4591 | 347.3555 | 0.43051 |  | 8704 | 50.77 | 75.82 | 5 | 347.3555
8705 | 33.97 | 105.8831 | 31.4629 | 359.8295 | 0.43434 |  | 8705 | 51.6 | 105.8831 | 5.7321 | 359.8295
8706 | 43.92 | 150.5216 | 39.4057 | 430.6658 | 0.43365 |  | 8706 | 55.2 | 150.5216 | 6 | 430.6658
8707 | 46.09 | 162.433 | 42.7176 | 482.637 | 0.42599 |  | 8707 | 63.83 | 162.433 | 5.7321 | 482.637
8708 | 46.24 | 141.4921 | 29.5816 | 434.9505 | 0.42664 |  | 8708 | 63.7 | 141.4921 | 5 | 434.9505
8709 | 45.33 | 117.6168 | 24.9764 | 453.6971 | 0.42138 |  | 8709 | 59.82 | 117.6168 | 4 | 453.6971
8710 | 40.68 | 106.6581 | 25.945 | 424.7519 | 0.42024 |  | 8710 | 52.06 | 106.6581 | 3 | 424.7519
8711 | 36.82 | 76.8107 | 27.6922 | 415.6114 | 0.41368 |  | 8711 | 50 | 76.8107 | 2.2679 | 415.6114
8712 | 30.4 | 40.6474 | 223.9111 | 466.751 | 0.39834 |  | 8712 | 43.18 | 40.6474 | 2 | 466.751
8713 | 30.12 | 35.715 | 25.2247 | 422.3784 | 0.38457 |  | 8713 | 35.23 | 35.715 | 2.2679 | 422.3784
8714 | 30.03 | 33.8572 | 22.5521 | 446.6816 | 0.37446 |  | 8714 | 42.2 | 33.8572 | 3 | 446.6816
8715 | 27.69 | 31.9944 | 29.4063 | 436.6416 | 0.36803 |  | 8715 | 39.3 | 31.9944 | 4 | 436.6416
8716 | 23.89 | 30.465 | 30.213 | 431.8126 | 0.36654 |  | 8716 | 36.83 | 30.465 | 5 | 431.8126
8717 | 22.95 | 29.2631 | 39.4439 | 394.7003 | 0.36667 |  | 8717 | 34.11 | 29.2631 | 5.7321 | 394.7003
8718 | 24.9 | 28.3153 | 18.7759 | 542.1757 | 0.37332 |  | 8718 | 34.99 | 28.3153 | 6 | 542.1757
8719 | 30.5 | 27.656 | 29.6025 | 515.7466 | 0.37962 |  | 8719 | 37.64 | 27.656 | 5.7321 | 515.7466
8720 | 40.1 | 29.979 | 36.0572 | 484.8143 | 0.39811 |  | 8720 | 41.05 | 29.979 | 5 | 484.8143
8721 | 43.54 | 56.3684 | 40.5216 | 447.4038 | 0.41073 |  | 8721 | 49.3 | 56.3684 | 4 | 447.4038
8722 | 42.42 | 69.0846 | 49.9062 | 377.8491 | 0.41057 |  | 8722 | 50.43 | 69.0846 | 3 | 377.8491
8723 | 42.42 | 72.6408 | 48.6534 | 426.0753 | 0.41312 |  | 8723 | 51.1 | 72.6408 | 2.2679 | 426.0753
8724 | 43.13 | 73.2649 | 40.1889 | 342.1843 | 0.41791 |  | 8724 | 51.14 | 73.2649 | 2 | 342.1843
8725 | 39.05 | 76.9348 | 51.1625 | 419.4443 | 0.41785 |  | 8725 | 50.96 | 76.9348 | 2.2679 | 419.4443
8726 | 39.72 | 75.5725 | 41.2959 | 359.967 | 0.41273 |  | 8726 | 40.72 | 75.5725 | 3 | 359.967
8727 | 36.95 | 69.5023 | 43.9809 | 295.7604 | 0.41175 |  | 8727 | 43.23 | 69.5023 | 4 | 295.7604
8728 | 38.4 | 74.1559 | 39.7524 | 306.8692 | 0.40841 |  | 8728 | 49.6 | 74.1559 | 5 | 306.8692
8729 | 39.17 | 90.8501 | 40.9476 | 300.8442 | 0.40911 |  | 8729 | 51.63 | 90.8501 | 5.7321 | 300.8442
8730 | 58.97 | 126.3127 | 36.3843 | 315.1065 | 0.41098 |  | 8730 | 54.43 | 126.3127 | 6 | 315.1065
8731 | 48.78 | 163.1619 | 52.2395 | 300.9455 | 0.40906 |  | 8731 | 63.95 | 163.1619 | 5.7321 | 300.9455
8732 | 53.27 | 146.7061 | 34.0235 | 350.463 | 0.41398 |  | 8732 | 57.2 | 146.7061 | 5 | 350.463
8733 | 39 | 120.2722 | 25.2958 | 287.9127 | 0.4154 |  | 8733 | 48.07 | 120.2722 | 4 | 287.9127
8734 | 34.81 | 105.9116 | 29.7686 | 251.4812 | 0.40677 |  | 8734 | 40 | 105.9116 | 3 | 251.4812
8735 | 32.89 | 91.3445 | 24.3498 | 220.3857 | 0.40611 |  | 8735 | 39.94 | 91.3445 | 2.2679 | 220.3857
8736 | 32.2 | 42.2307 | 30.777 | 223.0296 | 0.41073 |  | 8736 | 34.83 | 42.2307 | 2 | 223.0296
8737 | 29.4 | 34.7835 | 30.6664 | 211.6423 | 0.41502 |  | 8737 | 32.44 | 34.7835 | 2.2679 | 211.6423
8738 | 30 | 33.1881 | 35.3252 | 205.8239 | 0.41779 |  | 8738 | 36.01 | 33.1881 | 3 | 205.8239
8739 | 30.31 | 31.5301 | 35.1235 | 210.3702 | 0.41433 |  | 8739 | 35.96 | 31.5301 | 4 | 210.3702
8740 | 32.87 | 29.9361 | 29.872 | 217.3851 | 0.4138 |  | 8740 | 32.06 | 29.9361 | 5 | 217.3851
8741 | 33 | 28.7928 | 229.9948 | 260.3651 | 0.4187 |  | 8741 | 32.54 | 28.7928 | 5.7321 | 260.3651
8742 | 32.87 | 28.029 | 25.1175 | 313.0833 | 0.42198 |  | 8742 | 33.09 | 28.029 | 6 | 313.0833
8743 | 33.29 | 27.5882 | 24.5004 | 331.3091 | 0.43144 |  | 8743 | 33.09 | 27.5882 | 5.7321 | 331.3091
8744 | 32.96 | 30.1386 | 40.9353 | 312.2515 | 0.44667 |  | 8744 | 33.94 | 30.1386 | 5 | 312.2515
8745 | 36.56 | 56.0152 | 51.1845 | 262.0197 | 0.45711 |  | 8745 | 46 | 56.0152 | 4 | 262.0197
8746 | 41.85 | 69.1294 | 27.4644 | 235.1366 | 0.47012 |  | 8746 | 47.04 | 69.1294 | 3 | 235.1366
8747 | 47.76 | 71.9435 | 41.1982 | 307.0467 | 0.468 |  | 8747 | 47.19 | 71.9435 | 2.2679 | 307.0467
8748 | 38.98 | 74.3287 | 47.442 | 297.8507 | 0.46837 |  | 8748 | 43 | 74.3287 | 2 | 297.8507
8749 | 38.6 | 77.553 | 43.5471 | 226.5067 | 0.45954 |  | 8749 | 37.27 | 77.553 | 2.2679 | 226.5067
8750 | 37.9 | 78.2899 | 53.3145 | 241.3518 | 0.4629 |  | 8750 | 36.3 | 78.2899 | 3 | 241.3518
8751 | 38 | 72.8488 | 32.3741 | 239.7633 | 0.46953 |  | 8751 | 36.72 | 72.8488 | 4 | 239.7633
8752 | 39.58 | 72.6644 | 42.1164 | 253.1008 | 0.47344 |  | 8752 | 46 | 72.6644 | 5 | 253.1008
8753 | 42.28 | 83.6886 | 56.08 | 275.9215 | 0.47484 |  | 8753 | 52.63 | 83.6886 | 5.7321 | 275.9215
8754 | 46.06 | 120.3762 | 29.5645 | 365.3866 | 0.47309 |  | 8754 | 54.38 | 120.3762 | 6 | 365.3866
8755 | 47.73 | 136.0602 | 46.1755 | 314.2005 | 0.46888 |  | 8755 | 56.04 | 136.0602 | 5.7321 | 314.2005
8756 | 46 | 146.8617 | 36.7694 | 330.6638 | 0.46971 |  | 8756 | 49.94 | 146.8617 | 5 | 330.6638
8757 | 42.2 | 114.2598 | 31.655 | 304.2201 | 0.46925 |  | 8757 | 45 | 114.2598 | 4 | 304.2201
8758 | 39.74 | 100.8686 | 30.5553 | 334.8592 | 0.46989 |  | 8758 | 43.32 | 100.8686 | 3 | 334.8592
8759 | 38.88 | 86.2691 | 27.3242 | 271.4792 | 0.47165 |  | 8759 | 41.03 | 86.2691 | 2.2679 | 271.4792
8760 | 37.21 | 40.6764 | 26.9002 | 256.8858 | 0.47163 |  | 8760 | 40.55 | 40.6764 | 2 | 256.8858
30.12.2016 23:00 - 31.12.2016 00:00 | 36.8 | [5 empty] | 30.12.2016 23:00 - 31.12.2016 00:00 | 36.8
31.12.2016 00:00 - 31.12.2016 01:00 | 41.8 | [5 empty] | 31.12.2016 00:00 - 31.12.2016 01:00 | 41.8
31.12.2016 01:00 - 31.12.2016 02:00 | 40.84 | [5 empty] | 31.12.2016 01:00 - 31.12.2016 02:00 | 40.84
31.12.2016 02:00 - 31.12.2016 03:00 | 39 | [5 empty] | 31.12.2016 02:00 - 31.12.2016 03:00 | 39
31.12.2016 03:00 - 31.12.2016 04:00 | 34.49 | [5 empty] | 31.12.2016 03:00 - 31.12.2016 04:00 | 34.49
31.12.2016 04:00 - 31.12.2016 05:00 | 35 | [5 empty] | 31.12.2016 04:00 - 31.12.2016 05:00 | 35
31.12.2016 05:00 - 31.12.2016 06:00 | 35.1 | [5 empty] | 31.12.2016 05:00 - 31.12.2016 06:00 | 35.1
31.12.2016 06:00 - 31.12.2016 07:00 | 31.99 | [5 empty] | 31.12.2016 06:00 - 31.12.2016 07:00 | 31.99
31.12.2016 07:00 - 31.12.2016 08:00 | 34.41 | [5 empty] | 31.12.2016 07:00 - 31.12.2016 08:00 | 34.41
31.12.2016 08:00 - 31.12.2016 09:00 | 40 | [5 empty] | 31.12.2016 08:00 - 31.12.2016 09:00 | 40
31.12.2016 09:00 - 31.12.2016 10:00 | 47.4 | [5 empty] | 31.12.2016 09:00 - 31.12.2016 10:00 | 47.4
31.12.2016 10:00 - 31.12.2016 11:00 | 47.4 | [5 empty] | 31.12.2016 10:00 - 31.12.2016 11:00 | 47.4
31.12.2016 11:00 - 31.12.2016 12:00 | 47.4 | [5 empty] | 31.12.2016 11:00 - 31.12.2016 12:00 | 47.4
31.12.2016 12:00 - 31.12.2016 13:00 | 47.4 | [5 empty] | 31.12.2016 12:00 - 31.12.2016 13:00 | 47.4
31.12.2016 13:00 - 31.12.2016 14:00 | 50.04 | [5 empty] | 31.12.2016 13:00 - 31.12.2016 14:00 | 50.04
31.12.2016 14:00 - 31.12.2016 15:00 | 47.4 | [5 empty] | 31.12.2016 14:00 - 31.12.2016 15:00 | 47.4
31.12.2016 15:00 - 31.12.2016 16:00 | 47.4 | [5 empty] | 31.12.2016 15:00 - 31.12.2016 16:00 | 47.4
31.12.2016 16:00 - 31.12.2016 17:00 | 49.76 | [5 empty] | 31.12.2016 16:00 - 31.12.2016 17:00 | 49.76
31.12.2016 17:00 - 31.12.2016 18:00 | 53.98 | [5 empty] | 31.12.2016 17:00 - 31.12.2016 18:00 | 53.98
31.12.2016 18:00 - 31.12.2016 19:00 | 49.76 | [5 empty] | 31.12.2016 18:00 - 31.12.2016 19:00 | 49.76
31.12.2016 19:00 - 31.12.2016 20:00 | 40.84 | [5 empty] | 31.12.2016 19:00 - 31.12.2016 20:00 | 40.84
31.12.2016 20:00 - 31.12.2016 21:00 | 40.1 | [5 empty] | 31.12.2016 20:00 - 31.12.2016 21:00 | 40.1
31.12.2016 21:00 - 31.12.2016 22:00 | 36 | [5 empty] | 31.12.2016 21:00 - 31.12.2016 22:00 | 36
31.12.2016 22:00 - 31.12.2016 23:00 | 35 | [5 empty] | 31.12.2016 22:00 - 31.12.2016 23:00 | 35
31.12.2016 23:00 - 01.01.2017 00:00 | 34.94 | [5 empty] | 31.12.2016 23:00 - 01.01.2017 00:00 | 34.94
Note on D2: Annelies Boerman: from GROHW-Demand cf A1fuelst

## data table
wind [MW]
|  |  | 940 | 1880 | 2820 | 3760 | 4700 | 5640 | 6580 | 7520 | 8460 | 9400
|  | 0.84783 | 2.5 | 1.25 | 0.83333 | 0.625 | 0.5 | 0.41667 | 0.35714 | 0.3125 | 0.27778 | 0.25
PV [kWp] | 300 | 1686.3
| 600 | 3372.6
| 900 | 5058.9
| 1200 | 6745.2
| 1500 | 8431.5
| 1800 | 10117.8
| 2100 | 11804.1
| 2400 | 13490.4
| 2700 | 15176.7
| 3000 | 16863
wind [MW]
|  |  | 940 | 1880 | 2820 | 3760 | 4700 | 5640 | 6580 | 7520 | 8460 | 9400
|  | -0.022625 | 2.5 | 1.25 | 0.83333 | 0.625 | 0.5 | 0.41667 | 0.35714 | 0.3125 | 0.27778 | 0.25
PV [kWp] | 300 | 1686.3
| 600 | 3372.6
| 900 | 5058.9
| 1200 | 6745.2
| 1500 | 8431.5
| 1800 | 10117.8
| 2100 | 11804.1
| 2400 | 13490.4
| 2700 | 15176.7
| 3000 | 16863

## output
total results local energy sources + electricity import | [13 empty] | costs
De* | Dg* | Dg,h* | Ph,g | Ph,ng | Ing | Sg | Pg | St | De,g | De,c | Ce,g | Ie | Ee | C_Ie
kWh | kg | kg | kWh | kWh | kWh | kg | kg | kg | kWh | kWh | kWh | kWh | kWh | Euro
0 | 28.9376 | 0 | 0 | 0 | 0 | -28.9376 | 0 | 721.0624 | 0 | 0 | 0 | 0 | 0 | 0
0 | 29.1815 | 0 | 0 | 0 | 0 | -29.1815 | 0 | 691.8809 | 0 | 0 | 0 | 0 | 0 | 0
0 | 35.9061 | 0 | 0 | 0 | 0 | -35.9061 | 0 | 655.9748 | 0 | 0 | 0 | 0 | 0 | 0
0 | 30.1971 | 0 | 0 | 0 | 0 | 22.3029 | 52.5 | 678.2777 | 3000 | 39.8523 | 3039.8523 | 3039.8523 | 0 | 197.4992
0 | 39.6806 | 0 | 0 | 0 | 0 | 12.8194 | 52.5 | 691.0971 | 3000 | 22.9066 | 3022.9066 | 3022.9066 | 0 | 189.4153
0 | 28.9379 | 0 | 0 | 0 | 0 | 23.5621 | 52.5 | 714.6592 | 3000 | 42.1023 | 3042.1023 | 3042.1023 | 0 | 191.6524
0 | 34.4637 | 0 | 0 | 0 | 0 | 18.0363 | 52.5 | 732.6955 | 3000 | 32.2286 | 3032.2286 | 3032.2286 | 0 | 196.3368
0 | 49.7149 | 0 | 0 | 0 | 0 | -49.7149 | 0 | 682.9807 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.0359 | 0 | 0 | 0 | 0 | 0.46409 | 52.5 | 683.4448 | 3000 | 0.82927 | 3000.8293 | 2984.607 | 0 | 178.4795
0 | 39.1974 | 0 | 0 | 0 | 0 | 13.3026 | 52.5 | 696.7473 | 3000 | 23.7699 | 3023.7699 | 2915.6214 | 0 | 188.2908
0 | 42.405 | 0 | 0 | 0 | 0 | -42.405 | 0 | 654.3423 | 0 | 0 | 0 | 0 | 135.1856 | 0
0 | 52.6496 | 0 | 0 | 0 | 0 | -52.6496 | 0 | 601.6927 | 0 | 0 | 0 | 0 | 254.149 | 0
0 | 44.2398 | 0 | 0 | 0 | 0 | -44.2398 | 0 | 557.4528 | 0 | 0 | 0 | 0 | 173.0376 | 0
0 | 49.0333 | 0 | 0 | 0 | 0 | 3.4667 | 52.5 | 560.9195 | 3000 | 6.1945 | 3006.1945 | 2822.3421 | 0 | 185.5972
0 | 46.7205 | 0 | 0 | 0 | 0 | 5.7795 | 52.5 | 566.6991 | 3000 | 10.3273 | 3010.3273 | 2902.1788 | 0 | 188.4094
0 | 55.1097 | 0 | 0 | 0 | 0 | -2.6097 | 52.5 | 564.0894 | 3000 | 0 | 3000 | 2989.1851 | 0 | 194.4465
0 | 43.1132 | 0 | 0 | 0 | 0 | 9.3868 | 52.5 | 573.4762 | 3000 | 16.773 | 3016.773 | 3016.773 | 0 | 197.9003
0 | 41.6424 | 0 | 0 | 0 | 0 | -41.6424 | 0 | 531.8339 | 0 | 0 | 0 | 0 | 0 | 0
0 | 51.4645 | 0 | 0 | 0 | 0 | 1.0355 | 52.5 | 532.8694 | 3000 | 1.8504 | 3001.8504 | 3001.8504 | 0 | 196.6512
0 | 23.9224 | 0 | 0 | 0 | 0 | 28.5776 | 52.5 | 561.447 | 3000 | 51.0643 | 3051.0643 | 3051.0643 | 0 | 190.2339
0 | 27.3412 | 0 | 0 | 0 | 0 | 25.1588 | 52.5 | 586.6058 | 3000 | 44.9555 | 3044.9555 | 3044.9555 | 0 | 199.1401
0 | 35.8974 | 0 | 0 | 0 | 0 | 16.6026 | 52.5 | 603.2084 | 3000 | 29.6667 | 3029.6667 | 3029.6667 | 0 | 189.4451
0 | 22.2632 | 0 | 0 | 0 | 0 | 30.2368 | 52.5 | 633.4452 | 3000 | 54.0292 | 3054.0292 | 3054.0292 | 0 | 201.7492
0 | 31.9763 | 0 | 0 | 0 | 0 | 20.5237 | 52.5 | 653.9689 | 3000 | 36.673 | 3036.673 | 3036.673 | 0 | 189.9439
0 | 24.3883 | 0 | 0 | 0 | 0 | 28.1117 | 52.5 | 682.0806 | 3000 | 50.2319 | 3050.2319 | 3050.2319 | 0 | 195.2148
0 | 32.4641 | 0 | 0 | 0 | 0 | 20.0359 | 52.5 | 702.1165 | 3000 | 35.8015 | 3035.8015 | 3035.8015 | 0 | 187.0054
0 | 24.5208 | 0 | 0 | 0 | 0 | 27.9792 | 52.5 | 730.0957 | 3000 | 49.9951 | 3049.9951 | 3049.9951 | 0 | 187.8797
0 | 25.5111 | 0 | 0 | 0 | 0 | 26.9889 | 52.5 | 757.0846 | 3000 | 48.2255 | 3048.2255 | 3048.2255 | 0 | 185.1187
0 | 33.3961 | 0 | 0 | 0 | 0 | 19.1039 | 52.5 | 776.1885 | 3000 | 34.1361 | 3034.1361 | 3034.1361 | 0 | 185.1126
0 | 24.9132 | 0 | 0 | 0 | 0 | 27.5868 | 52.5 | 803.7753 | 3000 | 49.2939 | 3049.2939 | 3049.2939 | 0 | 187.3791
0 | 29.3418 | 0 | 0 | 0 | 0 | 23.1582 | 52.5 | 826.9335 | 3000 | 41.3806 | 3041.3806 | 3041.3806 | 0 | 191.1812
0 | 39.5093 | 0 | 0 | 0 | 0 | 12.9907 | 52.5 | 839.9242 | 3000 | 23.2126 | 3023.2126 | 3023.2126 | 0 | 194.9972
0 | 47.9677 | 0 | 0 | 0 | 0 | 4.5323 | 52.5 | 844.4564 | 3000 | 8.0986 | 3008.0986 | 2970.2466 | 0 | 200.254
0 | 248.5421 | 0 | 0 | 0 | 0 | -196.0421 | 52.5 | 648.4143 | 3000 | 0 | 3000 | 2870.2218 | 0 | 193.5104
0 | 45.9085 | 0 | 0 | 0 | 0 | 6.5915 | 52.5 | 655.0059 | 3000 | 11.7782 | 3011.7782 | 2757.6292 | 0 | 185.7539
0 | 48.5094 | 0 | 0 | 0 | 0 | 3.9906 | 52.5 | 658.9964 | 3000 | 7.1306 | 3007.1306 | 2601.5737 | 0 | 174.1493
0 | 42.1889 | 0 | 0 | 0 | 0 | 10.3111 | 52.5 | 669.3075 | 3000 | 18.4245 | 3018.4245 | 2666.9419 | 0 | 177.5917
0 | 48.4479 | 0 | 0 | 0 | 0 | 4.0521 | 52.5 | 673.3596 | 3000 | 7.2406 | 3007.2406 | 2693.6099 | 0 | 179.8523
0 | 54.0008 | 0 | 0 | 0 | 0 | -1.5008 | 52.5 | 671.8588 | 3000 | 0 | 3000 | 2886.4441 | 0 | 195.1525
0 | 43.9271 | 0 | 0 | 0 | 0 | -43.9271 | 0 | 627.9317 | 0 | 0 | 0 | 0 | 10.8149 | 0
0 | 46.6585 | 0 | 0 | 0 | 0 | -46.6585 | 0 | 581.2732 | 0 | 0 | 0 | 0 | 0 | 0
0 | 43.5524 | 0 | 0 | 0 | 0 | -43.5524 | 0 | 537.7208 | 0 | 0 | 0 | 0 | 0 | 0
0 | 43.9588 | 0 | 0 | 0 | 0 | -43.9588 | 0 | 493.762 | 0 | 0 | 0 | 0 | 0 | 0
0 | 31.2894 | 0 | 0 | 0 | 0 | -31.2894 | 0 | 462.4726 | 0 | 0 | 0 | 0 | 0 | 0
0 | 30.5482 | 0 | 0 | 0 | 0 | -30.5482 | 0 | 431.9244 | 0 | 0 | 0 | 0 | 0 | 0
0 | 30.2655 | 0 | 0 | 0 | 0 | -30.2655 | 0 | 401.6589 | 0 | 0 | 0 | 0 | 0 | 0
0 | 24.8339 | 0 | 0 | 0 | 0 | 27.6661 | 52.5 | 429.325 | 3000 | 49.4357 | 3049.4357 | 3049.4357 | 0 | 209.8317
0 | 28.2249 | 0 | 0 | 0 | 0 | 24.2751 | 52.5 | 453.6001 | 3000 | 43.3764 | 3043.3764 | 3043.3764 | 0 | 205.2149
0 | 23.9772 | 0 | 0 | 0 | 0 | 28.5228 | 52.5 | 482.1229 | 3000 | 50.9665 | 3050.9665 | 3050.9665 | 0 | 198.6789
0 | 27.9619 | 0 | 0 | 0 | 0 | 24.5381 | 52.5 | 506.6611 | 3000 | 43.8463 | 3043.8463 | 3043.8463 | 0 | 189.0229
0 | 25.8889 | 0 | 0 | 0 | 0 | 26.6111 | 52.5 | 533.2721 | 3000 | 47.5504 | 3047.5504 | 3047.5504 | 0 | 187.1196
0 | 23.8979 | 0 | 0 | 0 | 0 | 28.6021 | 52.5 | 561.8742 | 3000 | 51.1082 | 3051.1082 | 3051.1082 | 0 | 180.0154
0 | 28.6893 | 0 | 0 | 0 | 0 | 23.8107 | 52.5 | 585.685 | 3000 | 42.5466 | 3042.5466 | 3042.5466 | 0 | 179.1451
0 | 30.9944 | 0 | 0 | 0 | 0 | 21.5056 | 52.5 | 607.1906 | 3000 | 38.4277 | 3038.4277 | 3038.4277 | 0 | 185.101
0 | 36.1961 | 0 | 0 | 0 | 0 | 16.3039 | 52.5 | 623.4944 | 3000 | 29.1328 | 3029.1328 | 3029.1328 | 0 | 204.3453
0 | 42.1813 | 0 | 0 | 0 | 0 | -42.1813 | 0 | 581.3132 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 43.9248 | 0 | 0 | 0 | 0 | -43.9248 | 0 | 537.3883 | 0 | 0 | 0 | 0 | 54.0743 | 0
0 | 49.6227 | 0 | 0 | 0 | 0 | -49.6227 | 0 | 487.7656 | 0 | 0 | 0 | 0 | 146.0005 | 0
0 | 37.8531 | 0 | 0 | 0 | 0 | -37.8531 | 0 | 449.9125 | 0 | 0 | 0 | 0 | 275.7787 | 0
0 | 231.6315 | 0 | 0 | 0 | 0 | -231.6315 | 0 | 218.281 | 0 | 0 | 0 | 0 | 281.1861 | 0
0 | 41.9285 | 0 | 0 | 0 | 0 | -35.8722 | 6.0563 | 182.4088 | 346.0752 | 0 | 346.0752 | 0 | 0 | 0
0 | 28.5706 | 0 | 0 | 0 | 0 | -28.5706 | 0 | 153.8382 | 0 | 0 | 0 | 0 | 124.3708 | 0
0 | 57.7758 | 0 | 0 | 0 | 0 | -57.7758 | 0 | 96.0624 | 0 | 0 | 0 | 0 | 81.1114 | 0
0 | 25.2863 | 0 | 0 | 0 | 0 | -25.2863 | 0 | 70.7761 | 0 | 0 | 0 | 0 | 21.6297 | 0
0 | 46.8403 | 0 | 0 | 0 | 0 | -46.8403 | 0 | 23.9358 | 0 | 0 | 0 | 0 | 0 | 0
0 | 23.9358 | 0 | 0 | 0 | 0 | -23.9358 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 22.0088 | 0 | 0 | 0 | 0 | 30.4912 | 52.5 | 30.4912 | 3000 | 54.4838 | 3054.4838 | 3054.4838 | 0 | 210.179
0 | 28.3787 | 0 | 0 | 0 | 0 | 24.1213 | 52.5 | 54.6126 | 3000 | 43.1016 | 3043.1016 | 3043.1016 | 0 | 197.7407
0 | 35.2363 | 0 | 0 | 0 | 0 | 17.2637 | 52.5 | 71.8763 | 3000 | 30.8479 | 3030.8479 | 3030.8479 | 0 | 201.9454
0 | 22.4102 | 0 | 0 | 0 | 0 | 30.0898 | 52.5 | 101.9661 | 3000 | 53.7665 | 3053.7665 | 3053.7665 | 0 | 189.6694
0 | 31.9103 | 0 | 0 | 0 | 0 | 20.5897 | 52.5 | 122.5558 | 3000 | 36.791 | 3036.791 | 3036.791 | 0 | 188.4936
0 | 24.9303 | 0 | 0 | 0 | 0 | 27.5697 | 52.5 | 150.1255 | 3000 | 49.2635 | 3049.2635 | 3049.2635 | 0 | 186.6454
0 | 35.8227 | 0 | 0 | 0 | 0 | 16.6773 | 52.5 | 166.8029 | 3000 | 29.8001 | 3029.8001 | 3029.8001 | 0 | 187.8476
0 | 219.3029 | 0 | 0 | 0 | 0 | -166.8029 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 185.73
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8149 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.6297 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.2594 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.0743 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.852 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.0371 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.2223 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 35.1875 | 0 | 0 | 0 | 0 | 17.3125 | 52.5 | 17.3125 | 3000 | 30.9352 | 3030.9352 | 3030.9352 | 0 | 205.2852
0 | 23.4989 | 0 | 0 | 0 | 0 | 29.0011 | 52.5 | 46.3136 | 3000 | 51.8211 | 3051.8211 | 3051.8211 | 0 | 204.8382
0 | 29.8849 | 0 | 0 | 0 | 0 | 22.6151 | 52.5 | 68.9287 | 3000 | 40.4101 | 3040.4101 | 3040.4101 | 0 | 201.9744
0 | 27.9688 | 0 | 0 | 0 | 0 | 24.5312 | 52.5 | 93.4599 | 3000 | 43.834 | 3043.834 | 3043.834 | 0 | 199.7973
0 | 31.2013 | 0 | 0 | 0 | 0 | 21.2987 | 52.5 | 114.7586 | 3000 | 38.058 | 3038.058 | 3038.058 | 0 | 197.5345
0 | 22.9091 | 0 | 0 | 0 | 0 | 29.5909 | 52.5 | 144.3495 | 3000 | 52.8751 | 3052.8751 | 3052.8751 | 0 | 186.2254
0 | 32.0143 | 0 | 0 | 0 | 0 | 20.4857 | 52.5 | 164.8352 | 3000 | 36.6052 | 3036.6052 | 3036.6052 | 0 | 184.2612
0 | 22.1166 | 0 | 0 | 0 | 0 | 30.3834 | 52.5 | 195.2186 | 3000 | 54.291 | 3054.291 | 3054.291 | 0 | 184.7541
0 | 35.5603 | 0 | 0 | 0 | 0 | 16.9397 | 52.5 | 212.1583 | 3000 | 30.269 | 3030.269 | 3030.269 | 0 | 181.8161
0 | 22.1261 | 0 | 0 | 0 | 0 | 30.3739 | 52.5 | 242.5322 | 3000 | 54.2741 | 3054.2741 | 3054.2741 | 0 | 179.5913
0 | 23.3406 | 0 | 0 | 0 | 0 | 29.1594 | 52.5 | 271.6916 | 3000 | 52.104 | 3052.104 | 3052.104 | 0 | 185.8731
0 | 37.2854 | 0 | 0 | 0 | 0 | 15.2146 | 52.5 | 286.9062 | 3000 | 27.1865 | 3027.1865 | 3027.1865 | 0 | 186.7169
0 | 40.7334 | 0 | 0 | 0 | 0 | 11.7666 | 52.5 | 298.6728 | 3000 | 21.0253 | 3021.0253 | 2999.3956 | 0 | 199.9097
0 | 32.8957 | 0 | 0 | 0 | 0 | 19.6043 | 52.5 | 318.2771 | 3000 | 35.0302 | 3035.0302 | 2975.5486 | 0 | 200.5817
0 | 45.4595 | 0 | 0 | 0 | 0 | 7.0405 | 52.5 | 325.3175 | 3000 | 12.5804 | 3012.5804 | 2904.4319 | 0 | 196.3977
0 | 37.5915 | 0 | 0 | 0 | 0 | 14.9085 | 52.5 | 340.2261 | 3000 | 26.6396 | 3026.6396 | 2913.0836 | 0 | 197.2449
0 | 41.8928 | 0 | 0 | 0 | 0 | -41.8928 | 0 | 298.3333 | 0 | 0 | 0 | 0 | 97.3337 | 0
0 | 48.7033 | 0 | 0 | 0 | 0 | -48.7033 | 0 | 249.63 | 0 | 0 | 0 | 0 | 75.704 | 0
0 | 49.7054 | 0 | 0 | 0 | 0 | -49.7054 | 0 | 199.9246 | 0 | 0 | 0 | 0 | 32.4446 | 0
0 | 33.6307 | 0 | 0 | 0 | 0 | -33.6307 | 0 | 166.294 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 32.8219 | 0 | 0 | 0 | 0 | -32.8219 | 0 | 133.4721 | 0 | 0 | 0 | 0 | 0 | 0
0 | 43.4129 | 0 | 0 | 0 | 0 | -43.4129 | 0 | 90.0592 | 0 | 0 | 0 | 0 | 0 | 0
0 | 36.8413 | 0 | 0 | 0 | 0 | -36.8413 | 0 | 53.2179 | 0 | 0 | 0 | 0 | 0 | 0
0 | 32.8393 | 0 | 0 | 0 | 0 | -32.8393 | 0 | 20.3787 | 0 | 0 | 0 | 0 | 0 | 0
0 | 20.3787 | 0 | 0 | 0 | 0 | -20.3787 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 23.1862 | 0 | 0 | 0 | 0 | 29.3138 | 52.5 | 29.3138 | 3000 | 52.3799 | 3052.3799 | 3052.3799 | 0 | 209.4543
0 | 31.7762 | 0 | 0 | 0 | 0 | 20.7238 | 52.5 | 50.0376 | 3000 | 37.0306 | 3037.0306 | 3037.0306 | 0 | 205.9714
0 | 50.0376 | 0 | 0 | 0 | 0 | -50.0376 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 33.0922 | 0 | 0 | 0 | 0 | 19.4078 | 52.5 | 19.4078 | 3000 | 34.6792 | 3034.6792 | 3034.6792 | 0 | 203.1718
0 | 18.9229 | 0 | 0 | 0 | 0 | 33.5771 | 52.5 | 52.9849 | 3000 | 59.9978 | 3059.9978 | 3059.9978 | 0 | 198.8999
0 | 28.2923 | 0 | 0 | 0 | 0 | 24.2077 | 52.5 | 77.1927 | 3000 | 43.256 | 3043.256 | 3043.256 | 0 | 192.8816
0 | 27.6968 | 0 | 0 | 0 | 0 | 24.8032 | 52.5 | 101.9959 | 3000 | 44.3201 | 3044.3201 | 3044.3201 | 0 | 191.8531
0 | 29.9238 | 0 | 0 | 0 | 0 | 22.5762 | 52.5 | 124.5721 | 3000 | 40.3406 | 3040.3406 | 3040.3406 | 0 | 185.1871
0 | 26.377 | 0 | 0 | 0 | 0 | 26.123 | 52.5 | 150.6951 | 3000 | 46.6784 | 3046.6784 | 3046.6784 | 0 | 189.412
0 | 37.3332 | 0 | 0 | 0 | 0 | 15.1668 | 52.5 | 165.8619 | 3000 | 27.1011 | 3027.1011 | 3027.1011 | 0 | 191.2825
0 | 43.1001 | 0 | 0 | 0 | 0 | 9.3999 | 52.5 | 175.2618 | 3000 | 16.7964 | 3016.7964 | 3011.389 | 0 | 193.0601
0 | 52.5587 | 0 | 0 | 0 | 0 | -0.05867 | 52.5 | 175.2031 | 3000 | 0 | 3000 | 2967.5554 | 0 | 194.9684
0 | 42.8053 | 0 | 0 | 0 | 0 | 9.6947 | 52.5 | 184.8979 | 3000 | 17.3232 | 3017.3232 | 2882.1376 | 0 | 197.1382
0 | 45.2001 | 0 | 0 | 0 | 0 | -45.2001 | 0 | 139.6977 | 0 | 0 | 0 | 0 | 124.3708 | 0
0 | 48.3255 | 0 | 0 | 0 | 0 | -48.3255 | 0 | 91.3723 | 0 | 0 | 0 | 0 | 81.1114 | 0
0 | 32.9895 | 0 | 0 | 0 | 0 | -32.9895 | 0 | 58.3827 | 0 | 0 | 0 | 0 | 173.0376 | 0
0 | 38.7787 | 0 | 0 | 0 | 0 | -38.7787 | 0 | 19.604 | 0 | 0 | 0 | 0 | 167.6302 | 0
0 | 44.7976 | 0 | 0 | 0 | 0 | 7.7024 | 52.5 | 27.3064 | 3000 | 13.7631 | 3013.7631 | 2911.022 | 0 | 196.1738
0 | 40.2855 | 0 | 0 | 0 | 0 | 12.2145 | 52.5 | 39.5209 | 3000 | 21.8257 | 3021.8257 | 3011.0108 | 0 | 200.443
0 | 53.5259 | 0 | 0 | 0 | 0 | -1.0259 | 52.5 | 38.495 | 3000 | 0 | 3000 | 3000 | 0 | 209.13
0 | 38.495 | 0 | 0 | 0 | 0 | -38.495 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 30.977 | 0 | 0 | 0 | 0 | 21.523 | 52.5 | 21.523 | 3000 | 38.4588 | 3038.4588 | 3038.4588 | 0 | 203.2425
0 | 30.4247 | 0 | 0 | 0 | 0 | 22.0753 | 52.5 | 43.5983 | 3000 | 39.4456 | 3039.4456 | 3039.4456 | 0 | 185.4974
0 | 28.4062 | 0 | 0 | 0 | 0 | 24.0938 | 52.5 | 67.6921 | 3000 | 43.0525 | 3043.0525 | 3043.0525 | 0 | 191.6514
0 | 24.3526 | 0 | 0 | 0 | 0 | 28.1474 | 52.5 | 95.8395 | 3000 | 50.2956 | 3050.2956 | 3050.2956 | 0 | 191.6806
0 | 31.3259 | 0 | 0 | 0 | 0 | 21.1741 | 52.5 | 117.0136 | 3000 | 37.8353 | 3037.8353 | 3037.8353 | 0 | 185.6421
0 | 22.6671 | 0 | 0 | 0 | 0 | 29.8329 | 52.5 | 146.8465 | 3000 | 53.3074 | 3053.3074 | 3053.3074 | 0 | 186.496
0 | 22.858 | 0 | 0 | 0 | 0 | 29.642 | 52.5 | 176.4885 | 3000 | 52.9663 | 3052.9663 | 3052.9663 | 0 | 191.1767
0 | 176.4885 | 0 | 0 | 0 | 0 | -176.4885 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.4446 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.704 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.4817 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.8891 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.4817 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.852 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.2223 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 51.7915 | 0 | 0 | 0 | 0 | 0.70851 | 52.5 | 0.70851 | 3000 | 1.266 | 3001.266 | 3001.266 | 0 | 203.7559
0 | 31.3043 | 0 | 0 | 0 | 0 | 21.1957 | 52.5 | 21.9042 | 3000 | 37.8739 | 3037.8739 | 3037.8739 | 0 | 197.4618
0 | 34.7601 | 0 | 0 | 0 | 0 | 17.7399 | 52.5 | 39.6441 | 3000 | 31.6988 | 3031.6988 | 3031.6988 | 0 | 200.0921
0 | 21.5202 | 0 | 0 | 0 | 0 | 30.9798 | 52.5 | 70.6239 | 3000 | 55.3567 | 3055.3567 | 3055.3567 | 0 | 195.5428
0 | 23.6005 | 0 | 0 | 0 | 0 | 28.8995 | 52.5 | 99.5234 | 3000 | 51.6396 | 3051.6396 | 3051.6396 | 0 | 190.8495
0 | 33.523 | 0 | 0 | 0 | 0 | 18.977 | 52.5 | 118.5003 | 3000 | 33.9093 | 3033.9093 | 3033.9093 | 0 | 180.2142
0 | 171.0003 | 0 | 0 | 0 | 0 | -118.5003 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 155.1
0 | 25.3045 | 0 | 0 | 0 | 0 | 27.1955 | 52.5 | 27.1955 | 3000 | 48.5947 | 3048.5947 | 3048.5947 | 0 | 184.6229
0 | 35.6126 | 0 | 0 | 0 | 0 | 16.8874 | 52.5 | 44.0829 | 3000 | 30.1756 | 3030.1756 | 3030.1756 | 0 | 163.6295
0 | 23.8576 | 0 | 0 | 0 | 0 | 28.6424 | 52.5 | 72.7253 | 3000 | 51.1802 | 3051.1802 | 3051.1802 | 0 | 167.8149
0 | 23.7407 | 0 | 0 | 0 | 0 | 28.7593 | 52.5 | 101.4846 | 3000 | 51.3891 | 3051.3891 | 3051.3891 | 0 | 145.8564
0 | 26.0575 | 0 | 0 | 0 | 0 | 26.4425 | 52.5 | 127.9271 | 3000 | 47.2492 | 3047.2492 | 3047.2492 | 0 | 176.7405
0 | 27.2866 | 0 | 0 | 0 | 0 | 25.2134 | 52.5 | 153.1405 | 3000 | 45.0531 | 3045.0531 | 3045.0531 | 0 | 209.9869
0 | 52.6294 | 0 | 0 | 0 | 0 | -0.12939 | 52.5 | 153.0111 | 3000 | 0 | 3000 | 3000 | 0 | 204
0 | 43.1389 | 0 | 0 | 0 | 0 | -43.1389 | 0 | 109.8723 | 0 | 0 | 0 | 0 | 43.2594 | 0
0 | 50.5542 | 0 | 0 | 0 | 0 | -50.5542 | 0 | 59.3181 | 0 | 0 | 0 | 0 | 97.3337 | 0
0 | 51.7882 | 0 | 0 | 0 | 0 | -51.7882 | 0 | 7.5299 | 0 | 0 | 0 | 0 | 135.1856 | 0
0 | 60.0299 | 0 | 0 | 0 | 0 | -7.5299 | 52.5 | 0 | 3000 | 0 | 3000 | 2783.703 | 0 | 190.628
0 | 43.4748 | 0 | 0 | 0 | 0 | 9.0252 | 52.5 | 9.0252 | 3000 | 16.1269 | 3016.1269 | 2805.2373 | 0 | 178.6936
0 | 40.2777 | 0 | 0 | 0 | 0 | 12.2223 | 52.5 | 21.2475 | 3000 | 21.8396 | 3021.8396 | 2837.9871 | 0 | 181.6596
0 | 41.0516 | 0 | 0 | 0 | 0 | 11.4484 | 52.5 | 32.6959 | 3000 | 20.4567 | 3020.4567 | 2928.5305 | 0 | 197.3244
0 | 44.0272 | 0 | 0 | 0 | 0 | 8.4728 | 52.5 | 41.1686 | 3000 | 15.1397 | 3015.1397 | 3004.3249 | 0 | 202.4014
0 | 41.921 | 0 | 0 | 0 | 0 | 10.579 | 52.5 | 51.7477 | 3000 | 18.9033 | 3018.9033 | 3018.9033 | 0 | 204.8024
0 | 42.9007 | 0 | 0 | 0 | 0 | -42.9007 | 0 | 8.847 | 0 | 0 | 0 | 0 | 0 | 0
0 | 43.9097 | 0 | 0 | 0 | 0 | 8.5903 | 52.5 | 17.4373 | 3000 | 15.3498 | 3015.3498 | 3015.3498 | 0 | 202.9029
0 | 25.4261 | 0 | 0 | 0 | 0 | 27.0739 | 52.5 | 44.5113 | 3000 | 48.3775 | 3048.3775 | 3048.3775 | 0 | 193.2062
0 | 97.0113 | 0 | 0 | 0 | 0 | -44.5113 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 195.3
0 | 34.6662 | 0 | 0 | 0 | 0 | 17.8338 | 52.5 | 17.8338 | 3000 | 31.8667 | 3031.8667 | 3031.8667 | 0 | 200.467
0 | 32.2576 | 0 | 0 | 0 | 0 | 20.2424 | 52.5 | 38.0762 | 3000 | 36.1705 | 3036.1705 | 3036.1705 | 0 | 199.355
0 | 32.0297 | 0 | 0 | 0 | 0 | 20.4703 | 52.5 | 58.5465 | 3000 | 36.5777 | 3036.5777 | 3036.5777 | 0 | 187.4176
0 | 33.0117 | 0 | 0 | 0 | 0 | 19.4883 | 52.5 | 78.0348 | 3000 | 34.8229 | 3034.8229 | 3034.8229 | 0 | 174.8058
0 | 24.3904 | 0 | 0 | 0 | 0 | 28.1096 | 52.5 | 106.1443 | 3000 | 50.2281 | 3050.2281 | 3050.2281 | 0 | 166.2374
0 | 24.2588 | 0 | 0 | 0 | 0 | 28.2412 | 52.5 | 134.3855 | 3000 | 50.4632 | 3050.4632 | 3050.4632 | 0 | 158.6241
0 | 30.496 | 0 | 0 | 0 | 0 | 22.004 | 52.5 | 156.3895 | 3000 | 39.3182 | 3039.3182 | 3039.3182 | 0 | 174.4569
0 | 27.5075 | 0 | 0 | 0 | 0 | 24.9925 | 52.5 | 181.382 | 3000 | 44.6584 | 3044.6584 | 3044.6584 | 0 | 156.5563
0 | 22.0403 | 0 | 0 | 0 | 0 | 30.4597 | 52.5 | 211.8417 | 3000 | 54.4274 | 3054.4274 | 3054.4274 | 0 | 174.1024
0 | 34.1844 | 0 | 0 | 0 | 0 | 18.3156 | 52.5 | 230.1573 | 3000 | 32.7276 | 3032.7276 | 3032.7276 | 0 | 199.0379
0 | 45.2439 | 0 | 0 | 0 | 0 | -45.2439 | 0 | 184.9134 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 48.1079 | 0 | 0 | 0 | 0 | -48.1079 | 0 | 136.8055 | 0 | 0 | 0 | 0 | 75.704 | 0
0 | 38.6436 | 0 | 0 | 0 | 0 | -38.6436 | 0 | 98.1619 | 0 | 0 | 0 | 0 | 275.7787 | 0
0 | 49.0646 | 0 | 0 | 0 | 0 | -42.6297 | 6.4348 | 55.5322 | 367.7049 | 0 | 367.7049 | 0 | 0 | 0
0 | 50.2374 | 0 | 0 | 0 | 0 | 2.2626 | 52.5 | 57.7948 | 3000 | 4.0429 | 3004.0429 | 2544.4118 | 0 | 175.5644
0 | 41.5301 | 0 | 0 | 0 | 0 | 10.9699 | 52.5 | 68.7647 | 3000 | 19.6018 | 3019.6018 | 2614.0449 | 0 | 172.7622
0 | 54.9905 | 0 | 0 | 0 | 0 | -2.4905 | 52.5 | 66.2742 | 3000 | 0 | 3000 | 2740.4436 | 0 | 178.4029
0 | 47.071 | 0 | 0 | 0 | 0 | 5.429 | 52.5 | 71.7031 | 3000 | 9.7008 | 3009.7008 | 2874.5152 | 0 | 194.2022
0 | 40.3432 | 0 | 0 | 0 | 0 | 12.1568 | 52.5 | 83.8599 | 3000 | 21.7225 | 3021.7225 | 3005.5003 | 0 | 207.2292
0 | 25.8587 | 0 | 0 | 0 | 0 | -25.8587 | 0 | 58.0012 | 0 | 0 | 0 | 0 | 0 | 0
0 | 58.0012 | 0 | 0 | 0 | 0 | -58.0012 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 19.5394 | 0 | 0 | 0 | 0 | 32.9606 | 52.5 | 32.9606 | 3000 | 58.8961 | 3058.8961 | 3058.8961 | 0 | 213.2968
0 | 31.887 | 0 | 0 | 0 | 0 | 20.613 | 52.5 | 53.5736 | 3000 | 36.8327 | 3036.8327 | 3036.8327 | 0 | 197.4549
0 | 33.5202 | 0 | 0 | 0 | 0 | 18.9798 | 52.5 | 72.5534 | 3000 | 33.9144 | 3033.9144 | 3033.9144 | 0 | 205.214
0 | 36.0171 | 0 | 0 | 0 | 0 | 16.4829 | 52.5 | 89.0363 | 3000 | 29.4528 | 3029.4528 | 3029.4528 | 0 | 197.8536
0 | 28.021 | 0 | 0 | 0 | 0 | 24.479 | 52.5 | 113.5154 | 3000 | 43.7408 | 3043.7408 | 3043.7408 | 0 | 201.1
0 | 41.0792 | 0 | 0 | 0 | 0 | 11.4208 | 52.5 | 124.9362 | 3000 | 20.4075 | 3020.4075 | 3020.4075 | 0 | 195.1485
0 | 30.1636 | 0 | 0 | 0 | 0 | 22.3364 | 52.5 | 147.2726 | 3000 | 39.9121 | 3039.9121 | 3039.9121 | 0 | 193.4296
0 | 28.0007 | 0 | 0 | 0 | 0 | 24.4993 | 52.5 | 171.7719 | 3000 | 43.777 | 3043.777 | 3043.777 | 0 | 194.193
0 | 27.146 | 0 | 0 | 0 | 0 | 25.354 | 52.5 | 197.1259 | 3000 | 45.3042 | 3045.3042 | 3045.3042 | 0 | 193.3768
0 | 30.2858 | 0 | 0 | 0 | 0 | 22.2142 | 52.5 | 219.3401 | 3000 | 39.6939 | 3039.6939 | 3039.6939 | 0 | 196.9722
0 | 30.6458 | 0 | 0 | 0 | 0 | -30.6458 | 0 | 188.6943 | 0 | 0 | 0 | 0 | 0 | 0
0 | 42.6602 | 0 | 0 | 0 | 0 | -42.6602 | 0 | 146.0341 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.8529 | 0 | 0 | 0 | 0 | -52.8529 | 0 | 93.1812 | 0 | 0 | 0 | 0 | 21.6297 | 0
0 | 54.5596 | 0 | 0 | 0 | 0 | -54.5596 | 0 | 38.6216 | 0 | 0 | 0 | 0 | 59.4817 | 0
0 | 34.4641 | 0 | 0 | 0 | 0 | -34.4641 | 0 | 4.1576 | 0 | 0 | 0 | 0 | 75.704 | 0
0 | 4.1576 | 0 | 0 | 0 | 0 | -4.1576 | 0 | 0 | 0 | 0 | 0 | 0 | 108.1485 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7411 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 108.1485 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.8891 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8149 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 25.7918 | 0 | 0 | 0 | 0 | 26.7082 | 52.5 | 26.7082 | 3000 | 47.7241 | 3047.7241 | 3047.7241 | 0 | 201.3631
0 | 29.9687 | 0 | 0 | 0 | 0 | 22.5313 | 52.5 | 49.2396 | 3000 | 40.2605 | 3040.2605 | 3040.2605 | 0 | 185.4559
0 | 101.7396 | 0 | 0 | 0 | 0 | -49.2396 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 177.6
0 | 29.1475 | 0 | 0 | 0 | 0 | 23.3525 | 52.5 | 23.3525 | 3000 | 41.7278 | 3041.7278 | 3041.7278 | 0 | 183.8116
0 | 31.0844 | 0 | 0 | 0 | 0 | 21.4156 | 52.5 | 44.7681 | 3000 | 38.2668 | 3038.2668 | 3038.2668 | 0 | 186.6103
0 | 97.2681 | 0 | 0 | 0 | 0 | -44.7681 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 180
0 | 27.6725 | 0 | 0 | 0 | 0 | 24.8275 | 52.5 | 24.8275 | 3000 | 44.3634 | 3044.3634 | 3044.3634 | 0 | 178.0953
0 | 33.4882 | 0 | 0 | 0 | 0 | 19.0118 | 52.5 | 43.8392 | 3000 | 33.9715 | 3033.9715 | 3033.9715 | 0 | 197.2081
0 | 49.3691 | 0 | 0 | 0 | 0 | 3.1309 | 52.5 | 46.9701 | 3000 | 5.5945 | 3005.5945 | 3000.187 | 0 | 209.3531
0 | 30.8677 | 0 | 0 | 0 | 0 | -30.8677 | 0 | 16.1024 | 0 | 0 | 0 | 0 | 27.0371 | 0
0 | 16.1024 | 0 | 0 | 0 | 0 | -16.1024 | 0 | 0 | 0 | 0 | 0 | 0 | 59.4817 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.3708 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140.5931 | 0
0 | 28.2977 | 0 | 0 | 0 | 0 | 24.2023 | 52.5 | 24.2023 | 3000 | 43.2464 | 3043.2464 | 2848.5791 | 0 | 195.441
0 | 38.5729 | 0 | 0 | 0 | 0 | 13.9271 | 52.5 | 38.1295 | 3000 | 24.8859 | 3024.8859 | 2922.1448 | 0 | 197.1863
0 | 35.4517 | 0 | 0 | 0 | 0 | 17.0483 | 52.5 | 55.1778 | 3000 | 30.4631 | 3030.4631 | 2976.3889 | 0 | 196.3226
0 | 40.0605 | 0 | 0 | 0 | 0 | 12.4395 | 52.5 | 67.6173 | 3000 | 22.2277 | 3022.2277 | 3011.4128 | 0 | 197.8197
0 | 34.8538 | 0 | 0 | 0 | 0 | 17.6462 | 52.5 | 85.2635 | 3000 | 31.5314 | 3031.5314 | 3031.5314 | 0 | 200.5964
0 | 38.0373 | 0 | 0 | 0 | 0 | -38.0373 | 0 | 47.2262 | 0 | 0 | 0 | 0 | 0 | 0
0 | 42.5274 | 0 | 0 | 0 | 0 | 9.9726 | 52.5 | 57.1987 | 3000 | 17.8196 | 3017.8196 | 3017.8196 | 0 | 202.5259
0 | 25.3995 | 0 | 0 | 0 | 0 | 27.1005 | 52.5 | 84.2992 | 3000 | 48.425 | 3048.425 | 3048.425 | 0 | 202.0496
0 | 28.6898 | 0 | 0 | 0 | 0 | 23.8102 | 52.5 | 108.1095 | 3000 | 42.5457 | 3042.5457 | 3042.5457 | 0 | 201.3253
0 | 26.68 | 0 | 0 | 0 | 0 | 25.82 | 52.5 | 133.9295 | 3000 | 46.1369 | 3046.1369 | 3046.1369 | 0 | 189.9876
0 | 32.5721 | 0 | 0 | 0 | 0 | 19.9279 | 52.5 | 153.8574 | 3000 | 35.6085 | 3035.6085 | 3035.6085 | 0 | 186.5381
0 | 27.2078 | 0 | 0 | 0 | 0 | 25.2922 | 52.5 | 179.1496 | 3000 | 45.1937 | 3045.1937 | 3045.1937 | 0 | 185.3914
0 | 36.9587 | 0 | 0 | 0 | 0 | 15.5413 | 52.5 | 194.6909 | 3000 | 27.7702 | 3027.7702 | 3027.7702 | 0 | 187.1162
0 | 27.7303 | 0 | 0 | 0 | 0 | 24.7697 | 52.5 | 219.4606 | 3000 | 44.2602 | 3044.2602 | 3044.2602 | 0 | 187.1611
0 | 29.9659 | 0 | 0 | 0 | 0 | 22.5341 | 52.5 | 241.9947 | 3000 | 40.2655 | 3040.2655 | 3040.2655 | 0 | 194.577
0 | 31.0686 | 0 | 0 | 0 | 0 | 21.4314 | 52.5 | 263.4261 | 3000 | 38.2951 | 3038.2951 | 3038.2951 | 0 | 178.3175
0 | 230.4364 | 0 | 0 | 0 | 0 | -177.9364 | 52.5 | 85.4897 | 3000 | 0 | 3000 | 3000 | 0 | 183.81
0 | 29.7964 | 0 | 0 | 0 | 0 | 22.7036 | 52.5 | 108.1933 | 3000 | 40.5684 | 3040.5684 | 3040.5684 | 0 | 175.1367
0 | 29.0842 | 0 | 0 | 0 | 0 | 23.4158 | 52.5 | 131.6091 | 3000 | 41.8409 | 3041.8409 | 3041.8409 | 0 | 176.3659
0 | 49.5716 | 0 | 0 | 0 | 0 | 2.9284 | 52.5 | 134.5375 | 3000 | 5.2327 | 3005.2327 | 2999.8252 | 0 | 197.9585
0 | 54.3311 | 0 | 0 | 0 | 0 | -1.8311 | 52.5 | 132.7064 | 3000 | 0 | 3000 | 2972.9629 | 0 | 206.6209
0 | 38.4665 | 0 | 0 | 0 | 0 | -38.4665 | 0 | 94.24 | 0 | 0 | 0 | 0 | 21.6297 | 0
0 | 36.1302 | 0 | 0 | 0 | 0 | -36.1302 | 0 | 58.1097 | 0 | 0 | 0 | 0 | 48.6668 | 0
0 | 47.6277 | 0 | 0 | 0 | 0 | -47.6277 | 0 | 10.4821 | 0 | 0 | 0 | 0 | 70.2965 | 0
0 | 26.6245 | 0 | 0 | 0 | 0 | 25.8755 | 52.5 | 36.3575 | 3000 | 46.2361 | 3046.2361 | 2970.5321 | 0 | 198.9662
0 | 39.5272 | 0 | 0 | 0 | 0 | 12.9728 | 52.5 | 49.3304 | 3000 | 23.1807 | 3023.1807 | 2958.2916 | 0 | 189.3307
0 | 43.897 | 0 | 0 | 0 | 0 | 8.603 | 52.5 | 57.9334 | 3000 | 15.3724 | 3015.3724 | 2918.0388 | 0 | 194.7791
0 | 47.8077 | 0 | 0 | 0 | 0 | 4.6923 | 52.5 | 62.6257 | 3000 | 8.3845 | 3008.3845 | 2997.5697 | 0 | 202.336
0 | 44.7449 | 0 | 0 | 0 | 0 | 7.7551 | 52.5 | 70.3808 | 3000 | 13.8573 | 3013.8573 | 3013.8573 | 0 | 204.3697
0 | 46.293 | 0 | 0 | 0 | 0 | -46.293 | 0 | 24.0877 | 0 | 0 | 0 | 0 | 0 | 0
0 | 44.8239 | 0 | 0 | 0 | 0 | 7.6761 | 52.5 | 31.7639 | 3000 | 13.7162 | 3013.7162 | 3013.7162 | 0 | 195.5902
0 | 24.8297 | 0 | 0 | 0 | 0 | 27.6703 | 52.5 | 59.4342 | 3000 | 49.4432 | 3049.4432 | 3049.4432 | 0 | 196.9635
0 | 26.8345 | 0 | 0 | 0 | 0 | 25.6655 | 52.5 | 85.0997 | 3000 | 45.8609 | 3045.8609 | 3045.8609 | 0 | 193.1685
0 | 32.4557 | 0 | 0 | 0 | 0 | 20.0443 | 52.5 | 105.144 | 3000 | 35.8165 | 3035.8165 | 3035.8165 | 0 | 194.2923
0 | 25.1488 | 0 | 0 | 0 | 0 | 27.3512 | 52.5 | 132.4952 | 3000 | 48.8729 | 3048.8729 | 3048.8729 | 0 | 190.7985
0 | 28.9378 | 0 | 0 | 0 | 0 | 23.5622 | 52.5 | 156.0574 | 3000 | 42.1026 | 3042.1026 | 3042.1026 | 0 | 190.2835
0 | 28.351 | 0 | 0 | 0 | 0 | 24.149 | 52.5 | 180.2064 | 3000 | 43.1511 | 3043.1511 | 3043.1511 | 0 | 205.1084
0 | 24.858 | 0 | 0 | 0 | 0 | 27.642 | 52.5 | 207.8484 | 3000 | 49.3925 | 3049.3925 | 3049.3925 | 0 | 191.8983
0 | 34.4758 | 0 | 0 | 0 | 0 | 18.0242 | 52.5 | 225.8726 | 3000 | 32.2068 | 3032.2068 | 3032.2068 | 0 | 177.2022
0 | 29.2364 | 0 | 0 | 0 | 0 | 23.2636 | 52.5 | 249.1362 | 3000 | 41.569 | 3041.569 | 3041.569 | 0 | 147.4553
0 | 26.0787 | 0 | 0 | 0 | 0 | 26.4213 | 52.5 | 275.5575 | 3000 | 47.2113 | 3047.2113 | 3047.2113 | 0 | 151.2331
0 | 25.1098 | 0 | 0 | 0 | 0 | 27.3902 | 52.5 | 302.9477 | 3000 | 48.9427 | 3048.9427 | 3048.9427 | 0 | 151.319
0 | 32.6647 | 0 | 0 | 0 | 0 | 19.8353 | 52.5 | 322.783 | 3000 | 35.443 | 3035.443 | 3035.443 | 0 | 133.4684
0 | 39.8042 | 0 | 0 | 0 | 0 | 12.6958 | 52.5 | 335.4788 | 3000 | 22.6858 | 3022.6858 | 3022.6858 | 0 | 166.2477
0 | 54.5725 | 0 | 0 | 0 | 0 | -2.0725 | 52.5 | 333.4064 | 3000 | 0 | 3000 | 2989.1851 | 0 | 159.3236
0 | 52.0711 | 0 | 0 | 0 | 0 | 0.42889 | 52.5 | 333.8353 | 3000 | 0.76637 | 3000.7664 | 2952.0995 | 0 | 184.0044
0 | 34.9701 | 0 | 0 | 0 | 0 | 17.5299 | 52.5 | 351.3652 | 3000 | 31.3236 | 3031.3236 | 2971.8419 | 0 | 189.6035
0 | 54.6123 | 0 | 0 | 0 | 0 | -2.1123 | 52.5 | 349.2529 | 3000 | 0 | 3000 | 2935.1109 | 0 | 195.1849
0 | 43.6734 | 0 | 0 | 0 | 0 | 8.8266 | 52.5 | 358.0795 | 3000 | 15.7719 | 3015.7719 | 2945.4754 | 0 | 195.933
0 | 410.5795 | 0 | 0 | 0 | 0 | -358.0795 | 52.5 | 0 | 3000 | 0 | 3000 | 2967.5554 | 0 | 195.829
0 | 43.0241 | 0 | 0 | 0 | 0 | 9.4759 | 52.5 | 9.4759 | 3000 | 16.9321 | 3016.9321 | 2995.3024 | 0 | 194.6947
0 | 39.5461 | 0 | 0 | 0 | 0 | 12.9539 | 52.5 | 22.4298 | 3000 | 23.1469 | 3023.1469 | 3017.7395 | 0 | 198.688
0 | 49.749 | 0 | 0 | 0 | 0 | 2.751 | 52.5 | 25.1808 | 3000 | 4.9157 | 3004.9157 | 3004.9157 | 0 | 200.7885
0 | 25.1808 | 0 | 0 | 0 | 0 | -25.1808 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 40.1412 | 0 | 0 | 0 | 0 | 12.3588 | 52.5 | 12.3588 | 3000 | 22.0835 | 3022.0835 | 3022.0835 | 0 | 201.1197
0 | 33.0661 | 0 | 0 | 0 | 0 | 19.4339 | 52.5 | 31.7927 | 3000 | 34.7258 | 3034.7258 | 3034.7258 | 0 | 202.5072
0 | 30.2421 | 0 | 0 | 0 | 0 | 22.2579 | 52.5 | 54.0505 | 3000 | 39.7718 | 3039.7718 | 3039.7718 | 0 | 192.3568
0 | 22.2817 | 0 | 0 | 0 | 0 | 30.2183 | 52.5 | 84.2689 | 3000 | 53.9961 | 3053.9961 | 3053.9961 | 0 | 191.2107
0 | 28.1395 | 0 | 0 | 0 | 0 | 24.3605 | 52.5 | 108.6294 | 3000 | 43.529 | 3043.529 | 3043.529 | 0 | 182.9161
0 | 26.3932 | 0 | 0 | 0 | 0 | 26.1068 | 52.5 | 134.7362 | 3000 | 46.6494 | 3046.6494 | 3046.6494 | 0 | 174.2683
0 | 38.3196 | 0 | 0 | 0 | 0 | 14.1804 | 52.5 | 148.9166 | 3000 | 25.3386 | 3025.3386 | 3025.3386 | 0 | 186.1188
0 | 29.669 | 0 | 0 | 0 | 0 | 22.831 | 52.5 | 171.7477 | 3000 | 40.796 | 3040.796 | 3040.796 | 0 | 174.5417
0 | 27.646 | 0 | 0 | 0 | 0 | 24.854 | 52.5 | 196.6017 | 3000 | 44.4109 | 3044.4109 | 3044.4109 | 0 | 187.1704
0 | 33.1385 | 0 | 0 | 0 | 0 | 19.3615 | 52.5 | 215.9632 | 3000 | 34.5964 | 3034.5964 | 3034.5964 | 0 | 186.2332
0 | 23.683 | 0 | 0 | 0 | 0 | 28.817 | 52.5 | 244.7802 | 3000 | 51.4922 | 3051.4922 | 3051.4922 | 0 | 183.0895
0 | 25.2497 | 0 | 0 | 0 | 0 | 27.2503 | 52.5 | 272.0305 | 3000 | 48.6926 | 3048.6926 | 3048.6926 | 0 | 188.0129
0 | 31.1686 | 0 | 0 | 0 | 0 | 21.3314 | 52.5 | 293.3619 | 3000 | 38.1163 | 3038.1163 | 3038.1163 | 0 | 198.7232
0 | 43.3721 | 0 | 0 | 0 | 0 | -43.3721 | 0 | 249.9898 | 0 | 0 | 0 | 0 | 10.8149 | 0
0 | 50.3204 | 0 | 0 | 0 | 0 | -50.3204 | 0 | 199.6694 | 0 | 0 | 0 | 0 | 113.5559 | 0
0 | 45.8122 | 0 | 0 | 0 | 0 | -45.8122 | 0 | 153.8572 | 0 | 0 | 0 | 0 | 221.7044 | 0
0 | 46.7834 | 0 | 0 | 0 | 0 | -39.7808 | 7.0026 | 114.0764 | 400.1495 | 0 | 400.1495 | 0 | 0 | 0
0 | 42.5473 | 0 | 0 | 0 | 0 | 9.9527 | 52.5 | 124.0291 | 3000 | 17.7842 | 3017.7842 | 2666.3015 | 0 | 178.4822
0 | 50.8058 | 0 | 0 | 0 | 0 | 1.6942 | 52.5 | 125.7233 | 3000 | 3.0274 | 3003.0274 | 2619.1002 | 0 | 165.789
0 | 50.03 | 0 | 0 | 0 | 0 | 2.47 | 52.5 | 128.1933 | 3000 | 4.4135 | 3004.4135 | 2842.1907 | 0 | 189.2046
0 | 40.7372 | 0 | 0 | 0 | 0 | 11.7628 | 52.5 | 139.9561 | 3000 | 21.0186 | 3021.0186 | 2869.6107 | 0 | 191.4891
0 | 51.8051 | 0 | 0 | 0 | 0 | -51.8051 | 0 | 88.151 | 0 | 0 | 0 | 0 | 43.2594 | 0
0 | 88.151 | 0 | 0 | 0 | 0 | -88.151 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 27.929 | 0 | 0 | 0 | 0 | 24.571 | 52.5 | 24.571 | 3000 | 43.9051 | 3043.9051 | 3043.9051 | 0 | 204.3678
0 | 24.571 | 0 | 0 | 0 | 0 | -24.571 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 25.5159 | 0 | 0 | 0 | 0 | 26.9841 | 52.5 | 26.9841 | 3000 | 48.2169 | 3048.2169 | 3048.2169 | 0 | 203.2551
0 | 27.8932 | 0 | 0 | 0 | 0 | 24.6068 | 52.5 | 51.5908 | 3000 | 43.969 | 3043.969 | 3043.969 | 0 | 190.035
0 | 26.0457 | 0 | 0 | 0 | 0 | 26.4543 | 52.5 | 78.0451 | 3000 | 47.2702 | 3047.2702 | 3047.2702 | 0 | 187.9252
0 | 23.4963 | 0 | 0 | 0 | 0 | 29.0037 | 52.5 | 107.0488 | 3000 | 51.8258 | 3051.8258 | 3051.8258 | 0 | 173.9541
0 | 23.1824 | 0 | 0 | 0 | 0 | 29.3176 | 52.5 | 136.3664 | 3000 | 52.3866 | 3052.3866 | 3052.3866 | 0 | 162.6922
0 | 32.0736 | 0 | 0 | 0 | 0 | 20.4264 | 52.5 | 156.7927 | 3000 | 36.4992 | 3036.4992 | 3036.4992 | 0 | 154.8615
0 | 24.4647 | 0 | 0 | 0 | 0 | 28.0353 | 52.5 | 184.8281 | 3000 | 50.0954 | 3050.0954 | 3050.0954 | 0 | 174.4655
0 | 38.4082 | 0 | 0 | 0 | 0 | 14.0918 | 52.5 | 198.9198 | 3000 | 25.1801 | 3025.1801 | 3025.1801 | 0 | 179.3932
0 | 30.9335 | 0 | 0 | 0 | 0 | 21.5665 | 52.5 | 220.4863 | 3000 | 38.5365 | 3038.5365 | 3038.5365 | 0 | 189.6047
0 | 42.7928 | 0 | 0 | 0 | 0 | -42.7928 | 0 | 177.6935 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 54.5577 | 0 | 0 | 0 | 0 | -54.5577 | 0 | 123.1358 | 0 | 0 | 0 | 0 | 48.6668 | 0
0 | 42.2026 | 0 | 0 | 0 | 0 | -42.2026 | 0 | 80.9332 | 0 | 0 | 0 | 0 | 113.5559 | 0
0 | 41.3912 | 0 | 0 | 0 | 0 | -41.3912 | 0 | 39.542 | 0 | 0 | 0 | 0 | 135.1856 | 0
0 | 39.542 | 0 | 0 | 0 | 0 | -39.542 | 0 | 0 | 0 | 0 | 0 | 0 | 124.3708 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173.0376 | 0
0 | 29.2914 | 0 | 0 | 0 | 0 | 23.2086 | 52.5 | 23.2086 | 3000 | 41.4707 | 3041.4707 | 2879.2479 | 0 | 201.2594
0 | 46.3217 | 0 | 0 | 0 | 0 | 6.1783 | 52.5 | 29.3869 | 3000 | 11.0398 | 3011.0398 | 2951.5581 | 0 | 204.7496
0 | 51.2278 | 0 | 0 | 0 | 0 | 1.2722 | 52.5 | 30.6591 | 3000 | 2.2733 | 3002.2733 | 2991.4585 | 0 | 200.7867
0 | 28.1498 | 0 | 0 | 0 | 0 | -28.1498 | 0 | 2.5093 | 0 | 0 | 0 | 0 | 0 | 0
0 | 2.5093 | 0 | 0 | 0 | 0 | -2.5093 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 37.9944 | 0 | 0 | 0 | 0 | 14.5056 | 52.5 | 14.5056 | 3000 | 25.9196 | 3025.9196 | 3025.9196 | 0 | 199.2871
0 | 29.6628 | 0 | 0 | 0 | 0 | 22.8372 | 52.5 | 37.3428 | 3000 | 40.807 | 3040.807 | 3040.807 | 0 | 200.9061
0 | 26.6537 | 0 | 0 | 0 | 0 | 25.8463 | 52.5 | 63.1891 | 3000 | 46.1838 | 3046.1838 | 3046.1838 | 0 | 200.4998
0 | 27.4278 | 0 | 0 | 0 | 0 | 25.0722 | 52.5 | 88.2612 | 3000 | 44.8006 | 3044.8006 | 3044.8006 | 0 | 197.8816
0 | 29.1334 | 0 | 0 | 0 | 0 | 23.3666 | 52.5 | 111.6278 | 3000 | 41.753 | 3041.753 | 3041.753 | 0 | 194.0334
0 | 164.1278 | 0 | 0 | 0 | 0 | -111.6278 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 186.3
0 | 28.7125 | 0 | 0 | 0 | 0 | 23.7875 | 52.5 | 23.7875 | 3000 | 42.5051 | 3042.5051 | 3042.5051 | 0 | 172.2058
0 | 76.2875 | 0 | 0 | 0 | 0 | -23.7875 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 159.9
0 | 20.8378 | 0 | 0 | 0 | 0 | 31.6622 | 52.5 | 31.6622 | 3000 | 56.5762 | 3056.5762 | 3056.5762 | 0 | 180.9493
0 | 26.5316 | 0 | 0 | 0 | 0 | 25.9684 | 52.5 | 57.6307 | 3000 | 46.4021 | 3046.4021 | 3046.4021 | 0 | 173.9496
0 | 28.2154 | 0 | 0 | 0 | 0 | 24.2846 | 52.5 | 81.9153 | 3000 | 43.3933 | 3043.3933 | 3043.3933 | 0 | 166.4736
0 | 29.3027 | 0 | 0 | 0 | 0 | 23.1973 | 52.5 | 105.1126 | 3000 | 41.4505 | 3041.4505 | 3041.4505 | 0 | 164.2383
0 | 32.4015 | 0 | 0 | 0 | 0 | 20.0985 | 52.5 | 125.2111 | 3000 | 35.9133 | 3035.9133 | 3035.9133 | 0 | 187.1033
0 | 44.9524 | 0 | 0 | 0 | 0 | -44.9524 | 0 | 80.2587 | 0 | 0 | 0 | 0 | 0 | 0
0 | 38.9096 | 0 | 0 | 0 | 0 | -38.9096 | 0 | 41.349 | 0 | 0 | 0 | 0 | 10.8149 | 0
0 | 41.349 | 0 | 0 | 0 | 0 | -41.349 | 0 | 0 | 0 | 0 | 0 | 0 | 43.2594 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.8891 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.9634 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2886.4441 | 0 | 199.1646
0 | 34.0384 | 0 | 0 | 0 | 0 | 18.4616 | 52.5 | 18.4616 | 3000 | 32.9885 | 3032.9885 | 2973.5068 | 0 | 201.2767
0 | 18.4616 | 0 | 0 | 0 | 0 | -18.4616 | 0 | 0 | 0 | 0 | 0 | 0 | 37.852 | 0
0 | 47.3114 | 0 | 0 | 0 | 0 | 5.1886 | 52.5 | 5.1886 | 3000 | 9.2714 | 3009.2714 | 3003.864 | 0 | 206.4255
0 | 5.1886 | 0 | 0 | 0 | 0 | -5.1886 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 41.5012 | 0 | 0 | 0 | 0 | 10.9988 | 52.5 | 10.9988 | 3000 | 19.6534 | 3019.6534 | 3019.6534 | 0 | 204.3399
0 | 31.717 | 0 | 0 | 0 | 0 | 20.783 | 52.5 | 31.7818 | 3000 | 37.1364 | 3037.1364 | 3037.1364 | 0 | 200.208
0 | 27.5847 | 0 | 0 | 0 | 0 | 24.9153 | 52.5 | 56.6971 | 3000 | 44.5203 | 3044.5203 | 3044.5203 | 0 | 196.9805
0 | 26.3845 | 0 | 0 | 0 | 0 | 26.1155 | 52.5 | 82.8125 | 3000 | 46.6649 | 3046.6649 | 3046.6649 | 0 | 196.5099
0 | 23.1147 | 0 | 0 | 0 | 0 | 29.3853 | 52.5 | 112.1979 | 3000 | 52.5077 | 3052.5077 | 3052.5077 | 0 | 192.5522
0 | 164.6979 | 0 | 0 | 0 | 0 | -112.1979 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 189.6
0 | 18.0538 | 0 | 0 | 0 | 0 | 34.4462 | 52.5 | 34.4462 | 3000 | 61.5509 | 3061.5509 | 3061.5509 | 0 | 194.7146
0 | 28.6275 | 0 | 0 | 0 | 0 | 23.8725 | 52.5 | 58.3187 | 3000 | 42.6569 | 3042.6569 | 3042.6569 | 0 | 187.4277
0 | 28.882 | 0 | 0 | 0 | 0 | 23.618 | 52.5 | 81.9367 | 3000 | 42.2023 | 3042.2023 | 3042.2023 | 0 | 188.3123
0 | 26.4434 | 0 | 0 | 0 | 0 | 26.0566 | 52.5 | 107.9933 | 3000 | 46.5596 | 3046.5596 | 3046.5596 | 0 | 188.1555
0 | 27.9837 | 0 | 0 | 0 | 0 | 24.5163 | 52.5 | 132.5096 | 3000 | 43.8073 | 3043.8073 | 3043.8073 | 0 | 188.5334
0 | 37.1355 | 0 | 0 | 0 | 0 | 15.3645 | 52.5 | 147.8741 | 3000 | 27.4544 | 3027.4544 | 3027.4544 | 0 | 192.5461
0 | 28.4755 | 0 | 0 | 0 | 0 | 24.0245 | 52.5 | 171.8986 | 3000 | 42.9286 | 3042.9286 | 3042.9286 | 0 | 211.727
0 | 39.7175 | 0 | 0 | 0 | 0 | -39.7175 | 0 | 132.1811 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 43.9915 | 0 | 0 | 0 | 0 | -43.9915 | 0 | 88.1896 | 0 | 0 | 0 | 0 | 32.4446 | 0
0 | 38.4562 | 0 | 0 | 0 | 0 | -38.4562 | 0 | 49.7334 | 0 | 0 | 0 | 0 | 86.5188 | 0
0 | 38.615 | 0 | 0 | 0 | 0 | -38.615 | 0 | 11.1184 | 0 | 0 | 0 | 0 | 86.5188 | 0
0 | 11.1184 | 0 | 0 | 0 | 0 | -11.1184 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5188 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 254.149 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151.4079 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178.445 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.0371 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 19.4599 | 0 | 0 | 0 | 0 | 33.0401 | 52.5 | 33.0401 | 3000 | 59.0384 | 3059.0384 | 3059.0384 | 0 | 210.6148
0 | 25.8481 | 0 | 0 | 0 | 0 | 26.6519 | 52.5 | 59.692 | 3000 | 47.6234 | 3047.6234 | 3047.6234 | 0 | 198.0955
0 | 25.161 | 0 | 0 | 0 | 0 | 27.339 | 52.5 | 87.031 | 3000 | 48.8511 | 3048.8511 | 3048.8511 | 0 | 201.4071
0 | 25.1178 | 0 | 0 | 0 | 0 | 27.3822 | 52.5 | 114.4132 | 3000 | 48.9283 | 3048.9283 | 3048.9283 | 0 | 190.2531
0 | 29.8766 | 0 | 0 | 0 | 0 | 22.6234 | 52.5 | 137.0365 | 3000 | 40.4249 | 3040.4249 | 3040.4249 | 0 | 199.3607
0 | 32.6216 | 0 | 0 | 0 | 0 | 19.8784 | 52.5 | 156.9149 | 3000 | 35.5201 | 3035.5201 | 3035.5201 | 0 | 209.1473
0 | 209.4149 | 0 | 0 | 0 | 0 | -156.9149 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 193.98
0 | 24.9925 | 0 | 0 | 0 | 0 | 27.5075 | 52.5 | 27.5075 | 3000 | 49.1523 | 3049.1523 | 3049.1523 | 0 | 193.6822
0 | 30.1636 | 0 | 0 | 0 | 0 | 22.3364 | 52.5 | 49.8439 | 3000 | 39.9121 | 3039.9121 | 3039.9121 | 0 | 193.156
0 | 26.6804 | 0 | 0 | 0 | 0 | 25.8196 | 52.5 | 75.6634 | 3000 | 46.1361 | 3046.1361 | 3046.1361 | 0 | 193.4296
0 | 35.4311 | 0 | 0 | 0 | 0 | 17.0689 | 52.5 | 92.7324 | 3000 | 30.4999 | 3030.4999 | 3030.4999 | 0 | 202.5889
0 | 27.2988 | 0 | 0 | 0 | 0 | -27.2988 | 0 | 65.4336 | 0 | 0 | 0 | 0 | 0 | 0
0 | 46.6907 | 0 | 0 | 0 | 0 | -46.6907 | 0 | 18.7428 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 18.7428 | 0 | 0 | 0 | 0 | -18.7428 | 0 | 0 | 0 | 0 | 0 | 0 | 108.1485 | 0
0 | 6.6241 | 0 | 0 | 0 | 0 | 0 | 6.6241 | 0 | 378.5198 | 0 | 378.5198 | 0 | 0 | 0
0 | 9.2737 | 0 | 0 | 0 | 0 | 0 | 9.2737 | 0 | 529.9277 | 0 | 529.9277 | 0 | 0 | 0
0 | 8.706 | 0 | 0 | 0 | 0 | 0 | 8.706 | 0 | 497.4831 | 0 | 497.4831 | 0 | 0 | 0
0 | 8.3274 | 0 | 0 | 0 | 0 | 0 | 8.3274 | 0 | 475.8534 | 0 | 475.8534 | 0 | 0 | 0
0 | 6.7187 | 0 | 0 | 0 | 0 | 0 | 6.7187 | 0 | 383.9272 | 0 | 383.9272 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156.8153 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.0371 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 27.8855 | 0 | 0 | 0 | 0 | 24.6145 | 52.5 | 24.6145 | 3000 | 43.9829 | 3043.9829 | 3043.9829 | 0 | 207.4779
0 | 24.6145 | 0 | 0 | 0 | 0 | -24.6145 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 28.8184 | 0 | 0 | 0 | 0 | 23.6816 | 52.5 | 23.6816 | 3000 | 42.3159 | 3042.3159 | 3042.3159 | 0 | 209.5547
0 | 31.8114 | 0 | 0 | 0 | 0 | 20.6886 | 52.5 | 44.3702 | 3000 | 36.9678 | 3036.9678 | 3036.9678 | 0 | 208.6701
0 | 26.8685 | 0 | 0 | 0 | 0 | 25.6315 | 52.5 | 70.0018 | 3000 | 45.8001 | 3045.8001 | 3045.8001 | 0 | 208.4241
0 | 29.667 | 0 | 0 | 0 | 0 | -29.667 | 0 | 40.3347 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 40.3347 | 0 | 0 | 0 | 0 | -40.3347 | 0 | 0 | 0 | 0 | 0 | 0 | 97.3337 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.8896 | 0
0 | 6.5295 | 0 | 0 | 0 | 0 | 0 | 6.5295 | 0 | 373.1123 | 0 | 373.1123 | 0 | 0 | 0
0 | 8.706 | 0 | 0 | 0 | 0 | 0 | 8.706 | 0 | 497.4831 | 0 | 497.4831 | 0 | 0 | 0
0 | 9.0845 | 0 | 0 | 0 | 0 | 0 | 9.0845 | 0 | 519.1128 | 0 | 519.1128 | 0 | 0 | 0
0 | 5.6778 | 0 | 0 | 0 | 0 | 0 | 5.6778 | 0 | 324.4455 | 0 | 324.4455 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173.0376 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.852 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 22.2466 | 0 | 0 | 0 | 0 | 30.2534 | 52.5 | 30.2534 | 3000 | 54.0589 | 3054.0589 | 3054.0589 | 0 | 211.0355
0 | 27.7585 | 0 | 0 | 0 | 0 | 24.7415 | 52.5 | 54.9949 | 3000 | 44.2097 | 3044.2097 | 3044.2097 | 0 | 209.533
0 | 107.4949 | 0 | 0 | 0 | 0 | -54.9949 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 199.05
0 | 33.4539 | 0 | 0 | 0 | 0 | 19.0461 | 52.5 | 19.0461 | 3000 | 34.0328 | 3034.0328 | 3034.0328 | 0 | 198.5774
0 | 25.7861 | 0 | 0 | 0 | 0 | 26.7139 | 52.5 | 45.76 | 3000 | 47.7342 | 3047.7342 | 3047.7342 | 0 | 199.5352
0 | 27.1068 | 0 | 0 | 0 | 0 | 25.3932 | 52.5 | 71.1532 | 3000 | 45.3743 | 3045.3743 | 3045.3743 | 0 | 194.7821
0 | 40.8722 | 0 | 0 | 0 | 0 | 11.6278 | 52.5 | 82.7809 | 3000 | 20.7773 | 3020.7773 | 3015.3698 | 0 | 196.5117
0 | 38.8998 | 0 | 0 | 0 | 0 | 13.6002 | 52.5 | 96.3812 | 3000 | 24.3018 | 3024.3018 | 2889.1162 | 0 | 194.7553
0 | 46.9709 | 0 | 0 | 0 | 0 | -40.3468 | 6.6241 | 56.0344 | 378.5198 | 0 | 378.5198 | 0 | 0 | 0
0 | 50.5895 | 0 | 0 | 0 | 0 | -40.6533 | 9.9361 | 15.3811 | 567.7796 | 0 | 567.7796 | 0 | 0 | 0
0 | 29.7648 | 0 | 0 | 0 | 0 | -15.3811 | 14.3838 | 0 | 821.9286 | 0 | 821.9286 | 0 | 0 | 0
0 | 12.775 | 0 | 0 | 0 | 0 | 0 | 12.775 | 0 | 730.0024 | 0 | 730.0024 | 0 | 0 | 0
0 | 46.9616 | 0 | 0 | 0 | 0 | 5.5384 | 52.5 | 5.5384 | 3000 | 9.8963 | 3009.8963 | 2517.8206 | 0 | 173.4778
0 | 5.5384 | 0 | 0 | 0 | 0 | -5.5384 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2228 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 54.0743 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 204.06
0 | 26.7338 | 0 | 0 | 0 | 0 | 25.7662 | 52.5 | 25.7662 | 3000 | 46.0408 | 3046.0408 | 3046.0408 | 0 | 204.3893
0 | 37.3053 | 0 | 0 | 0 | 0 | 15.1947 | 52.5 | 40.9609 | 3000 | 27.1508 | 3027.1508 | 3027.1508 | 0 | 200.7304
0 | 35.9388 | 0 | 0 | 0 | 0 | 16.5612 | 52.5 | 57.5221 | 3000 | 29.5927 | 3029.5927 | 3029.5927 | 0 | 200.3773
0 | 35.081 | 0 | 0 | 0 | 0 | 17.419 | 52.5 | 74.9411 | 3000 | 31.1254 | 3031.1254 | 3031.1254 | 0 | 206.8137
0 | 74.9411 | 0 | 0 | 0 | 0 | -74.9411 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2228 | 0
0 | 6.5295 | 0 | 0 | 0 | 0 | 0 | 6.5295 | 0 | 373.1123 | 0 | 373.1123 | 0 | 0 | 0
0 | 7.9489 | 0 | 0 | 0 | 0 | 0 | 7.9489 | 0 | 454.2237 | 0 | 454.2237 | 0 | 0 | 0
0 | 11.5449 | 0 | 0 | 0 | 0 | 0 | 11.5449 | 0 | 659.7059 | 0 | 659.7059 | 0 | 0 | 0
0 | 11.7341 | 0 | 0 | 0 | 0 | 0 | 11.7341 | 0 | 670.5207 | 0 | 670.5207 | 0 | 0 | 0
0 | 7.0026 | 0 | 0 | 0 | 0 | 0 | 7.0026 | 0 | 400.1495 | 0 | 400.1495 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194.6673 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.2594 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 35.4996 | 0 | 0 | 0 | 0 | 17.0004 | 52.5 | 17.0004 | 3000 | 30.3774 | 3030.3774 | 3030.3774 | 0 | 207.8839
0 | 37.1881 | 0 | 0 | 0 | 0 | 15.3119 | 52.5 | 32.3123 | 3000 | 27.3604 | 3027.3604 | 3027.3604 | 0 | 204.3468
0 | 32.0932 | 0 | 0 | 0 | 0 | 20.4068 | 52.5 | 52.7191 | 3000 | 36.4642 | 3036.4642 | 3036.4642 | 0 | 188.5644
0 | 23.4575 | 0 | 0 | 0 | 0 | 29.0425 | 52.5 | 81.7616 | 3000 | 51.8951 | 3051.8951 | 3051.8951 | 0 | 194.2836
0 | 34.6788 | 0 | 0 | 0 | 0 | 17.8212 | 52.5 | 99.5828 | 3000 | 31.8441 | 3031.8441 | 3031.8441 | 0 | 192.2492
0 | 26.4522 | 0 | 0 | 0 | 0 | 26.0478 | 52.5 | 125.6306 | 3000 | 46.5439 | 3046.5439 | 3046.5439 | 0 | 200.4626
0 | 27.7879 | 0 | 0 | 0 | 0 | 24.7121 | 52.5 | 150.3427 | 3000 | 44.1572 | 3044.1572 | 3044.1572 | 0 | 203.1366
0 | 37.4635 | 0 | 0 | 0 | 0 | 15.0365 | 52.5 | 165.3792 | 3000 | 26.8682 | 3026.8682 | 3026.8682 | 0 | 189.4214
0 | 28.4818 | 0 | 0 | 0 | 0 | -28.4818 | 0 | 136.8974 | 0 | 0 | 0 | 0 | 0 | 0
0 | 136.8974 | 0 | 0 | 0 | 0 | -136.8974 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8149 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5188 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.8896 | 0
0 | 6.3402 | 0 | 0 | 0 | 0 | 0 | 6.3402 | 0 | 362.2975 | 0 | 362.2975 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.8896 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5188 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.3708 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.4817 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.6297 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 27.3671 | 0 | 0 | 0 | 0 | 25.1329 | 52.5 | 25.1329 | 3000 | 44.9092 | 3044.9092 | 3044.9092 | 0 | 206.1404
0 | 38.4743 | 0 | 0 | 0 | 0 | 14.0257 | 52.5 | 39.1586 | 3000 | 25.062 | 3025.062 | 3025.062 | 0 | 196.3265
0 | 22.8722 | 0 | 0 | 0 | 0 | 29.6278 | 52.5 | 68.7864 | 3000 | 52.9409 | 3052.9409 | 3052.9409 | 0 | 185.3135
0 | 26.6235 | 0 | 0 | 0 | 0 | 25.8765 | 52.5 | 94.6629 | 3000 | 46.2379 | 3046.2379 | 3046.2379 | 0 | 199.2544
0 | 19.6632 | 0 | 0 | 0 | 0 | 32.8368 | 52.5 | 127.4997 | 3000 | 58.6751 | 3058.6751 | 3058.6751 | 0 | 198.508
0 | 29.835 | 0 | 0 | 0 | 0 | 22.665 | 52.5 | 150.1647 | 3000 | 40.4993 | 3040.4993 | 3040.4993 | 0 | 201.2507
0 | 24.3884 | 0 | 0 | 0 | 0 | 28.1116 | 52.5 | 178.2763 | 3000 | 50.2316 | 3050.2316 | 3050.2316 | 0 | 201.3763
0 | 22.2841 | 0 | 0 | 0 | 0 | 30.2159 | 52.5 | 208.4922 | 3000 | 53.9919 | 3053.9919 | 3053.9919 | 0 | 213.1992
0 | 30.2185 | 0 | 0 | 0 | 0 | -30.2185 | 0 | 178.2737 | 0 | 0 | 0 | 0 | 0 | 0
0 | 44.2324 | 0 | 0 | 0 | 0 | -44.2324 | 0 | 134.0413 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 39.2411 | 0 | 0 | 0 | 0 | -39.2411 | 0 | 94.8002 | 0 | 0 | 0 | 0 | 43.2594 | 0
0 | 48.1178 | 0 | 0 | 0 | 0 | -48.1178 | 0 | 46.6824 | 0 | 0 | 0 | 0 | 97.3337 | 0
0 | 45.0172 | 0 | 0 | 0 | 0 | -45.0172 | 0 | 1.6652 | 0 | 0 | 0 | 0 | 162.2228 | 0
0 | 1.6652 | 0 | 0 | 0 | 0 | -1.6652 | 0 | 0 | 0 | 0 | 0 | 0 | 243.3341 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205.4822 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.7782 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2965 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.0371 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 33.4594 | 0 | 0 | 0 | 0 | 19.0406 | 52.5 | 19.0406 | 3000 | 34.0229 | 3034.0229 | 3034.0229 | 0 | 199.0319
0 | 19.0406 | 0 | 0 | 0 | 0 | -19.0406 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.2594 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.5559 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.8525 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205.4822 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.8525 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2228 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7411 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.4446 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8149 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 64.8891 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178.445 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 205.4822 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 243.3341 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 194.6673 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135.1856 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.9262 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 21.6297 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 32.1708 | 0 | 0 | 0 | 0 | 20.3292 | 52.5 | 20.3292 | 3000 | 36.3257 | 3036.3257 | 3036.3257 | 0 | 201.3995
0 | 26.9408 | 0 | 0 | 0 | 0 | 25.5592 | 52.5 | 45.8884 | 3000 | 45.6709 | 3045.6709 | 3045.6709 | 0 | 196.4458
0 | 23.3208 | 0 | 0 | 0 | 0 | 29.1792 | 52.5 | 75.0676 | 3000 | 52.1394 | 3052.1394 | 3052.1394 | 0 | 197.7786
0 | 23.849 | 0 | 0 | 0 | 0 | 28.651 | 52.5 | 103.7186 | 3000 | 51.1955 | 3051.1955 | 3051.1955 | 0 | 189.8149
0 | 26.3956 | 0 | 0 | 0 | 0 | 26.1044 | 52.5 | 129.823 | 3000 | 46.6451 | 3046.6451 | 3046.6451 | 0 | 176.7054
0 | 24.1461 | 0 | 0 | 0 | 0 | 28.3539 | 52.5 | 158.177 | 3000 | 50.6647 | 3050.6647 | 3050.6647 | 0 | 194.9375
0 | 29.7635 | 0 | 0 | 0 | 0 | 22.7365 | 52.5 | 180.9135 | 3000 | 40.6272 | 3040.6272 | 3040.6272 | 0 | 212.479
0 | 230.1806 | 0 | 0 | 0 | 0 | -177.6806 | 52.5 | 3.2329 | 3000 | 0 | 3000 | 3000 | 0 | 194.7
0 | 34.3061 | 0 | 0 | 0 | 0 | 18.1939 | 52.5 | 21.4268 | 3000 | 32.5101 | 3032.5101 | 3032.5101 | 0 | 172.7318
0 | 35.7783 | 0 | 0 | 0 | 0 | 16.7217 | 52.5 | 38.1485 | 3000 | 29.8795 | 3029.8795 | 3029.8795 | 0 | 171.6427
0 | 90.6485 | 0 | 0 | 0 | 0 | -38.1485 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 167.16
0 | 20.5303 | 0 | 0 | 0 | 0 | 31.9697 | 52.5 | 31.9697 | 3000 | 57.1256 | 3057.1256 | 3057.1256 | 0 | 172.8193
0 | 43.0221 | 0 | 0 | 0 | 0 | 9.4779 | 52.5 | 41.4476 | 3000 | 16.9358 | 3016.9358 | 3011.5284 | 0 | 188.2205
0 | 57.2012 | 0 | 0 | 0 | 0 | -4.7012 | 52.5 | 36.7464 | 3000 | 0 | 3000 | 2972.9629 | 0 | 197.3155
0 | 31.1815 | 0 | 0 | 0 | 0 | -31.1815 | 0 | 5.5649 | 0 | 0 | 0 | 0 | 43.2594 | 0
0 | 5.5649 | 0 | 0 | 0 | 0 | -5.5649 | 0 | 0 | 0 | 0 | 0 | 0 | 54.0743 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5188 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.704 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1114 | 0
0 | 32.3537 | 0 | 0 | 0 | 0 | 20.1463 | 52.5 | 20.1463 | 3000 | 35.9988 | 3035.9988 | 2965.7023 | 0 | 202.6168
0 | 39.2805 | 0 | 0 | 0 | 0 | 13.2195 | 52.5 | 33.3658 | 3000 | 23.6215 | 3023.6215 | 3001.9918 | 0 | 203.535
0 | 47.972 | 0 | 0 | 0 | 0 | 4.528 | 52.5 | 37.8938 | 3000 | 8.091 | 3008.091 | 3008.091 | 0 | 202.8657
0 | 35.0916 | 0 | 0 | 0 | 0 | -35.0916 | 0 | 2.8022 | 0 | 0 | 0 | 0 | 0 | 0
0 | 2.8022 | 0 | 0 | 0 | 0 | -2.8022 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 31.4108 | 0 | 0 | 0 | 0 | 21.0892 | 52.5 | 21.0892 | 3000 | 37.6836 | 3037.6836 | 3037.6836 | 0 | 205.8031
0 | 30.1674 | 0 | 0 | 0 | 0 | 22.3326 | 52.5 | 43.4218 | 3000 | 39.9054 | 3039.9054 | 3039.9054 | 0 | 189.6901
0 | 27.2466 | 0 | 0 | 0 | 0 | 25.2534 | 52.5 | 68.6752 | 3000 | 45.1244 | 3045.1244 | 3045.1244 | 0 | 182.677
0 | 31.0404 | 0 | 0 | 0 | 0 | 21.4596 | 52.5 | 90.1347 | 3000 | 38.3454 | 3038.3454 | 3038.3454 | 0 | 179.3839
0 | 27.1061 | 0 | 0 | 0 | 0 | 25.3939 | 52.5 | 115.5286 | 3000 | 45.3755 | 3045.3755 | 3045.3755 | 0 | 168.7138
0 | 25.322 | 0 | 0 | 0 | 0 | 27.178 | 52.5 | 142.7066 | 3000 | 48.5635 | 3048.5635 | 3048.5635 | 0 | 182.9138
0 | 34.7981 | 0 | 0 | 0 | 0 | 17.7019 | 52.5 | 160.4085 | 3000 | 31.631 | 3031.631 | 3031.631 | 0 | 190.9928
0 | 23.1989 | 0 | 0 | 0 | 0 | 29.3011 | 52.5 | 189.7096 | 3000 | 52.3572 | 3052.3572 | 3052.3572 | 0 | 181.9205
0 | 27.2568 | 0 | 0 | 0 | 0 | 25.2432 | 52.5 | 214.9528 | 3000 | 45.1062 | 3045.1062 | 3045.1062 | 0 | 164.1312
0 | 30.4834 | 0 | 0 | 0 | 0 | 22.0166 | 52.5 | 236.9695 | 3000 | 39.3408 | 3039.3408 | 3039.3408 | 0 | 147.6512
0 | 29.3472 | 0 | 0 | 0 | 0 | 23.1528 | 52.5 | 260.1223 | 3000 | 41.371 | 3041.371 | 3041.371 | 0 | 106.1438
0 | 31.6479 | 0 | 0 | 0 | 0 | 20.8521 | 52.5 | 280.9744 | 3000 | 37.26 | 3037.26 | 3037.26 | 0 | 124.5277
0 | 48.2197 | 0 | 0 | 0 | 0 | 4.2803 | 52.5 | 285.2547 | 3000 | 7.6484 | 3007.6484 | 3002.241 | 0 | 157.3174
0 | 40.666 | 0 | 0 | 0 | 0 | 11.834 | 52.5 | 297.0887 | 3000 | 21.1457 | 3021.1457 | 2983.2938 | 0 | 149.0752
0 | 30.9855 | 0 | 0 | 0 | 0 | 21.5145 | 52.5 | 318.6032 | 3000 | 38.4436 | 3038.4436 | 2957.3322 | 0 | 171.821
0 | 48.4308 | 0 | 0 | 0 | 0 | 4.0692 | 52.5 | 322.6724 | 3000 | 7.2711 | 3007.2711 | 2888.3077 | 0 | 200.3041
0 | 32.3611 | 0 | 0 | 0 | 0 | -32.3611 | 0 | 290.3113 | 0 | 0 | 0 | 0 | 108.1485 | 0
0 | 54.931 | 0 | 0 | 0 | 0 | -2.431 | 52.5 | 287.8803 | 3000 | 0 | 3000 | 2929.7035 | 0 | 181.5537
0 | 59.1787 | 0 | 0 | 0 | 0 | -6.6787 | 52.5 | 281.2016 | 3000 | 0 | 3000 | 2918.8886 | 0 | 170.0253
0 | 29.8432 | 0 | 0 | 0 | 0 | 22.6568 | 52.5 | 303.8584 | 3000 | 40.4847 | 3040.4847 | 2867.4471 | 0 | 161.2939
0 | 53.9323 | 0 | 0 | 0 | 0 | -1.4323 | 52.5 | 302.4261 | 3000 | 0 | 3000 | 2956.7406 | 0 | 164.6017
0 | 39.7132 | 0 | 0 | 0 | 0 | 12.7868 | 52.5 | 315.2129 | 3000 | 22.8483 | 3022.8483 | 3022.8483 | 0 | 170.0654
0 | 44.2596 | 0 | 0 | 0 | 0 | 8.2404 | 52.5 | 323.4533 | 3000 | 14.7245 | 3014.7245 | 3014.7245 | 0 | 187.6666
0 | 43.0407 | 0 | 0 | 0 | 0 | 9.4593 | 52.5 | 332.9126 | 3000 | 16.9025 | 3016.9025 | 3016.9025 | 0 | 204.0633
0 | 26.3463 | 0 | 0 | 0 | 0 | 26.1537 | 52.5 | 359.0663 | 3000 | 46.7332 | 3046.7332 | 3046.7332 | 0 | 207.056
0 | 28.7287 | 0 | 0 | 0 | 0 | 23.7713 | 52.5 | 382.8376 | 3000 | 42.4761 | 3042.4761 | 3042.4761 | 0 | 199.0996
0 | 31.9707 | 0 | 0 | 0 | 0 | 20.5293 | 52.5 | 403.3669 | 3000 | 36.6832 | 3036.6832 | 3036.6832 | 0 | 190.643
0 | 26.4573 | 0 | 0 | 0 | 0 | 26.0427 | 52.5 | 429.4096 | 3000 | 46.5348 | 3046.5348 | 3046.5348 | 0 | 200.5229
0 | 38.6188 | 0 | 0 | 0 | 0 | 13.8812 | 52.5 | 443.2908 | 3000 | 24.8039 | 3024.8039 | 3024.8039 | 0 | 181.0345
0 | 31.0334 | 0 | 0 | 0 | 0 | 21.4666 | 52.5 | 464.7574 | 3000 | 38.3579 | 3038.3579 | 3038.3579 | 0 | 195.6399
0 | 35.2486 | 0 | 0 | 0 | 0 | 17.2514 | 52.5 | 482.0087 | 3000 | 30.8259 | 3030.8259 | 3030.8259 | 0 | 169.6353
0 | 27.121 | 0 | 0 | 0 | 0 | 25.379 | 52.5 | 507.3877 | 3000 | 45.3489 | 3045.3489 | 3045.3489 | 0 | 168.7732
0 | 29.3082 | 0 | 0 | 0 | 0 | 23.1918 | 52.5 | 530.5795 | 3000 | 41.4406 | 3041.4406 | 3041.4406 | 0 | 160.5881
0 | 28.6285 | 0 | 0 | 0 | 0 | 23.8715 | 52.5 | 554.451 | 3000 | 42.6552 | 3042.6552 | 3042.6552 | 0 | 161.5346
0 | 225.7937 | 0 | 0 | 0 | 0 | -173.2937 | 52.5 | 381.1573 | 3000 | 0 | 3000 | 3000 | 0 | 170.49
0 | 24.7345 | 0 | 0 | 0 | 0 | 27.7655 | 52.5 | 408.9228 | 3000 | 49.6133 | 3049.6133 | 3049.6133 | 0 | 207.6482
0 | 44.1933 | 0 | 0 | 0 | 0 | -44.1933 | 0 | 364.7295 | 0 | 0 | 0 | 0 | 16.2223 | 0
0 | 38.2682 | 0 | 0 | 0 | 0 | -38.2682 | 0 | 326.4613 | 0 | 0 | 0 | 0 | 64.8891 | 0
0 | 41.3874 | 0 | 0 | 0 | 0 | -41.3874 | 0 | 285.0739 | 0 | 0 | 0 | 0 | 91.9262 | 0
0 | 41.6475 | 0 | 0 | 0 | 0 | 10.8525 | 52.5 | 295.9264 | 3000 | 19.392 | 3019.392 | 2905.836 | 0 | 198.8464
0 | 46.7255 | 0 | 0 | 0 | 0 | -46.7255 | 0 | 249.2009 | 0 | 0 | 0 | 0 | 183.8525 | 0
0 | 37.8249 | 0 | 0 | 0 | 0 | 14.6751 | 52.5 | 263.876 | 3000 | 26.2224 | 3026.2224 | 2772.0734 | 0 | 190.6909
0 | 52.261 | 0 | 0 | 0 | 0 | 0.239 | 52.5 | 264.115 | 3000 | 0.42706 | 3000.4271 | 2800.3523 | 0 | 182.0229
0 | 37.5801 | 0 | 0 | 0 | 0 | 14.9199 | 52.5 | 279.0349 | 3000 | 26.6599 | 3026.6599 | 2875.252 | 0 | 183.9011
0 | 237.1252 | 0 | 0 | 0 | 0 | -184.6252 | 52.5 | 94.4097 | 3000 | 0 | 3000 | 2929.7035 | 0 | 182.8135
0 | 25.5135 | 0 | 0 | 0 | 0 | 26.9865 | 52.5 | 121.3962 | 3000 | 48.2214 | 3048.2214 | 3042.8139 | 0 | 203.0774
0 | 35.0769 | 0 | 0 | 0 | 0 | -35.0769 | 0 | 86.3193 | 0 | 0 | 0 | 0 | 0 | 0
0 | 35.1314 | 0 | 0 | 0 | 0 | -35.1314 | 0 | 51.188 | 0 | 0 | 0 | 0 | 0 | 0
0 | 36.1082 | 0 | 0 | 0 | 0 | 16.3918 | 52.5 | 67.5798 | 3000 | 29.29 | 3029.29 | 3029.29 | 0 | 208.5666
0 | 34.3977 | 0 | 0 | 0 | 0 | 18.1023 | 52.5 | 85.6821 | 3000 | 32.3464 | 3032.3464 | 3032.3464 | 0 | 196.7993
0 | 29.1056 | 0 | 0 | 0 | 0 | 23.3944 | 52.5 | 109.0765 | 3000 | 41.8027 | 3041.8027 | 3041.8027 | 0 | 198.7818
0 | 28.4642 | 0 | 0 | 0 | 0 | 24.0358 | 52.5 | 133.1123 | 3000 | 42.9487 | 3042.9487 | 3042.9487 | 0 | 186.7153
0 | 34.7335 | 0 | 0 | 0 | 0 | 17.7665 | 52.5 | 150.8788 | 3000 | 31.7463 | 3031.7463 | 3031.7463 | 0 | 181.6016
0 | 26.9206 | 0 | 0 | 0 | 0 | 25.5794 | 52.5 | 176.4582 | 3000 | 45.7071 | 3045.7071 | 3045.7071 | 0 | 190.6613
0 | 30.4782 | 0 | 0 | 0 | 0 | 22.0218 | 52.5 | 198.48 | 3000 | 39.35 | 3039.35 | 3039.35 | 0 | 193.485
0 | 28.3494 | 0 | 0 | 0 | 0 | 24.1506 | 52.5 | 222.6306 | 3000 | 43.154 | 3043.154 | 3043.154 | 0 | 191.9926
0 | 30.1916 | 0 | 0 | 0 | 0 | 22.3084 | 52.5 | 244.939 | 3000 | 39.8622 | 3039.8622 | 3039.8622 | 0 | 183.0605
0 | 28.6293 | 0 | 0 | 0 | 0 | 23.8707 | 52.5 | 268.8097 | 3000 | 42.6538 | 3042.6538 | 3042.6538 | 0 | 185.5106
0 | 32.9765 | 0 | 0 | 0 | 0 | 19.5235 | 52.5 | 288.3333 | 3000 | 34.886 | 3034.886 | 3034.886 | 0 | 189.3769
0 | 24.2772 | 0 | 0 | 0 | 0 | -24.2772 | 0 | 264.0561 | 0 | 0 | 0 | 0 | 0 | 0
0 | 36.1468 | 0 | 0 | 0 | 0 | -36.1468 | 0 | 227.9092 | 0 | 0 | 0 | 0 | 32.4446 | 0
0 | 34.0107 | 0 | 0 | 0 | 0 | -34.0107 | 0 | 193.8986 | 0 | 0 | 0 | 0 | 210.8896 | 0
0 | 42.8377 | 0 | 0 | 0 | 0 | -34.6049 | 8.2328 | 159.2937 | 470.446 | 0 | 470.446 | 0 | 0 | 0
0 | 69.8699 | 0 | 0 | 0 | 0 | -61.2586 | 8.6113 | 98.0351 | 492.0757 | 0 | 492.0757 | 0 | 0 | 0
0 | 32.4136 | 0 | 0 | 0 | 0 | -22.3828 | 10.0308 | 75.6523 | 573.1871 | 0 | 573.1871 | 0 | 0 | 0
0 | 49.7578 | 0 | 0 | 0 | 0 | -40.6734 | 9.0845 | 34.9789 | 519.1128 | 0 | 519.1128 | 0 | 0 | 0
0 | 34.1743 | 0 | 0 | 0 | 0 | -26.1307 | 8.0435 | 8.8482 | 459.6311 | 0 | 459.6311 | 0 | 0 | 0
0 | 8.8482 | 0 | 0 | 0 | 0 | -8.8482 | 0 | 0 | 0 | 0 | 0 | 0 | 254.149 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1114 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 27.6854 | 0 | 0 | 0 | 0 | 24.8146 | 52.5 | 24.8146 | 3000 | 44.3404 | 3044.3404 | 3044.3404 | 0 | 208.446
0 | 27.3404 | 0 | 0 | 0 | 0 | 25.1596 | 52.5 | 49.9742 | 3000 | 44.9569 | 3044.9569 | 3044.9569 | 0 | 182.6974
0 | 34.6376 | 0 | 0 | 0 | 0 | 17.8624 | 52.5 | 67.8366 | 3000 | 31.9177 | 3031.9177 | 3031.9177 | 0 | 191.0108
0 | 25.831 | 0 | 0 | 0 | 0 | 26.669 | 52.5 | 94.5056 | 3000 | 47.6539 | 3047.6539 | 3047.6539 | 0 | 176.7639
0 | 26.8909 | 0 | 0 | 0 | 0 | 25.6091 | 52.5 | 120.1147 | 3000 | 45.7601 | 3045.7601 | 3045.7601 | 0 | 186.8878
0 | 172.6147 | 0 | 0 | 0 | 0 | -120.1147 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 180.3
0 | 33.6378 | 0 | 0 | 0 | 0 | 18.8622 | 52.5 | 18.8622 | 3000 | 33.7043 | 3033.7043 | 3033.7043 | 0 | 175.4998
0 | 22.4672 | 0 | 0 | 0 | 0 | 30.0328 | 52.5 | 48.895 | 3000 | 53.6646 | 3053.6646 | 3053.6646 | 0 | 176.3186
0 | 35.39 | 0 | 0 | 0 | 0 | 17.11 | 52.5 | 66.005 | 3000 | 30.5733 | 3030.5733 | 3030.5733 | 0 | 185.8954
0 | 40.2739 | 0 | 0 | 0 | 0 | 12.2261 | 52.5 | 78.2311 | 3000 | 21.8464 | 3021.8464 | 3021.8464 | 0 | 202.8263
0 | 40.3111 | 0 | 0 | 0 | 0 | -40.3111 | 0 | 37.92 | 0 | 0 | 0 | 0 | 10.8149 | 0
0 | 37.92 | 0 | 0 | 0 | 0 | -37.92 | 0 | 0 | 0 | 0 | 0 | 0 | 97.3337 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 210.8896 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 248.7416 | 0
0 | 5.3939 | 0 | 0 | 0 | 0 | 0 | 5.3939 | 0 | 308.2232 | 0 | 308.2232 | 0 | 0 | 0
0 | 7.8543 | 0 | 0 | 0 | 0 | 0 | 7.8543 | 0 | 448.8163 | 0 | 448.8163 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275.7787 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.6302 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.2594 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 23.9933 | 0 | 0 | 0 | 0 | 28.5067 | 52.5 | 28.5067 | 3000 | 50.9378 | 3050.9378 | 3050.9378 | 0 | 198.616
0 | 34.2359 | 0 | 0 | 0 | 0 | 18.2641 | 52.5 | 46.7709 | 3000 | 32.6355 | 3032.6355 | 3032.6355 | 0 | 188.3267
0 | 25.8696 | 0 | 0 | 0 | 0 | 26.6304 | 52.5 | 73.4013 | 3000 | 47.585 | 3047.585 | 3047.585 | 0 | 179.5028
0 | 27.0007 | 0 | 0 | 0 | 0 | 25.4993 | 52.5 | 98.9006 | 3000 | 45.5639 | 3045.5639 | 3045.5639 | 0 | 188.3377
0 | 29.368 | 0 | 0 | 0 | 0 | 23.132 | 52.5 | 122.0326 | 3000 | 41.3338 | 3041.3338 | 3041.3338 | 0 | 187.8936
0 | 26.95 | 0 | 0 | 0 | 0 | 25.55 | 52.5 | 147.5826 | 3000 | 45.6544 | 3045.6544 | 3045.6544 | 0 | 188.2824
0 | 200.0826 | 0 | 0 | 0 | 0 | -147.5826 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 180.24
0 | 23.2456 | 0 | 0 | 0 | 0 | 29.2544 | 52.5 | 29.2544 | 3000 | 52.2738 | 3052.2738 | 3052.2738 | 0 | 194.4298
0 | 19.5995 | 0 | 0 | 0 | 0 | -19.5995 | 0 | 9.6549 | 0 | 0 | 0 | 0 | 0 | 0
0 | 9.6549 | 0 | 0 | 0 | 0 | -9.6549 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8149 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2965 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.3708 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 178.445 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 200.0747 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 227.1119 | 0
0 | 6.0563 | 0 | 0 | 0 | 0 | 0 | 6.0563 | 0 | 346.0752 | 0 | 346.0752 | 0 | 0 | 0
0 | 5.2993 | 0 | 0 | 0 | 0 | 0 | 5.2993 | 0 | 302.8158 | 0 | 302.8158 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2965 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 18.6215 | 0 | 0 | 0 | 0 | 33.8785 | 52.5 | 33.8785 | 3000 | 60.5364 | 3060.5364 | 3060.5364 | 0 | 207.6268
0 | 37.4248 | 0 | 0 | 0 | 0 | 15.0752 | 52.5 | 48.9537 | 3000 | 26.9374 | 3026.9374 | 3026.9374 | 0 | 200.8676
0 | 31.8545 | 0 | 0 | 0 | 0 | 20.6455 | 52.5 | 69.5992 | 3000 | 36.8908 | 3036.8908 | 3036.8908 | 0 | 189.3805
0 | 27.7504 | 0 | 0 | 0 | 0 | 24.7496 | 52.5 | 94.3488 | 3000 | 44.2243 | 3044.2243 | 3044.2243 | 0 | 179.8832
0 | 29.4674 | 0 | 0 | 0 | 0 | 23.0326 | 52.5 | 117.3814 | 3000 | 41.1562 | 3041.1562 | 3041.1562 | 0 | 183.8987
0 | 21.0133 | 0 | 0 | 0 | 0 | 31.4867 | 52.5 | 148.8682 | 3000 | 56.2626 | 3056.2626 | 3056.2626 | 0 | 177.5689
0 | 26.8104 | 0 | 0 | 0 | 0 | 25.6896 | 52.5 | 174.5578 | 3000 | 45.9039 | 3045.9039 | 3045.9039 | 0 | 170.8752
0 | 19.0031 | 0 | 0 | 0 | 0 | 33.4969 | 52.5 | 208.0547 | 3000 | 59.8545 | 3059.8545 | 3059.8545 | 0 | 172.9124
0 | 30.8492 | 0 | 0 | 0 | 0 | 21.6508 | 52.5 | 229.7055 | 3000 | 38.6871 | 3038.6871 | 3038.6871 | 0 | 184.6306
0 | 29.3011 | 0 | 0 | 0 | 0 | 23.1989 | 52.5 | 252.9044 | 3000 | 41.4534 | 3041.4534 | 3041.4534 | 0 | 205.1156
0 | 236.7833 | 0 | 0 | 0 | 0 | -236.7833 | 0 | 16.1211 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 16.1211 | 0 | 0 | 0 | 0 | -16.1211 | 0 | 0 | 0 | 0 | 0 | 0 | 32.4446 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5188 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7411 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 113.5559 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.7782 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.7782 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7411 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.852 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 27.2169 | 0 | 0 | 0 | 0 | 25.2831 | 52.5 | 25.2831 | 3000 | 45.1776 | 3045.1776 | 3045.1776 | 0 | 210.1477
0 | 24.0932 | 0 | 0 | 0 | 0 | 28.4068 | 52.5 | 53.69 | 3000 | 50.7592 | 3050.7592 | 3050.7592 | 0 | 201.106
0 | 37.6227 | 0 | 0 | 0 | 0 | 14.8773 | 52.5 | 68.5673 | 3000 | 26.5838 | 3026.5838 | 3026.5838 | 0 | 194.3369
0 | 22.4747 | 0 | 0 | 0 | 0 | 30.0253 | 52.5 | 98.5926 | 3000 | 53.6513 | 3053.6513 | 3053.6513 | 0 | 189.5401
0 | 25.3056 | 0 | 0 | 0 | 0 | 27.1944 | 52.5 | 125.787 | 3000 | 48.5927 | 3048.5927 | 3048.5927 | 0 | 185.0496
0 | 30.016 | 0 | 0 | 0 | 0 | 22.484 | 52.5 | 148.271 | 3000 | 40.176 | 3040.176 | 3040.176 | 0 | 176.7558
0 | 25.4587 | 0 | 0 | 0 | 0 | 27.0413 | 52.5 | 175.3123 | 3000 | 48.3192 | 3048.3192 | 3048.3192 | 0 | 175.9185
0 | 25.1725 | 0 | 0 | 0 | 0 | 27.3275 | 52.5 | 202.6399 | 3000 | 48.8307 | 3048.8307 | 3048.8307 | 0 | 175.6126
0 | 20.1159 | 0 | 0 | 0 | 0 | 32.3841 | 52.5 | 235.024 | 3000 | 57.8662 | 3057.8662 | 3057.8662 | 0 | 178.7934
0 | 49.0612 | 0 | 0 | 0 | 0 | 3.4388 | 52.5 | 238.4628 | 3000 | 6.1446 | 3006.1446 | 3000.7372 | 0 | 188.0862
0 | 39.0939 | 0 | 0 | 0 | 0 | 13.4061 | 52.5 | 251.8688 | 3000 | 23.9548 | 3023.9548 | 2991.5103 | 0 | 198.8457
0 | 241.0984 | 0 | 0 | 0 | 0 | -241.0984 | 0 | 10.7704 | 0 | 0 | 0 | 0 | 75.704 | 0
0 | 10.7704 | 0 | 0 | 0 | 0 | -10.7704 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5188 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5188 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1114 | 0
0 | 43.6851 | 0 | 0 | 0 | 0 | 8.8149 | 52.5 | 8.8149 | 3000 | 15.751 | 3015.751 | 2918.4174 | 0 | 190.6602
0 | 25.37 | 0 | 0 | 0 | 0 | 27.13 | 52.5 | 35.9449 | 3000 | 48.4778 | 3048.4778 | 2951.1441 | 0 | 189.1388
0 | 39.0545 | 0 | 0 | 0 | 0 | 13.4455 | 52.5 | 49.3905 | 3000 | 24.0254 | 3024.0254 | 2964.5437 | 0 | 188.545
0 | 47.5025 | 0 | 0 | 0 | 0 | 4.9975 | 52.5 | 54.3879 | 3000 | 8.9298 | 3008.9298 | 2998.1149 | 0 | 193.0486
0 | 45.0717 | 0 | 0 | 0 | 0 | -45.0717 | 0 | 9.3162 | 0 | 0 | 0 | 0 | 0 | 0
0 | 9.3162 | 0 | 0 | 0 | 0 | -9.3162 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 27.0043 | 0 | 0 | 0 | 0 | 25.4957 | 52.5 | 25.4957 | 3000 | 45.5574 | 3045.5574 | 3045.5574 | 0 | 211.9403
0 | 23.9091 | 0 | 0 | 0 | 0 | 28.5909 | 52.5 | 54.0866 | 3000 | 51.0882 | 3051.0882 | 3051.0882 | 0 | 199.6327
0 | 26.7609 | 0 | 0 | 0 | 0 | 25.7391 | 52.5 | 79.8258 | 3000 | 45.9924 | 3045.9924 | 3045.9924 | 0 | 193.3596
0 | 31.1597 | 0 | 0 | 0 | 0 | 21.3403 | 52.5 | 101.1661 | 3000 | 38.1323 | 3038.1323 | 3038.1323 | 0 | 192.891
0 | 23.9608 | 0 | 0 | 0 | 0 | 28.5392 | 52.5 | 129.7053 | 3000 | 50.9958 | 3050.9958 | 3050.9958 | 0 | 186.2938
0 | 27.5059 | 0 | 0 | 0 | 0 | 24.9941 | 52.5 | 154.6994 | 3000 | 44.6611 | 3044.6611 | 3044.6611 | 0 | 174.4591
0 | 26.1358 | 0 | 0 | 0 | 0 | 26.3642 | 52.5 | 181.0635 | 3000 | 47.1093 | 3047.1093 | 3047.1093 | 0 | 171.5218
0 | 31.3816 | 0 | 0 | 0 | 0 | 21.1184 | 52.5 | 202.1819 | 3000 | 37.7357 | 3037.7357 | 3037.7357 | 0 | 168.5336
0 | 20.1976 | 0 | 0 | 0 | 0 | 32.3024 | 52.5 | 234.4843 | 3000 | 57.7201 | 3057.7201 | 3057.7201 | 0 | 165.1169
0 | 22.75 | 0 | 0 | 0 | 0 | 29.75 | 52.5 | 264.2343 | 3000 | 53.1594 | 3053.1594 | 3053.1594 | 0 | 164.5653
0 | 28.7945 | 0 | 0 | 0 | 0 | 23.7055 | 52.5 | 287.9398 | 3000 | 42.3585 | 3042.3585 | 3042.3585 | 0 | 162.6749
0 | 29.0732 | 0 | 0 | 0 | 0 | 23.4268 | 52.5 | 311.3666 | 3000 | 41.8606 | 3041.8606 | 3041.8606 | 0 | 166.9373
0 | 41.6938 | 0 | 0 | 0 | 0 | 10.8062 | 52.5 | 322.1727 | 3000 | 19.3092 | 3019.3092 | 2981.4572 | 0 | 166.8722
0 | 35.5276 | 0 | 0 | 0 | 0 | 16.9724 | 52.5 | 339.1452 | 3000 | 30.3275 | 3030.3275 | 2781.5859 | 0 | 163.5573
0 | 43.0105 | 0 | 0 | 0 | 0 | 9.4895 | 52.5 | 348.6346 | 3000 | 16.9564 | 3016.9564 | 2638.4366 | 0 | 163.715
0 | 36.8126 | 0 | 0 | 0 | 0 | 15.6874 | 52.5 | 364.322 | 3000 | 28.0313 | 3028.0313 | 2465.659 | 0 | 158.6158
0 | 47.7247 | 0 | 0 | 0 | 0 | 4.7753 | 52.5 | 369.0973 | 3000 | 8.5329 | 3008.5329 | 2343.4196 | 0 | 154.9235
0 | 41.086 | 0 | 0 | 0 | 0 | 11.414 | 52.5 | 380.5113 | 3000 | 20.3953 | 3020.3953 | 2479.6528 | 0 | 162.0453
0 | 237.5692 | 0 | 0 | 0 | 0 | -185.0692 | 52.5 | 195.4421 | 3000 | 0 | 3000 | 2502.5169 | 0 | 155.3813
0 | 46.9677 | 0 | 0 | 0 | 0 | 5.5323 | 52.5 | 200.9744 | 3000 | 9.8856 | 3009.8856 | 2717.8846 | 0 | 163.4536
0 | 30.4098 | 0 | 0 | 0 | 0 | 22.0902 | 52.5 | 223.0646 | 3000 | 39.4722 | 3039.4722 | 2898.8792 | 0 | 172.1934
0 | 48.7209 | 0 | 0 | 0 | 0 | 3.7791 | 52.5 | 226.8437 | 3000 | 6.7527 | 3006.7527 | 3001.3453 | 0 | 182.4518
0 | 48.0649 | 0 | 0 | 0 | 0 | 4.4351 | 52.5 | 231.2788 | 3000 | 7.9249 | 3007.9249 | 3007.9249 | 0 | 201.3505
0 | 47.478 | 0 | 0 | 0 | 0 | -47.478 | 0 | 183.8007 | 0 | 0 | 0 | 0 | 0 | 0
0 | 18.8247 | 0 | 0 | 0 | 0 | -18.8247 | 0 | 164.9761 | 0 | 0 | 0 | 0 | 0 | 0
0 | 23.5602 | 0 | 0 | 0 | 0 | -23.5602 | 0 | 141.4158 | 0 | 0 | 0 | 0 | 0 | 0
0 | 27.4282 | 0 | 0 | 0 | 0 | 25.0718 | 52.5 | 166.4876 | 3000 | 44.7999 | 3044.7999 | 3044.7999 | 0 | 203.8189
0 | 30.2065 | 0 | 0 | 0 | 0 | 22.2935 | 52.5 | 188.7811 | 3000 | 39.8355 | 3039.8355 | 3039.8355 | 0 | 186.1899
0 | 34.2735 | 0 | 0 | 0 | 0 | 18.2265 | 52.5 | 207.0076 | 3000 | 32.5683 | 3032.5683 | 3032.5683 | 0 | 172.1286
0 | 21.6424 | 0 | 0 | 0 | 0 | 30.8576 | 52.5 | 237.8652 | 3000 | 55.1385 | 3055.1385 | 3055.1385 | 0 | 168.0326
0 | 24.5274 | 0 | 0 | 0 | 0 | 27.9726 | 52.5 | 265.8378 | 3000 | 49.9833 | 3049.9833 | 3049.9833 | 0 | 168.0846
0 | 27.9379 | 0 | 0 | 0 | 0 | 24.5621 | 52.5 | 290.3999 | 3000 | 43.8892 | 3043.8892 | 3043.8892 | 0 | 165.6485
0 | 29.208 | 0 | 0 | 0 | 0 | 23.292 | 52.5 | 313.6919 | 3000 | 41.6198 | 3041.6198 | 3041.6198 | 0 | 164.8862
0 | 25.0777 | 0 | 0 | 0 | 0 | 27.4223 | 52.5 | 341.1142 | 3000 | 49 | 3049 | 3049 | 0 | 163.2739
0 | 27.7651 | 0 | 0 | 0 | 0 | 24.7349 | 52.5 | 365.8491 | 3000 | 44.198 | 3044.198 | 3044.198 | 0 | 169.3487
0 | 28.5627 | 0 | 0 | 0 | 0 | 23.9373 | 52.5 | 389.7864 | 3000 | 42.7728 | 3042.7728 | 3042.7728 | 0 | 189.1388
0 | 47.16 | 0 | 0 | 0 | 0 | -47.16 | 0 | 342.6264 | 0 | 0 | 0 | 0 | 32.4446 | 0
0 | 49.7525 | 0 | 0 | 0 | 0 | -49.7525 | 0 | 292.8739 | 0 | 0 | 0 | 0 | 97.3337 | 0
0 | 40.6511 | 0 | 0 | 0 | 0 | -40.6511 | 0 | 252.2228 | 0 | 0 | 0 | 0 | 173.0376 | 0
0 | 45.8572 | 0 | 0 | 0 | 0 | 6.6428 | 52.5 | 258.8656 | 3000 | 11.8698 | 3011.8698 | 2741.4985 | 0 | 186.4219
0 | 44.4598 | 0 | 0 | 0 | 0 | 8.0402 | 52.5 | 266.9058 | 3000 | 14.3668 | 3014.3668 | 2798.0698 | 0 | 167.0448
0 | 46.4712 | 0 | 0 | 0 | 0 | 6.0288 | 52.5 | 272.9345 | 3000 | 10.7726 | 3010.7726 | 2843.1424 | 0 | 161.1777
0 | 244.0736 | 0 | 0 | 0 | 0 | -191.5736 | 52.5 | 81.3609 | 3000 | 0 | 3000 | 2908.0738 | 0 | 162.2705
0 | 36.6149 | 0 | 0 | 0 | 0 | 15.8851 | 52.5 | 97.246 | 3000 | 28.3846 | 3028.3846 | 2952.6806 | 0 | 178.3419
0 | 46.1141 | 0 | 0 | 0 | 0 | 6.3859 | 52.5 | 103.6319 | 3000 | 11.4108 | 3011.4108 | 2957.3365 | 0 | 178.8893
0 | 51.9545 | 0 | 0 | 0 | 0 | 0.54555 | 52.5 | 104.1775 | 3000 | 0.97482 | 3000.9748 | 2995.5674 | 0 | 184.497
0 | 51.2205 | 0 | 0 | 0 | 0 | 1.2795 | 52.5 | 105.4569 | 3000 | 2.2863 | 3002.2863 | 3002.2863 | 0 | 194.8484
0 | 34.7958 | 0 | 0 | 0 | 0 | 17.7042 | 52.5 | 123.1611 | 3000 | 31.635 | 3031.635 | 3031.635 | 0 | 187.2944
0 | 31.2255 | 0 | 0 | 0 | 0 | 21.2745 | 52.5 | 144.4356 | 3000 | 38.0146 | 3038.0146 | 3038.0146 | 0 | 173.4099
0 | 26.4321 | 0 | 0 | 0 | 0 | 26.0679 | 52.5 | 170.5034 | 3000 | 46.5798 | 3046.5798 | 3046.5798 | 0 | 169.3594
0 | 23.7593 | 0 | 0 | 0 | 0 | 28.7407 | 52.5 | 199.2441 | 3000 | 51.3558 | 3051.3558 | 3051.3558 | 0 | 167.5194
0 | 31.5968 | 0 | 0 | 0 | 0 | 20.9032 | 52.5 | 220.1473 | 3000 | 37.3513 | 3037.3513 | 3037.3513 | 0 | 166.1431
0 | 30.4644 | 0 | 0 | 0 | 0 | 22.0356 | 52.5 | 242.1829 | 3000 | 39.3747 | 3039.3747 | 3039.3747 | 0 | 151.6648
0 | 22.7136 | 0 | 0 | 0 | 0 | 29.7864 | 52.5 | 271.9694 | 3000 | 53.2244 | 3053.2244 | 3053.2244 | 0 | 159.6836
0 | 31.2066 | 0 | 0 | 0 | 0 | 21.2934 | 52.5 | 293.2628 | 3000 | 38.0485 | 3038.0485 | 3038.0485 | 0 | 159.1937
0 | 18.8395 | 0 | 0 | 0 | 0 | 33.6605 | 52.5 | 326.9233 | 3000 | 60.1469 | 3060.1469 | 3060.1469 | 0 | 163.473
0 | 30.6296 | 0 | 0 | 0 | 0 | 21.8704 | 52.5 | 348.7937 | 3000 | 39.0796 | 3039.0796 | 3039.0796 | 0 | 166.8455
0 | 27.7787 | 0 | 0 | 0 | 0 | 24.7213 | 52.5 | 373.515 | 3000 | 44.1737 | 3044.1737 | 3044.1737 | 0 | 167.1251
0 | 27.9395 | 0 | 0 | 0 | 0 | 24.5605 | 52.5 | 398.0755 | 3000 | 43.8863 | 3043.8863 | 3043.8863 | 0 | 176.515
0 | 29.4204 | 0 | 0 | 0 | 0 | 23.0796 | 52.5 | 421.1551 | 3000 | 41.2402 | 3041.2402 | 3041.2402 | 0 | 210.2409
0 | 37.5687 | 0 | 0 | 0 | 0 | -37.5687 | 0 | 383.5864 | 0 | 0 | 0 | 0 | 10.8149 | 0
0 | 48.1803 | 0 | 0 | 0 | 0 | -48.1803 | 0 | 335.4061 | 0 | 0 | 0 | 0 | 48.6668 | 0
0 | 335.4061 | 0 | 0 | 0 | 0 | -335.4061 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1114 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97.3337 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 91.9262 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 124.3708 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2228 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2228 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 48.6668 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 23.2862 | 0 | 0 | 0 | 0 | 29.2138 | 52.5 | 29.2138 | 3000 | 52.2012 | 3052.2012 | 3052.2012 | 0 | 207.336
0 | 33.0772 | 0 | 0 | 0 | 0 | 19.4228 | 52.5 | 48.6367 | 3000 | 34.706 | 3034.706 | 3034.706 | 0 | 185.2081
0 | 35.2004 | 0 | 0 | 0 | 0 | 17.2996 | 52.5 | 65.9362 | 3000 | 30.912 | 3030.912 | 3030.912 | 0 | 174.5805
0 | 23.5877 | 0 | 0 | 0 | 0 | 28.9123 | 52.5 | 94.8485 | 3000 | 51.6624 | 3051.6624 | 3051.6624 | 0 | 176.3861
0 | 147.3485 | 0 | 0 | 0 | 0 | -94.8485 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 169.89
0 | 29.5932 | 0 | 0 | 0 | 0 | 22.9068 | 52.5 | 22.9068 | 3000 | 40.9314 | 3040.9314 | 3040.9314 | 0 | 168.7717
0 | 30.1307 | 0 | 0 | 0 | 0 | 22.3693 | 52.5 | 45.2761 | 3000 | 39.971 | 3039.971 | 3039.971 | 0 | 168.4144
0 | 24.4375 | 0 | 0 | 0 | 0 | 28.0625 | 52.5 | 73.3386 | 3000 | 50.1439 | 3050.1439 | 3050.1439 | 0 | 171.9671
0 | 31.9131 | 0 | 0 | 0 | 0 | 20.5869 | 52.5 | 93.9255 | 3000 | 36.7861 | 3036.7861 | 3036.7861 | 0 | 174.0382
0 | 24.5555 | 0 | 0 | 0 | 0 | 27.9445 | 52.5 | 121.87 | 3000 | 49.933 | 3049.933 | 3049.933 | 0 | 200.2586
0 | 39.646 | 0 | 0 | 0 | 0 | 12.854 | 52.5 | 134.7239 | 3000 | 22.9684 | 3022.9684 | 3006.7461 | 0 | 205.3608
0 | 47.9521 | 0 | 0 | 0 | 0 | -47.9521 | 0 | 86.7718 | 0 | 0 | 0 | 0 | 48.6668 | 0
0 | 40.9357 | 0 | 0 | 0 | 0 | 11.5643 | 52.5 | 98.3361 | 3000 | 20.6639 | 3020.6639 | 2934.1451 | 0 | 200.8422
0 | 27.0199 | 0 | 0 | 0 | 0 | -27.0199 | 0 | 71.3163 | 0 | 0 | 0 | 0 | 129.7782 | 0
0 | 44.072 | 0 | 0 | 0 | 0 | -44.072 | 0 | 27.2443 | 0 | 0 | 0 | 0 | 167.6302 | 0
0 | 42.7712 | 0 | 0 | 0 | 0 | 9.7288 | 52.5 | 36.9731 | 3000 | 17.3841 | 3017.3841 | 2882.1985 | 0 | 201.581
0 | 45.4015 | 0 | 0 | 0 | 0 | 7.0985 | 52.5 | 44.0716 | 3000 | 12.6841 | 3012.6841 | 2904.5356 | 0 | 202.0104
0 | 42.1481 | 0 | 0 | 0 | 0 | 10.3519 | 52.5 | 54.4235 | 3000 | 18.4975 | 3018.4975 | 2959.0158 | 0 | 201.0059
0 | 42.7899 | 0 | 0 | 0 | 0 | 9.7101 | 52.5 | 64.1336 | 3000 | 17.3507 | 3017.3507 | 2984.9061 | 0 | 206.854
0 | 38.3339 | 0 | 0 | 0 | 0 | -38.3339 | 0 | 25.7998 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 25.7998 | 0 | 0 | 0 | 0 | -25.7998 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 31.8933 | 0 | 0 | 0 | 0 | 20.6067 | 52.5 | 20.6067 | 3000 | 36.8214 | 3036.8214 | 3036.8214 | 0 | 210.6643
0 | 24.6425 | 0 | 0 | 0 | 0 | 27.8575 | 52.5 | 48.4641 | 3000 | 49.7776 | 3049.7776 | 3049.7776 | 0 | 199.7299
0 | 26.0042 | 0 | 0 | 0 | 0 | 26.4958 | 52.5 | 74.9599 | 3000 | 47.3444 | 3047.3444 | 3047.3444 | 0 | 196.5537
0 | 23.2878 | 0 | 0 | 0 | 0 | 29.2122 | 52.5 | 104.1721 | 3000 | 52.1983 | 3052.1983 | 3052.1983 | 0 | 186.7335
0 | 24.6623 | 0 | 0 | 0 | 0 | 27.8377 | 52.5 | 132.0098 | 3000 | 49.7423 | 3049.7423 | 3049.7423 | 0 | 186.7967
0 | 37.2879 | 0 | 0 | 0 | 0 | 15.2121 | 52.5 | 147.222 | 3000 | 27.182 | 3027.182 | 3027.182 | 0 | 182.2666
0 | 19.6873 | 0 | 0 | 0 | 0 | 32.8127 | 52.5 | 180.0347 | 3000 | 58.632 | 3058.632 | 3058.632 | 0 | 172.0175
0 | 37.0377 | 0 | 0 | 0 | 0 | 15.4623 | 52.5 | 195.4969 | 3000 | 27.629 | 3027.629 | 3027.629 | 0 | 160.6157
0 | 26.3852 | 0 | 0 | 0 | 0 | 26.1148 | 52.5 | 221.6118 | 3000 | 46.6637 | 3046.6637 | 3046.6637 | 0 | 158.4265
0 | 30.3763 | 0 | 0 | 0 | 0 | 22.1237 | 52.5 | 243.7354 | 3000 | 39.532 | 3039.532 | 3039.532 | 0 | 164.2563
0 | 27.107 | 0 | 0 | 0 | 0 | 25.393 | 52.5 | 269.1284 | 3000 | 45.3738 | 3045.3738 | 3045.3738 | 0 | 192.0413
0 | 248.2516 | 0 | 0 | 0 | 0 | -195.7516 | 52.5 | 73.3768 | 3000 | 0 | 3000 | 2994.5926 | 0 | 196.9544
0 | 35.2214 | 0 | 0 | 0 | 0 | 17.2786 | 52.5 | 90.6554 | 3000 | 30.8746 | 3030.8746 | 2933.541 | 0 | 204.7318
0 | 34.9352 | 0 | 0 | 0 | 0 | 17.5648 | 52.5 | 108.2202 | 3000 | 31.3859 | 3031.3859 | 2625.829 | 0 | 180.3945
0 | 51.2028 | 0 | 0 | 0 | 0 | 1.2972 | 52.5 | 109.5174 | 3000 | 2.318 | 3002.318 | 2445.3532 | 0 | 166.6997
0 | 41.4413 | 0 | 0 | 0 | 0 | 11.0587 | 52.5 | 120.5761 | 3000 | 19.7605 | 3019.7605 | 2441.166 | 0 | 158.6758
0 | 35.068 | 0 | 0 | 0 | 0 | 17.432 | 52.5 | 138.0081 | 3000 | 31.1486 | 3031.1486 | 2679.6659 | 0 | 172.7045
0 | 51.0973 | 0 | 0 | 0 | 0 | 1.4027 | 52.5 | 139.4108 | 3000 | 2.5065 | 3002.5065 | 2548.2828 | 0 | 155.6746
0 | 33.6938 | 0 | 0 | 0 | 0 | 18.8062 | 52.5 | 158.2171 | 3000 | 33.6042 | 3033.6042 | 2757.8255 | 0 | 158.7956
0 | 36.0503 | 0 | 0 | 0 | 0 | 16.4497 | 52.5 | 174.6667 | 3000 | 29.3934 | 3029.3934 | 2959.0969 | 0 | 172.5745
0 | 41.4148 | 0 | 0 | 0 | 0 | 11.0852 | 52.5 | 185.7519 | 3000 | 19.8077 | 3019.8077 | 3014.4003 | 0 | 184.7225
0 | 44.5421 | 0 | 0 | 0 | 0 | 7.9579 | 52.5 | 193.7098 | 3000 | 14.2197 | 3014.2197 | 3014.2197 | 0 | 200.8977
0 | 62.044 | 0 | 0 | 0 | 0 | -9.544 | 52.5 | 184.1659 | 3000 | 0 | 3000 | 3000 | 0 | 194.28
0 | 33.2646 | 0 | 0 | 0 | 0 | 19.2354 | 52.5 | 203.4013 | 3000 | 34.3712 | 3034.3712 | 3034.3712 | 0 | 183.276
0 | 31.5205 | 0 | 0 | 0 | 0 | 20.9795 | 52.5 | 224.3808 | 3000 | 37.4876 | 3037.4876 | 3037.4876 | 0 | 176.7514
0 | 222.9601 | 0 | 0 | 0 | 0 | -170.4601 | 52.5 | 53.9207 | 3000 | 0 | 3000 | 3000 | 0 | 182.1
0 | 35.5537 | 0 | 0 | 0 | 0 | 16.9463 | 52.5 | 70.867 | 3000 | 30.2808 | 3030.2808 | 3030.2808 | 0 | 177.4229
0 | 23.3612 | 0 | 0 | 0 | 0 | 29.1388 | 52.5 | 100.0058 | 3000 | 52.0671 | 3052.0671 | 3052.0671 | 0 | 173.9678
0 | 152.5058 | 0 | 0 | 0 | 0 | -100.0058 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 185.55
0 | 40.0163 | 0 | 0 | 0 | 0 | 12.4837 | 52.5 | 12.4837 | 3000 | 22.3067 | 3022.3067 | 3022.3067 | 0 | 181.3384
0 | 26.3415 | 0 | 0 | 0 | 0 | 26.1585 | 52.5 | 38.6422 | 3000 | 46.7418 | 3046.7418 | 3046.7418 | 0 | 185.8512
0 | 29.5425 | 0 | 0 | 0 | 0 | 22.9575 | 52.5 | 61.5997 | 3000 | 41.022 | 3041.022 | 3041.022 | 0 | 182.4613
0 | 17.8858 | 0 | 0 | 0 | 0 | 34.6142 | 52.5 | 96.2139 | 3000 | 61.8509 | 3061.8509 | 3061.8509 | 0 | 160.441
0 | 30.3243 | 0 | 0 | 0 | 0 | 22.1757 | 52.5 | 118.3896 | 3000 | 39.625 | 3039.625 | 3039.625 | 0 | 165.6292
0 | 19.8122 | 0 | 0 | 0 | 0 | 32.6878 | 52.5 | 151.0775 | 3000 | 58.4088 | 3058.4088 | 3058.4088 | 0 | 188.0921
0 | 42.4511 | 0 | 0 | 0 | 0 | -42.4511 | 0 | 108.6263 | 0 | 0 | 0 | 0 | 10.8149 | 0
0 | 54.071 | 0 | 0 | 0 | 0 | -54.071 | 0 | 54.5553 | 0 | 0 | 0 | 0 | 43.2594 | 0
0 | 44.275 | 0 | 0 | 0 | 0 | -44.275 | 0 | 10.2803 | 0 | 0 | 0 | 0 | 75.704 | 0
0 | 10.2803 | 0 | 0 | 0 | 0 | -10.2803 | 0 | 0 | 0 | 0 | 0 | 0 | 97.3337 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 129.7782 | 0
0 | 45.01 | 0 | 0 | 0 | 0 | 7.49 | 52.5 | 7.49 | 3000 | 13.3837 | 3013.3837 | 2883.6055 | 0 | 199.3436
0 | 59.99 | 0 | 0 | 0 | 0 | -7.49 | 52.5 | 0 | 3000 | 0 | 3000 | 2886.4441 | 0 | 191.8908
0 | 39.258 | 0 | 0 | 0 | 0 | 13.242 | 52.5 | 13.242 | 3000 | 23.6618 | 3023.6618 | 2964.1801 | 0 | 187.6622
0 | 38.5521 | 0 | 0 | 0 | 0 | 13.9479 | 52.5 | 27.19 | 3000 | 24.9231 | 3024.9231 | 2992.4785 | 0 | 180.8953
0 | 39.6061 | 0 | 0 | 0 | 0 | 12.8939 | 52.5 | 40.0838 | 3000 | 23.0396 | 3023.0396 | 3017.6322 | 0 | 183.472
0 | 43.7313 | 0 | 0 | 0 | 0 | 8.7687 | 52.5 | 48.8525 | 3000 | 15.6684 | 3015.6684 | 3015.6684 | 0 | 196.0184
0 | 37.5176 | 0 | 0 | 0 | 0 | 14.9824 | 52.5 | 63.8349 | 3000 | 26.7715 | 3026.7715 | 3026.7715 | 0 | 203.8228
0 | 28.6655 | 0 | 0 | 0 | 0 | 23.8345 | 52.5 | 87.6694 | 3000 | 42.5891 | 3042.5891 | 3042.5891 | 0 | 190.4357
0 | 25.8979 | 0 | 0 | 0 | 0 | 26.6021 | 52.5 | 114.2715 | 3000 | 47.5344 | 3047.5344 | 3047.5344 | 0 | 190.1661
0 | 31.4318 | 0 | 0 | 0 | 0 | 21.0682 | 52.5 | 135.3397 | 3000 | 37.6461 | 3037.6461 | 3037.6461 | 0 | 187.3013
0 | 27.4449 | 0 | 0 | 0 | 0 | 25.0551 | 52.5 | 160.3948 | 3000 | 44.7701 | 3044.7701 | 3044.7701 | 0 | 187.0402
0 | 26.3503 | 0 | 0 | 0 | 0 | 26.1497 | 52.5 | 186.5445 | 3000 | 46.7261 | 3046.7261 | 3046.7261 | 0 | 187.3432
0 | 23.6011 | 0 | 0 | 0 | 0 | 28.8989 | 52.5 | 215.4434 | 3000 | 51.6385 | 3051.6385 | 3051.6385 | 0 | 186.7603
0 | 25.2462 | 0 | 0 | 0 | 0 | 27.2538 | 52.5 | 242.6972 | 3000 | 48.699 | 3048.699 | 3048.699 | 0 | 167.6784
0 | 34.6299 | 0 | 0 | 0 | 0 | 17.8701 | 52.5 | 260.5674 | 3000 | 31.9316 | 3031.9316 | 3031.9316 | 0 | 166.3621
0 | 28.945 | 0 | 0 | 0 | 0 | 23.555 | 52.5 | 284.1223 | 3000 | 42.0896 | 3042.0896 | 3042.0896 | 0 | 158.4929
0 | 27.2492 | 0 | 0 | 0 | 0 | 25.2508 | 52.5 | 309.3732 | 3000 | 45.1199 | 3045.1199 | 3045.1199 | 0 | 146.7139
0 | 23.6823 | 0 | 0 | 0 | 0 | 28.8177 | 52.5 | 338.1909 | 3000 | 51.4934 | 3051.4934 | 3051.4934 | 0 | 137.7139
0 | 224.6306 | 0 | 0 | 0 | 0 | -172.1306 | 52.5 | 166.0603 | 3000 | 0 | 3000 | 3000 | 0 | 159
0 | 49.5732 | 0 | 0 | 0 | 0 | 2.9268 | 52.5 | 168.987 | 3000 | 5.2297 | 3005.2297 | 2956.5629 | 0 | 165.9223
0 | 50.3067 | 0 | 0 | 0 | 0 | 2.1933 | 52.5 | 171.1803 | 3000 | 3.9192 | 3003.9192 | 2836.289 | 0 | 166.8305
0 | 50.8606 | 0 | 0 | 0 | 0 | 1.6394 | 52.5 | 172.8197 | 3000 | 2.9293 | 3002.9293 | 2792.0397 | 0 | 177.4062
0 | 36.3732 | 0 | 0 | 0 | 0 | 16.1268 | 52.5 | 188.9465 | 3000 | 28.8164 | 3028.8164 | 2644.8892 | 0 | 171.6533
0 | 31.0576 | 0 | 0 | 0 | 0 | 21.4424 | 52.5 | 210.3889 | 3000 | 38.3147 | 3038.3147 | 2773.3509 | 0 | 172.1974
0 | 45.1264 | 0 | 0 | 0 | 0 | 7.3736 | 52.5 | 217.7625 | 3000 | 13.1756 | 3013.1756 | 2461.6182 | 0 | 152.1772
0 | 46.1026 | 0 | 0 | 0 | 0 | 6.3974 | 52.5 | 224.1598 | 3000 | 11.4312 | 3011.4312 | 2854.6159 | 0 | 167.2805
0 | 42.3906 | 0 | 0 | 0 | 0 | 10.1094 | 52.5 | 234.2692 | 3000 | 18.0641 | 3018.0641 | 2915.323 | 0 | 157.1359
0 | 47.518 | 0 | 0 | 0 | 0 | 4.982 | 52.5 | 239.2512 | 3000 | 8.9022 | 3008.9022 | 2949.4205 | 0 | 169.2967
0 | 39.5822 | 0 | 0 | 0 | 0 | 12.9178 | 52.5 | 252.169 | 3000 | 23.0824 | 3023.0824 | 3017.675 | 0 | 176.0813
0 | 55.5223 | 0 | 0 | 0 | 0 | -3.0223 | 52.5 | 249.1467 | 3000 | 0 | 3000 | 3000 | 0 | 208.11
0 | 41.6583 | 0 | 0 | 0 | 0 | 10.8417 | 52.5 | 259.9884 | 3000 | 19.3726 | 3019.3726 | 3019.3726 | 0 | 199.2182
0 | 30.995 | 0 | 0 | 0 | 0 | 21.505 | 52.5 | 281.4933 | 3000 | 38.4265 | 3038.4265 | 3038.4265 | 0 | 197.5281
0 | 29.7065 | 0 | 0 | 0 | 0 | 22.7935 | 52.5 | 304.2869 | 3000 | 40.729 | 3040.729 | 3040.729 | 0 | 203.7593
0 | 23.928 | 0 | 0 | 0 | 0 | 28.572 | 52.5 | 332.8589 | 3000 | 51.0543 | 3051.0543 | 3051.0543 | 0 | 178.7918
0 | 24.9093 | 0 | 0 | 0 | 0 | 27.5907 | 52.5 | 360.4495 | 3000 | 49.3008 | 3049.3008 | 3049.3008 | 0 | 186.9221
0 | 26.9518 | 0 | 0 | 0 | 0 | 25.5482 | 52.5 | 385.9977 | 3000 | 45.6513 | 3045.6513 | 3045.6513 | 0 | 186.3329
0 | 29.4341 | 0 | 0 | 0 | 0 | 23.0659 | 52.5 | 409.0636 | 3000 | 41.2157 | 3041.2157 | 3041.2157 | 0 | 184.1456
0 | 35.1751 | 0 | 0 | 0 | 0 | 17.3249 | 52.5 | 426.3885 | 3000 | 30.9573 | 3030.9573 | 3030.9573 | 0 | 180.6451
0 | 28.5457 | 0 | 0 | 0 | 0 | 23.9543 | 52.5 | 450.3428 | 3000 | 42.8032 | 3042.8032 | 3042.8032 | 0 | 181.3511
0 | 24.1631 | 0 | 0 | 0 | 0 | 28.3369 | 52.5 | 478.6798 | 3000 | 50.6343 | 3050.6343 | 3050.6343 | 0 | 167.7849
0 | 24.3309 | 0 | 0 | 0 | 0 | 28.1691 | 52.5 | 506.8489 | 3000 | 50.3345 | 3050.3345 | 3050.3345 | 0 | 159.2275
0 | 232.5897 | 0 | 0 | 0 | 0 | -180.0897 | 52.5 | 326.7592 | 3000 | 0 | 3000 | 3000 | 0 | 156.3
0 | 27.8458 | 0 | 0 | 0 | 0 | 24.6542 | 52.5 | 351.4134 | 3000 | 44.0537 | 3044.0537 | 3044.0537 | 0 | 197.8635
0 | 43.8683 | 0 | 0 | 0 | 0 | 8.6317 | 52.5 | 360.045 | 3000 | 15.4236 | 3015.4236 | 3010.0162 | 0 | 181.2331
0 | 37.3215 | 0 | 0 | 0 | 0 | 15.1785 | 52.5 | 375.2235 | 3000 | 27.1219 | 3027.1219 | 3005.4922 | 0 | 180.3295
0 | 31.0052 | 0 | 0 | 0 | 0 | 21.4948 | 52.5 | 396.7183 | 3000 | 38.4083 | 3038.4083 | 2951.8895 | 0 | 188.4781
0 | 40.8518 | 0 | 0 | 0 | 0 | 11.6482 | 52.5 | 408.3665 | 3000 | 20.8138 | 3020.8138 | 2847.7762 | 0 | 183.0835
0 | 50.4274 | 0 | 0 | 0 | 0 | 2.0726 | 52.5 | 410.4392 | 3000 | 3.7035 | 3003.7035 | 2922.5922 | 0 | 189.9685
0 | 49.6145 | 0 | 0 | 0 | 0 | 2.8855 | 52.5 | 413.3246 | 3000 | 5.156 | 3005.156 | 2907.8223 | 0 | 203.2568
0 | 45.5072 | 0 | 0 | 0 | 0 | 6.9928 | 52.5 | 420.3174 | 3000 | 12.4951 | 3012.4951 | 2877.3095 | 0 | 171.4876
0 | 246.1374 | 0 | 0 | 0 | 0 | -193.6374 | 52.5 | 226.68 | 3000 | 0 | 3000 | 2956.7406 | 0 | 178.5871
0 | 34.0574 | 0 | 0 | 0 | 0 | 18.4426 | 52.5 | 245.1227 | 3000 | 32.9546 | 3032.9546 | 3011.3249 | 0 | 179.475
0 | 38.4819 | 0 | 0 | 0 | 0 | 14.0181 | 52.5 | 259.1408 | 3000 | 25.0485 | 3025.0485 | 3019.641 | 0 | 186.2213
0 | 46.4548 | 0 | 0 | 0 | 0 | 6.0452 | 52.5 | 265.186 | 3000 | 10.802 | 3010.802 | 3010.802 | 0 | 198.8635
0 | 53.5073 | 0 | 0 | 0 | 0 | -1.0073 | 52.5 | 264.1786 | 3000 | 0 | 3000 | 3000 | 0 | 199.11
0 | 32.3672 | 0 | 0 | 0 | 0 | 20.1328 | 52.5 | 284.3114 | 3000 | 35.9746 | 3035.9746 | 3035.9746 | 0 | 200.7386
0 | 25.0118 | 0 | 0 | 0 | 0 | 27.4882 | 52.5 | 311.7996 | 3000 | 49.1177 | 3049.1177 | 3049.1177 | 0 | 197.3694
0 | 28.3948 | 0 | 0 | 0 | 0 | 24.1052 | 52.5 | 335.9048 | 3000 | 43.0728 | 3043.0728 | 3043.0728 | 0 | 184.8362
0 | 28.7864 | 0 | 0 | 0 | 0 | 23.7136 | 52.5 | 359.6184 | 3000 | 42.373 | 3042.373 | 3042.373 | 0 | 180.4127
0 | 33.1314 | 0 | 0 | 0 | 0 | 19.3686 | 52.5 | 378.987 | 3000 | 34.6091 | 3034.6091 | 3034.6091 | 0 | 180.8627
0 | 30.5124 | 0 | 0 | 0 | 0 | 21.9876 | 52.5 | 400.9746 | 3000 | 39.2889 | 3039.2889 | 3039.2889 | 0 | 175.0326
0 | 23.8835 | 0 | 0 | 0 | 0 | 28.6165 | 52.5 | 429.5911 | 3000 | 51.1339 | 3051.1339 | 3051.1339 | 0 | 172.084
0 | 26.5428 | 0 | 0 | 0 | 0 | 25.9572 | 52.5 | 455.5483 | 3000 | 46.3821 | 3046.3821 | 3046.3821 | 0 | 166.9417
0 | 28.4619 | 0 | 0 | 0 | 0 | 24.0381 | 52.5 | 479.5864 | 3000 | 42.9529 | 3042.9529 | 3042.9529 | 0 | 166.7538
0 | 28.7163 | 0 | 0 | 0 | 0 | 23.7837 | 52.5 | 503.3701 | 3000 | 42.4982 | 3042.4982 | 3042.4982 | 0 | 172.2054
0 | 34.3446 | 0 | 0 | 0 | 0 | 18.1554 | 52.5 | 521.5255 | 3000 | 32.4412 | 3032.4412 | 3032.4412 | 0 | 182.0374
0 | 27.7669 | 0 | 0 | 0 | 0 | -27.7669 | 0 | 493.7586 | 0 | 0 | 0 | 0 | 0 | 0
0 | 38.0501 | 0 | 0 | 0 | 0 | -38.0501 | 0 | 455.7085 | 0 | 0 | 0 | 0 | 21.6297 | 0
0 | 43.9983 | 0 | 0 | 0 | 0 | -43.9983 | 0 | 411.7102 | 0 | 0 | 0 | 0 | 167.6302 | 0
0 | 39.764 | 0 | 0 | 0 | 0 | -31.7205 | 8.0435 | 379.9897 | 459.6311 | 0 | 459.6311 | 0 | 0 | 0
0 | 39.4625 | 0 | 0 | 0 | 0 | -28.3908 | 11.0717 | 351.599 | 632.6688 | 0 | 632.6688 | 0 | 0 | 0
0 | 39.1737 | 0 | 0 | 0 | 0 | -29.5214 | 9.6523 | 322.0775 | 551.5574 | 0 | 551.5574 | 0 | 0 | 0
0 | 243.3209 | 0 | 0 | 0 | 0 | -190.8209 | 52.5 | 131.2566 | 3000 | 0 | 3000 | 2616.0728 | 0 | 169.7831
0 | 45.9509 | 0 | 0 | 0 | 0 | 6.5491 | 52.5 | 137.8057 | 3000 | 11.7024 | 3011.7024 | 2346.5891 | 0 | 133.0516
0 | 43.7861 | 0 | 0 | 0 | 0 | 8.7139 | 52.5 | 146.5196 | 3000 | 15.5706 | 3015.5706 | 2707.3473 | 0 | 175.4632
0 | 45.9544 | 0 | 0 | 0 | 0 | 6.5456 | 52.5 | 153.0652 | 3000 | 11.6961 | 3011.6961 | 2822.4362 | 0 | 174.991
0 | 27.7805 | 0 | 0 | 0 | 0 | -27.7805 | 0 | 125.2847 | 0 | 0 | 0 | 0 | 16.2223 | 0
0 | 51.6142 | 0 | 0 | 0 | 0 | -51.6142 | 0 | 73.6705 | 0 | 0 | 0 | 0 | 0 | 0
0 | 45.2656 | 0 | 0 | 0 | 0 | -45.2656 | 0 | 28.405 | 0 | 0 | 0 | 0 | 0 | 0
0 | 28.405 | 0 | 0 | 0 | 0 | -28.405 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 33.9295 | 0 | 0 | 0 | 0 | 18.5705 | 52.5 | 18.5705 | 3000 | 33.183 | 3033.183 | 3033.183 | 0 | 181.991
0 | 29.3875 | 0 | 0 | 0 | 0 | 23.1125 | 52.5 | 41.683 | 3000 | 41.2989 | 3041.2989 | 3041.2989 | 0 | 166.6632
0 | 23.8371 | 0 | 0 | 0 | 0 | 28.6629 | 52.5 | 70.3459 | 3000 | 51.2169 | 3051.2169 | 3051.2169 | 0 | 168.7323
0 | 24.6604 | 0 | 0 | 0 | 0 | 27.8396 | 52.5 | 98.1855 | 3000 | 49.7456 | 3049.7456 | 3049.7456 | 0 | 158.5868
0 | 28.5887 | 0 | 0 | 0 | 0 | 23.9113 | 52.5 | 122.0969 | 3000 | 42.7264 | 3042.7264 | 3042.7264 | 0 | 159.1954
0 | 28.3262 | 0 | 0 | 0 | 0 | 24.1738 | 52.5 | 146.2707 | 3000 | 43.1955 | 3043.1955 | 3043.1955 | 0 | 159.4634
0 | 27.6011 | 0 | 0 | 0 | 0 | 24.8989 | 52.5 | 171.1696 | 3000 | 44.4911 | 3044.4911 | 3044.4911 | 0 | 159.2269
0 | 24.82 | 0 | 0 | 0 | 0 | 27.68 | 52.5 | 198.8496 | 3000 | 49.4604 | 3049.4604 | 3049.4604 | 0 | 167.7813
0 | 28.984 | 0 | 0 | 0 | 0 | 23.516 | 52.5 | 222.3656 | 3000 | 42.0199 | 3042.0199 | 3042.0199 | 0 | 187.0842
0 | 32.7683 | 0 | 0 | 0 | 0 | -32.7683 | 0 | 189.5973 | 0 | 0 | 0 | 0 | 32.4446 | 0
0 | 32.9742 | 0 | 0 | 0 | 0 | -32.9742 | 0 | 156.6231 | 0 | 0 | 0 | 0 | 140.5931 | 0
0 | 156.6231 | 0 | 0 | 0 | 0 | -156.6231 | 0 | 0 | 0 | 0 | 0 | 0 | 248.7416 | 0
0 | 6.3402 | 0 | 0 | 0 | 0 | 0 | 6.3402 | 0 | 362.2975 | 0 | 362.2975 | 0 | 0 | 0
0 | 8.9898 | 0 | 0 | 0 | 0 | 0 | 8.9898 | 0 | 513.7054 | 0 | 513.7054 | 0 | 0 | 0
0 | 41.9084 | 0 | 0 | 0 | 0 | 10.5916 | 52.5 | 10.5916 | 3000 | 18.9257 | 3018.9257 | 2483.5907 | 0 | 170.9207
0 | 34.4938 | 0 | 0 | 0 | 0 | 18.0062 | 52.5 | 28.5978 | 3000 | 32.1746 | 3032.1746 | 2545.5064 | 0 | 165.407
0 | 35.4983 | 0 | 0 | 0 | 0 | 17.0017 | 52.5 | 45.5995 | 3000 | 30.3798 | 3030.3798 | 2743.7862 | 0 | 178.2912
0 | 42.7753 | 0 | 0 | 0 | 0 | 9.7247 | 52.5 | 55.3241 | 3000 | 17.3767 | 3017.3767 | 2898.4134 | 0 | 188.8896
0 | 42.8639 | 0 | 0 | 0 | 0 | 9.6361 | 52.5 | 64.9603 | 3000 | 17.2185 | 3017.2185 | 2990.1814 | 0 | 202.8539
0 | 41.2231 | 0 | 0 | 0 | 0 | -41.2231 | 0 | 23.7372 | 0 | 0 | 0 | 0 | 0 | 0
0 | 23.7372 | 0 | 0 | 0 | 0 | -23.7372 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 23.4302 | 0 | 0 | 0 | 0 | 29.0698 | 52.5 | 29.0698 | 3000 | 51.9438 | 3051.9438 | 3051.9438 | 0 | 202.2523
0 | 26.2641 | 0 | 0 | 0 | 0 | 26.2359 | 52.5 | 55.3056 | 3000 | 46.88 | 3046.88 | 3046.88 | 0 | 185.7378
0 | 32.2023 | 0 | 0 | 0 | 0 | 20.2977 | 52.5 | 75.6033 | 3000 | 36.2692 | 3036.2692 | 3036.2692 | 0 | 171.8528
0 | 25.4473 | 0 | 0 | 0 | 0 | 27.0527 | 52.5 | 102.656 | 3000 | 48.3397 | 3048.3397 | 3048.3397 | 0 | 182.5955
0 | 26.6711 | 0 | 0 | 0 | 0 | 25.8289 | 52.5 | 128.485 | 3000 | 46.1529 | 3046.1529 | 3046.1529 | 0 | 168.1476
0 | 29.407 | 0 | 0 | 0 | 0 | 23.093 | 52.5 | 151.578 | 3000 | 41.2641 | 3041.2641 | 3041.2641 | 0 | 166.9654
0 | 27.5506 | 0 | 0 | 0 | 0 | 24.9494 | 52.5 | 176.5274 | 3000 | 44.5813 | 3044.5813 | 3044.5813 | 0 | 160.145
0 | 17.0821 | 0 | 0 | 0 | 0 | 35.4179 | 52.5 | 211.9453 | 3000 | 63.2871 | 3063.2871 | 3063.2871 | 0 | 157.1466
0 | 34.6764 | 0 | 0 | 0 | 0 | 17.8236 | 52.5 | 229.7689 | 3000 | 31.8484 | 3031.8484 | 3031.8484 | 0 | 154.6243
0 | 231.695 | 0 | 0 | 0 | 0 | -179.195 | 52.5 | 50.5739 | 3000 | 0 | 3000 | 3000 | 0 | 157.74
0 | 103.0739 | 0 | 0 | 0 | 0 | -50.5739 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 156.54
0 | 33.7219 | 0 | 0 | 0 | 0 | 18.7781 | 52.5 | 18.7781 | 3000 | 33.5539 | 3033.5539 | 3033.5539 | 0 | 183.894
0 | 49.4646 | 0 | 0 | 0 | 0 | 3.0354 | 52.5 | 21.8135 | 3000 | 5.4239 | 3005.4239 | 2983.7942 | 0 | 202.5996
0 | 21.8135 | 0 | 0 | 0 | 0 | -21.8135 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5188 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 135.1856 | 0
0 | 44.9306 | 0 | 0 | 0 | 0 | 7.5694 | 52.5 | 7.5694 | 3000 | 13.5256 | 3013.5256 | 2905.3771 | 0 | 188.8495
0 | 36.5325 | 0 | 0 | 0 | 0 | 15.9675 | 52.5 | 23.537 | 3000 | 28.5319 | 3028.5319 | 2909.5685 | 0 | 185.1358
0 | 37.8937 | 0 | 0 | 0 | 0 | 14.6063 | 52.5 | 38.1433 | 3000 | 26.0995 | 3026.0995 | 2880.099 | 0 | 182.8575
0 | 48.6118 | 0 | 0 | 0 | 0 | 3.8882 | 52.5 | 42.0315 | 3000 | 6.9478 | 3006.9478 | 2898.7993 | 0 | 181.4648
0 | 52.9352 | 0 | 0 | 0 | 0 | -0.43524 | 52.5 | 41.5963 | 3000 | 0 | 3000 | 2897.2589 | 0 | 177.602
0 | 41.5837 | 0 | 0 | 0 | 0 | 10.9163 | 52.5 | 52.5126 | 3000 | 19.5059 | 3019.5059 | 2916.7649 | 0 | 180.3144
0 | 56.8597 | 0 | 0 | 0 | 0 | -4.3597 | 52.5 | 48.1529 | 3000 | 0 | 3000 | 2972.9629 | 0 | 192.3804
0 | 39.355 | 0 | 0 | 0 | 0 | 13.145 | 52.5 | 61.2979 | 3000 | 23.4883 | 3023.4883 | 3023.4883 | 0 | 208.4393
0 | 49.5728 | 0 | 0 | 0 | 0 | -49.5728 | 0 | 11.7251 | 0 | 0 | 0 | 0 | 0 | 0
0 | 30.7738 | 0 | 0 | 0 | 0 | 21.7262 | 52.5 | 33.4513 | 3000 | 38.8219 | 3038.8219 | 3038.8219 | 0 | 210.7119
0 | 28.5097 | 0 | 0 | 0 | 0 | 23.9903 | 52.5 | 57.4416 | 3000 | 42.8675 | 3042.8675 | 3042.8675 | 0 | 198.182
0 | 27.2214 | 0 | 0 | 0 | 0 | 25.2786 | 52.5 | 82.7203 | 3000 | 45.1696 | 3045.1696 | 3045.1696 | 0 | 188.0697
0 | 25.1594 | 0 | 0 | 0 | 0 | 27.3406 | 52.5 | 110.0609 | 3000 | 48.854 | 3048.854 | 3048.854 | 0 | 181.4068
0 | 30.7699 | 0 | 0 | 0 | 0 | 21.7301 | 52.5 | 131.7909 | 3000 | 38.8287 | 3038.8287 | 3038.8287 | 0 | 175.7962
0 | 21.3458 | 0 | 0 | 0 | 0 | 31.1542 | 52.5 | 162.9451 | 3000 | 55.6684 | 3055.6684 | 3055.6684 | 0 | 163.7838
0 | 215.4451 | 0 | 0 | 0 | 0 | -162.9451 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 162.45
0 | 24.7531 | 0 | 0 | 0 | 0 | 27.7469 | 52.5 | 27.7469 | 3000 | 49.58 | 3049.58 | 3049.58 | 0 | 163.4575
0 | 22.8626 | 0 | 0 | 0 | 0 | 29.6374 | 52.5 | 57.3842 | 3000 | 52.958 | 3052.958 | 3052.958 | 0 | 164.8597
0 | 34.7696 | 0 | 0 | 0 | 0 | 17.7304 | 52.5 | 75.1147 | 3000 | 31.6819 | 3031.6819 | 3031.6819 | 0 | 162.104
0 | 20.9508 | 0 | 0 | 0 | 0 | 31.5492 | 52.5 | 106.6638 | 3000 | 56.3741 | 3056.3741 | 3056.3741 | 0 | 177.392
0 | 31.1328 | 0 | 0 | 0 | 0 | 21.3672 | 52.5 | 128.031 | 3000 | 38.1804 | 3038.1804 | 3038.1804 | 0 | 191.1015
0 | 45.0834 | 0 | 0 | 0 | 0 | -45.0834 | 0 | 82.9477 | 0 | 0 | 0 | 0 | 64.8891 | 0
0 | 43.5904 | 0 | 0 | 0 | 0 | -43.5904 | 0 | 39.3573 | 0 | 0 | 0 | 0 | 264.9638 | 0
0 | 43.8907 | 0 | 0 | 0 | 0 | -35.2794 | 8.6113 | 4.0779 | 492.0757 | 0 | 492.0757 | 0 | 0 | 0
0 | 15.9066 | 0 | 0 | 0 | 0 | -4.0779 | 11.8287 | 0 | 675.9282 | 0 | 675.9282 | 0 | 0 | 0
0 | 47.3425 | 0 | 0 | 0 | 0 | 5.1575 | 52.5 | 5.1575 | 3000 | 9.2157 | 3009.2157 | 2241.3613 | 0 | 136.992
0 | 45.5004 | 0 | 0 | 0 | 0 | 6.9996 | 52.5 | 12.1571 | 3000 | 12.5073 | 3012.5073 | 2255.4678 | 0 | 133.0726
0 | 37.169 | 0 | 0 | 0 | 0 | 15.331 | 52.5 | 27.488 | 3000 | 27.3944 | 3027.3944 | 2373.0959 | 0 | 141.5552
0 | 45.7035 | 0 | 0 | 0 | 0 | 6.7965 | 52.5 | 34.2845 | 3000 | 12.1444 | 3012.1444 | 2557.9207 | 0 | 152.5032
0 | 54.903 | 0 | 0 | 0 | 0 | -2.403 | 52.5 | 31.8815 | 3000 | 0 | 3000 | 2751.2584 | 0 | 170.9082
0 | 41.5162 | 0 | 0 | 0 | 0 | 10.9838 | 52.5 | 42.8652 | 3000 | 19.6265 | 3019.6265 | 2997.9968 | 0 | 202.035
0 | 38.3835 | 0 | 0 | 0 | 0 | -38.3835 | 0 | 4.4817 | 0 | 0 | 0 | 0 | 0 | 0
0 | 4.4817 | 0 | 0 | 0 | 0 | -4.4817 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 26.8361 | 0 | 0 | 0 | 0 | 25.6639 | 52.5 | 25.6639 | 3000 | 45.858 | 3045.858 | 3045.858 | 0 | 213.1187
0 | 26.6508 | 0 | 0 | 0 | 0 | 25.8492 | 52.5 | 51.5131 | 3000 | 46.1891 | 3046.1891 | 3046.1891 | 0 | 197.058
0 | 29.3156 | 0 | 0 | 0 | 0 | 23.1844 | 52.5 | 74.6975 | 3000 | 41.4274 | 3041.4274 | 3041.4274 | 0 | 189.7547
0 | 24.7294 | 0 | 0 | 0 | 0 | 27.7706 | 52.5 | 102.4681 | 3000 | 49.6223 | 3049.6223 | 3049.6223 | 0 | 172.3342
0 | 154.9681 | 0 | 0 | 0 | 0 | -102.4681 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 171.9
0 | 32.6275 | 0 | 0 | 0 | 0 | 19.8725 | 52.5 | 19.8725 | 3000 | 35.5096 | 3035.5096 | 3035.5096 | 0 | 173.6008
0 | 29.7883 | 0 | 0 | 0 | 0 | 22.7117 | 52.5 | 42.5843 | 3000 | 40.5828 | 3040.5828 | 3040.5828 | 0 | 172.4619
0 | 24.6405 | 0 | 0 | 0 | 0 | 27.8595 | 52.5 | 70.4438 | 3000 | 49.7813 | 3049.7813 | 3049.7813 | 0 | 168.3174
0 | 28.1922 | 0 | 0 | 0 | 0 | 24.3078 | 52.5 | 94.7516 | 3000 | 43.4348 | 3043.4348 | 3043.4348 | 0 | 170.7367
0 | 22.7569 | 0 | 0 | 0 | 0 | 29.7431 | 52.5 | 124.4946 | 3000 | 53.1469 | 3053.1469 | 3053.1469 | 0 | 179.1281
0 | 36.4643 | 0 | 0 | 0 | 0 | 16.0357 | 52.5 | 140.5303 | 3000 | 28.6536 | 3028.6536 | 3028.6536 | 0 | 205.8879
0 | 40.4196 | 0 | 0 | 0 | 0 | -40.4196 | 0 | 100.1108 | 0 | 0 | 0 | 0 | 97.3337 | 0
0 | 37.2901 | 0 | 0 | 0 | 0 | -30.9499 | 6.3402 | 69.1609 | 362.2975 | 0 | 362.2975 | 0 | 0 | 0
0 | 43.8243 | 0 | 0 | 0 | 0 | -33.8881 | 9.9361 | 35.2728 | 567.7796 | 0 | 567.7796 | 0 | 0 | 0
0 | 47.7576 | 0 | 0 | 0 | 0 | 4.7424 | 52.5 | 40.0152 | 3000 | 8.4741 | 3008.4741 | 2273.0643 | 0 | 148.3174
0 | 54.3189 | 0 | 0 | 0 | 0 | -1.8189 | 52.5 | 38.1963 | 3000 | 0 | 3000 | 2178.0714 | 0 | 121.6235
0 | 38.784 | 0 | 0 | 0 | 0 | 13.716 | 52.5 | 51.9123 | 3000 | 24.5086 | 3024.5086 | 2224.2097 | 0 | 124.667
0 | 40.0597 | 0 | 0 | 0 | 0 | 12.4403 | 52.5 | 64.3526 | 3000 | 22.2291 | 3022.2291 | 2335.4861 | 0 | 130.7872
0 | 53.9211 | 0 | 0 | 0 | 0 | -1.4211 | 52.5 | 62.9314 | 3000 | 0 | 3000 | 2513.3317 | 0 | 144.5668
0 | 47.3188 | 0 | 0 | 0 | 0 | 5.1812 | 52.5 | 68.1127 | 3000 | 9.2582 | 3009.2582 | 2749.7017 | 0 | 163.3598
0 | 50.9669 | 0 | 0 | 0 | 0 | 1.5331 | 52.5 | 69.6457 | 3000 | 2.7394 | 3002.7394 | 2975.7023 | 0 | 188.0049
0 | 122.1457 | 0 | 0 | 0 | 0 | -69.6457 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 205.83
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 27.4702 | 0 | 0 | 0 | 0 | 25.0298 | 52.5 | 25.0298 | 3000 | 44.725 | 3044.725 | 3044.725 | 0 | 197.6027
0 | 26.8576 | 0 | 0 | 0 | 0 | 25.6424 | 52.5 | 50.6722 | 3000 | 45.8195 | 3045.8195 | 3045.8195 | 0 | 171.0228
0 | 22.0869 | 0 | 0 | 0 | 0 | 30.4131 | 52.5 | 81.0853 | 3000 | 54.3442 | 3054.3442 | 3054.3442 | 0 | 185.8874
0 | 133.5853 | 0 | 0 | 0 | 0 | -81.0853 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 170.79
0 | 36.4563 | 0 | 0 | 0 | 0 | 16.0437 | 52.5 | 16.0437 | 3000 | 28.6679 | 3028.6679 | 3028.6679 | 0 | 170.1203
0 | 25.5304 | 0 | 0 | 0 | 0 | 26.9696 | 52.5 | 43.0132 | 3000 | 48.191 | 3048.191 | 3048.191 | 0 | 167.0104
0 | 32.9379 | 0 | 0 | 0 | 0 | 19.5621 | 52.5 | 62.5754 | 3000 | 34.9549 | 3034.9549 | 3034.9549 | 0 | 154.7827
0 | 26.9056 | 0 | 0 | 0 | 0 | 25.5944 | 52.5 | 88.1698 | 3000 | 45.7339 | 3045.7339 | 3045.7339 | 0 | 156.2157
0 | 24.1278 | 0 | 0 | 0 | 0 | 28.3722 | 52.5 | 116.542 | 3000 | 50.6973 | 3050.6973 | 3050.6973 | 0 | 157.1719
0 | 31.6212 | 0 | 0 | 0 | 0 | 20.8788 | 52.5 | 137.4208 | 3000 | 37.3076 | 3037.3076 | 3037.3076 | 0 | 167.0519
0 | 32.2698 | 0 | 0 | 0 | 0 | 20.2302 | 52.5 | 157.651 | 3000 | 36.1487 | 3036.1487 | 3036.1487 | 0 | 176.4002
0 | 39.131 | 0 | 0 | 0 | 0 | 13.369 | 52.5 | 171.0199 | 3000 | 23.8886 | 3023.8886 | 2915.7401 | 0 | 174.9444
0 | 49.2088 | 0 | 0 | 0 | 0 | 3.2912 | 52.5 | 174.3111 | 3000 | 5.8809 | 3005.8809 | 2643.5834 | 0 | 172.7317
0 | 35.4681 | 0 | 0 | 0 | 0 | -26.0051 | 9.463 | 148.306 | 540.7425 | 0 | 540.7425 | 0 | 0 | 0
0 | 67.5506 | 0 | 0 | 0 | 0 | -54.2078 | 13.3428 | 94.0982 | 762.447 | 0 | 762.447 | 0 | 0 | 0
0 | 47.064 | 0 | 0 | 0 | 0 | 5.436 | 52.5 | 99.5342 | 3000 | 9.7135 | 3009.7135 | 2252.6739 | 0 | 121.1939
0 | 32.9211 | 0 | 0 | 0 | 0 | 19.5789 | 52.5 | 119.1131 | 3000 | 34.9848 | 3034.9848 | 2353.6492 | 0 | 119.1417
0 | 43.4233 | 0 | 0 | 0 | 0 | 9.0767 | 52.5 | 128.1898 | 3000 | 16.2189 | 3016.2189 | 2399.7724 | 0 | 122.3884
0 | 34.3999 | 0 | 0 | 0 | 0 | 18.1001 | 52.5 | 146.2899 | 3000 | 32.3425 | 3032.3425 | 2599.7484 | 0 | 135.7329
0 | 43.5748 | 0 | 0 | 0 | 0 | 8.9252 | 52.5 | 155.2151 | 3000 | 15.9482 | 3015.9482 | 2788.8363 | 0 | 152.2984
0 | 43.6336 | 0 | 0 | 0 | 0 | 8.8664 | 52.5 | 164.0815 | 3000 | 15.8431 | 3015.8431 | 2972.5837 | 0 | 169.7643
0 | 49.7645 | 0 | 0 | 0 | 0 | 2.7355 | 52.5 | 166.817 | 3000 | 4.888 | 3004.888 | 3004.888 | 0 | 185.7922
0 | 39.933 | 0 | 0 | 0 | 0 | 12.567 | 52.5 | 179.384 | 3000 | 22.4555 | 3022.4555 | 3022.4555 | 0 | 205.9199
0 | 179.384 | 0 | 0 | 0 | 0 | -179.384 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 27.0908 | 0 | 0 | 0 | 0 | 25.4092 | 52.5 | 25.4092 | 3000 | 45.4029 | 3045.4029 | 3045.4029 | 0 | 187.2009
0 | 32.1955 | 0 | 0 | 0 | 0 | 20.3045 | 52.5 | 45.7138 | 3000 | 36.2815 | 3036.2815 | 3036.2815 | 0 | 169.0298
0 | 22.8427 | 0 | 0 | 0 | 0 | 29.6573 | 52.5 | 75.3711 | 3000 | 52.9936 | 3052.9936 | 3052.9936 | 0 | 175.0281
0 | 26.425 | 0 | 0 | 0 | 0 | 26.075 | 52.5 | 101.4461 | 3000 | 46.5926 | 3046.5926 | 3046.5926 | 0 | 169.6952
0 | 29.4357 | 0 | 0 | 0 | 0 | 23.0643 | 52.5 | 124.5104 | 3000 | 41.2128 | 3041.2128 | 3041.2128 | 0 | 164.2255
0 | 23.2053 | 0 | 0 | 0 | 0 | 29.2947 | 52.5 | 153.8051 | 3000 | 52.3457 | 3052.3457 | 3052.3457 | 0 | 167.7874
0 | 31.0175 | 0 | 0 | 0 | 0 | 21.4825 | 52.5 | 175.2876 | 3000 | 38.3864 | 3038.3864 | 3038.3864 | 0 | 158.7253
0 | 27.141 | 0 | 0 | 0 | 0 | 25.359 | 52.5 | 200.6465 | 3000 | 45.3131 | 3045.3131 | 3045.3131 | 0 | 156.1332
0 | 26.1936 | 0 | 0 | 0 | 0 | 26.3064 | 52.5 | 226.953 | 3000 | 47.0061 | 3047.0061 | 3047.0061 | 0 | 155.7934
0 | 28.4477 | 0 | 0 | 0 | 0 | 24.0523 | 52.5 | 251.0053 | 3000 | 42.9783 | 3042.9783 | 3042.9783 | 0 | 157.4437
0 | 21.9522 | 0 | 0 | 0 | 0 | 30.5478 | 52.5 | 281.5531 | 3000 | 54.5849 | 3054.5849 | 3054.5849 | 0 | 157.3722
0 | 44.1421 | 0 | 0 | 0 | 0 | 8.3579 | 52.5 | 289.911 | 3000 | 14.9345 | 3014.9345 | 2928.4157 | 0 | 157.6073
0 | 37.7402 | 0 | 0 | 0 | 0 | 14.7598 | 52.5 | 304.6708 | 3000 | 26.3739 | 3026.3739 | 2685.7061 | 0 | 147.7138
0 | 44.1891 | 0 | 0 | 0 | 0 | 8.3109 | 52.5 | 312.9817 | 3000 | 14.8505 | 3014.8505 | 2474.1079 | 0 | 133.3049
0 | 31.5079 | 0 | 0 | 0 | 0 | 20.9921 | 52.5 | 333.9738 | 3000 | 37.5101 | 3037.5101 | 2323.73 | 0 | 120.6248
0 | 57.305 | 0 | 0 | 0 | 0 | -4.805 | 52.5 | 329.1688 | 3000 | 0 | 3000 | 2199.7011 | 0 | 113.2846
0 | 38.8158 | 0 | 0 | 0 | 0 | 13.6842 | 52.5 | 342.8531 | 3000 | 24.4519 | 3024.4519 | 2310.6718 | 0 | 121.1023
0 | 47.2483 | 0 | 0 | 0 | 0 | 5.2517 | 52.5 | 348.1047 | 3000 | 9.384 | 3009.384 | 2365.9004 | 0 | 118.508
0 | 49.2801 | 0 | 0 | 0 | 0 | 3.2199 | 52.5 | 351.3246 | 3000 | 5.7535 | 3005.7535 | 2567.7521 | 0 | 128.6957
0 | 40.9252 | 0 | 0 | 0 | 0 | 11.5748 | 52.5 | 362.8994 | 3000 | 20.6827 | 3020.6827 | 2766.5337 | 0 | 141.8402
0 | 230.6516 | 0 | 0 | 0 | 0 | -178.1516 | 52.5 | 184.7478 | 3000 | 0 | 3000 | 2945.9257 | 0 | 160.1405
0 | 29.5804 | 0 | 0 | 0 | 0 | 22.9196 | 52.5 | 207.6675 | 3000 | 40.9543 | 3040.9543 | 3040.9543 | 0 | 179.5075
0 | 48.6306 | 0 | 0 | 0 | 0 | 3.8694 | 52.5 | 211.5368 | 3000 | 6.9141 | 3006.9141 | 3006.9141 | 0 | 194.2466
0 | 24.325 | 0 | 0 | 0 | 0 | 28.175 | 52.5 | 239.7118 | 3000 | 50.3449 | 3050.3449 | 3050.3449 | 0 | 198.4859
0 | 31.7448 | 0 | 0 | 0 | 0 | 20.7552 | 52.5 | 260.467 | 3000 | 37.0868 | 3037.0868 | 3037.0868 | 0 | 185.7179
0 | 30.443 | 0 | 0 | 0 | 0 | 22.057 | 52.5 | 282.524 | 3000 | 39.4129 | 3039.4129 | 3039.4129 | 0 | 167.1677
0 | 36.0715 | 0 | 0 | 0 | 0 | 16.4285 | 52.5 | 298.9525 | 3000 | 29.3555 | 3029.3555 | 3029.3555 | 0 | 175.1876
0 | 30.4415 | 0 | 0 | 0 | 0 | 22.0585 | 52.5 | 321.0109 | 3000 | 39.4155 | 3039.4155 | 3039.4155 | 0 | 163.3686
0 | 25.9321 | 0 | 0 | 0 | 0 | 26.5679 | 52.5 | 347.5788 | 3000 | 47.4733 | 3047.4733 | 3047.4733 | 0 | 165.813
0 | 36.6097 | 0 | 0 | 0 | 0 | 15.8903 | 52.5 | 363.4691 | 3000 | 28.3938 | 3028.3938 | 3028.3938 | 0 | 162.867
0 | 21.7514 | 0 | 0 | 0 | 0 | 30.7486 | 52.5 | 394.2177 | 3000 | 54.9437 | 3054.9437 | 3054.9437 | 0 | 164.2949
0 | 30.231 | 0 | 0 | 0 | 0 | 22.269 | 52.5 | 416.4867 | 3000 | 39.7918 | 3039.7918 | 3039.7918 | 0 | 161.7169
0 | 27.5763 | 0 | 0 | 0 | 0 | 24.9237 | 52.5 | 441.4105 | 3000 | 44.5354 | 3044.5354 | 3044.5354 | 0 | 163.796
0 | 34.6538 | 0 | 0 | 0 | 0 | 17.8462 | 52.5 | 459.2566 | 3000 | 31.8888 | 3031.8888 | 3031.8888 | 0 | 166.7539
0 | 32.5374 | 0 | 0 | 0 | 0 | 19.9626 | 52.5 | 479.2192 | 3000 | 35.6704 | 3035.6704 | 3030.263 | 0 | 202.1791
0 | 240.2765 | 0 | 0 | 0 | 0 | -240.2765 | 0 | 238.9427 | 0 | 0 | 0 | 0 | 108.1485 | 0
0 | 26.2217 | 0 | 0 | 0 | 0 | -20.1654 | 6.0563 | 218.7772 | 346.0752 | 0 | 346.0752 | 0 | 0 | 0
0 | 37.5956 | 0 | 0 | 0 | 0 | 14.9044 | 52.5 | 233.6817 | 3000 | 26.6323 | 3026.6323 | 2458.8526 | 0 | 166.243
0 | 51.9836 | 0 | 0 | 0 | 0 | 0.51636 | 52.5 | 234.198 | 3000 | 0.92266 | 3000.9227 | 2270.9203 | 0 | 144.0445
0 | 46.4926 | 0 | 0 | 0 | 0 | 6.0074 | 52.5 | 240.2055 | 3000 | 10.7345 | 3010.7345 | 2205.0281 | 0 | 132.2135
0 | 36.62 | 0 | 0 | 0 | 0 | 15.88 | 52.5 | 256.0854 | 3000 | 28.3754 | 3028.3754 | 2249.7061 | 0 | 131.0679
0 | 51.4722 | 0 | 0 | 0 | 0 | 1.0278 | 52.5 | 257.1132 | 3000 | 1.8366 | 3001.8366 | 2385.3901 | 0 | 138.5196
0 | 32.7394 | 0 | 0 | 0 | 0 | 19.7606 | 52.5 | 276.8739 | 3000 | 35.3096 | 3035.3096 | 2564.8636 | 0 | 153.1993
0 | 246.4878 | 0 | 0 | 0 | 0 | -193.9878 | 52.5 | 82.886 | 3000 | 0 | 3000 | 2778.2956 | 0 | 173.2267
0 | 35.7134 | 0 | 0 | 0 | 0 | 16.7866 | 52.5 | 99.6726 | 3000 | 29.9954 | 3029.9954 | 2981.3285 | 0 | 196.4696
0 | 34.4785 | 0 | 0 | 0 | 0 | 18.0215 | 52.5 | 117.6941 | 3000 | 32.2021 | 3032.2021 | 3032.2021 | 0 | 206.0078
0 | 36.8884 | 0 | 0 | 0 | 0 | -36.8884 | 0 | 80.8057 | 0 | 0 | 0 | 0 | 0 | 0
0 | 32.293 | 0 | 0 | 0 | 0 | -32.293 | 0 | 48.5127 | 0 | 0 | 0 | 0 | 0 | 0
0 | 32.4077 | 0 | 0 | 0 | 0 | 20.0923 | 52.5 | 68.6051 | 3000 | 35.9023 | 3035.9023 | 3035.9023 | 0 | 203.1322
0 | 28.7458 | 0 | 0 | 0 | 0 | 23.7542 | 52.5 | 92.3592 | 3000 | 42.4455 | 3042.4455 | 3042.4455 | 0 | 179.4434
0 | 34.4025 | 0 | 0 | 0 | 0 | 18.0975 | 52.5 | 110.4567 | 3000 | 32.3378 | 3032.3378 | 3032.3378 | 0 | 166.7786
0 | 25.8467 | 0 | 0 | 0 | 0 | 26.6533 | 52.5 | 137.11 | 3000 | 47.6259 | 3047.6259 | 3047.6259 | 0 | 163.048
0 | 27.3773 | 0 | 0 | 0 | 0 | 25.1227 | 52.5 | 162.2326 | 3000 | 44.8909 | 3044.8909 | 3044.8909 | 0 | 155.5939
0 | 32.2122 | 0 | 0 | 0 | 0 | 20.2878 | 52.5 | 182.5204 | 3000 | 36.2516 | 3036.2516 | 3036.2516 | 0 | 153.1182
0 | 23.1628 | 0 | 0 | 0 | 0 | 29.3372 | 52.5 | 211.8576 | 3000 | 52.4217 | 3052.4217 | 3052.4217 | 0 | 153.9031
0 | 19.3406 | 0 | 0 | 0 | 0 | 33.1594 | 52.5 | 245.017 | 3000 | 59.2515 | 3059.2515 | 3059.2515 | 0 | 156.0218
0 | 27.5506 | 0 | 0 | 0 | 0 | 24.9494 | 52.5 | 269.9664 | 3000 | 44.5813 | 3044.5813 | 3044.5813 | 0 | 155.5172
0 | 62.2706 | 0 | 0 | 0 | 0 | -9.7706 | 52.5 | 260.1959 | 3000 | 0 | 3000 | 3000 | 0 | 159.3
0 | 102.6407 | 0 | 0 | 0 | 0 | -50.1407 | 52.5 | 210.0552 | 3000 | 0 | 3000 | 3000 | 0 | 181.08
0 | 60.577 | 0 | 0 | 0 | 0 | -8.077 | 52.5 | 201.9782 | 3000 | 0 | 3000 | 2891.8515 | 0 | 184.2688
0 | 58.7983 | 0 | 0 | 0 | 0 | -6.2983 | 52.5 | 195.6799 | 3000 | 0 | 3000 | 2632.2951 | 0 | 163.6498
0 | 51.2601 | 0 | 0 | 0 | 0 | -43.0273 | 8.2328 | 152.6526 | 470.446 | 0 | 470.446 | 0 | 0 | 0
0 | 48.852 | 0 | 0 | 0 | 0 | -39.3891 | 9.463 | 113.2636 | 540.7425 | 0 | 540.7425 | 0 | 0 | 0
0 | 17.4057 | 0 | 0 | 0 | 0 | 35.0943 | 52.5 | 148.3579 | 3000 | 62.7089 | 3062.7089 | 2722.0411 | 0 | 155.2924
0 | 200.8579 | 0 | 0 | 0 | 0 | -148.3579 | 52.5 | 0 | 3000 | 0 | 3000 | 2605.258 | 0 | 139.6418
0 | 31.2054 | 0 | 0 | 0 | 0 | 21.2946 | 52.5 | 21.2946 | 3000 | 38.0506 | 3038.0506 | 2773.0867 | 0 | 148.6374
0 | 49.9978 | 0 | 0 | 0 | 0 | 2.5022 | 52.5 | 23.7968 | 3000 | 4.4712 | 3004.4712 | 2761.137 | 0 | 147.9969
0 | 52.2237 | 0 | 0 | 0 | 0 | 0.27626 | 52.5 | 24.0731 | 3000 | 0.49363 | 3000.4936 | 2827.456 | 0 | 162.296
0 | 39.6635 | 0 | 0 | 0 | 0 | 12.8365 | 52.5 | 36.9095 | 3000 | 22.9371 | 3022.9371 | 3001.3074 | 0 | 176.777
0 | 34.3569 | 0 | 0 | 0 | 0 | 18.1431 | 52.5 | 55.0527 | 3000 | 32.4193 | 3032.4193 | 3032.4193 | 0 | 199.8971
0 | 44.8131 | 0 | 0 | 0 | 0 | 7.6869 | 52.5 | 62.7395 | 3000 | 13.7354 | 3013.7354 | 3013.7354 | 0 | 208.219
0 | 27.5067 | 0 | 0 | 0 | 0 | 24.9933 | 52.5 | 87.7328 | 3000 | 44.6596 | 3044.6596 | 3044.6596 | 0 | 205.271
0 | 22.2128 | 0 | 0 | 0 | 0 | 30.2872 | 52.5 | 118.02 | 3000 | 54.1192 | 3054.1192 | 3054.1192 | 0 | 182.9417
0 | 32.6506 | 0 | 0 | 0 | 0 | 19.8494 | 52.5 | 137.8694 | 3000 | 35.4682 | 3035.4682 | 3035.4682 | 0 | 171.8986
0 | 28.0464 | 0 | 0 | 0 | 0 | 24.4536 | 52.5 | 162.323 | 3000 | 43.6954 | 3043.6954 | 3043.6954 | 0 | 173.4298
0 | 28.0002 | 0 | 0 | 0 | 0 | 24.4998 | 52.5 | 186.8227 | 3000 | 43.7778 | 3043.7778 | 3043.7778 | 0 | 154.2891
0 | 31.9262 | 0 | 0 | 0 | 0 | 20.5738 | 52.5 | 207.3965 | 3000 | 36.7626 | 3036.7626 | 3036.7626 | 0 | 154.8749
0 | 27.9796 | 0 | 0 | 0 | 0 | 24.5204 | 52.5 | 231.917 | 3000 | 43.8148 | 3043.8148 | 3043.8148 | 0 | 153.4083
0 | 36.7374 | 0 | 0 | 0 | 0 | 15.7626 | 52.5 | 247.6796 | 3000 | 28.1657 | 3028.1657 | 3028.1657 | 0 | 145.2005
0 | 32.8994 | 0 | 0 | 0 | 0 | 19.6006 | 52.5 | 267.2802 | 3000 | 35.0237 | 3035.0237 | 3035.0237 | 0 | 153.2687
0 | 224.9573 | 0 | 0 | 0 | 0 | -172.4573 | 52.5 | 94.823 | 3000 | 0 | 3000 | 3000 | 0 | 153.18
0 | 61.9691 | 0 | 0 | 0 | 0 | -9.4691 | 52.5 | 85.3538 | 3000 | 0 | 3000 | 3000 | 0 | 159.18
0 | 107.3517 | 0 | 0 | 0 | 0 | -54.8517 | 52.5 | 30.5021 | 3000 | 0 | 3000 | 2994.5926 | 0 | 191.8037
0 | 83.0021 | 0 | 0 | 0 | 0 | -30.5021 | 52.5 | 0 | 3000 | 0 | 3000 | 2913.4812 | 0 | 202.6035
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2729.6287 | 0 | 189.9276
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2572.8134 | 0 | 175.1571
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2459.2575 | 0 | 164.9916
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2334.8867 | 0 | 149.4561
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2448.4426 | 0 | 142.6463
0 | 48.978 | 0 | 0 | 0 | 0 | 3.522 | 52.5 | 3.522 | 3000 | 6.2933 | 3006.2933 | 2519.6251 | 0 | 151.3035
0 | 49.7731 | 0 | 0 | 0 | 0 | 2.7269 | 52.5 | 6.2489 | 3000 | 4.8726 | 3004.8726 | 2685.8345 | 0 | 162.7079
0 | 36.5299 | 0 | 0 | 0 | 0 | 15.9701 | 52.5 | 22.219 | 3000 | 28.5364 | 3028.5364 | 2887.9433 | 0 | 176.1934
0 | 53.0981 | 0 | 0 | 0 | 0 | -0.59807 | 52.5 | 21.6209 | 3000 | 0 | 3000 | 2956.7406 | 0 | 191.5672
0 | 45.0473 | 0 | 0 | 0 | 0 | 7.4527 | 52.5 | 29.0736 | 3000 | 13.317 | 3013.317 | 3013.317 | 0 | 201.7717
0 | 58.6069 | 0 | 0 | 0 | 0 | -6.1069 | 52.5 | 22.9667 | 3000 | 0 | 3000 | 3000 | 0 | 207.75
0 | 68.4782 | 0 | 0 | 0 | 0 | -15.9782 | 52.5 | 6.9884 | 3000 | 0 | 3000 | 3000 | 0 | 207.15
0 | 59.4884 | 0 | 0 | 0 | 0 | -6.9884 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 194.91
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 166.77
0 | 41.7079 | 0 | 0 | 0 | 0 | 10.7921 | 52.5 | 10.7921 | 3000 | 19.284 | 3019.284 | 3019.284 | 0 | 163.2527
0 | 63.2921 | 0 | 0 | 0 | 0 | -10.7921 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 151.8
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 156.39
0 | 27.8851 | 0 | 0 | 0 | 0 | 24.6149 | 52.5 | 24.6149 | 3000 | 43.9835 | 3043.9835 | 3043.9835 | 0 | 155.2432
0 | 23.0899 | 0 | 0 | 0 | 0 | 29.4101 | 52.5 | 54.025 | 3000 | 52.552 | 3052.552 | 3052.552 | 0 | 154.1233
0 | 31.7035 | 0 | 0 | 0 | 0 | 20.7965 | 52.5 | 74.8215 | 3000 | 37.1607 | 3037.1607 | 3037.1607 | 0 | 152.9514
0 | 25.3711 | 0 | 0 | 0 | 0 | 27.1289 | 52.5 | 101.9504 | 3000 | 48.4758 | 3048.4758 | 3048.4758 | 0 | 155.7161
0 | 35.1376 | 0 | 0 | 0 | 0 | 17.3624 | 52.5 | 119.3129 | 3000 | 31.0243 | 3031.0243 | 3031.0243 | 0 | 160.3412
0 | 41.8434 | 0 | 0 | 0 | 0 | 10.6566 | 52.5 | 129.9694 | 3000 | 19.0418 | 3019.0418 | 3013.6344 | 0 | 165.4485
0 | 101.2642 | 0 | 0 | 0 | 0 | -48.7642 | 52.5 | 81.2052 | 3000 | 0 | 3000 | 2924.296 | 0 | 169.6092
0 | 119.0344 | 0 | 0 | 0 | 0 | -66.5344 | 52.5 | 14.6708 | 3000 | 0 | 3000 | 2843.1847 | 0 | 186.2286
0 | 14.6708 | 0 | 0 | 0 | 0 | -14.6708 | 0 | 0 | 0 | 0 | 0 | 0 | 156.8153 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2680.9619 | 0 | 147.1848
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2551.1837 | 0 | 135.723
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2740.4436 | 0 | 141.6809
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2810.7401 | 0 | 147.4233
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2913.4812 | 0 | 157.9981
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2962.148 | 0 | 171.6269
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2983.7777 | 0 | 182.9056
0 | 45.916 | 0 | 0 | 0 | 0 | 6.584 | 52.5 | 6.584 | 3000 | 11.7648 | 3011.7648 | 3011.7648 | 0 | 197.6019
0 | 41.7146 | 0 | 0 | 0 | 0 | 10.7854 | 52.5 | 17.3694 | 3000 | 19.272 | 3019.272 | 3019.272 | 0 | 205.6124
0 | 31.1198 | 0 | 0 | 0 | 0 | 21.3802 | 52.5 | 38.7496 | 3000 | 38.2036 | 3038.2036 | 3038.2036 | 0 | 206.5371
0 | 33.4178 | 0 | 0 | 0 | 0 | 19.0822 | 52.5 | 57.8318 | 3000 | 34.0974 | 3034.0974 | 3034.0974 | 0 | 201.4337
0 | 29.2893 | 0 | 0 | 0 | 0 | 23.2107 | 52.5 | 81.0425 | 3000 | 41.4744 | 3041.4744 | 3041.4744 | 0 | 185.9253
0 | 25.94 | 0 | 0 | 0 | 0 | 26.56 | 52.5 | 107.6025 | 3000 | 47.4591 | 3047.4591 | 3047.4591 | 0 | 183.0913
0 | 26.4008 | 0 | 0 | 0 | 0 | 26.0992 | 52.5 | 133.7016 | 3000 | 46.6357 | 3046.6357 | 3046.6357 | 0 | 175.7604
0 | 25.5502 | 0 | 0 | 0 | 0 | 26.9498 | 52.5 | 160.6514 | 3000 | 48.1557 | 3048.1557 | 3048.1557 | 0 | 172.4646
0 | 25.5442 | 0 | 0 | 0 | 0 | 26.9558 | 52.5 | 187.6072 | 3000 | 48.1665 | 3048.1665 | 3048.1665 | 0 | 168.6246
0 | 31.083 | 0 | 0 | 0 | 0 | 21.417 | 52.5 | 209.0243 | 3000 | 38.2694 | 3038.2694 | 3038.2694 | 0 | 166.6187
0 | 31.1269 | 0 | 0 | 0 | 0 | 21.3731 | 52.5 | 230.3974 | 3000 | 38.1909 | 3038.1909 | 3038.1909 | 0 | 165.8548
0 | 24.4974 | 0 | 0 | 0 | 0 | 28.0026 | 52.5 | 258.4 | 3000 | 50.037 | 3050.037 | 3050.037 | 0 | 165.7695
0 | 22.6206 | 0 | 0 | 0 | 0 | 29.8794 | 52.5 | 288.2794 | 3000 | 53.3905 | 3053.3905 | 3053.3905 | 0 | 174.0433
0 | 33.8785 | 0 | 0 | 0 | 0 | 18.6215 | 52.5 | 306.901 | 3000 | 33.2742 | 3033.2742 | 3027.8668 | 0 | 197.75
0 | 41.3453 | 0 | 0 | 0 | 0 | 11.1547 | 52.5 | 318.0557 | 3000 | 19.932 | 3019.932 | 2992.8949 | 0 | 209.2931
0 | 66.6415 | 0 | 0 | 0 | 0 | -66.6415 | 0 | 251.4142 | 0 | 0 | 0 | 0 | 97.3337 | 0
0 | 251.4142 | 0 | 0 | 0 | 0 | -251.4142 | 0 | 0 | 0 | 0 | 0 | 0 | 275.7787 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2626.8877 | 0 | 181.623
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2583.6283 | 0 | 175.8417
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2594.4431 | 0 | 172.4007
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2518.7392 | 0 | 161.1741
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2664.7396 | 0 | 162.2293
0 | 46.5037 | 0 | 0 | 0 | 0 | 5.9963 | 52.5 | 5.9963 | 3000 | 10.7146 | 3010.7146 | 2870.1215 | 0 | 173.2979
0 | 45.5327 | 0 | 0 | 0 | 0 | 6.9673 | 52.5 | 12.9635 | 3000 | 12.4496 | 3012.4496 | 2985.4124 | 0 | 191.753
0 | 43.2745 | 0 | 0 | 0 | 0 | 9.2255 | 52.5 | 22.189 | 3000 | 16.4847 | 3016.4847 | 3016.4847 | 0 | 203.0999
0 | 41.3517 | 0 | 0 | 0 | 0 | 11.1483 | 52.5 | 33.3373 | 3000 | 19.9205 | 3019.9205 | 3019.9205 | 0 | 206.8042
0 | 15.3494 | 0 | 0 | 0 | 0 | 37.1506 | 52.5 | 70.4879 | 3000 | 66.3832 | 3066.3832 | 3066.3832 | 0 | 198.027
0 | 34.1867 | 0 | 0 | 0 | 0 | 18.3133 | 52.5 | 88.8012 | 3000 | 32.7234 | 3032.7234 | 3032.7234 | 0 | 179.8405
0 | 25.8198 | 0 | 0 | 0 | 0 | 26.6802 | 52.5 | 115.4814 | 3000 | 47.6739 | 3047.6739 | 3047.6739 | 0 | 176.826
0 | 34.4782 | 0 | 0 | 0 | 0 | 18.0218 | 52.5 | 133.5032 | 3000 | 32.2026 | 3032.2026 | 3032.2026 | 0 | 177.111
0 | 21.5272 | 0 | 0 | 0 | 0 | 30.9728 | 52.5 | 164.476 | 3000 | 55.3443 | 3055.3443 | 3055.3443 | 0 | 166.8218
0 | 29.3284 | 0 | 0 | 0 | 0 | 23.1716 | 52.5 | 187.6476 | 3000 | 41.4045 | 3041.4045 | 3041.4045 | 0 | 161.3161
0 | 28.63 | 0 | 0 | 0 | 0 | 23.87 | 52.5 | 211.5176 | 3000 | 42.6526 | 3042.6526 | 3042.6526 | 0 | 156.8183
0 | 226.2449 | 0 | 0 | 0 | 0 | -173.7449 | 52.5 | 37.7727 | 3000 | 0 | 3000 | 3000 | 0 | 153.18
0 | 34.7195 | 0 | 0 | 0 | 0 | 17.7805 | 52.5 | 55.5532 | 3000 | 31.7713 | 3031.7713 | 3031.7713 | 0 | 154.6507
0 | 22.126 | 0 | 0 | 0 | 0 | 30.374 | 52.5 | 85.9272 | 3000 | 54.2743 | 3054.2743 | 3054.2743 | 0 | 154.5768
0 | 29.3256 | 0 | 0 | 0 | 0 | 23.1744 | 52.5 | 109.1016 | 3000 | 41.4095 | 3041.4095 | 3041.4095 | 0 | 155.2031
0 | 34.9674 | 0 | 0 | 0 | 0 | 17.5326 | 52.5 | 126.6342 | 3000 | 31.3284 | 3031.3284 | 3025.921 | 0 | 158.2557
0 | 48.1763 | 0 | 0 | 0 | 0 | 4.3237 | 52.5 | 130.9578 | 3000 | 7.7258 | 3007.7258 | 2861.7253 | 0 | 160.5714
0 | 33.5846 | 0 | 0 | 0 | 0 | 18.9154 | 52.5 | 149.8732 | 3000 | 33.7992 | 3033.7992 | 2671.5017 | 0 | 156.4699
0 | 52.4977 | 0 | 0 | 0 | 0 | 0.0023102 | 52.5 | 149.8755 | 3000 | 0.0041281 | 3000.0041 | 2394.3725 | 0 | 158.4117
0 | 39.3677 | 0 | 0 | 0 | 0 | 13.1323 | 52.5 | 163.0078 | 3000 | 23.4657 | 3023.4657 | 2277.2411 | 0 | 127.3889
0 | 215.5078 | 0 | 0 | 0 | 0 | -163.0078 | 52.5 | 0 | 3000 | 0 | 3000 | 2145.6268 | 0 | 113.7611
0 | 30.4606 | 0 | 0 | 0 | 0 | 22.0394 | 52.5 | 22.0394 | 3000 | 39.3815 | 3039.3815 | 2179.6008 | 0 | 110.4186
0 | 48.0361 | 0 | 0 | 0 | 0 | 4.4639 | 52.5 | 26.5033 | 3000 | 7.9764 | 3007.9764 | 2294.1962 | 0 | 115.444
0 | 42.3136 | 0 | 0 | 0 | 0 | 10.1864 | 52.5 | 36.6896 | 3000 | 18.2017 | 3018.2017 | 2439.6072 | 0 | 123.4929
0 | 41.2712 | 0 | 0 | 0 | 0 | 11.2288 | 52.5 | 47.9184 | 3000 | 20.0643 | 3020.0643 | 2663.1743 | 0 | 134.4903
0 | 31.2217 | 0 | 0 | 0 | 0 | 21.2783 | 52.5 | 69.1967 | 3000 | 38.0215 | 3038.0215 | 2940.6878 | 0 | 177.8234
0 | 50.7787 | 0 | 0 | 0 | 0 | 1.7213 | 52.5 | 70.918 | 3000 | 3.0757 | 3003.0757 | 3003.0757 | 0 | 187.6622
0 | 37.9285 | 0 | 0 | 0 | 0 | 14.5715 | 52.5 | 85.4895 | 3000 | 26.0374 | 3026.0374 | 3026.0374 | 0 | 203.3497
0 | 28.901 | 0 | 0 | 0 | 0 | 23.599 | 52.5 | 109.0885 | 3000 | 42.1683 | 3042.1683 | 3042.1683 | 0 | 200.6918
0 | 161.5885 | 0 | 0 | 0 | 0 | -109.0885 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 185.97
0 | 24.3479 | 0 | 0 | 0 | 0 | 28.1521 | 52.5 | 28.1521 | 3000 | 50.304 | 3050.304 | 3050.304 | 0 | 168.8343
0 | 27.179 | 0 | 0 | 0 | 0 | 25.321 | 52.5 | 53.4731 | 3000 | 45.2453 | 3045.2453 | 3045.2453 | 0 | 172.3304
0 | 29.7341 | 0 | 0 | 0 | 0 | 22.7659 | 52.5 | 76.239 | 3000 | 40.6797 | 3040.6797 | 3040.6797 | 0 | 164.1967
0 | 25.7631 | 0 | 0 | 0 | 0 | 26.7369 | 52.5 | 102.976 | 3000 | 47.7753 | 3047.7753 | 3047.7753 | 0 | 160.9835
0 | 36.7342 | 0 | 0 | 0 | 0 | 15.7658 | 52.5 | 118.7417 | 3000 | 28.1713 | 3028.1713 | 3028.1713 | 0 | 158.9184
0 | 26.1432 | 0 | 0 | 0 | 0 | 26.3568 | 52.5 | 145.0985 | 3000 | 47.096 | 3047.096 | 3047.096 | 0 | 159.9116
0 | 31.5286 | 0 | 0 | 0 | 0 | 20.9714 | 52.5 | 166.0699 | 3000 | 37.4731 | 3037.4731 | 3037.4731 | 0 | 155.549
0 | 22.7249 | 0 | 0 | 0 | 0 | 29.7751 | 52.5 | 195.845 | 3000 | 53.2042 | 3053.2042 | 3053.2042 | 0 | 156.3546
0 | 28.5585 | 0 | 0 | 0 | 0 | 23.9415 | 52.5 | 219.7866 | 3000 | 42.7804 | 3042.7804 | 3042.7804 | 0 | 158.3463
0 | 18.6602 | 0 | 0 | 0 | 0 | 33.8398 | 52.5 | 253.6264 | 3000 | 60.4673 | 3060.4673 | 3044.245 | 0 | 159.214
0 | 30.6706 | 0 | 0 | 0 | 0 | 21.8294 | 52.5 | 275.4559 | 3000 | 39.0063 | 3039.0063 | 2801.0796 | 0 | 148.4012
0 | 37.9893 | 0 | 0 | 0 | 0 | 14.5107 | 52.5 | 289.9666 | 3000 | 25.9288 | 3025.9288 | 2555.4828 | 0 | 138.2772
0 | 43.9613 | 0 | 0 | 0 | 0 | 8.5387 | 52.5 | 298.5053 | 3000 | 15.2575 | 3015.2575 | 2323.107 | 0 | 127.283
0 | 44.933 | 0 | 0 | 0 | 0 | 7.567 | 52.5 | 306.0722 | 3000 | 13.5212 | 3013.5212 | 2175.3703 | 0 | 114.5332
0 | 48.2779 | 0 | 0 | 0 | 0 | 4.2221 | 52.5 | 310.2943 | 3000 | 7.5443 | 3007.5443 | 2066.6523 | 0 | 107.5899
0 | 39.9926 | 0 | 0 | 0 | 0 | 12.5074 | 52.5 | 322.8018 | 3000 | 22.3491 | 3022.3491 | 2092.272 | 0 | 109.0911
0 | 46.5387 | 0 | 0 | 0 | 0 | 5.9613 | 52.5 | 328.763 | 3000 | 10.652 | 3010.652 | 2199.5382 | 0 | 109.9769
0 | 41.4245 | 0 | 0 | 0 | 0 | 11.0755 | 52.5 | 339.8385 | 3000 | 19.7904 | 3019.7904 | 2473.6405 | 0 | 122.5442
0 | 33.9934 | 0 | 0 | 0 | 0 | 18.5066 | 52.5 | 358.3451 | 3000 | 33.0688 | 3033.0688 | 2735.6604 | 0 | 137.4669
0 | 254.8892 | 0 | 0 | 0 | 0 | -202.3892 | 52.5 | 155.9559 | 3000 | 0 | 3000 | 2935.1109 | 0 | 157.2339
0 | 54.3854 | 0 | 0 | 0 | 0 | -1.8854 | 52.5 | 154.0705 | 3000 | 0 | 3000 | 3000 | 0 | 182.25
0 | 38.2547 | 0 | 0 | 0 | 0 | 14.2453 | 52.5 | 168.3158 | 3000 | 25.4544 | 3025.4544 | 3025.4544 | 0 | 201.7373
0 | 33.2418 | 0 | 0 | 0 | 0 | 19.2582 | 52.5 | 187.5739 | 3000 | 34.4118 | 3034.4118 | 3034.4118 | 0 | 201.6974
0 | 27.6025 | 0 | 0 | 0 | 0 | 24.8975 | 52.5 | 212.4715 | 3000 | 44.4886 | 3044.4886 | 3044.4886 | 0 | 197.8918
0 | 26.8306 | 0 | 0 | 0 | 0 | 25.6694 | 52.5 | 238.1409 | 3000 | 45.8678 | 3045.8678 | 3045.8678 | 0 | 181.1073
0 | 29.9744 | 0 | 0 | 0 | 0 | 22.5256 | 52.5 | 260.6665 | 3000 | 40.2503 | 3040.2503 | 3040.2503 | 0 | 190.4717
0 | 25.6796 | 0 | 0 | 0 | 0 | 26.8204 | 52.5 | 287.4869 | 3000 | 47.9245 | 3047.9245 | 3047.9245 | 0 | 180.1323
0 | 25.1535 | 0 | 0 | 0 | 0 | 27.3465 | 52.5 | 314.8334 | 3000 | 48.8645 | 3048.8645 | 3048.8645 | 0 | 163.724
0 | 28.1988 | 0 | 0 | 0 | 0 | 24.3012 | 52.5 | 339.1346 | 3000 | 43.423 | 3043.423 | 3043.423 | 0 | 158.3189
0 | 23.7947 | 0 | 0 | 0 | 0 | 28.7053 | 52.5 | 367.8399 | 3000 | 51.2926 | 3051.2926 | 3051.2926 | 0 | 158.6672
0 | 20.2424 | 0 | 0 | 0 | 0 | 32.2576 | 52.5 | 400.0975 | 3000 | 57.6401 | 3057.6401 | 3057.6401 | 0 | 157.071
0 | 32.6515 | 0 | 0 | 0 | 0 | 19.8485 | 52.5 | 419.946 | 3000 | 35.4666 | 3035.4666 | 3035.4666 | 0 | 154.9909
0 | 25.8483 | 0 | 0 | 0 | 0 | 26.6517 | 52.5 | 446.5977 | 3000 | 47.623 | 3047.623 | 3047.623 | 0 | 167.8326
0 | 27.2882 | 0 | 0 | 0 | 0 | 25.2118 | 52.5 | 471.8094 | 3000 | 45.05 | 3045.05 | 3034.2352 | 0 | 197.286
0 | 42.7214 | 0 | 0 | 0 | 0 | -42.7214 | 0 | 429.088 | 0 | 0 | 0 | 0 | 189.2599 | 0
0 | 46.1006 | 0 | 0 | 0 | 0 | -37.7732 | 8.3274 | 391.3149 | 475.8534 | 0 | 475.8534 | 0 | 0 | 0
0 | 53.4257 | 0 | 0 | 0 | 0 | -0.92569 | 52.5 | 390.3892 | 3000 | 0 | 3000 | 2286.2199 | 0 | 150.2504
0 | 23.2805 | 0 | 0 | 0 | 0 | 29.2195 | 52.5 | 419.6086 | 3000 | 52.2113 | 3052.2113 | 2192.4307 | 0 | 120.6495
0 | 234.3032 | 0 | 0 | 0 | 0 | -181.8032 | 52.5 | 237.8055 | 3000 | 0 | 3000 | 2037.4783 | 0 | 109.9627
0 | 45.7535 | 0 | 0 | 0 | 0 | 6.7465 | 52.5 | 244.552 | 3000 | 12.0552 | 3012.0552 | 2054.9409 | 0 | 107.6789
0 | 31.8517 | 0 | 0 | 0 | 0 | 20.6483 | 52.5 | 265.2003 | 3000 | 36.8958 | 3036.8958 | 2285.2637 | 0 | 123.3585
0 | 46.2365 | 0 | 0 | 0 | 0 | 6.2635 | 52.5 | 271.4639 | 3000 | 11.1921 | 3011.1921 | 2438.005 | 0 | 128.9217
0 | 41.7134 | 0 | 0 | 0 | 0 | 10.7866 | 52.5 | 282.2504 | 3000 | 19.2742 | 3019.2742 | 2635.347 | 0 | 150.2148
0 | 32.8088 | 0 | 0 | 0 | 0 | 19.6912 | 52.5 | 301.9417 | 3000 | 35.1856 | 3035.1856 | 2910.8148 | 0 | 172.9024
0 | 42.2842 | 0 | 0 | 0 | 0 | 10.2158 | 52.5 | 312.1575 | 3000 | 18.2543 | 3018.2543 | 3018.2543 | 0 | 205.9657
0 | 48.1761 | 0 | 0 | 0 | 0 | -48.1761 | 0 | 263.9814 | 0 | 0 | 0 | 0 | 0 | 0
0 | 28.9345 | 0 | 0 | 0 | 0 | 23.5655 | 52.5 | 287.5469 | 3000 | 42.1084 | 3042.1084 | 3042.1084 | 0 | 211.1223
0 | 25.6343 | 0 | 0 | 0 | 0 | 26.8657 | 52.5 | 314.4126 | 3000 | 48.0055 | 3048.0055 | 3048.0055 | 0 | 199.9796
0 | 31.3575 | 0 | 0 | 0 | 0 | 21.1425 | 52.5 | 335.5551 | 3000 | 37.7789 | 3037.7789 | 3037.7789 | 0 | 176.4646
0 | 24.5776 | 0 | 0 | 0 | 0 | 27.9224 | 52.5 | 363.4775 | 3000 | 49.8935 | 3049.8935 | 3049.8935 | 0 | 175.0639
0 | 26.0664 | 0 | 0 | 0 | 0 | 26.4336 | 52.5 | 389.9111 | 3000 | 47.2333 | 3047.2333 | 3047.2333 | 0 | 168.8167
0 | 32.2527 | 0 | 0 | 0 | 0 | 20.2473 | 52.5 | 410.1584 | 3000 | 36.1792 | 3036.1792 | 3036.1792 | 0 | 158.1849
0 | 229.5003 | 0 | 0 | 0 | 0 | -177.0003 | 52.5 | 233.1581 | 3000 | 0 | 3000 | 3000 | 0 | 156
0 | 238.28 | 0 | 0 | 0 | 0 | -185.78 | 52.5 | 47.3781 | 3000 | 0 | 3000 | 3000 | 0 | 155.52
0 | 26.1604 | 0 | 0 | 0 | 0 | 26.3396 | 52.5 | 73.7176 | 3000 | 47.0653 | 3047.0653 | 3047.0653 | 0 | 155.0347
0 | 27.8738 | 0 | 0 | 0 | 0 | 24.6262 | 52.5 | 98.3438 | 3000 | 44.0037 | 3044.0037 | 3044.0037 | 0 | 157.5881
0 | 23.5772 | 0 | 0 | 0 | 0 | 28.9228 | 52.5 | 127.2666 | 3000 | 51.6812 | 3051.6812 | 3051.6812 | 0 | 166.042
0 | 33.1877 | 0 | 0 | 0 | 0 | 19.3123 | 52.5 | 146.5789 | 3000 | 34.5084 | 3034.5084 | 3018.2862 | 0 | 192.3856
0 | 31.868 | 0 | 0 | 0 | 0 | 20.632 | 52.5 | 167.2109 | 3000 | 36.8667 | 3036.8667 | 2820.5697 | 0 | 191.9116
0 | 24.141 | 0 | 0 | 0 | 0 | 28.359 | 52.5 | 195.5699 | 3000 | 50.6737 | 3050.6737 | 2574.8203 | 0 | 172.204
0 | 43.3 | 0 | 0 | 0 | 0 | 9.2 | 52.5 | 204.7698 | 3000 | 16.4391 | 3016.4391 | 2308.0664 | 0 | 149.8397
0 | 31.8794 | 0 | 0 | 0 | 0 | 20.6206 | 52.5 | 225.3904 | 3000 | 36.8463 | 3036.8463 | 2187.8805 | 0 | 124.7092
0 | 37.0738 | 0 | 0 | 0 | 0 | 15.4262 | 52.5 | 240.8167 | 3000 | 27.5646 | 3027.5646 | 2075.8578 | 0 | 112.2624
0 | 43.9036 | 0 | 0 | 0 | 0 | 8.5964 | 52.5 | 249.4131 | 3000 | 15.3607 | 3015.3607 | 2096.0984 | 0 | 113.7762
0 | 31.9359 | 0 | 0 | 0 | 0 | 20.5641 | 52.5 | 269.9772 | 3000 | 36.7453 | 3036.7453 | 2236.4464 | 0 | 120.7681
0 | 47.3822 | 0 | 0 | 0 | 0 | 5.1178 | 52.5 | 275.095 | 3000 | 9.1449 | 3009.1449 | 2403.5133 | 0 | 127.1699
0 | 37.6085 | 0 | 0 | 0 | 0 | 14.8915 | 52.5 | 289.9865 | 3000 | 26.6092 | 3026.6092 | 2664.3117 | 0 | 150.4004
0 | 255.094 | 0 | 0 | 0 | 0 | -202.594 | 52.5 | 87.3925 | 3000 | 0 | 3000 | 2902.6663 | 0 | 174.5664
0 | 40.461 | 0 | 0 | 0 | 0 | -40.461 | 0 | 46.9315 | 0 | 0 | 0 | 0 | 0 | 0
0 | 39.1968 | 0 | 0 | 0 | 0 | -39.1968 | 0 | 7.7347 | 0 | 0 | 0 | 0 | 0 | 0
0 | 23.6679 | 0 | 0 | 0 | 0 | 28.8321 | 52.5 | 36.5668 | 3000 | 51.5191 | 3051.5191 | 3051.5191 | 0 | 213.4232
0 | 29.8453 | 0 | 0 | 0 | 0 | 22.6547 | 52.5 | 59.2215 | 3000 | 40.4809 | 3040.4809 | 3040.4809 | 0 | 201.2494
0 | 32.0434 | 0 | 0 | 0 | 0 | 20.4566 | 52.5 | 79.6781 | 3000 | 36.5532 | 3036.5532 | 3036.5532 | 0 | 189.9971
0 | 23.1248 | 0 | 0 | 0 | 0 | 29.3752 | 52.5 | 109.0533 | 3000 | 52.4897 | 3052.4897 | 3052.4897 | 0 | 188.6439
0 | 28.0898 | 0 | 0 | 0 | 0 | 24.4102 | 52.5 | 133.4635 | 3000 | 43.6177 | 3043.6177 | 3043.6177 | 0 | 171.6905
0 | 31.9329 | 0 | 0 | 0 | 0 | 20.5671 | 52.5 | 154.0306 | 3000 | 36.7506 | 3036.7506 | 3036.7506 | 0 | 169.9973
0 | 31.8125 | 0 | 0 | 0 | 0 | 20.6875 | 52.5 | 174.7181 | 3000 | 36.9658 | 3036.9658 | 3036.9658 | 0 | 165.2717
0 | 28.4381 | 0 | 0 | 0 | 0 | 24.0619 | 52.5 | 198.78 | 3000 | 42.9954 | 3042.9954 | 3042.9954 | 0 | 163.0437
0 | 26.8738 | 0 | 0 | 0 | 0 | 25.6262 | 52.5 | 224.4062 | 3000 | 45.7906 | 3045.7906 | 3045.7906 | 0 | 161.3964
0 | 30.6236 | 0 | 0 | 0 | 0 | 21.8764 | 52.5 | 246.2826 | 3000 | 39.0903 | 3039.0903 | 3039.0903 | 0 | 162.8648
0 | 27.1077 | 0 | 0 | 0 | 0 | 25.3923 | 52.5 | 271.6749 | 3000 | 45.3727 | 3045.3727 | 3045.3727 | 0 | 172.0027
0 | 219.9795 | 0 | 0 | 0 | 0 | -167.4795 | 52.5 | 104.1954 | 3000 | 0 | 3000 | 2972.9629 | 0 | 195.4723
0 | 38.4709 | 0 | 0 | 0 | 0 | -38.4709 | 0 | 65.7245 | 0 | 0 | 0 | 0 | 259.5564 | 0
0 | 36.623 | 0 | 0 | 0 | 0 | 15.877 | 52.5 | 81.6015 | 3000 | 28.3701 | 3028.3701 | 2541.7018 | 0 | 175.8603
0 | 47.2718 | 0 | 0 | 0 | 0 | 5.2282 | 52.5 | 86.8297 | 3000 | 9.3421 | 3009.3421 | 2279.3397 | 0 | 148.0431
0 | 45.644 | 0 | 0 | 0 | 0 | 6.856 | 52.5 | 93.6857 | 3000 | 12.2507 | 3012.2507 | 2147.0626 | 0 | 127.9005
0 | 51.2707 | 0 | 0 | 0 | 0 | 1.2293 | 52.5 | 94.9149 | 3000 | 2.1965 | 3002.1965 | 2028.86 | 0 | 113.1901
0 | 42.8951 | 0 | 0 | 0 | 0 | 9.6049 | 52.5 | 104.5198 | 3000 | 17.1626 | 3017.1626 | 2054.6409 | 0 | 112.245
0 | 39.8213 | 0 | 0 | 0 | 0 | 12.6787 | 52.5 | 117.1985 | 3000 | 22.6551 | 3022.6551 | 2179.0968 | 0 | 118.9351
0 | 36.9745 | 0 | 0 | 0 | 0 | 15.5255 | 52.5 | 132.724 | 3000 | 27.742 | 3027.742 | 2400.4807 | 0 | 132.1705
0 | 54.2859 | 0 | 0 | 0 | 0 | -1.7859 | 52.5 | 130.9381 | 3000 | 0 | 3000 | 2626.8877 | 0 | 146.1075
0 | 36.0543 | 0 | 0 | 0 | 0 | 16.4457 | 52.5 | 147.3838 | 3000 | 29.3863 | 3029.3863 | 2921.2378 | 0 | 172.1193
0 | 44.398 | 0 | 0 | 0 | 0 | 8.102 | 52.5 | 155.4859 | 3000 | 14.4773 | 3014.4773 | 3014.4773 | 0 | 205.4668
0 | 32.9151 | 0 | 0 | 0 | 0 | 19.5849 | 52.5 | 175.0707 | 3000 | 34.9956 | 3034.9956 | 3034.9956 | 0 | 210.8715
0 | 227.5707 | 0 | 0 | 0 | 0 | -175.0707 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 200.46
0 | 22.7522 | 0 | 0 | 0 | 0 | 29.7478 | 52.5 | 29.7478 | 3000 | 53.1553 | 3053.1553 | 3053.1553 | 0 | 188.3492
0 | 29.6175 | 0 | 0 | 0 | 0 | 22.8825 | 52.5 | 52.6303 | 3000 | 40.8879 | 3040.8879 | 3040.8879 | 0 | 172.0534
0 | 20.0647 | 0 | 0 | 0 | 0 | 32.4353 | 52.5 | 85.0656 | 3000 | 57.9577 | 3057.9577 | 3057.9577 | 0 | 172.4382
0 | 33.8752 | 0 | 0 | 0 | 0 | 18.6248 | 52.5 | 103.6904 | 3000 | 33.28 | 3033.28 | 3033.28 | 0 | 158.9439
0 | 28.7071 | 0 | 0 | 0 | 0 | 23.7929 | 52.5 | 127.4833 | 3000 | 42.5148 | 3042.5148 | 3042.5148 | 0 | 159.732
0 | 30.796 | 0 | 0 | 0 | 0 | 21.704 | 52.5 | 149.1873 | 3000 | 38.7822 | 3038.7822 | 3038.7822 | 0 | 160.9947
0 | 35.1562 | 0 | 0 | 0 | 0 | 17.3438 | 52.5 | 166.5311 | 3000 | 30.9911 | 3030.9911 | 3030.9911 | 0 | 159.127
0 | 28.5349 | 0 | 0 | 0 | 0 | 23.9651 | 52.5 | 190.4963 | 3000 | 42.8225 | 3042.8225 | 3042.8225 | 0 | 163.0953
0 | 33.4113 | 0 | 0 | 0 | 0 | 19.0887 | 52.5 | 209.5849 | 3000 | 34.109 | 3034.109 | 3034.109 | 0 | 155.9532
0 | 29.1302 | 0 | 0 | 0 | 0 | 23.3698 | 52.5 | 232.9548 | 3000 | 41.7588 | 3041.7588 | 3041.7588 | 0 | 151.7838
0 | 25.2602 | 0 | 0 | 0 | 0 | 27.2398 | 52.5 | 260.1945 | 3000 | 48.6738 | 3048.6738 | 3027.0441 | 0 | 173.9037
0 | 243.733 | 0 | 0 | 0 | 0 | -191.233 | 52.5 | 68.9615 | 3000 | 0 | 3000 | 2832.3698 | 0 | 182.9428
0 | 44.7512 | 0 | 0 | 0 | 0 | -44.7512 | 0 | 24.2103 | 0 | 0 | 0 | 0 | 264.9638 | 0
0 | 32.0646 | 0 | 0 | 0 | 0 | -24.2103 | 7.8543 | 0 | 448.8163 | 0 | 448.8163 | 0 | 0 | 0
0 | 41.9151 | 0 | 0 | 0 | 0 | 10.5849 | 52.5 | 10.5849 | 3000 | 18.9138 | 3018.9138 | 2434.9119 | 0 | 140.397
0 | 45.1593 | 0 | 0 | 0 | 0 | 7.3407 | 52.5 | 17.9256 | 3000 | 13.1168 | 3013.1168 | 2439.9298 | 0 | 131.4878
0 | 51.8574 | 0 | 0 | 0 | 0 | 0.64258 | 52.5 | 18.5682 | 3000 | 1.1482 | 3001.1482 | 2384.7017 | 0 | 126.3892
0 | 41.1282 | 0 | 0 | 0 | 0 | 11.3718 | 52.5 | 29.94 | 3000 | 20.32 | 3020.32 | 2355.2067 | 0 | 122.6592
0 | 35.5145 | 0 | 0 | 0 | 0 | 16.9855 | 52.5 | 46.9255 | 3000 | 30.3508 | 3030.3508 | 2641.0162 | 0 | 140.1059
0 | 99.4255 | 0 | 0 | 0 | 0 | -46.9255 | 52.5 | 0 | 3000 | 0 | 3000 | 2935.1109 | 0 | 175.1674
0 | 40.8765 | 0 | 0 | 0 | 0 | 11.6235 | 52.5 | 11.6235 | 3000 | 20.7697 | 3020.7697 | 2982.9177 | 0 | 186.2832
0 | 38.8053 | 0 | 0 | 0 | 0 | 13.6947 | 52.5 | 25.3183 | 3000 | 24.4707 | 3024.4707 | 3024.4707 | 0 | 207.6904
0 | 35.9454 | 0 | 0 | 0 | 0 | 16.5546 | 52.5 | 41.8729 | 3000 | 29.5809 | 3029.5809 | 3029.5809 | 0 | 208.314
0 | 94.3729 | 0 | 0 | 0 | 0 | -41.8729 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 197.91
0 | 27.7613 | 0 | 0 | 0 | 0 | 24.7387 | 52.5 | 24.7387 | 3000 | 44.2047 | 3044.2047 | 3044.2047 | 0 | 195.4379
0 | 30.7411 | 0 | 0 | 0 | 0 | 21.7589 | 52.5 | 46.4976 | 3000 | 38.8803 | 3038.8803 | 3038.8803 | 0 | 179.9017
0 | 32.5301 | 0 | 0 | 0 | 0 | 19.9699 | 52.5 | 66.4675 | 3000 | 35.6836 | 3035.6836 | 3035.6836 | 0 | 176.7071
0 | 30.4671 | 0 | 0 | 0 | 0 | 22.0329 | 52.5 | 88.5004 | 3000 | 39.3699 | 3039.3699 | 3039.3699 | 0 | 171.542
0 | 28.6062 | 0 | 0 | 0 | 0 | 23.8938 | 52.5 | 112.3942 | 3000 | 42.6951 | 3042.6951 | 3042.6951 | 0 | 165.5226
0 | 39.244 | 0 | 0 | 0 | 0 | 13.256 | 52.5 | 125.6503 | 3000 | 23.6868 | 3023.6868 | 3023.6868 | 0 | 159.3483
0 | 33.092 | 0 | 0 | 0 | 0 | 19.408 | 52.5 | 145.0583 | 3000 | 34.6795 | 3034.6795 | 3034.6795 | 0 | 158.5013
0 | 27.2554 | 0 | 0 | 0 | 0 | 25.2446 | 52.5 | 170.3028 | 3000 | 45.1087 | 3045.1087 | 3045.1087 | 0 | 160.5381
0 | 31.9511 | 0 | 0 | 0 | 0 | 20.5489 | 52.5 | 190.8517 | 3000 | 36.7181 | 3036.7181 | 3036.7181 | 0 | 167.2017
0 | 30.7816 | 0 | 0 | 0 | 0 | 21.7184 | 52.5 | 212.5702 | 3000 | 38.808 | 3038.808 | 3038.808 | 0 | 173.0905
0 | 23.793 | 0 | 0 | 0 | 0 | 28.707 | 52.5 | 241.2772 | 3000 | 51.2956 | 3051.2956 | 3051.2956 | 0 | 188.4175
0 | 229.6018 | 0 | 0 | 0 | 0 | -177.1018 | 52.5 | 64.1754 | 3000 | 0 | 3000 | 2978.3703 | 0 | 187.5778
0 | 43.2744 | 0 | 0 | 0 | 0 | 9.2256 | 52.5 | 73.401 | 3000 | 16.4849 | 3016.4849 | 2973.2255 | 0 | 195.1031
0 | 51.0547 | 0 | 0 | 0 | 0 | 1.4453 | 52.5 | 74.8462 | 3000 | 2.5825 | 3002.5825 | 2910.6563 | 0 | 192.3362
0 | 40.3414 | 0 | 0 | 0 | 0 | 12.1586 | 52.5 | 87.0049 | 3000 | 21.7259 | 3021.7259 | 2859.5031 | 0 | 192.1872
0 | 48.4341 | 0 | 0 | 0 | 0 | 4.0659 | 52.5 | 91.0708 | 3000 | 7.2652 | 3007.2652 | 2904.5242 | 0 | 194.6903
0 | 52.3009 | 0 | 0 | 0 | 0 | 0.19912 | 52.5 | 91.2699 | 3000 | 0.35581 | 3000.3558 | 2811.0959 | 0 | 178.6733
0 | 48.2735 | 0 | 0 | 0 | 0 | 4.2265 | 52.5 | 95.4964 | 3000 | 7.5522 | 3007.5522 | 2812.8849 | 0 | 175.524
0 | 50.6356 | 0 | 0 | 0 | 0 | 1.8644 | 52.5 | 97.3608 | 3000 | 3.3314 | 3003.3314 | 2878.9606 | 0 | 178.2365
0 | 46.4818 | 0 | 0 | 0 | 0 | 6.0182 | 52.5 | 103.379 | 3000 | 10.7537 | 3010.7537 | 2962.0869 | 0 | 184.5676
0 | 54.5943 | 0 | 0 | 0 | 0 | -2.0943 | 52.5 | 101.2847 | 3000 | 0 | 3000 | 2978.3703 | 0 | 193.7132
0 | 32.1278 | 0 | 0 | 0 | 0 | 20.3722 | 52.5 | 121.6569 | 3000 | 36.4024 | 3036.4024 | 3036.4024 | 0 | 208.2668
0 | 39.5041 | 0 | 0 | 0 | 0 | -39.5041 | 0 | 82.1528 | 0 | 0 | 0 | 0 | 0 | 0
0 | 23.1742 | 0 | 0 | 0 | 0 | 29.3258 | 52.5 | 111.4786 | 3000 | 52.4013 | 3052.4013 | 3052.4013 | 0 | 206.0066
0 | 31.8165 | 0 | 0 | 0 | 0 | 20.6835 | 52.5 | 132.1621 | 3000 | 36.9587 | 3036.9587 | 3036.9587 | 0 | 193.3328
0 | 184.6621 | 0 | 0 | 0 | 0 | -132.1621 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 184.59
0 | 37.1524 | 0 | 0 | 0 | 0 | 15.3476 | 52.5 | 15.3476 | 3000 | 27.4242 | 3027.4242 | 3027.4242 | 0 | 183.6133
0 | 24.8183 | 0 | 0 | 0 | 0 | 27.6817 | 52.5 | 43.0294 | 3000 | 49.4636 | 3049.4636 | 3049.4636 | 0 | 181.1686
0 | 26.907 | 0 | 0 | 0 | 0 | 25.593 | 52.5 | 68.6223 | 3000 | 45.7312 | 3045.7312 | 3045.7312 | 0 | 180.2768
0 | 30.2771 | 0 | 0 | 0 | 0 | 22.2229 | 52.5 | 90.8453 | 3000 | 39.7094 | 3039.7094 | 3039.7094 | 0 | 177.1543
0 | 32.0587 | 0 | 0 | 0 | 0 | 20.4413 | 52.5 | 111.2866 | 3000 | 36.5259 | 3036.5259 | 3036.5259 | 0 | 170.3187
0 | 35.3944 | 0 | 0 | 0 | 0 | 17.1056 | 52.5 | 128.3921 | 3000 | 30.5653 | 3030.5653 | 3030.5653 | 0 | 165.1355
0 | 30.6516 | 0 | 0 | 0 | 0 | 21.8484 | 52.5 | 150.2405 | 3000 | 39.0401 | 3039.0401 | 3039.0401 | 0 | 169.0618
0 | 36.7951 | 0 | 0 | 0 | 0 | 15.7049 | 52.5 | 165.9454 | 3000 | 28.0625 | 3028.0625 | 3028.0625 | 0 | 166.4526
0 | 35.8599 | 0 | 0 | 0 | 0 | 16.6401 | 52.5 | 182.5855 | 3000 | 29.7337 | 3029.7337 | 3018.9189 | 0 | 170.3274
0 | 38.138 | 0 | 0 | 0 | 0 | 14.362 | 52.5 | 196.9475 | 3000 | 25.663 | 3025.663 | 2987.811 | 0 | 176.0418
0 | 33.5468 | 0 | 0 | 0 | 0 | 18.9532 | 52.5 | 215.9007 | 3000 | 33.8669 | 3033.8669 | 2968.9778 | 0 | 186.719
0 | 47.6502 | 0 | 0 | 0 | 0 | 4.8498 | 52.5 | 220.7506 | 3000 | 8.666 | 3008.666 | 2905.9249 | 0 | 184.8168
0 | 255.8809 | 0 | 0 | 0 | 0 | -203.3809 | 52.5 | 17.3696 | 3000 | 0 | 3000 | 2534.9614 | 0 | 159.4491
0 | 39.2557 | 0 | 0 | 0 | 0 | 13.2443 | 52.5 | 30.614 | 3000 | 23.6659 | 3023.6659 | 2412.6268 | 0 | 146.7842
0 | 46.0372 | 0 | 0 | 0 | 0 | 6.4628 | 52.5 | 37.0768 | 3000 | 11.5482 | 3011.5482 | 2184.2121 | 0 | 128.6501
0 | 58.6992 | 0 | 0 | 0 | 0 | -6.1992 | 52.5 | 30.8775 | 3000 | 0 | 3000 | 2367.3312 | 0 | 130.7004
0 | 52.6907 | 0 | 0 | 0 | 0 | -0.19067 | 52.5 | 30.6869 | 3000 | 0 | 3000 | 2470.0723 | 0 | 137.5336
0 | 46.9533 | 0 | 0 | 0 | 0 | 5.5467 | 52.5 | 36.2335 | 3000 | 9.9111 | 3009.9111 | 2847.6884 | 0 | 159.5845
0 | 32.1282 | 0 | 0 | 0 | 0 | 20.3718 | 52.5 | 56.6054 | 3000 | 36.4018 | 3036.4018 | 3014.7721 | 0 | 171.5707
0 | 37.0082 | 0 | 0 | 0 | 0 | 15.4918 | 52.5 | 72.0972 | 3000 | 27.6819 | 3027.6819 | 3027.6819 | 0 | 181.9637
0 | 33.2466 | 0 | 0 | 0 | 0 | 19.2534 | 52.5 | 91.3506 | 3000 | 34.4033 | 3034.4033 | 3034.4033 | 0 | 186.5855
0 | 34.0591 | 0 | 0 | 0 | 0 | 18.4409 | 52.5 | 109.7915 | 3000 | 32.9514 | 3032.9514 | 3032.9514 | 0 | 187.4364
0 | 31.9849 | 0 | 0 | 0 | 0 | 20.5151 | 52.5 | 130.3066 | 3000 | 36.6578 | 3036.6578 | 3036.6578 | 0 | 168.413
0 | 34.2913 | 0 | 0 | 0 | 0 | 18.2087 | 52.5 | 148.5153 | 3000 | 32.5365 | 3032.5365 | 3032.5365 | 0 | 166.4863
0 | 29.0835 | 0 | 0 | 0 | 0 | 23.4165 | 52.5 | 171.9318 | 3000 | 41.8421 | 3041.8421 | 3041.8421 | 0 | 166.9971
0 | 35.0135 | 0 | 0 | 0 | 0 | 17.4865 | 52.5 | 189.4182 | 3000 | 31.246 | 3031.246 | 3031.246 | 0 | 162.3838
0 | 31.5357 | 0 | 0 | 0 | 0 | 20.9643 | 52.5 | 210.3826 | 3000 | 37.4605 | 3037.4605 | 3037.4605 | 0 | 166.7566
0 | 230.642 | 0 | 0 | 0 | 0 | -178.142 | 52.5 | 32.2406 | 3000 | 0 | 3000 | 3000 | 0 | 165.57
0 | 33.6174 | 0 | 0 | 0 | 0 | 18.8826 | 52.5 | 51.1232 | 3000 | 33.7407 | 3033.7407 | 3033.7407 | 0 | 157.4511
0 | 26.5491 | 0 | 0 | 0 | 0 | 25.9509 | 52.5 | 77.0741 | 3000 | 46.3708 | 3046.3708 | 3046.3708 | 0 | 159.2033
0 | 36.3983 | 0 | 0 | 0 | 0 | 16.1017 | 52.5 | 93.1758 | 3000 | 28.7716 | 3028.7716 | 3028.7716 | 0 | 156.5875
0 | 25.333 | 0 | 0 | 0 | 0 | 27.167 | 52.5 | 120.3429 | 3000 | 48.5439 | 3048.5439 | 3048.5439 | 0 | 154.5917
0 | 33.1298 | 0 | 0 | 0 | 0 | 19.3702 | 52.5 | 139.7131 | 3000 | 34.612 | 3034.612 | 3029.2046 | 0 | 163.0621
0 | 49.5516 | 0 | 0 | 0 | 0 | 2.9484 | 52.5 | 142.6615 | 3000 | 5.2684 | 3005.2684 | 2978.2313 | 0 | 167.8829
0 | 37.7809 | 0 | 0 | 0 | 0 | 14.7191 | 52.5 | 157.3806 | 3000 | 26.3011 | 3026.3011 | 2950.5972 | 0 | 156.3817
0 | 39.7608 | 0 | 0 | 0 | 0 | 12.7392 | 52.5 | 170.1198 | 3000 | 22.7633 | 3022.7633 | 2936.2445 | 0 | 176.527
0 | 222.6198 | 0 | 0 | 0 | 0 | -170.1198 | 52.5 | 0 | 3000 | 0 | 3000 | 2886.4441 | 0 | 193.4495
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2228 | 0
0 | 47.9744 | 0 | 0 | 0 | 0 | 4.5256 | 52.5 | 4.5256 | 3000 | 8.0866 | 3008.0866 | 2889.1233 | 0 | 191.1444
0 | 47.129 | 0 | 0 | 0 | 0 | 5.371 | 52.5 | 9.8966 | 3000 | 9.5972 | 3009.5972 | 2879.819 | 0 | 167.9798
0 | 44.534 | 0 | 0 | 0 | 0 | 7.966 | 52.5 | 17.8626 | 3000 | 14.2342 | 3014.2342 | 2954.7525 | 0 | 161.7727
0 | 29.2902 | 0 | 0 | 0 | 0 | 23.2098 | 52.5 | 41.0724 | 3000 | 41.4729 | 3041.4729 | 2987.3986 | 0 | 159.2283
0 | 45.1879 | 0 | 0 | 0 | 0 | 7.3121 | 52.5 | 48.3845 | 3000 | 13.0658 | 3013.0658 | 3002.251 | 0 | 146.5098
0 | 53.6667 | 0 | 0 | 0 | 0 | -1.1667 | 52.5 | 47.2178 | 3000 | 0 | 3000 | 3000 | 0 | 165
0 | 99.7178 | 0 | 0 | 0 | 0 | -47.2178 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 162
0 | 22.5984 | 0 | 0 | 0 | 0 | 29.9016 | 52.5 | 29.9016 | 3000 | 53.4302 | 3053.4302 | 3053.4302 | 0 | 173.4348
0 | 36.8827 | 0 | 0 | 0 | 0 | 15.6173 | 52.5 | 45.5189 | 3000 | 27.9061 | 3027.9061 | 3027.9061 | 0 | 178.919
0 | 33.4707 | 0 | 0 | 0 | 0 | 19.0293 | 52.5 | 64.5482 | 3000 | 34.0028 | 3034.0028 | 3034.0028 | 0 | 169.5401
0 | 31.5959 | 0 | 0 | 0 | 0 | 20.9041 | 52.5 | 85.4523 | 3000 | 37.3529 | 3037.3529 | 3037.3529 | 0 | 172.8254
0 | 35.662 | 0 | 0 | 0 | 0 | 16.838 | 52.5 | 102.2903 | 3000 | 30.0872 | 3030.0872 | 3030.0872 | 0 | 175.2602
0 | 36.4641 | 0 | 0 | 0 | 0 | 16.0359 | 52.5 | 118.3262 | 3000 | 28.654 | 3028.654 | 3028.654 | 0 | 167.3331
0 | 23.5752 | 0 | 0 | 0 | 0 | 28.9248 | 52.5 | 147.251 | 3000 | 51.6848 | 3051.6848 | 3051.6848 | 0 | 168.7887
0 | 30.2902 | 0 | 0 | 0 | 0 | 22.2098 | 52.5 | 169.4608 | 3000 | 39.686 | 3039.686 | 3039.686 | 0 | 166.5748
0 | 35.8145 | 0 | 0 | 0 | 0 | 16.6855 | 52.5 | 186.1463 | 3000 | 29.8148 | 3029.8148 | 3029.8148 | 0 | 166.5489
0 | 37.0185 | 0 | 0 | 0 | 0 | 15.4815 | 52.5 | 201.6279 | 3000 | 27.6634 | 3027.6634 | 3027.6634 | 0 | 155.0164
0 | 30.2612 | 0 | 0 | 0 | 0 | 22.2388 | 52.5 | 223.8667 | 3000 | 39.7378 | 3039.7378 | 3039.7378 | 0 | 166.456
0 | 29.1414 | 0 | 0 | 0 | 0 | 23.3586 | 52.5 | 247.2253 | 3000 | 41.7387 | 3041.7387 | 3041.7387 | 0 | 167.5998
0 | 47.6429 | 0 | 0 | 0 | 0 | 4.8571 | 52.5 | 252.0824 | 3000 | 8.6791 | 3008.6791 | 2943.7899 | 0 | 166.5302
0 | 46.3601 | 0 | 0 | 0 | 0 | 6.1399 | 52.5 | 258.2223 | 3000 | 10.9711 | 3010.9711 | 2854.1558 | 0 | 172.6193
0 | 39.3985 | 0 | 0 | 0 | 0 | 13.1015 | 52.5 | 271.3238 | 3000 | 23.4107 | 3023.4107 | 2801.7063 | 0 | 194.5225
0 | 43.5696 | 0 | 0 | 0 | 0 | -35.0529 | 8.5167 | 236.2709 | 486.6683 | 0 | 486.6683 | 0 | 0 | 0
0 | 43.6353 | 0 | 0 | 0 | 0 | 8.8647 | 52.5 | 245.1355 | 3000 | 15.84 | 3015.84 | 2621.0979 | 0 | 156.034
0 | 45.2178 | 0 | 0 | 0 | 0 | 7.2822 | 52.5 | 252.4177 | 3000 | 13.0123 | 3013.0123 | 2564.196 | 0 | 145.0822
0 | 54.3604 | 0 | 0 | 0 | 0 | -1.8604 | 52.5 | 250.5573 | 3000 | 0 | 3000 | 2659.3322 | 0 | 153.1509
0 | 37.8748 | 0 | 0 | 0 | 0 | 14.6252 | 52.5 | 265.1825 | 3000 | 26.1333 | 3026.1333 | 2550.2799 | 0 | 151.1041
0 | 43.0465 | 0 | 0 | 0 | 0 | 9.4535 | 52.5 | 274.636 | 3000 | 16.8922 | 3016.8922 | 2622.1501 | 0 | 157.0668
0 | 44.581 | 0 | 0 | 0 | 0 | 7.919 | 52.5 | 282.555 | 3000 | 14.1503 | 3014.1503 | 2900.5943 | 0 | 181.6932
0 | 51.2811 | 0 | 0 | 0 | 0 | 1.2189 | 52.5 | 283.7739 | 3000 | 2.1779 | 3002.1779 | 2996.7705 | 0 | 178.7574
0 | 44.8298 | 0 | 0 | 0 | 0 | 7.6702 | 52.5 | 291.4441 | 3000 | 13.7057 | 3013.7057 | 3013.7057 | 0 | 179.3758
0 | 25.469 | 0 | 0 | 0 | 0 | 27.031 | 52.5 | 318.4752 | 3000 | 48.3008 | 3048.3008 | 3048.3008 | 0 | 181.191
0 | 34.1754 | 0 | 0 | 0 | 0 | 18.3246 | 52.5 | 336.7997 | 3000 | 32.7436 | 3032.7436 | 3032.7436 | 0 | 179.2351
0 | 37.3744 | 0 | 0 | 0 | 0 | 15.1256 | 52.5 | 351.9254 | 3000 | 27.0275 | 3027.0275 | 3027.0275 | 0 | 179.3514
0 | 29.762 | 0 | 0 | 0 | 0 | 22.738 | 52.5 | 374.6634 | 3000 | 40.6298 | 3040.6298 | 3040.6298 | 0 | 169.8496
0 | 32.5639 | 0 | 0 | 0 | 0 | 19.9361 | 52.5 | 394.5994 | 3000 | 35.6231 | 3035.6231 | 3035.6231 | 0 | 167.8396
0 | 22.2649 | 0 | 0 | 0 | 0 | 30.2351 | 52.5 | 424.8345 | 3000 | 54.0261 | 3054.0261 | 3054.0261 | 0 | 157.2823
0 | 235.1355 | 0 | 0 | 0 | 0 | -182.6355 | 52.5 | 242.199 | 3000 | 0 | 3000 | 3000 | 0 | 152.1
0 | 35.6054 | 0 | 0 | 0 | 0 | 16.8946 | 52.5 | 259.0936 | 3000 | 30.1884 | 3030.1884 | 3030.1884 | 0 | 157.8728
0 | 27.0673 | 0 | 0 | 0 | 0 | 25.4327 | 52.5 | 284.5264 | 3000 | 45.4449 | 3045.4449 | 3045.4449 | 0 | 154.4041
0 | 34.4067 | 0 | 0 | 0 | 0 | 18.0933 | 52.5 | 302.6197 | 3000 | 32.3303 | 3032.3303 | 3032.3303 | 0 | 157.6812
0 | 27.0999 | 0 | 0 | 0 | 0 | 25.4001 | 52.5 | 328.0197 | 3000 | 45.3865 | 3045.3865 | 3045.3865 | 0 | 167.4963
0 | 30.0618 | 0 | 0 | 0 | 0 | 22.4382 | 52.5 | 350.4579 | 3000 | 40.0941 | 3040.0941 | 3013.0569 | 0 | 168.6408
0 | 56.9653 | 0 | 0 | 0 | 0 | -4.4653 | 52.5 | 345.9926 | 3000 | 0 | 3000 | 2767.4807 | 0 | 168.0138
0 | 47.9629 | 0 | 0 | 0 | 0 | -38.973 | 8.9898 | 307.0196 | 513.7054 | 0 | 513.7054 | 0 | 0 | 0
0 | 44.9127 | 0 | 0 | 0 | 0 | -38.7617 | 6.1509 | 268.2579 | 351.4826 | 0 | 351.4826 | 0 | 0 | 0
0 | 33.9334 | 0 | 0 | 0 | 0 | 18.5666 | 52.5 | 286.8245 | 3000 | 33.1761 | 3033.1761 | 2351.8405 | 0 | 152.6344
0 | 52.1703 | 0 | 0 | 0 | 0 | 0.3297 | 52.5 | 287.1542 | 3000 | 0.58913 | 3000.5891 | 2443.6243 | 0 | 148.719
0 | 32.3641 | 0 | 0 | 0 | 0 | 20.1359 | 52.5 | 307.2901 | 3000 | 35.9802 | 3035.9802 | 2570.9416 | 0 | 148.0605
0 | 53.3295 | 0 | 0 | 0 | 0 | -0.82949 | 52.5 | 306.4606 | 3000 | 0 | 3000 | 2388.9609 | 0 | 137.1025
0 | 46.4153 | 0 | 0 | 0 | 0 | 6.0847 | 52.5 | 312.5453 | 3000 | 10.8725 | 3010.8725 | 2713.4641 | 0 | 155.6714
0 | 45.0649 | 0 | 0 | 0 | 0 | 7.4351 | 52.5 | 319.9803 | 3000 | 13.2855 | 3013.2855 | 2694.2474 | 0 | 159.2031
0 | 47.6501 | 0 | 0 | 0 | 0 | 4.8499 | 52.5 | 324.8302 | 3000 | 8.6661 | 3008.6661 | 2868.073 | 0 | 176.071
0 | 37.4655 | 0 | 0 | 0 | 0 | 15.0345 | 52.5 | 339.8646 | 3000 | 26.8646 | 3026.8646 | 3021.4572 | 0 | 194.1891
0 | 45.3056 | 0 | 0 | 0 | 0 | -45.3056 | 0 | 294.559 | 0 | 0 | 0 | 0 | 0 | 0
0 | 32.4877 | 0 | 0 | 0 | 0 | -32.4877 | 0 | 262.0713 | 0 | 0 | 0 | 0 | 0 | 0
0 | 27.2338 | 0 | 0 | 0 | 0 | 25.2662 | 52.5 | 287.3375 | 3000 | 45.1473 | 3045.1473 | 3045.1473 | 0 | 201.2842
0 | 31.8474 | 0 | 0 | 0 | 0 | 20.6526 | 52.5 | 307.9901 | 3000 | 36.9034 | 3036.9034 | 3036.9034 | 0 | 191.5982
0 | 26.6374 | 0 | 0 | 0 | 0 | 25.8626 | 52.5 | 333.8527 | 3000 | 46.213 | 3046.213 | 3046.213 | 0 | 186.0932
0 | 39.1157 | 0 | 0 | 0 | 0 | 13.3843 | 52.5 | 347.237 | 3000 | 23.916 | 3023.916 | 3023.916 | 0 | 170.9722
0 | 36.2639 | 0 | 0 | 0 | 0 | 16.2361 | 52.5 | 363.473 | 3000 | 29.0117 | 3029.0117 | 3029.0117 | 0 | 154.7219
0 | 30.9167 | 0 | 0 | 0 | 0 | 21.5833 | 52.5 | 385.0563 | 3000 | 38.5664 | 3038.5664 | 3038.5664 | 0 | 154.9669
0 | 26.7791 | 0 | 0 | 0 | 0 | 25.7209 | 52.5 | 410.7771 | 3000 | 45.9597 | 3045.9597 | 3045.9597 | 0 | 152.2371
0 | 31.4124 | 0 | 0 | 0 | 0 | 21.0876 | 52.5 | 431.8647 | 3000 | 37.6807 | 3037.6807 | 3037.6807 | 0 | 154.9217
0 | 23.3627 | 0 | 0 | 0 | 0 | 29.1373 | 52.5 | 461.002 | 3000 | 52.0644 | 3052.0644 | 3052.0644 | 0 | 149.5512
0 | 229.5452 | 0 | 0 | 0 | 0 | -177.0452 | 52.5 | 283.9567 | 3000 | 0 | 3000 | 3000 | 0 | 150
0 | 228.413 | 0 | 0 | 0 | 0 | -175.913 | 52.5 | 108.0437 | 3000 | 0 | 3000 | 2983.7777 | 0 | 173.6559
0 | 56.0616 | 0 | 0 | 0 | 0 | -3.5616 | 52.5 | 104.4822 | 3000 | 0 | 3000 | 2951.3332 | 0 | 190.7742
0 | 63.4485 | 0 | 0 | 0 | 0 | -10.9485 | 52.5 | 93.5337 | 3000 | 0 | 3000 | 2843.1847 | 0 | 183.0158
0 | 78.7215 | 0 | 0 | 0 | 0 | -26.2215 | 52.5 | 67.3122 | 3000 | 0 | 3000 | 2729.6287 | 0 | 189.0541
0 | 56.0951 | 0 | 0 | 0 | 0 | -49.0925 | 7.0026 | 18.2197 | 400.1495 | 0 | 400.1495 | 0 | 0 | 0
0 | 25.6008 | 0 | 0 | 0 | 0 | -18.2197 | 7.3811 | 0 | 421.7792 | 0 | 421.7792 | 0 | 0 | 0
0 | 44.2024 | 0 | 0 | 0 | 0 | 8.2976 | 52.5 | 8.2976 | 3000 | 14.8268 | 3014.8268 | 2690.3812 | 0 | 169.0905
0 | 49.1345 | 0 | 0 | 0 | 0 | 3.3655 | 52.5 | 11.6632 | 3000 | 6.0138 | 3006.0138 | 2784.3093 | 0 | 174.2699
0 | 35.1411 | 0 | 0 | 0 | 0 | 17.3589 | 52.5 | 29.0221 | 3000 | 31.0181 | 3031.0181 | 2863.3879 | 0 | 177.9309
0 | 47.685 | 0 | 0 | 0 | 0 | 4.815 | 52.5 | 33.837 | 3000 | 8.6037 | 3008.6037 | 2932.8997 | 0 | 180.4613
0 | 38.8063 | 0 | 0 | 0 | 0 | 13.6937 | 52.5 | 47.5307 | 3000 | 24.4688 | 3024.4688 | 2981.2094 | 0 | 184.3878
0 | 27.5434 | 0 | 0 | 0 | 0 | 24.9566 | 52.5 | 72.4874 | 3000 | 44.5942 | 3044.5942 | 3044.5942 | 0 | 189.4955
0 | 50.9555 | 0 | 0 | 0 | 0 | 1.5445 | 52.5 | 74.0319 | 3000 | 2.7598 | 3002.7598 | 3002.7598 | 0 | 187.3722
0 | 27.4479 | 0 | 0 | 0 | 0 | 25.0521 | 52.5 | 99.084 | 3000 | 44.7648 | 3044.7648 | 3044.7648 | 0 | 205.0649
0 | 29.5776 | 0 | 0 | 0 | 0 | 22.9224 | 52.5 | 122.0063 | 3000 | 40.9592 | 3040.9592 | 3040.9592 | 0 | 197.6623
0 | 30.2139 | 0 | 0 | 0 | 0 | 22.2861 | 52.5 | 144.2924 | 3000 | 39.8223 | 3039.8223 | 3039.8223 | 0 | 175.0938
0 | 29.9906 | 0 | 0 | 0 | 0 | 22.5094 | 52.5 | 166.8018 | 3000 | 40.2212 | 3040.2212 | 3040.2212 | 0 | 170.5564
0 | 27.7837 | 0 | 0 | 0 | 0 | 24.7163 | 52.5 | 191.5181 | 3000 | 44.1648 | 3044.1648 | 3044.1648 | 0 | 169.286
0 | 37.0385 | 0 | 0 | 0 | 0 | 15.4615 | 52.5 | 206.9796 | 3000 | 27.6276 | 3027.6276 | 3027.6276 | 0 | 157.4366
0 | 31.7854 | 0 | 0 | 0 | 0 | 20.7146 | 52.5 | 227.6942 | 3000 | 37.0143 | 3037.0143 | 3037.0143 | 0 | 165.6084
0 | 32.7945 | 0 | 0 | 0 | 0 | 19.7055 | 52.5 | 247.3997 | 3000 | 35.2111 | 3035.2111 | 3035.2111 | 0 | 158.6201
0 | 28.146 | 0 | 0 | 0 | 0 | 24.354 | 52.5 | 271.7537 | 3000 | 43.5173 | 3043.5173 | 3043.5173 | 0 | 159.4803
0 | 28.7611 | 0 | 0 | 0 | 0 | 23.7389 | 52.5 | 295.4926 | 3000 | 42.4183 | 3042.4183 | 3042.4183 | 0 | 154.2506
0 | 29.2497 | 0 | 0 | 0 | 0 | 23.2503 | 52.5 | 318.7429 | 3000 | 41.5452 | 3041.5452 | 3041.5452 | 0 | 152.351
0 | 22.5559 | 0 | 0 | 0 | 0 | 29.9441 | 52.5 | 348.687 | 3000 | 53.5061 | 3053.5061 | 3048.0986 | 0 | 164.7802
0 | 48.2746 | 0 | 0 | 0 | 0 | 4.2254 | 52.5 | 352.9124 | 3000 | 7.5503 | 3007.5503 | 2958.8834 | 0 | 187.3565
0 | 45.3621 | 0 | 0 | 0 | 0 | 7.1379 | 52.5 | 360.0503 | 3000 | 12.7545 | 3012.7545 | 2882.9763 | 0 | 190.2764
0 | 247.1829 | 0 | 0 | 0 | 0 | -194.6829 | 52.5 | 165.3674 | 3000 | 0 | 3000 | 2551.1837 | 0 | 163.7605
0 | 39.6731 | 0 | 0 | 0 | 0 | 12.8269 | 52.5 | 178.1943 | 3000 | 22.9199 | 3022.9199 | 2579.511 | 0 | 165.1403
0 | 49.1693 | 0 | 0 | 0 | 0 | 3.3307 | 52.5 | 181.525 | 3000 | 5.9515 | 3005.9515 | 2622.0243 | 0 | 157.8459
0 | 42.246 | 0 | 0 | 0 | 0 | 10.254 | 52.5 | 191.779 | 3000 | 18.3225 | 3018.3225 | 2526.2468 | 0 | 138.6909
0 | 51.8545 | 0 | 0 | 0 | 0 | 0.64548 | 52.5 | 192.4245 | 3000 | 1.1534 | 3001.1534 | 2384.7069 | 0 | 135.9283
0 | 40.4271 | 0 | 0 | 0 | 0 | 12.0729 | 52.5 | 204.4974 | 3000 | 21.5727 | 3021.5727 | 2459.2005 | 0 | 130.4114
0 | 46.4218 | 0 | 0 | 0 | 0 | 6.0782 | 52.5 | 210.5756 | 3000 | 10.8609 | 3010.8609 | 2729.6748 | 0 | 147.4024
0 | 36.7641 | 0 | 0 | 0 | 0 | 15.7359 | 52.5 | 226.3115 | 3000 | 28.1179 | 3028.1179 | 2947.0065 | 0 | 166.7122
0 | 35.9406 | 0 | 0 | 0 | 0 | 16.5594 | 52.5 | 242.8709 | 3000 | 29.5895 | 3029.5895 | 3024.1821 | 0 | 176.2191
0 | 49.8903 | 0 | 0 | 0 | 0 | 2.6097 | 52.5 | 245.4805 | 3000 | 4.6631 | 3004.6631 | 3004.6631 | 0 | 177.1249
0 | 26.8571 | 0 | 0 | 0 | 0 | 25.6429 | 52.5 | 271.1235 | 3000 | 45.8205 | 3045.8205 | 3045.8205 | 0 | 187.2875
0 | 24.5774 | 0 | 0 | 0 | 0 | 27.9226 | 52.5 | 299.046 | 3000 | 49.8939 | 3049.8939 | 3049.8939 | 0 | 174.7589
0 | 33.095 | 0 | 0 | 0 | 0 | 19.405 | 52.5 | 318.451 | 3000 | 34.6741 | 3034.6741 | 3034.6741 | 0 | 166.9071
0 | 24.9176 | 0 | 0 | 0 | 0 | 27.5824 | 52.5 | 346.0334 | 3000 | 49.2861 | 3049.2861 | 3049.2861 | 0 | 171.4614
0 | 33.6072 | 0 | 0 | 0 | 0 | 18.8928 | 52.5 | 364.9263 | 3000 | 33.759 | 3033.759 | 3033.759 | 0 | 164.1264
0 | 33.1101 | 0 | 0 | 0 | 0 | 19.3899 | 52.5 | 384.3162 | 3000 | 34.6472 | 3034.6472 | 3034.6472 | 0 | 148.6977
0 | 35.8479 | 0 | 0 | 0 | 0 | 16.6521 | 52.5 | 400.9683 | 3000 | 29.7551 | 3029.7551 | 3029.7551 | 0 | 166.6365
0 | 36.0878 | 0 | 0 | 0 | 0 | 16.4122 | 52.5 | 417.3805 | 3000 | 29.3264 | 3029.3264 | 3029.3264 | 0 | 151.4663
0 | 30.9532 | 0 | 0 | 0 | 0 | 21.5468 | 52.5 | 438.9273 | 3000 | 38.5012 | 3038.5012 | 3038.5012 | 0 | 163.1675
0 | 34.6234 | 0 | 0 | 0 | 0 | 17.8766 | 52.5 | 456.8039 | 3000 | 31.9431 | 3031.9431 | 3031.9431 | 0 | 166.7569
0 | 29.7346 | 0 | 0 | 0 | 0 | 22.7654 | 52.5 | 479.5692 | 3000 | 40.6787 | 3040.6787 | 3040.6787 | 0 | 149.9055
0 | 24.7515 | 0 | 0 | 0 | 0 | 27.7485 | 52.5 | 507.3177 | 3000 | 49.5828 | 3049.5828 | 3027.9531 | 0 | 187.0972
0 | 40.5854 | 0 | 0 | 0 | 0 | 11.9146 | 52.5 | 519.2323 | 3000 | 21.2898 | 3021.2898 | 2821.2151 | 0 | 169.4986
0 | 41.1165 | 0 | 0 | 0 | 0 | -33.3569 | 7.7597 | 485.8754 | 443.4089 | 0 | 443.4089 | 0 | 0 | 0
0 | 51.0804 | 0 | 0 | 0 | 0 | -43.3207 | 7.7597 | 442.5547 | 443.4089 | 0 | 443.4089 | 0 | 0 | 0
0 | 49.9506 | 0 | 0 | 0 | 0 | 2.5494 | 52.5 | 445.104 | 3000 | 4.5554 | 3004.5554 | 2231.2936 | 0 | 140.5715
0 | 51.363 | 0 | 0 | 0 | 0 | 1.137 | 52.5 | 446.241 | 3000 | 2.0316 | 3002.0316 | 2401.8074 | 0 | 137.6476
0 | 30.4656 | 0 | 0 | 0 | 0 | 22.0344 | 52.5 | 468.2754 | 3000 | 39.3725 | 3039.3725 | 2239.0736 | 0 | 126.4853
0 | 40.9262 | 0 | 0 | 0 | 0 | 11.5738 | 52.5 | 479.8491 | 3000 | 20.6808 | 3020.6808 | 2182.5299 | 0 | 119.8209
0 | 41.0126 | 0 | 0 | 0 | 0 | 11.4874 | 52.5 | 491.3365 | 3000 | 20.5264 | 3020.5264 | 2404.08 | 0 | 131.5513
0 | 47.2654 | 0 | 0 | 0 | 0 | 5.2346 | 52.5 | 496.5711 | 3000 | 9.3535 | 3009.3535 | 2782.2417 | 0 | 152.7451
0 | 35.2574 | 0 | 0 | 0 | 0 | 17.2426 | 52.5 | 513.8137 | 3000 | 30.8103 | 3030.8103 | 2949.6989 | 0 | 159.5787
0 | 245.605 | 0 | 0 | 0 | 0 | -193.105 | 52.5 | 320.7088 | 3000 | 0 | 3000 | 2994.5926 | 0 | 173.896
0 | 39.9277 | 0 | 0 | 0 | 0 | 12.5723 | 52.5 | 333.2811 | 3000 | 22.4651 | 3022.4651 | 3022.4651 | 0 | 191.8963
0 | 26.4766 | 0 | 0 | 0 | 0 | 26.0234 | 52.5 | 359.3045 | 3000 | 46.5004 | 3046.5004 | 3046.5004 | 0 | 199.363
0 | 35.5327 | 0 | 0 | 0 | 0 | 16.9673 | 52.5 | 376.2719 | 3000 | 30.3183 | 3030.3183 | 3030.3183 | 0 | 178.91
0 | 31.4867 | 0 | 0 | 0 | 0 | 21.0133 | 52.5 | 397.2852 | 3000 | 37.548 | 3037.548 | 3037.548 | 0 | 168.7965
0 | 32.1143 | 0 | 0 | 0 | 0 | 20.3857 | 52.5 | 417.6708 | 3000 | 36.4265 | 3036.4265 | 3036.4265 | 0 | 164.6958
0 | 21.2597 | 0 | 0 | 0 | 0 | 31.2403 | 52.5 | 448.9111 | 3000 | 55.8222 | 3055.8222 | 3055.8222 | 0 | 156.7637
0 | 28.4663 | 0 | 0 | 0 | 0 | 24.0337 | 52.5 | 472.9448 | 3000 | 42.945 | 3042.945 | 3042.945 | 0 | 152.1472
0 | 34.9075 | 0 | 0 | 0 | 0 | 17.5925 | 52.5 | 490.5372 | 3000 | 31.4354 | 3031.4354 | 3031.4354 | 0 | 148.5403
0 | 228.4701 | 0 | 0 | 0 | 0 | -175.9701 | 52.5 | 314.5671 | 3000 | 0 | 3000 | 3000 | 0 | 150
0 | 40.7128 | 0 | 0 | 0 | 0 | 11.7872 | 52.5 | 326.3544 | 3000 | 21.0622 | 3021.0622 | 3021.0622 | 0 | 143.1983
0 | 30.0395 | 0 | 0 | 0 | 0 | 22.4605 | 52.5 | 348.8148 | 3000 | 40.1339 | 3040.1339 | 3040.1339 | 0 | 114.4306
0 | 30.7758 | 0 | 0 | 0 | 0 | 21.7242 | 52.5 | 370.539 | 3000 | 38.8182 | 3038.8182 | 3038.8182 | 0 | 120.945
0 | 36.511 | 0 | 0 | 0 | 0 | 15.989 | 52.5 | 386.528 | 3000 | 28.5702 | 3028.5702 | 2985.3108 | 0 | 155.2362
0 | 46.9455 | 0 | 0 | 0 | 0 | 5.5545 | 52.5 | 392.0825 | 3000 | 9.9251 | 3009.9251 | 2853.1098 | 0 | 133.2402
0 | 51.2527 | 0 | 0 | 0 | 0 | 1.2473 | 52.5 | 393.3298 | 3000 | 2.2287 | 3002.2287 | 2823.7837 | 0 | 145.4813
0 | 50.2248 | 0 | 0 | 0 | 0 | 2.2752 | 52.5 | 395.605 | 3000 | 4.0655 | 3004.0655 | 2587.6937 | 0 | 171.7194
0 | 31.1369 | 0 | 0 | 0 | 0 | 21.3631 | 52.5 | 416.968 | 3000 | 38.173 | 3038.173 | 2513.6527 | 0 | 162.7841
0 | 40.5859 | 0 | 0 | 0 | 0 | 11.9141 | 52.5 | 428.8822 | 3000 | 21.289 | 3021.289 | 2642.7692 | 0 | 151.1664
0 | 39.7755 | 0 | 0 | 0 | 0 | 12.7245 | 52.5 | 441.6067 | 3000 | 22.737 | 3022.737 | 2676.6618 | 0 | 145.8781
0 | 39.2139 | 0 | 0 | 0 | 0 | 13.2861 | 52.5 | 454.8928 | 3000 | 23.7405 | 3023.7405 | 2769.5915 | 0 | 153.7123
0 | 48.9566 | 0 | 0 | 0 | 0 | 3.5434 | 52.5 | 458.4362 | 3000 | 6.3315 | 3006.3315 | 2881.9607 | 0 | 149.862
0 | 33.8662 | 0 | 0 | 0 | 0 | 18.6338 | 52.5 | 477.07 | 3000 | 33.2961 | 3033.2961 | 2681.8135 | 0 | 134.3589
0 | 28.7317 | 0 | 0 | 0 | 0 | 23.7683 | 52.5 | 500.8383 | 3000 | 42.4708 | 3042.4708 | 2923.5075 | 0 | 166.4938
0 | 39.1039 | 0 | 0 | 0 | 0 | 13.3961 | 52.5 | 514.2344 | 3000 | 23.937 | 3023.937 | 3018.5296 | 0 | 173.0523
0 | 41.9399 | 0 | 0 | 0 | 0 | 10.5601 | 52.5 | 524.7945 | 3000 | 18.8694 | 3018.8694 | 3018.8694 | 0 | 164.2265
0 | 27.7553 | 0 | 0 | 0 | 0 | 24.7447 | 52.5 | 549.5392 | 3000 | 44.2155 | 3044.2155 | 3044.2155 | 0 | 197.5696
0 | 35.3577 | 0 | 0 | 0 | 0 | 17.1423 | 52.5 | 566.6815 | 3000 | 30.631 | 3030.631 | 3030.631 | 0 | 181.8379
0 | 29.7552 | 0 | 0 | 0 | 0 | 22.7448 | 52.5 | 589.4262 | 3000 | 40.6419 | 3040.6419 | 3040.6419 | 0 | 191.5604
0 | 26.9766 | 0 | 0 | 0 | 0 | -26.9766 | 0 | 562.4497 | 0 | 0 | 0 | 0 | 0 | 0
0 | 36.4314 | 0 | 0 | 0 | 0 | -36.4314 | 0 | 526.0182 | 0 | 0 | 0 | 0 | 0 | 0
0 | 27.2436 | 0 | 0 | 0 | 0 | -27.2436 | 0 | 498.7746 | 0 | 0 | 0 | 0 | 0 | 0
0 | 32.0459 | 0 | 0 | 0 | 0 | -32.0459 | 0 | 466.7287 | 0 | 0 | 0 | 0 | 0 | 0
0 | 27.9961 | 0 | 0 | 0 | 0 | -27.9961 | 0 | 438.7326 | 0 | 0 | 0 | 0 | 0 | 0
0 | 40.4501 | 0 | 0 | 0 | 0 | -40.4501 | 0 | 398.2825 | 0 | 0 | 0 | 0 | 0 | 0
0 | 35.8916 | 0 | 0 | 0 | 0 | 16.6084 | 52.5 | 414.8909 | 3000 | 29.6769 | 3029.6769 | 3029.6769 | 0 | 210.2596
0 | 29.9987 | 0 | 0 | 0 | 0 | 22.5013 | 52.5 | 437.3922 | 3000 | 40.2069 | 3040.2069 | 3040.2069 | 0 | 182.23
0 | 30.6296 | 0 | 0 | 0 | 0 | 21.8704 | 52.5 | 459.2626 | 3000 | 39.0795 | 3039.0795 | 3028.2647 | 0 | 172.2477
0 | 41.4976 | 0 | 0 | 0 | 0 | 11.0024 | 52.5 | 470.265 | 3000 | 19.6599 | 3019.6599 | 2970.993 | 0 | 127.9012
0 | 49.8529 | 0 | 0 | 0 | 0 | 2.6471 | 52.5 | 472.9121 | 3000 | 4.73 | 3004.73 | 2826.2849 | 0 | 160.533
0 | 45.0688 | 0 | 0 | 0 | 0 | 7.4312 | 52.5 | 480.3433 | 3000 | 13.2786 | 3013.2786 | 2775.3519 | 0 | 159.0277
0 | 49.7324 | 0 | 0 | 0 | 0 | 2.7676 | 52.5 | 483.1109 | 3000 | 4.9453 | 3004.9453 | 2826.5003 | 0 | 161.6193
0 | 49.6807 | 0 | 0 | 0 | 0 | 2.8193 | 52.5 | 485.9302 | 3000 | 5.0378 | 3005.0378 | 2891.4818 | 0 | 165.5663
0 | 37.1697 | 0 | 0 | 0 | 0 | 15.3303 | 52.5 | 501.2605 | 3000 | 27.3932 | 3027.3932 | 2919.2447 | 0 | 183.0366
0 | 33.8197 | 0 | 0 | 0 | 0 | 18.6803 | 52.5 | 519.9408 | 3000 | 33.3792 | 3033.3792 | 2925.2307 | 0 | 146.2615
0 | 44.2521 | 0 | 0 | 0 | 0 | 8.2479 | 52.5 | 528.1888 | 3000 | 14.738 | 3014.738 | 2901.1821 | 0 | 142.0129
0 | 49.9008 | 0 | 0 | 0 | 0 | 2.5992 | 52.5 | 530.7879 | 3000 | 4.6443 | 3004.6443 | 2939.7552 | 0 | 142.6075
0 | 50.9619 | 0 | 0 | 0 | 0 | 1.5381 | 52.5 | 532.3261 | 3000 | 2.7485 | 3002.7485 | 2970.3039 | 0 | 145.3964
0 | 41.3734 | 0 | 0 | 0 | 0 | 11.1266 | 52.5 | 543.4527 | 3000 | 19.8818 | 3019.8818 | 3014.4744 | 0 | 157.8379
0 | 32.7823 | 0 | 0 | 0 | 0 | 19.7177 | 52.5 | 563.1704 | 3000 | 35.2328 | 3035.2328 | 3035.2328 | 0 | 171.1871
0 | 34.174 | 0 | 0 | 0 | 0 | 18.326 | 52.5 | 581.4964 | 3000 | 32.7462 | 3032.7462 | 3032.7462 | 0 | 169.5912
0 | 236.8405 | 0 | 0 | 0 | 0 | -184.3405 | 52.5 | 397.1559 | 3000 | 0 | 3000 | 3000 | 0 | 153
0 | 29.2427 | 0 | 0 | 0 | 0 | 23.2573 | 52.5 | 420.4132 | 3000 | 41.5577 | 3041.5577 | 3041.5577 | 0 | 159.3776
0 | 21.9321 | 0 | 0 | 0 | 0 | 30.5679 | 52.5 | 450.9811 | 3000 | 54.6207 | 3054.6207 | 3054.6207 | 0 | 166.8434
0 | 39.499 | 0 | 0 | 0 | 0 | 13.001 | 52.5 | 463.9821 | 3000 | 23.2311 | 3023.2311 | 3023.2311 | 0 | 148.0174
0 | 34.751 | 0 | 0 | 0 | 0 | 17.749 | 52.5 | 481.7311 | 3000 | 31.7151 | 3031.7151 | 3031.7151 | 0 | 149.4636
0 | 32.4425 | 0 | 0 | 0 | 0 | 20.0575 | 52.5 | 501.7886 | 3000 | 35.8402 | 3035.8402 | 3035.8402 | 0 | 166.6676
0 | 28.4048 | 0 | 0 | 0 | 0 | 24.0952 | 52.5 | 525.8838 | 3000 | 43.0549 | 3043.0549 | 3043.0549 | 0 | 171.5674
0 | 26.5259 | 0 | 0 | 0 | 0 | 25.9741 | 52.5 | 551.8579 | 3000 | 46.4123 | 3046.4123 | 3046.4123 | 0 | 153.5392
0 | 35.7827 | 0 | 0 | 0 | 0 | 16.7173 | 52.5 | 568.5752 | 3000 | 29.8716 | 3029.8716 | 3029.8716 | 0 | 148.3425
0 | 41.9766 | 0 | 0 | 0 | 0 | 10.5234 | 52.5 | 579.0986 | 3000 | 18.804 | 3018.804 | 3018.804 | 0 | 150.6383
0 | 27.6151 | 0 | 0 | 0 | 0 | 24.8849 | 52.5 | 603.9835 | 3000 | 44.4659 | 3044.4659 | 3012.0214 | 0 | 167.2575
0 | 36.6502 | 0 | 0 | 0 | 0 | 15.8498 | 52.5 | 619.8333 | 3000 | 28.3214 | 3028.3214 | 2925.5803 | 0 | 184.1945
0 | 35.3225 | 0 | 0 | 0 | 0 | 17.1775 | 52.5 | 637.0108 | 3000 | 30.694 | 3030.694 | 2776.545 | 0 | 175.0889
0 | 47.4126 | 0 | 0 | 0 | 0 | 5.0874 | 52.5 | 642.0982 | 3000 | 9.0905 | 3009.0905 | 2392.644 | 0 | 147.9611
0 | 25.4146 | 0 | 0 | 0 | 0 | 27.0854 | 52.5 | 669.1836 | 3000 | 48.398 | 3048.398 | 2475.2109 | 0 | 149.28
0 | 35.024 | 0 | 0 | 0 | 0 | 17.476 | 52.5 | 686.6595 | 3000 | 31.2272 | 3031.2272 | 2539.1515 | 0 | 146.4075
0 | 42.9188 | 0 | 0 | 0 | 0 | 9.5812 | 52.5 | 696.2407 | 3000 | 17.1203 | 3017.1203 | 2573.7115 | 0 | 141.4254
0 | 41.1662 | 0 | 0 | 0 | 0 | 11.3338 | 52.5 | 707.5746 | 3000 | 20.2521 | 3020.2521 | 2766.1031 | 0 | 148.5121
0 | 36.5219 | 0 | 0 | 0 | 0 | 15.9781 | 52.5 | 723.5527 | 3000 | 28.5508 | 3028.5508 | 2725.735 | 0 | 141.4656
0 | 44.3664 | 0 | 0 | 0 | 0 | 8.1336 | 52.5 | 731.6863 | 3000 | 14.5336 | 3014.5336 | 2900.9777 | 0 | 151.1699
0 | 53.8893 | 0 | 0 | 0 | 0 | -1.3893 | 52.5 | 730.2969 | 3000 | 0 | 3000 | 2843.1847 | 0 | 156.6595
0 | 39.1573 | 0 | 0 | 0 | 0 | 13.3427 | 52.5 | 743.6397 | 3000 | 23.8417 | 3023.8417 | 3013.0268 | 0 | 184.6383
0 | 54.2402 | 0 | 0 | 0 | 0 | -1.7402 | 52.5 | 741.8995 | 3000 | 0 | 3000 | 3000 | 0 | 195.87
0 | 33.0628 | 0 | 0 | 0 | 0 | -33.0628 | 0 | 708.8367 | 0 | 0 | 0 | 0 | 0 | 0
0 | 27.0138 | 0 | 0 | 0 | 0 | 25.4862 | 52.5 | 734.3229 | 3000 | 45.5404 | 3045.5404 | 3045.5404 | 0 | 198.1429
0 | 38.4173 | 0 | 0 | 0 | 0 | 14.0827 | 52.5 | 748.4056 | 3000 | 25.1639 | 3025.1639 | 3025.1639 | 0 | 190.3131
0 | 230.9903 | 0 | 0 | 0 | 0 | -178.4903 | 52.5 | 569.9153 | 3000 | 0 | 3000 | 3000 | 0 | 187.83
0 | 34.4672 | 0 | 0 | 0 | 0 | 18.0328 | 52.5 | 587.9481 | 3000 | 32.2222 | 3032.2222 | 3032.2222 | 0 | 178.9314
0 | 37.8145 | 0 | 0 | 0 | 0 | 14.6855 | 52.5 | 602.6335 | 3000 | 26.241 | 3026.241 | 3026.241 | 0 | 169.409
0 | 29.8473 | 0 | 0 | 0 | 0 | 22.6527 | 52.5 | 625.2862 | 3000 | 40.4773 | 3040.4773 | 3040.4773 | 0 | 164.0946
0 | 28.2225 | 0 | 0 | 0 | 0 | 24.2775 | 52.5 | 649.5637 | 3000 | 43.3807 | 3043.3807 | 3043.3807 | 0 | 157.9819
0 | 30.3241 | 0 | 0 | 0 | 0 | 22.1759 | 52.5 | 671.7395 | 3000 | 39.6253 | 3039.6253 | 3039.6253 | 0 | 151.9813
0 | 36.6134 | 0 | 0 | 0 | 0 | 15.8866 | 52.5 | 687.6262 | 3000 | 28.3873 | 3028.3873 | 3028.3873 | 0 | 145.1203
0 | 23.2582 | 0 | 0 | 0 | 0 | 29.2418 | 52.5 | 716.868 | 3000 | 52.2512 | 3052.2512 | 3052.2512 | 0 | 156.5805
0 | 31.2376 | 0 | 0 | 0 | 0 | 21.2624 | 52.5 | 738.1304 | 3000 | 37.9931 | 3037.9931 | 3016.3634 | 0 | 186.5017
0 | 48.2551 | 0 | 0 | 0 | 0 | 4.2449 | 52.5 | 742.3753 | 3000 | 7.5851 | 3007.5851 | 2931.8811 | 0 | 196.5826
0 | 42.4688 | 0 | 0 | 0 | 0 | 10.0312 | 52.5 | 752.4065 | 3000 | 17.9245 | 3017.9245 | 2790.8126 | 0 | 185.2262
0 | 50.5803 | 0 | 0 | 0 | 0 | 1.9197 | 52.5 | 754.3262 | 3000 | 3.4303 | 3003.4303 | 2743.8739 | 0 | 172.9189
0 | 42.4784 | 0 | 0 | 0 | 0 | 10.0216 | 52.5 | 764.3479 | 3000 | 17.9073 | 3017.9073 | 2606.943 | 0 | 157.7722
0 | 40.4167 | 0 | 0 | 0 | 0 | 12.0833 | 52.5 | 776.4311 | 3000 | 21.5912 | 3021.5912 | 2551.1452 | 0 | 151.385
0 | 52.1221 | 0 | 0 | 0 | 0 | 0.37792 | 52.5 | 776.8091 | 3000 | 0.6753 | 3000.6753 | 2416.6734 | 0 | 142.1487
0 | 49.6931 | 0 | 0 | 0 | 0 | 2.8069 | 52.5 | 779.616 | 3000 | 5.0156 | 3005.0156 | 2637.3107 | 0 | 155.153
0 | 41.3322 | 0 | 0 | 0 | 0 | 11.1678 | 52.5 | 790.7838 | 3000 | 19.9553 | 3019.9553 | 2846.9177 | 0 | 166.6016
0 | 47.027 | 0 | 0 | 0 | 0 | 5.473 | 52.5 | 796.2567 | 3000 | 9.7795 | 3009.7795 | 2896.2236 | 0 | 168.5312
0 | 32.322 | 0 | 0 | 0 | 0 | 20.178 | 52.5 | 816.4348 | 3000 | 36.0554 | 3036.0554 | 2998.2035 | 0 | 172.0069
0 | 57.9718 | 0 | 0 | 0 | 0 | -5.4718 | 52.5 | 810.963 | 3000 | 0 | 3000 | 2994.5926 | 0 | 170.6918
0 | 44.5247 | 0 | 0 | 0 | 0 | 7.9753 | 52.5 | 818.9383 | 3000 | 14.2509 | 3014.2509 | 3014.2509 | 0 | 177.9011
0 | 28.7272 | 0 | 0 | 0 | 0 | 23.7728 | 52.5 | 842.7111 | 3000 | 42.4788 | 3042.4788 | 3042.4788 | 0 | 197.7611
0 | 34.0732 | 0 | 0 | 0 | 0 | 18.4268 | 52.5 | 861.1379 | 3000 | 32.9262 | 3032.9262 | 3032.9262 | 0 | 190.2555
0 | 35.8907 | 0 | 0 | 0 | 0 | 16.6093 | 52.5 | 877.7472 | 3000 | 29.6786 | 3029.6786 | 3029.6786 | 0 | 166.3294
0 | 45.1241 | 0 | 0 | 0 | 0 | 7.3759 | 52.5 | 885.123 | 3000 | 13.1797 | 3013.1797 | 3013.1797 | 0 | 164.5196
0 | 31.2926 | 0 | 0 | 0 | 0 | 21.2074 | 52.5 | 906.3305 | 3000 | 37.8949 | 3037.8949 | 3037.8949 | 0 | 159.1857
0 | 27.6197 | 0 | 0 | 0 | 0 | 24.8803 | 52.5 | 931.2107 | 3000 | 44.4577 | 3044.4577 | 3044.4577 | 0 | 151.0051
0 | 26.0867 | 0 | 0 | 0 | 0 | 26.4133 | 52.5 | 957.6241 | 3000 | 47.1971 | 3047.1971 | 3047.1971 | 0 | 156.6259
0 | 27.1478 | 0 | 0 | 0 | 0 | 25.3522 | 52.5 | 982.9763 | 3000 | 45.3011 | 3045.3011 | 3045.3011 | 0 | 154.0922
0 | 30.1167 | 0 | 0 | 0 | 0 | 22.3833 | 52.5 | 1005.3596 | 3000 | 39.996 | 3039.996 | 3039.996 | 0 | 159.2958
0 | 31.1995 | 0 | 0 | 0 | 0 | 21.3005 | 52.5 | 1026.6601 | 3000 | 38.0611 | 3038.0611 | 3038.0611 | 0 | 151.2954
0 | 33.4659 | 0 | 0 | 0 | 0 | 19.0341 | 52.5 | 1045.6942 | 3000 | 34.0115 | 3034.0115 | 3034.0115 | 0 | 136.5305
0 | 30.7657 | 0 | 0 | 0 | 0 | 21.7343 | 52.5 | 1067.4285 | 3000 | 38.8363 | 3038.8363 | 3017.2066 | 0 | 158.1016
0 | 250.9535 | 0 | 0 | 0 | 0 | -198.4535 | 52.5 | 868.975 | 3000 | 0 | 3000 | 2935.1109 | 0 | 173.6412
0 | 28.0395 | 0 | 0 | 0 | 0 | -28.0395 | 0 | 840.9356 | 0 | 0 | 0 | 0 | 167.6302 | 0
0 | 31.5817 | 0 | 0 | 0 | 0 | 20.9183 | 52.5 | 861.8539 | 3000 | 37.3782 | 3037.3782 | 2799.4515 | 0 | 181.9643
0 | 36.6513 | 0 | 0 | 0 | 0 | 15.8487 | 52.5 | 877.7026 | 3000 | 28.3195 | 3028.3195 | 2898.5413 | 0 | 174.6951
0 | 35.3682 | 0 | 0 | 0 | 0 | 17.1318 | 52.5 | 894.8343 | 3000 | 30.6122 | 3030.6122 | 2911.6488 | 0 | 174.4369
0 | 50.0977 | 0 | 0 | 0 | 0 | 2.4023 | 52.5 | 897.2367 | 3000 | 4.2927 | 3004.2927 | 2815.0328 | 0 | 167.7478
0 | 89.7848 | 0 | 0 | 0 | 0 | -37.2848 | 52.5 | 859.9519 | 3000 | 0 | 3000 | 2713.4065 | 0 | 161.1221
0 | 58.7852 | 0 | 0 | 0 | 0 | -6.2852 | 52.5 | 853.6666 | 3000 | 0 | 3000 | 2534.9614 | 0 | 143.3014
0 | 52.0456 | 0 | 0 | 0 | 0 | 0.45437 | 52.5 | 854.121 | 3000 | 0.8119 | 3000.8119 | 2681.7738 | 0 | 151.6007
0 | 46.3781 | 0 | 0 | 0 | 0 | 6.1219 | 52.5 | 860.2429 | 3000 | 10.939 | 3010.939 | 2843.3088 | 0 | 161.3578
0 | 53.9843 | 0 | 0 | 0 | 0 | -1.4843 | 52.5 | 858.7586 | 3000 | 0 | 3000 | 2978.3703 | 0 | 175.9025
0 | 40.5227 | 0 | 0 | 0 | 0 | 11.9773 | 52.5 | 870.7359 | 3000 | 21.4019 | 3021.4019 | 3021.4019 | 0 | 166.4792
0 | 26.3758 | 0 | 0 | 0 | 0 | 26.1242 | 52.5 | 896.8601 | 3000 | 46.6805 | 3046.6805 | 3046.6805 | 0 | 193.0377
0 | 36.3956 | 0 | 0 | 0 | 0 | 16.1044 | 52.5 | 912.9645 | 3000 | 28.7765 | 3028.7765 | 3028.7765 | 0 | 170.7927
0 | 36.4512 | 0 | 0 | 0 | 0 | 16.0488 | 52.5 | 929.0133 | 3000 | 28.677 | 3028.677 | 3028.677 | 0 | 169.6059
0 | 27.3874 | 0 | 0 | 0 | 0 | 25.1126 | 52.5 | 954.1259 | 3000 | 44.8729 | 3044.8729 | 3044.8729 | 0 | 169.1731
0 | 32.8739 | 0 | 0 | 0 | 0 | 19.6261 | 52.5 | 973.752 | 3000 | 35.0693 | 3035.0693 | 3035.0693 | 0 | 159.0376
0 | 23.7499 | 0 | 0 | 0 | 0 | 28.7501 | 52.5 | 1002.5021 | 3000 | 51.3727 | 3051.3727 | 3051.3727 | 0 | 159.007
0 | 30.4381 | 0 | 0 | 0 | 0 | 22.0619 | 52.5 | 1024.5641 | 3000 | 39.4217 | 3039.4217 | 3039.4217 | 0 | 155.3145
0 | 31.2 | 0 | 0 | 0 | 0 | 21.3 | 52.5 | 1045.8641 | 3000 | 38.0603 | 3038.0603 | 3038.0603 | 0 | 161.9286
0 | 31.4411 | 0 | 0 | 0 | 0 | 21.0589 | 52.5 | 1066.9229 | 3000 | 37.6294 | 3037.6294 | 3037.6294 | 0 | 145.8062
0 | 32.5156 | 0 | 0 | 0 | 0 | 19.9844 | 52.5 | 1086.9073 | 3000 | 35.7095 | 3035.7095 | 3035.7095 | 0 | 129.0177
0 | 51.3089 | 0 | 0 | 0 | 0 | 1.1911 | 52.5 | 1088.0985 | 3000 | 2.1284 | 3002.1284 | 3002.1284 | 0 | 127.8606
0 | 88.544 | 0 | 0 | 0 | 0 | -36.044 | 52.5 | 1052.0545 | 3000 | 0 | 3000 | 2983.7777 | 0 | 157.2152
0 | 47.5974 | 0 | 0 | 0 | 0 | 4.9026 | 52.5 | 1056.9571 | 3000 | 8.7604 | 3008.7604 | 2970.9084 | 0 | 181.2551
0 | 47.121 | 0 | 0 | 0 | 0 | 5.379 | 52.5 | 1062.3361 | 3000 | 9.6116 | 3009.6116 | 2912.2779 | 0 | 179.1633
0 | 35.514 | 0 | 0 | 0 | 0 | 16.986 | 52.5 | 1079.3221 | 3000 | 30.3517 | 3030.3517 | 2873.5364 | 0 | 179.2512
0 | 72.281 | 0 | 0 | 0 | 0 | -19.781 | 52.5 | 1059.5412 | 3000 | 0 | 3000 | 2816.1475 | 0 | 170.9683
0 | 125.6339 | 0 | 0 | 0 | 0 | -73.1339 | 52.5 | 986.4072 | 3000 | 0 | 3000 | 2918.8886 | 0 | 175.3085
0 | 115.2543 | 0 | 0 | 0 | 0 | -62.7543 | 52.5 | 923.6529 | 3000 | 0 | 3000 | 2810.7401 | 0 | 168.279
0 | 311.1724 | 0 | 0 | 0 | 0 | -258.6724 | 52.5 | 664.9806 | 3000 | 0 | 3000 | 2686.3693 | 0 | 152.2634
0 | 59.7733 | 0 | 0 | 0 | 0 | -7.2733 | 52.5 | 657.7073 | 3000 | 0 | 3000 | 2675.5545 | 0 | 144.4799
0 | 41.536 | 0 | 0 | 0 | 0 | 10.964 | 52.5 | 668.6713 | 3000 | 19.5913 | 3019.5913 | 2641.0715 | 0 | 143.9384
0 | 46.6149 | 0 | 0 | 0 | 0 | 5.8851 | 52.5 | 674.5564 | 3000 | 10.5159 | 3010.5159 | 2772.5892 | 0 | 155.265
0 | 243.2733 | 0 | 0 | 0 | 0 | -190.7733 | 52.5 | 483.7831 | 3000 | 0 | 3000 | 2983.7777 | 0 | 171.0301
0 | 47.0934 | 0 | 0 | 0 | 0 | 5.4066 | 52.5 | 489.1897 | 3000 | 9.6609 | 3009.6609 | 3009.6609 | 0 | 170.8284
0 | 33.4122 | 0 | 0 | 0 | 0 | 19.0878 | 52.5 | 508.2775 | 3000 | 34.1073 | 3034.1073 | 3034.1073 | 0 | 194.4559
0 | 34.4947 | 0 | 0 | 0 | 0 | 18.0053 | 52.5 | 526.2828 | 3000 | 32.173 | 3032.173 | 3032.173 | 0 | 187.2367
0 | 36.4885 | 0 | 0 | 0 | 0 | 16.0115 | 52.5 | 542.2943 | 3000 | 28.6105 | 3028.6105 | 3028.6105 | 0 | 161.7278
0 | 40.6367 | 0 | 0 | 0 | 0 | 11.8633 | 52.5 | 554.1575 | 3000 | 21.1981 | 3021.1981 | 3021.1981 | 0 | 166.1659
0 | 30.2776 | 0 | 0 | 0 | 0 | 22.2224 | 52.5 | 576.3799 | 3000 | 39.7085 | 3039.7085 | 3039.7085 | 0 | 167.184
0 | 28.8369 | 0 | 0 | 0 | 0 | 23.6631 | 52.5 | 600.043 | 3000 | 42.2828 | 3042.2828 | 3042.2828 | 0 | 137.1157
0 | 22.7174 | 0 | 0 | 0 | 0 | 29.7826 | 52.5 | 629.8256 | 3000 | 53.2175 | 3053.2175 | 3053.2175 | 0 | 165.2096
0 | 35.0865 | 0 | 0 | 0 | 0 | 17.4135 | 52.5 | 647.2391 | 3000 | 31.1157 | 3031.1157 | 3031.1157 | 0 | 160.0429
0 | 21.3687 | 0 | 0 | 0 | 0 | 31.1313 | 52.5 | 678.3704 | 3000 | 55.6274 | 3055.6274 | 3055.6274 | 0 | 152.7814
0 | 27.3437 | 0 | 0 | 0 | 0 | 25.1563 | 52.5 | 703.5267 | 3000 | 44.951 | 3044.951 | 3044.951 | 0 | 155.597
0 | 31.607 | 0 | 0 | 0 | 0 | 20.893 | 52.5 | 724.4197 | 3000 | 37.3329 | 3037.3329 | 3037.3329 | 0 | 141.8434
0 | 45.5664 | 0 | 0 | 0 | 0 | 6.9336 | 52.5 | 731.3533 | 3000 | 12.3895 | 3012.3895 | 2974.5375 | 0 | 151.7014
0 | 118.9999 | 0 | 0 | 0 | 0 | -66.4999 | 52.5 | 664.8535 | 3000 | 0 | 3000 | 2913.4812 | 0 | 174.8089
0 | 94.4256 | 0 | 0 | 0 | 0 | -41.9256 | 52.5 | 622.9278 | 3000 | 0 | 3000 | 2891.8515 | 0 | 169.8095
0 | 62.6047 | 0 | 0 | 0 | 0 | -10.1047 | 52.5 | 612.8231 | 3000 | 0 | 3000 | 2875.6292 | 0 | 165.6075
0 | 101.7567 | 0 | 0 | 0 | 0 | -49.2567 | 52.5 | 563.5663 | 3000 | 0 | 3000 | 2605.258 | 0 | 147.3013
0 | 121.6368 | 0 | 0 | 0 | 0 | -69.1368 | 52.5 | 494.4295 | 3000 | 0 | 3000 | 2718.8139 | 0 | 152.172
0 | 96.0117 | 0 | 0 | 0 | 0 | -43.5117 | 52.5 | 450.9179 | 3000 | 0 | 3000 | 2680.9619 | 0 | 147.2116
0 | 44.2411 | 0 | 0 | 0 | 0 | 8.2589 | 52.5 | 459.1768 | 3000 | 14.7576 | 3014.7576 | 2695.7195 | 0 | 138.56
0 | 29.8314 | 0 | 0 | 0 | 0 | 22.6686 | 52.5 | 481.8454 | 3000 | 40.5057 | 3040.5057 | 2753.9122 | 0 | 156.2845
0 | 50.2543 | 0 | 0 | 0 | 0 | 2.2457 | 52.5 | 484.0911 | 3000 | 4.0129 | 3004.0129 | 2679.5673 | 0 | 151.7707
0 | 49.1579 | 0 | 0 | 0 | 0 | 3.3421 | 52.5 | 487.4332 | 3000 | 5.9719 | 3005.9719 | 2832.9343 | 0 | 160.7407
0 | 31.3393 | 0 | 0 | 0 | 0 | 21.1607 | 52.5 | 508.5939 | 3000 | 37.8113 | 3037.8113 | 3016.1816 | 0 | 173.4304
0 | 32.1315 | 0 | 0 | 0 | 0 | 20.3685 | 52.5 | 528.9624 | 3000 | 36.3959 | 3036.3959 | 3036.3959 | 0 | 167.0018
0 | 30.8179 | 0 | 0 | 0 | 0 | 21.6821 | 52.5 | 550.6445 | 3000 | 38.7429 | 3038.7429 | 3038.7429 | 0 | 187.6424
0 | 29.5241 | 0 | 0 | 0 | 0 | 22.9759 | 52.5 | 573.6204 | 3000 | 41.0549 | 3041.0549 | 3041.0549 | 0 | 179.3918
0 | 17.2187 | 0 | 0 | 0 | 0 | 35.2813 | 52.5 | 608.9017 | 3000 | 63.0429 | 3063.0429 | 3063.0429 | 0 | 168.7737
0 | 27.2581 | 0 | 0 | 0 | 0 | 25.2419 | 52.5 | 634.1436 | 3000 | 45.104 | 3045.104 | 3045.104 | 0 | 168.0288
0 | 232.6561 | 0 | 0 | 0 | 0 | -180.1561 | 52.5 | 453.9874 | 3000 | 0 | 3000 | 3000 | 0 | 164.64
0 | 19.5913 | 0 | 0 | 0 | 0 | 32.9087 | 52.5 | 486.8961 | 3000 | 58.8035 | 3058.8035 | 3058.8035 | 0 | 168.173
0 | 36.3607 | 0 | 0 | 0 | 0 | 16.1393 | 52.5 | 503.0355 | 3000 | 28.8388 | 3028.8388 | 3028.8388 | 0 | 166.1621
0 | 34.9225 | 0 | 0 | 0 | 0 | 17.5775 | 52.5 | 520.613 | 3000 | 31.4087 | 3031.4087 | 3031.4087 | 0 | 166.4243
0 | 33.5008 | 0 | 0 | 0 | 0 | 18.9992 | 52.5 | 539.6122 | 3000 | 33.949 | 3033.949 | 3033.949 | 0 | 165.1075
0 | 30.964 | 0 | 0 | 0 | 0 | 21.536 | 52.5 | 561.1482 | 3000 | 38.482 | 3038.482 | 3038.482 | 0 | 165.7188
0 | 63.6136 | 0 | 0 | 0 | 0 | -11.1136 | 52.5 | 550.0346 | 3000 | 0 | 3000 | 3000 | 0 | 163.95
0 | 139.6332 | 0 | 0 | 0 | 0 | -87.1332 | 52.5 | 462.9014 | 3000 | 0 | 3000 | 2978.3703 | 0 | 153.0882
0 | 110.6568 | 0 | 0 | 0 | 0 | -58.1568 | 52.5 | 404.7445 | 3000 | 0 | 3000 | 2940.5183 | 0 | 138.2044
0 | 49.3994 | 0 | 0 | 0 | 0 | 3.1006 | 52.5 | 407.8452 | 3000 | 5.5404 | 3005.5404 | 2919.0216 | 0 | 147.1187
0 | 71.778 | 0 | 0 | 0 | 0 | -19.278 | 52.5 | 388.5672 | 3000 | 0 | 3000 | 2870.2218 | 0 | 150.4857
0 | 83.1714 | 0 | 0 | 0 | 0 | -30.6714 | 52.5 | 357.8958 | 3000 | 0 | 3000 | 2821.555 | 0 | 150.1632
0 | 48.9312 | 0 | 0 | 0 | 0 | 3.5688 | 52.5 | 361.4646 | 3000 | 6.3769 | 3006.3769 | 2730.5983 | 0 | 143.0833
0 | 44.2842 | 0 | 0 | 0 | 0 | 8.2158 | 52.5 | 369.6804 | 3000 | 14.6806 | 3014.6806 | 2733.4945 | 0 | 136.4014
0 | 42.6178 | 0 | 0 | 0 | 0 | 9.8822 | 52.5 | 379.5626 | 3000 | 17.6582 | 3017.6582 | 2877.0652 | 0 | 119.0242
0 | 46.9758 | 0 | 0 | 0 | 0 | 5.5242 | 52.5 | 385.0868 | 3000 | 9.871 | 3009.871 | 2890.9076 | 0 | 137.3181
0 | 43.2553 | 0 | 0 | 0 | 0 | 9.2447 | 52.5 | 394.3315 | 3000 | 16.519 | 3016.519 | 2913.7779 | 0 | 140.5606
0 | 38.043 | 0 | 0 | 0 | 0 | 14.457 | 52.5 | 408.7884 | 3000 | 25.8327 | 3025.8327 | 2977.1659 | 0 | 141.4154
0 | 33.365 | 0 | 0 | 0 | 0 | 19.135 | 52.5 | 427.9234 | 3000 | 34.1917 | 3034.1917 | 3023.3768 | 0 | 160.239
0 | 41.1476 | 0 | 0 | 0 | 0 | 11.3524 | 52.5 | 439.2758 | 3000 | 20.2852 | 3020.2852 | 3020.2852 | 0 | 165.8137
0 | 218.5972 | 0 | 0 | 0 | 0 | -166.0972 | 52.5 | 273.1786 | 3000 | 0 | 3000 | 3000 | 0 | 160.5
0 | 38.0471 | 0 | 0 | 0 | 0 | 14.4529 | 52.5 | 287.6314 | 3000 | 25.8253 | 3025.8253 | 3025.8253 | 0 | 155.5274
0 | 38.8737 | 0 | 0 | 0 | 0 | 13.6263 | 52.5 | 301.2578 | 3000 | 24.3484 | 3024.3484 | 3024.3484 | 0 | 150.915
0 | 28.3128 | 0 | 0 | 0 | 0 | 24.1872 | 52.5 | 325.4449 | 3000 | 43.2192 | 3043.2192 | 3043.2192 | 0 | 142.1183
0 | 23.6714 | 0 | 0 | 0 | 0 | 28.8286 | 52.5 | 354.2735 | 3000 | 51.5128 | 3051.5128 | 3051.5128 | 0 | 152.5756
0 | 42.4537 | 0 | 0 | 0 | 0 | 10.0463 | 52.5 | 364.3197 | 3000 | 17.9513 | 3017.9513 | 3017.9513 | 0 | 150.8976
0 | 39.9028 | 0 | 0 | 0 | 0 | 12.5972 | 52.5 | 376.917 | 3000 | 22.5096 | 3022.5096 | 3022.5096 | 0 | 125.4341
0 | 28.977 | 0 | 0 | 0 | 0 | 23.523 | 52.5 | 400.44 | 3000 | 42.0326 | 3042.0326 | 3042.0326 | 0 | 106.7753
0 | 36.7476 | 0 | 0 | 0 | 0 | 15.7524 | 52.5 | 416.1924 | 3000 | 28.1474 | 3028.1474 | 3028.1474 | 0 | 45.725
0 | 23.6316 | 0 | 0 | 0 | 0 | 28.8684 | 52.5 | 445.0608 | 3000 | 51.584 | 3051.584 | 3051.584 | 0 | 73.238
0 | 22.2919 | 0 | 0 | 0 | 0 | 30.2081 | 52.5 | 475.2689 | 3000 | 53.9779 | 3053.9779 | 3053.9779 | 0 | 152.6989
0 | 24.0053 | 0 | 0 | 0 | 0 | 28.4947 | 52.5 | 503.7637 | 3000 | 50.9162 | 3050.9162 | 3013.0643 | 0 | 161.6208
0 | 53.1179 | 0 | 0 | 0 | 0 | -0.61786 | 52.5 | 503.1458 | 3000 | 0 | 3000 | 2702.5916 | 0 | 138.3727
0 | 27.4312 | 0 | 0 | 0 | 0 | 25.0688 | 52.5 | 528.2145 | 3000 | 44.7945 | 3044.7945 | 2741.9787 | 0 | 140.1151
0 | 37.9729 | 0 | 0 | 0 | 0 | 14.5271 | 52.5 | 542.7416 | 3000 | 25.958 | 3025.958 | 2344.6224 | 0 | 126.6096
0 | 32.4809 | 0 | 0 | 0 | 0 | 20.0191 | 52.5 | 562.7607 | 3000 | 35.7714 | 3035.7714 | 2435.5472 | 0 | 128.5969
0 | 39.9349 | 0 | 0 | 0 | 0 | 12.5651 | 52.5 | 575.3257 | 3000 | 22.4521 | 3022.4521 | 2730.4511 | 0 | 140.2087
0 | 37.8473 | 0 | 0 | 0 | 0 | 14.6527 | 52.5 | 589.9784 | 3000 | 26.1824 | 3026.1824 | 2036.6236 | 0 | 106.7191
0 | 52.1944 | 0 | 0 | 0 | 0 | 0.30559 | 52.5 | 590.284 | 3000 | 0.54605 | 3000.546 | 2054.2466 | 0 | 106.6154
0 | 447.1197 | 0 | 0 | 0 | 0 | -394.6197 | 52.5 | 195.6643 | 3000 | 0 | 3000 | 2199.7011 | 0 | 108.8852
0 | 46.7489 | 0 | 0 | 0 | 0 | 5.7511 | 52.5 | 201.4154 | 3000 | 10.2764 | 3010.2764 | 2518.2007 | 0 | 126.1619
0 | 34.511 | 0 | 0 | 0 | 0 | 17.989 | 52.5 | 219.4044 | 3000 | 32.1439 | 3032.1439 | 2837.4766 | 0 | 142.4413
0 | 54.2537 | 0 | 0 | 0 | 0 | -1.7537 | 52.5 | 217.6507 | 3000 | 0 | 3000 | 2972.9629 | 0 | 162.9481
0 | 30.5396 | 0 | 0 | 0 | 0 | 21.9604 | 52.5 | 239.6111 | 3000 | 39.2403 | 3039.2403 | 3039.2403 | 0 | 159.6817
0 | 36.8594 | 0 | 0 | 0 | 0 | 15.6406 | 52.5 | 255.2517 | 3000 | 27.9477 | 3027.9477 | 3027.9477 | 0 | 195.9688
0 | 29.7895 | 0 | 0 | 0 | 0 | 22.7105 | 52.5 | 277.9622 | 3000 | 40.5806 | 3040.5806 | 3040.5806 | 0 | 182.4348
0 | 31.2622 | 0 | 0 | 0 | 0 | 21.2378 | 52.5 | 299.2 | 3000 | 37.9492 | 3037.9492 | 3037.9492 | 0 | 163.5024
0 | 34.5177 | 0 | 0 | 0 | 0 | 17.9823 | 52.5 | 317.1823 | 3000 | 32.132 | 3032.132 | 3032.132 | 0 | 164.7054
0 | 25.2956 | 0 | 0 | 0 | 0 | 27.2044 | 52.5 | 344.3867 | 3000 | 48.6106 | 3048.6106 | 3048.6106 | 0 | 166.1493
0 | 31.941 | 0 | 0 | 0 | 0 | 20.559 | 52.5 | 364.9457 | 3000 | 36.7363 | 3036.7363 | 3036.7363 | 0 | 145.7633
0 | 32.8599 | 0 | 0 | 0 | 0 | 19.6401 | 52.5 | 384.5858 | 3000 | 35.0943 | 3035.0943 | 3035.0943 | 0 | 148.7196
0 | 29.2657 | 0 | 0 | 0 | 0 | 23.2343 | 52.5 | 407.8202 | 3000 | 41.5166 | 3041.5166 | 3041.5166 | 0 | 152.0758
0 | 37.7729 | 0 | 0 | 0 | 0 | 14.7271 | 52.5 | 422.5472 | 3000 | 26.3153 | 3026.3153 | 3026.3153 | 0 | 159.4868
0 | 39.9101 | 0 | 0 | 0 | 0 | 12.5899 | 52.5 | 435.1372 | 3000 | 22.4965 | 3022.4965 | 3022.4965 | 0 | 160.0412
0 | 35.3465 | 0 | 0 | 0 | 0 | 17.1535 | 52.5 | 452.2907 | 3000 | 30.6511 | 3030.6511 | 3025.2436 | 0 | 165.3598
0 | 39.1146 | 0 | 0 | 0 | 0 | 13.3854 | 52.5 | 465.6761 | 3000 | 23.918 | 3023.918 | 2883.3249 | 0 | 164.8109
0 | 49.8763 | 0 | 0 | 0 | 0 | 2.6237 | 52.5 | 468.2999 | 3000 | 4.6883 | 3004.6883 | 2707.2799 | 0 | 171.3437
0 | 33.7681 | 0 | 0 | 0 | 0 | -20.8038 | 12.9643 | 447.4961 | 740.8173 | 0 | 740.8173 | 0 | 0 | 0
0 | 44.4691 | 0 | 0 | 0 | 0 | 8.0309 | 52.5 | 455.527 | 3000 | 14.3501 | 3014.3501 | 2322.1997 | 0 | 142.4437
0 | 246.305 | 0 | 0 | 0 | 0 | -193.805 | 52.5 | 261.722 | 3000 | 0 | 3000 | 2415.9981 | 0 | 139.1615
0 | 59.3942 | 0 | 0 | 0 | 0 | -6.8942 | 52.5 | 254.8278 | 3000 | 0 | 3000 | 1945.5521 | 0 | 107.1999
0 | 43.5998 | 0 | 0 | 0 | 0 | 8.9002 | 52.5 | 263.728 | 3000 | 15.9035 | 3015.9035 | 1950.6408 | 0 | 97.532
0 | 42.0825 | 0 | 0 | 0 | 0 | 10.4175 | 52.5 | 274.1455 | 3000 | 18.6147 | 3018.6147 | 1888.4628 | 0 | 96.6893
0 | 34.5899 | 0 | 0 | 0 | 0 | 17.9101 | 52.5 | 292.0556 | 3000 | 32.0029 | 3032.0029 | 2529.1124 | 0 | 129.4906
0 | 50.7764 | 0 | 0 | 0 | 0 | 1.7236 | 52.5 | 293.7792 | 3000 | 3.0799 | 3003.0799 | 2678.6344 | 0 | 141.3515
0 | 47.4389 | 0 | 0 | 0 | 0 | 5.0611 | 52.5 | 298.8403 | 3000 | 9.0436 | 3009.0436 | 2857.6357 | 0 | 151.4547
0 | 56.2656 | 0 | 0 | 0 | 0 | -3.7656 | 52.5 | 295.0748 | 3000 | 0 | 3000 | 2983.7777 | 0 | 186.1877
0 | 46.9691 | 0 | 0 | 0 | 0 | 5.5309 | 52.5 | 300.6057 | 3000 | 9.883 | 3009.883 | 3009.883 | 0 | 183.964
0 | 35.1815 | 0 | 0 | 0 | 0 | 17.3185 | 52.5 | 317.9242 | 3000 | 30.9459 | 3030.9459 | 3030.9459 | 0 | 206.1043
0 | 21.857 | 0 | 0 | 0 | 0 | 30.643 | 52.5 | 348.5672 | 3000 | 54.755 | 3054.755 | 3054.755 | 0 | 186.3401
0 | 32.7919 | 0 | 0 | 0 | 0 | 19.7081 | 52.5 | 368.2753 | 3000 | 35.2157 | 3035.2157 | 3035.2157 | 0 | 180.2615
0 | 32.9264 | 0 | 0 | 0 | 0 | 19.5736 | 52.5 | 387.8489 | 3000 | 34.9755 | 3034.9755 | 3034.9755 | 0 | 172.0831
0 | 31.8867 | 0 | 0 | 0 | 0 | 20.6133 | 52.5 | 408.4622 | 3000 | 36.8333 | 3036.8333 | 3036.8333 | 0 | 169.2731
0 | 35.2066 | 0 | 0 | 0 | 0 | 17.2934 | 52.5 | 425.7556 | 3000 | 30.901 | 3030.901 | 3030.901 | 0 | 163.9111
0 | 25.743 | 0 | 0 | 0 | 0 | 26.757 | 52.5 | 452.5126 | 3000 | 47.8111 | 3047.8111 | 3047.8111 | 0 | 163.0274
0 | 34.0696 | 0 | 0 | 0 | 0 | 18.4304 | 52.5 | 470.943 | 3000 | 32.9327 | 3032.9327 | 3032.9327 | 0 | 159.0773
0 | 231.7525 | 0 | 0 | 0 | 0 | -179.2525 | 52.5 | 291.6905 | 3000 | 0 | 3000 | 3000 | 0 | 154.41
0 | 38.2959 | 0 | 0 | 0 | 0 | 14.2041 | 52.5 | 305.8945 | 3000 | 25.3808 | 3025.3808 | 3025.3808 | 0 | 155.5651
0 | 21.5926 | 0 | 0 | 0 | 0 | 30.9074 | 52.5 | 336.802 | 3000 | 55.2274 | 3055.2274 | 3044.4126 | 0 | 168.3256
0 | 25.6548 | 0 | 0 | 0 | 0 | 26.8452 | 52.5 | 363.6472 | 3000 | 47.9688 | 3047.9688 | 2885.7461 | 0 | 178.8008
0 | 49.2117 | 0 | 0 | 0 | 0 | 3.2883 | 52.5 | 366.9355 | 3000 | 5.8757 | 3005.8757 | 2551.652 | 0 | 169.098
0 | 44.534 | 0 | 0 | 0 | 0 | 7.966 | 52.5 | 374.9015 | 3000 | 14.2343 | 3014.2343 | 2262.6021 | 0 | 156.9793
0 | 65.6063 | 0 | 0 | 0 | 0 | -13.1063 | 52.5 | 361.7951 | 3000 | 0 | 3000 | 2010.4412 | 0 | 130.0554
0 | 51.6483 | 0 | 0 | 0 | 0 | 0.85173 | 52.5 | 362.6469 | 3000 | 1.5219 | 3001.5219 | 1855.1478 | 0 | 113.7391
0 | 61.8134 | 0 | 0 | 0 | 0 | -9.3134 | 52.5 | 353.3334 | 3000 | 0 | 3000 | 1869.8481 | 0 | 111.3495
0 | 47.2021 | 0 | 0 | 0 | 0 | 5.2979 | 52.5 | 358.6313 | 3000 | 9.4666 | 3009.4666 | 2409.2424 | 0 | 140.4829
0 | 40.7458 | 0 | 0 | 0 | 0 | 11.7542 | 52.5 | 370.3855 | 3000 | 21.0031 | 3021.0031 | 2139.5928 | 0 | 123.861
0 | 51.9982 | 0 | 0 | 0 | 0 | 0.50178 | 52.5 | 370.8873 | 3000 | 0.89662 | 3000.8966 | 2406.0798 | 0 | 138.3015
0 | 32.8289 | 0 | 0 | 0 | 0 | 19.6711 | 52.5 | 390.5584 | 3000 | 35.1497 | 3035.1497 | 2705.2968 | 0 | 158.9091
0 | 43.3892 | 0 | 0 | 0 | 0 | 9.1108 | 52.5 | 399.6693 | 3000 | 16.2798 | 3016.2798 | 2886.5016 | 0 | 172.0644
0 | 34.7819 | 0 | 0 | 0 | 0 | 17.7181 | 52.5 | 417.3874 | 3000 | 31.6599 | 3031.6599 | 3010.0302 | 0 | 192.5215
0 | 44.9428 | 0 | 0 | 0 | 0 | -44.9428 | 0 | 372.4446 | 0 | 0 | 0 | 0 | 0 | 0
0 | 34.8618 | 0 | 0 | 0 | 0 | -34.8618 | 0 | 337.5828 | 0 | 0 | 0 | 0 | 0 | 0
0 | 21.6637 | 0 | 0 | 0 | 0 | 30.8363 | 52.5 | 368.4191 | 3000 | 55.1004 | 3055.1004 | 3055.1004 | 0 | 206.372
0 | 31.4166 | 0 | 0 | 0 | 0 | 21.0834 | 52.5 | 389.5026 | 3000 | 37.6733 | 3037.6733 | 3037.6733 | 0 | 186.6954
0 | 38.5289 | 0 | 0 | 0 | 0 | 13.9711 | 52.5 | 403.4736 | 3000 | 24.9645 | 3024.9645 | 3024.9645 | 0 | 180.6509
0 | 230.8286 | 0 | 0 | 0 | 0 | -178.3286 | 52.5 | 225.1451 | 3000 | 0 | 3000 | 3000 | 0 | 168.24
0 | 27.1802 | 0 | 0 | 0 | 0 | 25.3198 | 52.5 | 250.4649 | 3000 | 45.2431 | 3045.2431 | 3045.2431 | 0 | 162.2506
0 | 32.3422 | 0 | 0 | 0 | 0 | 20.1578 | 52.5 | 270.6227 | 3000 | 36.0193 | 3036.0193 | 3036.0193 | 0 | 155.7478
0 | 32.4888 | 0 | 0 | 0 | 0 | 20.0112 | 52.5 | 290.6339 | 3000 | 35.7574 | 3035.7574 | 3035.7574 | 0 | 151.9397
0 | 30.6076 | 0 | 0 | 0 | 0 | 21.8924 | 52.5 | 312.5263 | 3000 | 39.1188 | 3039.1188 | 3039.1188 | 0 | 149.9197
0 | 33.2415 | 0 | 0 | 0 | 0 | 19.2585 | 52.5 | 331.7848 | 3000 | 34.4123 | 3034.4123 | 3034.4123 | 0 | 150.7799
0 | 53.0787 | 0 | 0 | 0 | 0 | -0.57867 | 52.5 | 331.2061 | 3000 | 0 | 3000 | 2983.7777 | 0 | 155.7532
0 | 120.6565 | 0 | 0 | 0 | 0 | -68.1565 | 52.5 | 263.0496 | 3000 | 0 | 3000 | 2908.0738 | 0 | 163.521
0 | 117.7526 | 0 | 0 | 0 | 0 | -65.2526 | 52.5 | 197.797 | 3000 | 0 | 3000 | 2843.1847 | 0 | 172.1833
0 | 123.0306 | 0 | 0 | 0 | 0 | -70.5306 | 52.5 | 127.2664 | 3000 | 0 | 3000 | 2680.9619 | 0 | 182.1446
0 | 77.5184 | 0 | 0 | 0 | 0 | -25.0184 | 52.5 | 102.2481 | 3000 | 0 | 3000 | 2680.9619 | 0 | 164.5038
0 | 47.8353 | 0 | 0 | 0 | 0 | 4.6647 | 52.5 | 106.9128 | 3000 | 8.3352 | 3008.3352 | 2613.5932 | 0 | 153.9145
0 | 159.4128 | 0 | 0 | 0 | 0 | -106.9128 | 52.5 | 0 | 3000 | 0 | 3000 | 2589.0357 | 0 | 142.0345
0 | 49.9015 | 0 | 0 | 0 | 0 | 2.5985 | 52.5 | 2.5985 | 3000 | 4.6431 | 3004.6431 | 2712.6421 | 0 | 142.6578
0 | 55.0077 | 0 | 0 | 0 | 0 | -2.5077 | 52.5 | 0.090757 | 3000 | 0 | 3000 | 2772.8881 | 0 | 145.4934
0 | 32.6199 | 0 | 0 | 0 | 0 | 19.8801 | 52.5 | 19.9709 | 3000 | 35.5231 | 3035.5231 | 2759.7445 | 0 | 146.708
0 | 39.0837 | 0 | 0 | 0 | 0 | 13.4163 | 52.5 | 33.3872 | 3000 | 23.9732 | 3023.9732 | 2888.7875 | 0 | 159.9233
0 | 39.5392 | 0 | 0 | 0 | 0 | 12.9608 | 52.5 | 46.348 | 3000 | 23.1592 | 3023.1592 | 2969.0849 | 0 | 169.5347
0 | 46.4998 | 0 | 0 | 0 | 0 | 6.0002 | 52.5 | 52.3481 | 3000 | 10.7215 | 3010.7215 | 2999.9066 | 0 | 181.4644
0 | 46.7282 | 0 | 0 | 0 | 0 | 5.7718 | 52.5 | 58.1199 | 3000 | 10.3134 | 3010.3134 | 3010.3134 | 0 | 198.6807
0 | 29.8667 | 0 | 0 | 0 | 0 | -29.8667 | 0 | 28.2531 | 0 | 0 | 0 | 0 | 0 | 0
0 | 22.2939 | 0 | 0 | 0 | 0 | 30.2061 | 52.5 | 58.4592 | 3000 | 53.9743 | 3053.9743 | 3053.9743 | 0 | 194.6603
0 | 34.0707 | 0 | 0 | 0 | 0 | 18.4293 | 52.5 | 76.8885 | 3000 | 32.9307 | 3032.9307 | 3032.9307 | 0 | 179.6708
0 | 129.3885 | 0 | 0 | 0 | 0 | -76.8885 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 173.22
0 | 31.2788 | 0 | 0 | 0 | 0 | 21.2212 | 52.5 | 21.2212 | 3000 | 37.9195 | 3037.9195 | 3037.9195 | 0 | 162.9844
0 | 23.9903 | 0 | 0 | 0 | 0 | 28.5097 | 52.5 | 49.731 | 3000 | 50.9431 | 3050.9431 | 3050.9431 | 0 | 153.9811
0 | 28.8543 | 0 | 0 | 0 | 0 | 23.6457 | 52.5 | 73.3766 | 3000 | 42.2517 | 3042.2517 | 3042.2517 | 0 | 151.1999
0 | 27.5433 | 0 | 0 | 0 | 0 | 24.9567 | 52.5 | 98.3333 | 3000 | 44.5943 | 3044.5943 | 3044.5943 | 0 | 147.6933
0 | 31.6933 | 0 | 0 | 0 | 0 | 20.8067 | 52.5 | 119.14 | 3000 | 37.1787 | 3037.1787 | 3037.1787 | 0 | 145.9061
0 | 29.2861 | 0 | 0 | 0 | 0 | 23.2139 | 52.5 | 142.3539 | 3000 | 41.4801 | 3041.4801 | 3041.4801 | 0 | 146.2952
0 | 35.2188 | 0 | 0 | 0 | 0 | 17.2812 | 52.5 | 159.6351 | 3000 | 30.8793 | 3030.8793 | 3020.0644 | 0 | 153.8119
0 | 32.6395 | 0 | 0 | 0 | 0 | 19.8605 | 52.5 | 179.4956 | 3000 | 35.4881 | 3035.4881 | 2916.5247 | 0 | 172.075
0 | 42.8204 | 0 | 0 | 0 | 0 | 9.6796 | 52.5 | 189.1752 | 3000 | 17.2962 | 3017.2962 | 2741.5175 | 0 | 159.8579
0 | 38.4578 | 0 | 0 | 0 | 0 | 14.0422 | 52.5 | 203.2174 | 3000 | 25.0915 | 3025.0915 | 2554.6455 | 0 | 153.9429
0 | 43.2399 | 0 | 0 | 0 | 0 | 9.2601 | 52.5 | 212.4775 | 3000 | 16.5466 | 3016.5466 | 2513.656 | 0 | 152.2019
0 | 29.9838 | 0 | 0 | 0 | 0 | 22.5162 | 52.5 | 234.9937 | 3000 | 40.2335 | 3040.2335 | 2504.8984 | 0 | 134.0121
0 | 43.7262 | 0 | 0 | 0 | 0 | 8.7738 | 52.5 | 243.7675 | 3000 | 15.6776 | 3015.6776 | 2128.8598 | 0 | 108.3377
0 | 38.3952 | 0 | 0 | 0 | 0 | 14.1048 | 52.5 | 257.8723 | 3000 | 25.2034 | 3025.2034 | 2165.4228 | 0 | 109.2023
0 | 42.927 | 0 | 0 | 0 | 0 | 9.573 | 52.5 | 267.4453 | 3000 | 17.1057 | 3017.1057 | 2189.7696 | 0 | 108.3936
0 | 40.6619 | 0 | 0 | 0 | 0 | 11.8381 | 52.5 | 279.2834 | 3000 | 21.1531 | 3021.1531 | 2356.0398 | 0 | 117.5664
0 | 47.2999 | 0 | 0 | 0 | 0 | 5.2001 | 52.5 | 284.4835 | 3000 | 9.2918 | 3009.2918 | 2582.1052 | 0 | 133.7789
0 | 52.8673 | 0 | 0 | 0 | 0 | -0.36733 | 52.5 | 284.1161 | 3000 | 0 | 3000 | 2740.4436 | 0 | 148.7239
0 | 47.7718 | 0 | 0 | 0 | 0 | 4.7282 | 52.5 | 288.8443 | 3000 | 8.4487 | 3008.4487 | 2970.5967 | 0 | 173.4828
0 | 46.0152 | 0 | 0 | 0 | 0 | 6.4848 | 52.5 | 295.3291 | 3000 | 11.5875 | 3011.5875 | 3011.5875 | 0 | 185.8149
0 | 25.9611 | 0 | 0 | 0 | 0 | -25.9611 | 0 | 269.368 | 0 | 0 | 0 | 0 | 0 | 0
0 | 29.9907 | 0 | 0 | 0 | 0 | 22.5093 | 52.5 | 291.8774 | 3000 | 40.2212 | 3040.2212 | 3040.2212 | 0 | 190.105
0 | 29.4502 | 0 | 0 | 0 | 0 | 23.0498 | 52.5 | 314.9272 | 3000 | 41.187 | 3041.187 | 3041.187 | 0 | 179.1867
0 | 25.5132 | 0 | 0 | 0 | 0 | 26.9868 | 52.5 | 341.914 | 3000 | 48.2219 | 3048.2219 | 3048.2219 | 0 | 173.5658
0 | 28.4148 | 0 | 0 | 0 | 0 | 24.0852 | 52.5 | 365.9993 | 3000 | 43.0371 | 3043.0371 | 3043.0371 | 0 | 164.5979
0 | 228.7024 | 0 | 0 | 0 | 0 | -176.2024 | 52.5 | 189.7968 | 3000 | 0 | 3000 | 3000 | 0 | 162
0 | 32.5664 | 0 | 0 | 0 | 0 | 19.9336 | 52.5 | 209.7305 | 3000 | 35.6187 | 3035.6187 | 3035.6187 | 0 | 154.6648
0 | 29.0187 | 0 | 0 | 0 | 0 | 23.4813 | 52.5 | 233.2118 | 3000 | 41.958 | 3041.958 | 3041.958 | 0 | 157.2388
0 | 30.9514 | 0 | 0 | 0 | 0 | 21.5486 | 52.5 | 254.7604 | 3000 | 38.5045 | 3038.5045 | 3038.5045 | 0 | 156.1487
0 | 34.1517 | 0 | 0 | 0 | 0 | 18.3483 | 52.5 | 273.1087 | 3000 | 32.786 | 3032.786 | 3032.786 | 0 | 155.5213
0 | 32.7748 | 0 | 0 | 0 | 0 | 19.7252 | 52.5 | 292.8339 | 3000 | 35.2463 | 3035.2463 | 3029.8388 | 0 | 166.4896
0 | 41.3413 | 0 | 0 | 0 | 0 | 11.1587 | 52.5 | 303.9926 | 3000 | 19.9392 | 3019.9392 | 2982.0872 | 0 | 181.9371
0 | 98.3187 | 0 | 0 | 0 | 0 | -45.8187 | 52.5 | 258.1739 | 3000 | 0 | 3000 | 2864.8144 | 0 | 189.0205
0 | 137.8162 | 0 | 0 | 0 | 0 | -85.3162 | 52.5 | 172.8577 | 3000 | 0 | 3000 | 2724.2213 | 0 | 174.895
0 | 139.6796 | 0 | 0 | 0 | 0 | -87.1796 | 52.5 | 85.6781 | 3000 | 0 | 3000 | 2232.1456 | 0 | 133.8618
0 | 138.1781 | 0 | 0 | 0 | 0 | -85.6781 | 52.5 | 0 | 3000 | 0 | 3000 | 1907.7001 | 0 | 105.7057
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1842.811 | 0 | 95.0338
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1837.4036 | 0 | 91.8702
0 | 52.4704 | 0 | 0 | 0 | 0 | 0.029634 | 52.5 | 0.029634 | 3000 | 0.052951 | 3000.053 | 1929.3828 | 0 | 95.1186
0 | 33.9329 | 0 | 0 | 0 | 0 | 18.5671 | 52.5 | 18.5968 | 3000 | 33.177 | 3033.177 | 2162.5816 | 0 | 106.9613
0 | 55.2407 | 0 | 0 | 0 | 0 | -2.7407 | 52.5 | 15.8561 | 3000 | 0 | 3000 | 2415.9981 | 0 | 120.7999
0 | 48.0737 | 0 | 0 | 0 | 0 | 4.4263 | 52.5 | 20.2825 | 3000 | 7.9093 | 3007.9093 | 2721.3158 | 0 | 143.631
0 | 38.0818 | 0 | 0 | 0 | 0 | 14.4182 | 52.5 | 34.7007 | 3000 | 25.7634 | 3025.7634 | 2982.504 | 0 | 174.8046
0 | 48.9171 | 0 | 0 | 0 | 0 | 3.5829 | 52.5 | 38.2836 | 3000 | 6.4021 | 3006.4021 | 3006.4021 | 0 | 186.1264
0 | 33.0719 | 0 | 0 | 0 | 0 | 19.4281 | 52.5 | 57.7116 | 3000 | 34.7154 | 3034.7154 | 3034.7154 | 0 | 197.7724
0 | 26.854 | 0 | 0 | 0 | 0 | 25.646 | 52.5 | 83.3576 | 3000 | 45.826 | 3045.826 | 3045.826 | 0 | 185.7954
0 | 26.4825 | 0 | 0 | 0 | 0 | 26.0175 | 52.5 | 109.3751 | 3000 | 46.4898 | 3046.4898 | 3046.4898 | 0 | 169.4153
0 | 29.0185 | 0 | 0 | 0 | 0 | 23.4815 | 52.5 | 132.8566 | 3000 | 41.9583 | 3041.9583 | 3041.9583 | 0 | 167.0035
0 | 32.975 | 0 | 0 | 0 | 0 | 19.525 | 52.5 | 152.3816 | 3000 | 34.8886 | 3034.8886 | 3034.8886 | 0 | 158.1784
0 | 27.6152 | 0 | 0 | 0 | 0 | 24.8848 | 52.5 | 177.2664 | 3000 | 44.4659 | 3044.4659 | 3044.4659 | 0 | 153.8369
0 | 25.1603 | 0 | 0 | 0 | 0 | 27.3397 | 52.5 | 204.6061 | 3000 | 48.8524 | 3048.8524 | 3048.8524 | 0 | 152.2597
0 | 42.635 | 0 | 0 | 0 | 0 | 9.865 | 52.5 | 214.4711 | 3000 | 17.6274 | 3017.6274 | 3017.6274 | 0 | 150.5796
0 | 28.7569 | 0 | 0 | 0 | 0 | 23.7431 | 52.5 | 238.2143 | 3000 | 42.4258 | 3042.4258 | 3042.4258 | 0 | 146.3407
0 | 32.1692 | 0 | 0 | 0 | 0 | 20.3308 | 52.5 | 258.545 | 3000 | 36.3284 | 3036.3284 | 3036.3284 | 0 | 145.8956
0 | 27.1946 | 0 | 0 | 0 | 0 | 25.3054 | 52.5 | 283.8504 | 3000 | 45.2173 | 3045.2173 | 3039.8099 | 0 | 150.7746
0 | 226.8986 | 0 | 0 | 0 | 0 | -174.3986 | 52.5 | 109.4518 | 3000 | 0 | 3000 | 2956.7406 | 0 | 152.6861
0 | 161.9518 | 0 | 0 | 0 | 0 | -109.4518 | 52.5 | 0 | 3000 | 0 | 3000 | 2870.2218 | 0 | 154.5901
0 | 30.4658 | 0 | 0 | 0 | 0 | 22.0342 | 52.5 | 22.0342 | 3000 | 39.3721 | 3039.3721 | 2833.8899 | 0 | 151.4147
0 | 41.178 | 0 | 0 | 0 | 0 | 11.322 | 52.5 | 33.3562 | 3000 | 20.231 | 3020.231 | 2749.8597 | 0 | 152.2322
0 | 42.1579 | 0 | 0 | 0 | 0 | 10.3421 | 52.5 | 43.6982 | 3000 | 18.4799 | 3018.4799 | 2715.6641 | 0 | 142.1379
0 | 48.0239 | 0 | 0 | 0 | 0 | 4.4761 | 52.5 | 48.1743 | 3000 | 7.9981 | 3007.9981 | 2710.5897 | 0 | 139.9206
0 | 34.4791 | 0 | 0 | 0 | 0 | 18.0209 | 52.5 | 66.1952 | 3000 | 32.2009 | 3032.2009 | 2740.2 | 0 | 139.7502
0 | 41.2522 | 0 | 0 | 0 | 0 | 11.2478 | 52.5 | 77.443 | 3000 | 20.0984 | 3020.0984 | 2792.9865 | 0 | 128.7567
0 | 37.1101 | 0 | 0 | 0 | 0 | 15.3899 | 52.5 | 92.8329 | 3000 | 27.4997 | 3027.4997 | 2686.8319 | 0 | 121.1761
0 | 43.3719 | 0 | 0 | 0 | 0 | 9.1281 | 52.5 | 101.961 | 3000 | 16.3107 | 3016.3107 | 2610.7538 | 0 | 120.3558
0 | 49.43 | 0 | 0 | 0 | 0 | 3.07 | 52.5 | 105.031 | 3000 | 5.4857 | 3005.4857 | 2745.9293 | 0 | 130.6513
0 | 47.6573 | 0 | 0 | 0 | 0 | 4.8427 | 52.5 | 109.8738 | 3000 | 8.6533 | 3008.6533 | 2949.1716 | 0 | 158.4
0 | 56.662 | 0 | 0 | 0 | 0 | -4.162 | 52.5 | 105.7117 | 3000 | 0 | 3000 | 3000 | 0 | 168.81
0 | 24.4756 | 0 | 0 | 0 | 0 | 28.0244 | 52.5 | 133.7362 | 3000 | 50.076 | 3050.076 | 3050.076 | 0 | 182.9741
0 | 34.0936 | 0 | 0 | 0 | 0 | 18.4064 | 52.5 | 152.1426 | 3000 | 32.8898 | 3032.8898 | 3032.8898 | 0 | 173.6329
0 | 31.4487 | 0 | 0 | 0 | 0 | 21.0513 | 52.5 | 173.1938 | 3000 | 37.6158 | 3037.6158 | 3037.6158 | 0 | 164.335
0 | 34.5531 | 0 | 0 | 0 | 0 | 17.9469 | 52.5 | 191.1407 | 3000 | 32.0687 | 3032.0687 | 3032.0687 | 0 | 167.825
0 | 22.5081 | 0 | 0 | 0 | 0 | 29.9919 | 52.5 | 221.1326 | 3000 | 53.5915 | 3053.5915 | 3053.5915 | 0 | 161.6266
0 | 31.22 | 0 | 0 | 0 | 0 | 21.28 | 52.5 | 242.4126 | 3000 | 38.0246 | 3038.0246 | 3038.0246 | 0 | 164.509
0 | 25.2947 | 0 | 0 | 0 | 0 | 27.2053 | 52.5 | 269.6179 | 3000 | 48.6122 | 3048.6122 | 3048.6122 | 0 | 155.6317
0 | 33.8394 | 0 | 0 | 0 | 0 | 18.6606 | 52.5 | 288.2785 | 3000 | 33.344 | 3033.344 | 3033.344 | 0 | 149.9989
0 | 30.5588 | 0 | 0 | 0 | 0 | 21.9412 | 52.5 | 310.2197 | 3000 | 39.206 | 3039.206 | 3039.206 | 0 | 147.7358
0 | 28.2815 | 0 | 0 | 0 | 0 | 24.2185 | 52.5 | 334.4382 | 3000 | 43.2753 | 3043.2753 | 3043.2753 | 0 | 148.664
0 | 30.3601 | 0 | 0 | 0 | 0 | 22.1399 | 52.5 | 356.578 | 3000 | 39.561 | 3039.561 | 3028.7461 | 0 | 149.0143
0 | 34.7608 | 0 | 0 | 0 | 0 | 17.7392 | 52.5 | 374.3172 | 3000 | 31.6976 | 3031.6976 | 2826.2154 | 0 | 139.3889
0 | 42.7847 | 0 | 0 | 0 | 0 | 9.7153 | 52.5 | 384.0326 | 3000 | 17.36 | 3017.36 | 2525.2843 | 0 | 126.2137
0 | 52.2002 | 0 | 0 | 0 | 0 | 0.29976 | 52.5 | 384.3323 | 3000 | 0.53563 | 3000.5356 | 2394.904 | 0 | 123.577
0 | 45.3539 | 0 | 0 | 0 | 0 | 7.1461 | 52.5 | 391.4784 | 3000 | 12.7691 | 3012.7691 | 2531.5083 | 0 | 128.6259
0 | 43.3408 | 0 | 0 | 0 | 0 | 9.1592 | 52.5 | 400.6376 | 3000 | 16.3662 | 3016.3662 | 2199.845 | 0 | 107.3084
0 | 48.0608 | 0 | 0 | 0 | 0 | 4.4392 | 52.5 | 405.0768 | 3000 | 7.9323 | 3007.9323 | 2018.3735 | 0 | 94.8837
0 | 34.8256 | 0 | 0 | 0 | 0 | 17.6744 | 52.5 | 422.7512 | 3000 | 31.5818 | 3031.5818 | 1814.9111 | 0 | 83.6674
0 | 34.1483 | 0 | 0 | 0 | 0 | 18.3517 | 52.5 | 441.1029 | 3000 | 32.7921 | 3032.7921 | 1913.455 | 0 | 76.6913
0 | 44.6147 | 0 | 0 | 0 | 0 | 7.8853 | 52.5 | 448.9883 | 3000 | 14.0901 | 3014.0901 | 2056.9758 | 0 | 80.4895
0 | 52.4606 | 0 | 0 | 0 | 0 | 0.03943 | 52.5 | 449.0277 | 3000 | 0.070457 | 3000.0705 | 2302.5126 | 0 | 89.3145
0 | 48.9917 | 0 | 0 | 0 | 0 | 3.5083 | 52.5 | 452.536 | 3000 | 6.2689 | 3006.2689 | 2746.7125 | 0 | 110.1432
0 | 45.312 | 0 | 0 | 0 | 0 | 7.188 | 52.5 | 459.7241 | 3000 | 12.844 | 3012.844 | 2969.5846 | 0 | 153.2306
0 | 44.6673 | 0 | 0 | 0 | 0 | 7.8327 | 52.5 | 467.5568 | 3000 | 13.9961 | 3013.9961 | 3013.9961 | 0 | 163.871
0 | 25.6898 | 0 | 0 | 0 | 0 | 26.8102 | 52.5 | 494.367 | 3000 | 47.9064 | 3047.9064 | 3047.9064 | 0 | 176.5652
0 | 33.5434 | 0 | 0 | 0 | 0 | 18.9566 | 52.5 | 513.3237 | 3000 | 33.8729 | 3033.8729 | 3033.8729 | 0 | 168.5316
0 | 34.2507 | 0 | 0 | 0 | 0 | 18.2493 | 52.5 | 531.573 | 3000 | 32.6092 | 3032.6092 | 3032.6092 | 0 | 159.5152
0 | 31.3138 | 0 | 0 | 0 | 0 | 21.1862 | 52.5 | 552.7592 | 3000 | 37.8569 | 3037.8569 | 3037.8569 | 0 | 167.0821
0 | 38.0566 | 0 | 0 | 0 | 0 | 14.4434 | 52.5 | 567.2026 | 3000 | 25.8085 | 3025.8085 | 3025.8085 | 0 | 160.973
0 | 32.4601 | 0 | 0 | 0 | 0 | 20.0399 | 52.5 | 587.2425 | 3000 | 35.8087 | 3035.8087 | 3035.8087 | 0 | 119.4287
0 | 234.781 | 0 | 0 | 0 | 0 | -182.281 | 52.5 | 404.9615 | 3000 | 0 | 3000 | 3000 | 0 | 112.5
0 | 30.1585 | 0 | 0 | 0 | 0 | 22.3415 | 52.5 | 427.303 | 3000 | 39.9212 | 3039.9212 | 3039.9212 | 0 | 121.5968
0 | 32.8412 | 0 | 0 | 0 | 0 | 19.6588 | 52.5 | 446.9619 | 3000 | 35.1277 | 3035.1277 | 3035.1277 | 0 | 113.5138
0 | 40.1665 | 0 | 0 | 0 | 0 | 12.3335 | 52.5 | 459.2953 | 3000 | 22.0382 | 3022.0382 | 3022.0382 | 0 | 128.7388
0 | 20.3379 | 0 | 0 | 0 | 0 | 32.1621 | 52.5 | 491.4574 | 3000 | 57.4694 | 3057.4694 | 3052.062 | 0 | 131.2387
0 | 27.5042 | 0 | 0 | 0 | 0 | 24.9958 | 52.5 | 516.4532 | 3000 | 44.6641 | 3044.6641 | 2979.775 | 0 | 147.3499
0 | 32.5867 | 0 | 0 | 0 | 0 | 19.9133 | 52.5 | 536.3665 | 3000 | 35.5824 | 3035.5824 | 2754.3963 | 0 | 157.0006
0 | 28.3694 | 0 | 0 | 0 | 0 | 24.1306 | 52.5 | 560.4971 | 3000 | 43.1182 | 3043.1182 | 2459.1163 | 0 | 138.1532
0 | 41.2693 | 0 | 0 | 0 | 0 | 11.2307 | 52.5 | 571.7278 | 3000 | 20.0678 | 3020.0678 | 2208.954 | 0 | 120.8077
0 | 55.05 | 0 | 0 | 0 | 0 | -2.55 | 52.5 | 569.1778 | 3000 | 0 | 3000 | 2172.6639 | 0 | 107.7859
0 | 39.8061 | 0 | 0 | 0 | 0 | 12.6939 | 52.5 | 581.8717 | 3000 | 22.6822 | 3022.6822 | 2233.1981 | 0 | 109.4267
0 | 44.3968 | 0 | 0 | 0 | 0 | 8.1032 | 52.5 | 589.9749 | 3000 | 14.4794 | 3014.4794 | 2414.2552 | 0 | 116.0291
0 | 44.9774 | 0 | 0 | 0 | 0 | 7.5226 | 52.5 | 597.4976 | 3000 | 13.442 | 3013.442 | 2342.9212 | 0 | 111.0545
0 | 51.9839 | 0 | 0 | 0 | 0 | 0.51609 | 52.5 | 598.0136 | 3000 | 0.92218 | 3000.9222 | 2319.5866 | 0 | 107.1649
0 | 50.5294 | 0 | 0 | 0 | 0 | 1.9706 | 52.5 | 599.9843 | 3000 | 3.5213 | 3003.5213 | 2711.5203 | 0 | 126.1399
0 | 56.0319 | 0 | 0 | 0 | 0 | -3.5319 | 52.5 | 596.4523 | 3000 | 0 | 3000 | 2843.1847 | 0 | 134.767
0 | 49.452 | 0 | 0 | 0 | 0 | 3.048 | 52.5 | 599.5003 | 3000 | 5.4463 | 3005.4463 | 2951.3721 | 0 | 152.5269
0 | 45.5382 | 0 | 0 | 0 | 0 | 6.9618 | 52.5 | 606.4622 | 3000 | 12.4399 | 3012.4399 | 3012.4399 | 0 | 169.2991
0 | 33.0368 | 0 | 0 | 0 | 0 | 19.4632 | 52.5 | 625.9254 | 3000 | 34.7782 | 3034.7782 | 3034.7782 | 0 | 192.7084
0 | 32.8028 | 0 | 0 | 0 | 0 | 19.6972 | 52.5 | 645.6226 | 3000 | 35.1963 | 3035.1963 | 3035.1963 | 0 | 176.7091
0 | 21.5492 | 0 | 0 | 0 | 0 | 30.9508 | 52.5 | 676.5734 | 3000 | 55.3049 | 3055.3049 | 3055.3049 | 0 | 167.4613
0 | 32.8884 | 0 | 0 | 0 | 0 | 19.6116 | 52.5 | 696.185 | 3000 | 35.0434 | 3035.0434 | 3035.0434 | 0 | 166.897
0 | 33.2787 | 0 | 0 | 0 | 0 | 19.2213 | 52.5 | 715.4062 | 3000 | 34.3458 | 3034.3458 | 3034.3458 | 0 | 159.4852
0 | 31.4783 | 0 | 0 | 0 | 0 | 21.0217 | 52.5 | 736.428 | 3000 | 37.563 | 3037.563 | 3037.563 | 0 | 146.5624
0 | 33.4113 | 0 | 0 | 0 | 0 | 19.0887 | 52.5 | 755.5166 | 3000 | 34.1089 | 3034.1089 | 3034.1089 | 0 | 140.4792
0 | 226.1812 | 0 | 0 | 0 | 0 | -173.6812 | 52.5 | 581.8354 | 3000 | 0 | 3000 | 3000 | 0 | 138.6
0 | 32.3386 | 0 | 0 | 0 | 0 | 20.1614 | 52.5 | 601.9968 | 3000 | 36.0258 | 3036.0258 | 3036.0258 | 0 | 140.568
0 | 30.1305 | 0 | 0 | 0 | 0 | 22.3695 | 52.5 | 624.3663 | 3000 | 39.9712 | 3039.9712 | 3039.9712 | 0 | 140.7507
0 | 32.3429 | 0 | 0 | 0 | 0 | 20.1571 | 52.5 | 644.5234 | 3000 | 36.018 | 3036.018 | 3019.7957 | 0 | 143.4403
0 | 35.7432 | 0 | 0 | 0 | 0 | 16.7568 | 52.5 | 661.2801 | 3000 | 29.9422 | 3029.9422 | 2900.1639 | 0 | 156.6089
0 | 253.7034 | 0 | 0 | 0 | 0 | -201.2034 | 52.5 | 460.0768 | 3000 | 0 | 3000 | 2740.4436 | 0 | 158.3976
0 | 44.5429 | 0 | 0 | 0 | 0 | 7.9571 | 52.5 | 468.0339 | 3000 | 14.2183 | 3014.2183 | 2576.2168 | 0 | 148.7765
0 | 44.0188 | 0 | 0 | 0 | 0 | 8.4812 | 52.5 | 476.5151 | 3000 | 15.1548 | 3015.1548 | 2625.8202 | 0 | 144.4201
0 | 44.865 | 0 | 0 | 0 | 0 | 7.635 | 52.5 | 484.1501 | 3000 | 13.6427 | 3013.6427 | 2532.3819 | 0 | 144.3458
0 | 53.3303 | 0 | 0 | 0 | 0 | -0.83034 | 52.5 | 483.3197 | 3000 | 0 | 3000 | 2415.9981 | 0 | 130.5847
0 | 51.7373 | 0 | 0 | 0 | 0 | 0.76266 | 52.5 | 484.0824 | 3000 | 1.3628 | 3001.3628 | 2493.0648 | 0 | 134.077
0 | 37.0778 | 0 | 0 | 0 | 0 | 15.4222 | 52.5 | 499.5046 | 3000 | 27.5574 | 3027.5574 | 2438.1481 | 0 | 127.759
0 | 36.0817 | 0 | 0 | 0 | 0 | 16.4183 | 52.5 | 515.9229 | 3000 | 29.3372 | 3029.3372 | 2629.1878 | 0 | 134.3515
0 | 39.5472 | 0 | 0 | 0 | 0 | 12.9528 | 52.5 | 528.8756 | 3000 | 23.1449 | 3023.1449 | 2785.2182 | 0 | 136.1972
0 | 32.9316 | 0 | 0 | 0 | 0 | 19.5684 | 52.5 | 548.444 | 3000 | 34.9661 | 3034.9661 | 2894.373 | 0 | 141.8243
0 | 42.5849 | 0 | 0 | 0 | 0 | 9.9151 | 52.5 | 558.3591 | 3000 | 17.7169 | 3017.7169 | 2969.0501 | 0 | 162.5852
0 | 36.7782 | 0 | 0 | 0 | 0 | 15.7218 | 52.5 | 574.0809 | 3000 | 28.0928 | 3028.0928 | 3028.0928 | 0 | 175.6294
0 | 27.2888 | 0 | 0 | 0 | 0 | 25.2112 | 52.5 | 599.2922 | 3000 | 45.0491 | 3045.0491 | 3045.0491 | 0 | 196.1012
0 | 34.2568 | 0 | 0 | 0 | 0 | 18.2432 | 52.5 | 617.5354 | 3000 | 32.5982 | 3032.5982 | 3032.5982 | 0 | 186.2319
0 | 29.0374 | 0 | 0 | 0 | 0 | 23.4626 | 52.5 | 640.9979 | 3000 | 41.9245 | 3041.9245 | 3041.9245 | 0 | 177.5571
0 | 30.5627 | 0 | 0 | 0 | 0 | 21.9373 | 52.5 | 662.9352 | 3000 | 39.199 | 3039.199 | 3039.199 | 0 | 174.0853
0 | 30.3329 | 0 | 0 | 0 | 0 | 22.1671 | 52.5 | 685.1023 | 3000 | 39.6096 | 3039.6096 | 3039.6096 | 0 | 162.3759
0 | 28.5312 | 0 | 0 | 0 | 0 | 23.9688 | 52.5 | 709.0711 | 3000 | 42.8291 | 3042.8291 | 3042.8291 | 0 | 157.0708
0 | 34.3863 | 0 | 0 | 0 | 0 | 18.1137 | 52.5 | 727.1848 | 3000 | 32.3667 | 3032.3667 | 3032.3667 | 0 | 151.0422
0 | 30.1765 | 0 | 0 | 0 | 0 | 22.3235 | 52.5 | 749.5083 | 3000 | 39.8892 | 3039.8892 | 3039.8892 | 0 | 149.7753
0 | 28.49 | 0 | 0 | 0 | 0 | 24.01 | 52.5 | 773.5182 | 3000 | 42.9026 | 3042.9026 | 3042.9026 | 0 | 147.1852
0 | 33.2326 | 0 | 0 | 0 | 0 | 19.2674 | 52.5 | 792.7857 | 3000 | 34.4283 | 3034.4283 | 3034.4283 | 0 | 149.1118
0 | 37.4154 | 0 | 0 | 0 | 0 | 15.0846 | 52.5 | 807.8703 | 3000 | 26.9541 | 3026.9541 | 3010.7319 | 0 | 156.0161
0 | 34.0432 | 0 | 0 | 0 | 0 | 18.4568 | 52.5 | 826.3271 | 3000 | 32.9799 | 3032.9799 | 2816.6829 | 0 | 160.5791
0 | 38.0389 | 0 | 0 | 0 | 0 | 14.4611 | 52.5 | 840.7881 | 3000 | 25.84 | 3025.84 | 2485.0975 | 0 | 151.5909
0 | 38.2867 | 0 | 0 | 0 | 0 | 14.2133 | 52.5 | 855.0014 | 3000 | 25.3973 | 3025.3973 | 2203.4686 | 0 | 136.7032
0 | 45.0647 | 0 | 0 | 0 | 0 | 7.4353 | 52.5 | 862.4368 | 3000 | 13.286 | 3013.286 | 2094.0237 | 0 | 123.4218
0 | 43.7343 | 0 | 0 | 0 | 0 | 8.7657 | 52.5 | 871.2024 | 3000 | 15.6631 | 3015.6631 | 1809.8072 | 0 | 102.2179
0 | 46.5593 | 0 | 0 | 0 | 0 | 5.9407 | 52.5 | 877.1431 | 3000 | 10.6153 | 3010.6153 | 1885.8708 | 0 | 104.8733
0 | 77.4823 | 0 | 0 | 0 | 0 | -24.9823 | 52.5 | 852.1608 | 3000 | 0 | 3000 | 1945.5521 | 0 | 107.0054
0 | 56.5547 | 0 | 0 | 0 | 0 | -4.0547 | 52.5 | 848.1062 | 3000 | 0 | 3000 | 2140.2194 | 0 | 116.8132
0 | 101.0474 | 0 | 0 | 0 | 0 | -48.5474 | 52.5 | 799.5587 | 3000 | 0 | 3000 | 2578.2208 | 0 | 138.5794
0 | 88.2117 | 0 | 0 | 0 | 0 | -35.7117 | 52.5 | 763.847 | 3000 | 0 | 3000 | 2691.7768 | 0 | 144.683
0 | 46.505 | 0 | 0 | 0 | 0 | 5.995 | 52.5 | 769.842 | 3000 | 10.7122 | 3010.7122 | 2859.3043 | 0 | 154.9171
0 | 48.4536 | 0 | 0 | 0 | 0 | 4.0464 | 52.5 | 773.8883 | 3000 | 7.2303 | 3007.2303 | 2980.1932 | 0 | 168.3511
0 | 239.1611 | 0 | 0 | 0 | 0 | -186.6611 | 52.5 | 587.2272 | 3000 | 0 | 3000 | 3000 | 0 | 177.51
0 | 23.4436 | 0 | 0 | 0 | 0 | 29.0564 | 52.5 | 616.2836 | 3000 | 51.9199 | 3051.9199 | 3051.9199 | 0 | 191.2943
0 | 29.8544 | 0 | 0 | 0 | 0 | 22.6456 | 52.5 | 638.9292 | 3000 | 40.4647 | 3040.4647 | 3040.4647 | 0 | 179.357
0 | 28.4945 | 0 | 0 | 0 | 0 | 24.0055 | 52.5 | 662.9347 | 3000 | 42.8947 | 3042.8947 | 3042.8947 | 0 | 171.0715
0 | 31.166 | 0 | 0 | 0 | 0 | 21.334 | 52.5 | 684.2688 | 3000 | 38.1211 | 3038.1211 | 3038.1211 | 0 | 169.6183
0 | 28.4689 | 0 | 0 | 0 | 0 | 24.0311 | 52.5 | 708.2998 | 3000 | 42.9403 | 3042.9403 | 3042.9403 | 0 | 157.9895
0 | 28.5725 | 0 | 0 | 0 | 0 | 23.9275 | 52.5 | 732.2274 | 3000 | 42.7553 | 3042.7553 | 3042.7553 | 0 | 145.2307
0 | 32.5545 | 0 | 0 | 0 | 0 | 19.9455 | 52.5 | 752.1729 | 3000 | 35.64 | 3035.64 | 3035.64 | 0 | 147.7446
0 | 31.2581 | 0 | 0 | 0 | 0 | 21.2419 | 52.5 | 773.4148 | 3000 | 37.9565 | 3037.9565 | 3037.9565 | 0 | 146.9763
0 | 45.7117 | 0 | 0 | 0 | 0 | 6.7883 | 52.5 | 780.2031 | 3000 | 12.1298 | 3012.1298 | 3012.1298 | 0 | 145.4557
0 | 91.9545 | 0 | 0 | 0 | 0 | -39.4545 | 52.5 | 740.7486 | 3000 | 0 | 3000 | 3000 | 0 | 144.36
0 | 128.7132 | 0 | 0 | 0 | 0 | -76.2132 | 52.5 | 664.5354 | 3000 | 0 | 3000 | 2989.1851 | 0 | 154.4512
0 | 110.4251 | 0 | 0 | 0 | 0 | -57.9251 | 52.5 | 606.6104 | 3000 | 0 | 3000 | 2951.3332 | 0 | 175.5453
0 | 114.0528 | 0 | 0 | 0 | 0 | -61.5528 | 52.5 | 545.0575 | 3000 | 0 | 3000 | 2783.703 | 0 | 178.324
0 | 132.3298 | 0 | 0 | 0 | 0 | -79.8298 | 52.5 | 465.2277 | 3000 | 0 | 3000 | 2686.3693 | 0 | 170.665
0 | 129.7277 | 0 | 0 | 0 | 0 | -77.2277 | 52.5 | 388 | 3000 | 0 | 3000 | 2648.5174 | 0 | 163.6254
0 | 127.7049 | 0 | 0 | 0 | 0 | -75.2049 | 52.5 | 312.7951 | 3000 | 0 | 3000 | 2545.7763 | 0 | 150.5063
0 | 132.1164 | 0 | 0 | 0 | 0 | -79.6164 | 52.5 | 233.1788 | 3000 | 0 | 3000 | 2378.1461 | 0 | 138.7886
0 | 109.9745 | 0 | 0 | 0 | 0 | -57.4745 | 52.5 | 175.7042 | 3000 | 0 | 3000 | 2491.702 | 0 | 143.3725
0 | 60.8747 | 0 | 0 | 0 | 0 | -8.3747 | 52.5 | 167.3295 | 3000 | 0 | 3000 | 2707.999 | 0 | 155.4121
0 | 48.5717 | 0 | 0 | 0 | 0 | 3.9283 | 52.5 | 171.2578 | 3000 | 7.0194 | 3007.0194 | 2801.5372 | 0 | 158.9592
0 | 49.6871 | 0 | 0 | 0 | 0 | 2.8129 | 52.5 | 174.0707 | 3000 | 5.0263 | 3005.0263 | 2810.359 | 0 | 160.0218
0 | 45.5737 | 0 | 0 | 0 | 0 | 6.9263 | 52.5 | 180.9971 | 3000 | 12.3765 | 3012.3765 | 2877.1908 | 0 | 165.5248
0 | 42.5775 | 0 | 0 | 0 | 0 | 9.9225 | 52.5 | 190.9196 | 3000 | 17.7303 | 3017.7303 | 2979.8783 | 0 | 180.9978
0 | 44.1287 | 0 | 0 | 0 | 0 | 8.3713 | 52.5 | 199.2909 | 3000 | 14.9584 | 3014.9584 | 3014.9584 | 0 | 188.8871
0 | 28.5645 | 0 | 0 | 0 | 0 | 23.9355 | 52.5 | 223.2264 | 3000 | 42.7695 | 3042.7695 | 3042.7695 | 0 | 205.8738
0 | 36.4933 | 0 | 0 | 0 | 0 | 16.0067 | 52.5 | 239.2331 | 3000 | 28.6019 | 3028.6019 | 3028.6019 | 0 | 185.835
0 | 35.5242 | 0 | 0 | 0 | 0 | 16.9758 | 52.5 | 256.2089 | 3000 | 30.3335 | 3030.3335 | 3030.3335 | 0 | 176.6684
0 | 224.2516 | 0 | 0 | 0 | 0 | -171.7516 | 52.5 | 84.4572 | 3000 | 0 | 3000 | 3000 | 0 | 172.14
0 | 35.9158 | 0 | 0 | 0 | 0 | 16.5842 | 52.5 | 101.0414 | 3000 | 29.6338 | 3029.6338 | 3029.6338 | 0 | 164.5697
0 | 28.1219 | 0 | 0 | 0 | 0 | 24.3781 | 52.5 | 125.4195 | 3000 | 43.5604 | 3043.5604 | 3043.5604 | 0 | 165.2045
0 | 30.6469 | 0 | 0 | 0 | 0 | 21.8531 | 52.5 | 147.2726 | 3000 | 39.0485 | 3039.0485 | 3039.0485 | 0 | 149.2173
0 | 199.7726 | 0 | 0 | 0 | 0 | -147.2726 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 148.32
0 | 40.1253 | 0 | 0 | 0 | 0 | 12.3747 | 52.5 | 12.3747 | 3000 | 22.1119 | 3022.1119 | 3022.1119 | 0 | 149.5039
0 | 64.8747 | 0 | 0 | 0 | 0 | -12.3747 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 149.97
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2972.9629 | 0 | 157.686
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2778.2956 | 0 | 168.2536
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2480.8872 | 0 | 157.1146
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2178.0714 | 0 | 136.3908
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1967.1818 | 0 | 114.2342
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1821.1813 | 0 | 96.8868
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1761.6996 | 0 | 87.1865
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1761.6996 | 0 | 85.3191
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1886.0704 | 0 | 90.2862
0 | 41.1339 | 0 | 0 | 0 | 0 | 11.3661 | 52.5 | 11.3661 | 3000 | 20.3097 | 3020.3097 | 2128.0845 | 0 | 100.8712
0 | 48.0511 | 0 | 0 | 0 | 0 | 4.4489 | 52.5 | 15.815 | 3000 | 7.9496 | 3007.9496 | 2407.7254 | 0 | 115.8838
0 | 68.315 | 0 | 0 | 0 | 0 | -15.815 | 52.5 | 0 | 3000 | 0 | 3000 | 2713.4065 | 0 | 138.4109
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2929.7035 | 0 | 170.7138
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 190.53
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 192.21
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 187.86
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 174.12
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 173.25
0 | 47.2228 | 0 | 0 | 0 | 0 | 5.2772 | 52.5 | 5.2772 | 3000 | 9.4297 | 3009.4297 | 3009.4297 | 0 | 163.4722
0 | 49.1592 | 0 | 0 | 0 | 0 | 3.3408 | 52.5 | 8.618 | 3000 | 5.9695 | 3005.9695 | 3005.9695 | 0 | 157.7833
0 | 61.118 | 0 | 0 | 0 | 0 | -8.618 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 155.04
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 148.08
0 | 27.068 | 0 | 0 | 0 | 0 | 25.432 | 52.5 | 25.432 | 3000 | 45.4437 | 3045.4437 | 3045.4437 | 0 | 151.0845
0 | 36.8691 | 0 | 0 | 0 | 0 | 15.6309 | 52.5 | 41.0629 | 3000 | 27.9303 | 3027.9303 | 3027.9303 | 0 | 151.0937
0 | 32.2428 | 0 | 0 | 0 | 0 | 20.2572 | 52.5 | 61.3202 | 3000 | 36.197 | 3036.197 | 2992.9376 | 0 | 149.7067
0 | 23.7445 | 0 | 0 | 0 | 0 | 28.7555 | 52.5 | 90.0756 | 3000 | 51.3822 | 3051.3822 | 2791.8258 | 0 | 135.4315
0 | 51.8104 | 0 | 0 | 0 | 0 | 0.68956 | 52.5 | 90.7652 | 3000 | 1.2322 | 3001.2322 | 2433.4525 | 0 | 126.2719
0 | 104.5738 | 0 | 0 | 0 | 0 | -52.0738 | 52.5 | 38.6913 | 3000 | 0 | 3000 | 2145.6268 | 0 | 111.7872
0 | 91.1913 | 0 | 0 | 0 | 0 | -38.6913 | 52.5 | 0 | 3000 | 0 | 3000 | 1945.5521 | 0 | 93.7172
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1848.2184 | 0 | 86.1824
0 | 48.5033 | 0 | 0 | 0 | 0 | 3.9967 | 52.5 | 3.9967 | 3000 | 7.1415 | 3007.1415 | 1936.4714 | 0 | 93.9189
0 | 43.3064 | 0 | 0 | 0 | 0 | 9.1936 | 52.5 | 13.1903 | 3000 | 16.4277 | 3016.4277 | 2367.5367 | 0 | 117.6666
0 | 45.3589 | 0 | 0 | 0 | 0 | 7.1411 | 52.5 | 20.3314 | 3000 | 12.7602 | 3012.7602 | 2563.9439 | 0 | 121.5309
0 | 31.1513 | 0 | 0 | 0 | 0 | 21.3487 | 52.5 | 41.6801 | 3000 | 38.1473 | 3038.1473 | 2600.1459 | 0 | 128.4472
0 | 49.2308 | 0 | 0 | 0 | 0 | 3.2692 | 52.5 | 44.9493 | 3000 | 5.8417 | 3005.8417 | 2665.1739 | 0 | 122.1982
0 | 42.887 | 0 | 0 | 0 | 0 | 9.613 | 52.5 | 54.5623 | 3000 | 17.1771 | 3017.1771 | 2773.843 | 0 | 137.0278
0 | 46.8483 | 0 | 0 | 0 | 0 | 5.6517 | 52.5 | 60.2141 | 3000 | 10.0989 | 3010.0989 | 2928.9875 | 0 | 161.9437
0 | 112.7141 | 0 | 0 | 0 | 0 | -60.2141 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 185.43
0 | 29.4714 | 0 | 0 | 0 | 0 | 23.0286 | 52.5 | 23.0286 | 3000 | 41.149 | 3041.149 | 3041.149 | 0 | 187.3956
0 | 30.3076 | 0 | 0 | 0 | 0 | 22.1924 | 52.5 | 45.221 | 3000 | 39.655 | 3039.655 | 3039.655 | 0 | 176.5432
0 | 27.1001 | 0 | 0 | 0 | 0 | 25.3999 | 52.5 | 70.6209 | 3000 | 45.3862 | 3045.3862 | 3045.3862 | 0 | 169.1103
0 | 34.632 | 0 | 0 | 0 | 0 | 17.868 | 52.5 | 88.4888 | 3000 | 31.9277 | 3031.9277 | 3031.9277 | 0 | 169.3635
0 | 25.8187 | 0 | 0 | 0 | 0 | 26.6813 | 52.5 | 115.1701 | 3000 | 47.6759 | 3047.6759 | 3047.6759 | 0 | 158.022
0 | 29.3839 | 0 | 0 | 0 | 0 | 23.1161 | 52.5 | 138.2862 | 3000 | 41.3055 | 3041.3055 | 3041.3055 | 0 | 167.5759
0 | 27.2693 | 0 | 0 | 0 | 0 | 25.2307 | 52.5 | 163.5169 | 3000 | 45.0838 | 3045.0838 | 3045.0838 | 0 | 159.3492
0 | 23.1126 | 0 | 0 | 0 | 0 | 29.3874 | 52.5 | 192.9043 | 3000 | 52.5114 | 3052.5114 | 3052.5114 | 0 | 167.9797
0 | 34.5605 | 0 | 0 | 0 | 0 | 17.9395 | 52.5 | 210.8438 | 3000 | 32.0555 | 3032.0555 | 3032.0555 | 0 | 158.8191
0 | 38.4306 | 0 | 0 | 0 | 0 | 14.0694 | 52.5 | 224.9132 | 3000 | 25.1402 | 3025.1402 | 3025.1402 | 0 | 147.2336
0 | 30.5288 | 0 | 0 | 0 | 0 | 21.9712 | 52.5 | 246.8845 | 3000 | 39.2597 | 3039.2597 | 3023.0374 | 0 | 142.0828
0 | 23.2885 | 0 | 0 | 0 | 0 | 29.2115 | 52.5 | 276.0959 | 3000 | 52.197 | 3052.197 | 2971.0857 | 0 | 145.5238
0 | 38.6542 | 0 | 0 | 0 | 0 | 13.8458 | 52.5 | 289.9417 | 3000 | 24.7405 | 3024.7405 | 2797.6287 | 0 | 134.482
0 | 40.0581 | 0 | 0 | 0 | 0 | 12.4419 | 52.5 | 302.3837 | 3000 | 22.2321 | 3022.2321 | 2362.5262 | 0 | 121.1503
0 | 44.9755 | 0 | 0 | 0 | 0 | 7.5245 | 52.5 | 309.9082 | 3000 | 13.4453 | 3013.4453 | 1856.2563 | 0 | 97.305
0 | 46.5826 | 0 | 0 | 0 | 0 | 5.9174 | 52.5 | 315.8256 | 3000 | 10.5737 | 3010.5737 | 1918.2738 | 0 | 100.4792
0 | 34.5203 | 0 | 0 | 0 | 0 | 17.9797 | 52.5 | 333.8053 | 3000 | 32.1273 | 3032.1273 | 1680.271 | 0 | 67.4629
0 | 49.3426 | 0 | 0 | 0 | 0 | 3.1574 | 52.5 | 336.9627 | 3000 | 5.6418 | 3005.6418 | 1886.3048 | 0 | 86.3928
0 | 59.3306 | 0 | 0 | 0 | 0 | -6.8306 | 52.5 | 330.1321 | 3000 | 0 | 3000 | 1853.6259 | 0 | 73.9597
0 | 40.3649 | 0 | 0 | 0 | 0 | 12.1351 | 52.5 | 342.2671 | 3000 | 21.6837 | 3021.6837 | 2032.1249 | 0 | 51.0063
0 | 46.7864 | 0 | 0 | 0 | 0 | 5.7136 | 52.5 | 347.9807 | 3000 | 10.2095 | 3010.2095 | 2323.4665 | 0 | 81.4607
0 | 34.6281 | 0 | 0 | 0 | 0 | 17.8719 | 52.5 | 365.8527 | 3000 | 31.9348 | 3031.9348 | 2685.8596 | 0 | 112.0809
0 | 46.1327 | 0 | 0 | 0 | 0 | 6.3673 | 52.5 | 372.22 | 3000 | 11.3776 | 3011.3776 | 2919.4514 | 0 | 142.9655
0 | 241.7813 | 0 | 0 | 0 | 0 | -189.2813 | 52.5 | 182.9387 | 3000 | 0 | 3000 | 3000 | 0 | 161.07
0 | 28.7473 | 0 | 0 | 0 | 0 | 23.7527 | 52.5 | 206.6914 | 3000 | 42.4429 | 3042.4429 | 3042.4429 | 0 | 172.8108
0 | 26.5596 | 0 | 0 | 0 | 0 | 25.9404 | 52.5 | 232.6319 | 3000 | 46.3521 | 3046.3521 | 3046.3521 | 0 | 164.7467
0 | 30.6268 | 0 | 0 | 0 | 0 | 21.8732 | 52.5 | 254.5051 | 3000 | 39.0846 | 3039.0846 | 3039.0846 | 0 | 168.0614
0 | 38.9492 | 0 | 0 | 0 | 0 | 13.5508 | 52.5 | 268.0559 | 3000 | 24.2134 | 3024.2134 | 3024.2134 | 0 | 158.8014
0 | 27.9538 | 0 | 0 | 0 | 0 | 24.5462 | 52.5 | 292.6021 | 3000 | 43.8608 | 3043.8608 | 3043.8608 | 0 | 140.2002
0 | 32.2826 | 0 | 0 | 0 | 0 | 20.2174 | 52.5 | 312.8195 | 3000 | 36.1257 | 3036.1257 | 3036.1257 | 0 | 136.5042
0 | 28.1898 | 0 | 0 | 0 | 0 | 24.3102 | 52.5 | 337.1297 | 3000 | 43.4391 | 3043.4391 | 3043.4391 | 0 | 140.2112
0 | 24.0793 | 0 | 0 | 0 | 0 | 28.4207 | 52.5 | 365.5504 | 3000 | 50.784 | 3050.784 | 3050.784 | 0 | 139.2073
0 | 21.2136 | 0 | 0 | 0 | 0 | 31.2864 | 52.5 | 396.8368 | 3000 | 55.9046 | 3055.9046 | 3055.9046 | 0 | 139.0437
0 | 28.362 | 0 | 0 | 0 | 0 | 24.138 | 52.5 | 420.9748 | 3000 | 43.1315 | 3043.1315 | 3043.1315 | 0 | 156.9343
0 | 23.776 | 0 | 0 | 0 | 0 | 28.724 | 52.5 | 449.6988 | 3000 | 51.326 | 3051.326 | 2997.2517 | 0 | 182.6225
0 | 34.0159 | 0 | 0 | 0 | 0 | -34.0159 | 0 | 415.6828 | 0 | 0 | 0 | 0 | 297.4084 | 0
0 | 33.1535 | 0 | 0 | 0 | 0 | 19.3465 | 52.5 | 435.0293 | 3000 | 34.5696 | 3034.5696 | 2401.9008 | 0 | 164.6743
0 | 52.5802 | 0 | 0 | 0 | 0 | -0.080239 | 52.5 | 434.9491 | 3000 | 0 | 3000 | 2069.9229 | 0 | 126.1618
0 | 25.6467 | 0 | 0 | 0 | 0 | 26.8533 | 52.5 | 461.8023 | 3000 | 47.9832 | 3047.9832 | 1901.6091 | 0 | 108.772
0 | 42.7183 | 0 | 0 | 0 | 0 | 9.7817 | 52.5 | 471.5841 | 3000 | 17.4787 | 3017.4787 | 1719.6966 | 0 | 93.0528
0 | 42.5212 | 0 | 0 | 0 | 0 | 9.9788 | 52.5 | 481.5629 | 3000 | 17.8308 | 3017.8308 | 1665.9744 | 0 | 82.1325
0 | 38.5622 | 0 | 0 | 0 | 0 | 13.9378 | 52.5 | 495.5006 | 3000 | 24.9049 | 3024.9049 | 1683.8635 | 0 | 79.6299
0 | 37.7082 | 0 | 0 | 0 | 0 | 14.7918 | 52.5 | 510.2924 | 3000 | 26.4309 | 3026.4309 | 1798.9454 | 0 | 82.9314
0 | 50.7431 | 0 | 0 | 0 | 0 | 1.7569 | 52.5 | 512.0492 | 3000 | 3.1393 | 3003.1393 | 1997.3582 | 0 | 92.977
0 | 35.9436 | 0 | 0 | 0 | 0 | 16.5564 | 52.5 | 528.6056 | 3000 | 29.5841 | 3029.5841 | 2321.2114 | 0 | 108.6327
0 | 53.2993 | 0 | 0 | 0 | 0 | -0.7993 | 52.5 | 527.8063 | 3000 | 0 | 3000 | 2648.5174 | 0 | 134.3858
0 | 253.3833 | 0 | 0 | 0 | 0 | -200.8833 | 52.5 | 326.923 | 3000 | 0 | 3000 | 2902.6663 | 0 | 171.0832
0 | 35.6051 | 0 | 0 | 0 | 0 | 16.8949 | 52.5 | 343.8179 | 3000 | 30.1889 | 3030.1889 | 3030.1889 | 0 | 182.1144
0 | 35.8393 | 0 | 0 | 0 | 0 | 16.6607 | 52.5 | 360.4786 | 3000 | 29.7705 | 3029.7705 | 3029.7705 | 0 | 181.968
0 | 29.5165 | 0 | 0 | 0 | 0 | 22.9835 | 52.5 | 383.4621 | 3000 | 41.0685 | 3041.0685 | 3041.0685 | 0 | 165.4645
0 | 27.2136 | 0 | 0 | 0 | 0 | 25.2864 | 52.5 | 408.7485 | 3000 | 45.1834 | 3045.1834 | 3045.1834 | 0 | 154.6953
0 | 21.835 | 0 | 0 | 0 | 0 | 30.665 | 52.5 | 439.4136 | 3000 | 54.7944 | 3054.7944 | 3054.7944 | 0 | 158.2689
0 | 30.8103 | 0 | 0 | 0 | 0 | 21.6897 | 52.5 | 461.1033 | 3000 | 38.7566 | 3038.7566 | 3038.7566 | 0 | 149.598
0 | 26.4346 | 0 | 0 | 0 | 0 | 26.0654 | 52.5 | 487.1686 | 3000 | 46.5753 | 3046.5753 | 3046.5753 | 0 | 149.2822
0 | 32.9183 | 0 | 0 | 0 | 0 | 19.5817 | 52.5 | 506.7504 | 3000 | 34.99 | 3034.99 | 3034.99 | 0 | 151.7495
0 | 18.5639 | 0 | 0 | 0 | 0 | 33.9361 | 52.5 | 540.6864 | 3000 | 60.6392 | 3060.6392 | 3060.6392 | 0 | 140.4833
0 | 30.0732 | 0 | 0 | 0 | 0 | 22.4268 | 52.5 | 563.1133 | 3000 | 40.0738 | 3040.0738 | 3040.0738 | 0 | 139.5394
0 | 26.4375 | 0 | 0 | 0 | 0 | 26.0625 | 52.5 | 589.1758 | 3000 | 46.5702 | 3046.5702 | 3046.5702 | 0 | 140.2641
0 | 24.7729 | 0 | 0 | 0 | 0 | 27.7271 | 52.5 | 616.9029 | 3000 | 49.5446 | 3049.5446 | 2979.2481 | 0 | 164.7226
0 | 22.0975 | 0 | 0 | 0 | 0 | 30.4025 | 52.5 | 647.3054 | 3000 | 54.3252 | 3054.3252 | 2800.1762 | 0 | 164.5944
0 | 35.7067 | 0 | 0 | 0 | 0 | 16.7933 | 52.5 | 664.0987 | 3000 | 30.0075 | 3030.0075 | 2456.8204 | 0 | 148.8342
0 | 37.2552 | 0 | 0 | 0 | 0 | 15.2448 | 52.5 | 679.3435 | 3000 | 27.2405 | 3027.2405 | 2194.497 | 0 | 140.6892
0 | 47.3055 | 0 | 0 | 0 | 0 | 5.1945 | 52.5 | 684.538 | 3000 | 9.2818 | 3009.2818 | 2090.0195 | 0 | 135.8513
0 | 48.3753 | 0 | 0 | 0 | 0 | 4.1247 | 52.5 | 688.6627 | 3000 | 7.3703 | 3007.3703 | 1920.4778 | 0 | 105.5687
0 | 35.2005 | 0 | 0 | 0 | 0 | 17.2995 | 52.5 | 705.9622 | 3000 | 30.9119 | 3030.9119 | 2160.3164 | 0 | 137.6122
0 | 50.1484 | 0 | 0 | 0 | 0 | 2.3516 | 52.5 | 708.3137 | 3000 | 4.2019 | 3004.2019 | 2398.5703 | 0 | 138.8292
0 | 39.1395 | 0 | 0 | 0 | 0 | 13.3605 | 52.5 | 721.6743 | 3000 | 23.8735 | 3023.8735 | 2867.0582 | 0 | 154.8785
0 | 41.7908 | 0 | 0 | 0 | 0 | 10.7092 | 52.5 | 732.3834 | 3000 | 19.1359 | 3019.1359 | 2932.6171 | 0 | 154.4316
0 | 40.5847 | 0 | 0 | 0 | 0 | 11.9153 | 52.5 | 744.2987 | 3000 | 21.291 | 3021.291 | 2691.4381 | 0 | 134.5719
0 | 51.8021 | 0 | 0 | 0 | 0 | 0.69791 | 52.5 | 744.9966 | 3000 | 1.2471 | 3001.2471 | 2730.8758 | 0 | 136.7623
0 | 29.2107 | 0 | 0 | 0 | 0 | 23.2893 | 52.5 | 768.286 | 3000 | 41.6149 | 3041.6149 | 3025.3927 | 0 | 168.6051
0 | 39.8188 | 0 | 0 | 0 | 0 | 12.6812 | 52.5 | 780.9672 | 3000 | 22.6597 | 3022.6597 | 3022.6597 | 0 | 175.7677
0 | 27.7327 | 0 | 0 | 0 | 0 | 24.7673 | 52.5 | 805.7345 | 3000 | 44.2558 | 3044.2558 | 3044.2558 | 0 | 175.7753
0 | 31.6073 | 0 | 0 | 0 | 0 | 20.8927 | 52.5 | 826.6271 | 3000 | 37.3324 | 3037.3324 | 3037.3324 | 0 | 161.5861
0 | 27.6616 | 0 | 0 | 0 | 0 | 24.8384 | 52.5 | 851.4655 | 3000 | 44.3829 | 3044.3829 | 3044.3829 | 0 | 152.4627
0 | 27.3696 | 0 | 0 | 0 | 0 | 25.1304 | 52.5 | 876.5959 | 3000 | 44.9047 | 3044.9047 | 3044.9047 | 0 | 140.0961
0 | 33.2374 | 0 | 0 | 0 | 0 | 19.2626 | 52.5 | 895.8585 | 3000 | 34.4197 | 3034.4197 | 3034.4197 | 0 | 142.3143
0 | 32.9861 | 0 | 0 | 0 | 0 | 19.5139 | 52.5 | 915.3724 | 3000 | 34.8687 | 3034.8687 | 3034.8687 | 0 | 141.1214
0 | 28.9539 | 0 | 0 | 0 | 0 | 23.5461 | 52.5 | 938.9185 | 3000 | 42.0738 | 3042.0738 | 3042.0738 | 0 | 140.1788
0 | 46.6139 | 0 | 0 | 0 | 0 | 5.8861 | 52.5 | 944.8046 | 3000 | 10.5176 | 3010.5176 | 3010.5176 | 0 | 139.0558
0 | 95.8814 | 0 | 0 | 0 | 0 | -43.3814 | 52.5 | 901.4232 | 3000 | 0 | 3000 | 3000 | 0 | 142.71
0 | 123.5004 | 0 | 0 | 0 | 0 | -71.0004 | 52.5 | 830.4228 | 3000 | 0 | 3000 | 3000 | 0 | 150
0 | 116.6134 | 0 | 0 | 0 | 0 | -64.1134 | 52.5 | 766.3095 | 3000 | 0 | 3000 | 2978.3703 | 0 | 172.6859
0 | 130.1734 | 0 | 0 | 0 | 0 | -77.6734 | 52.5 | 688.6361 | 3000 | 0 | 3000 | 2821.555 | 0 | 178.4634
0 | 116.442 | 0 | 0 | 0 | 0 | -63.942 | 52.5 | 624.6941 | 3000 | 0 | 3000 | 2745.851 | 0 | 185.1253
0 | 112.679 | 0 | 0 | 0 | 0 | -60.179 | 52.5 | 564.5151 | 3000 | 0 | 3000 | 2480.8872 | 0 | 172.9675
0 | 126.9689 | 0 | 0 | 0 | 0 | -74.4689 | 52.5 | 490.0463 | 3000 | 0 | 3000 | 2507.9243 | 0 | 161.6859
0 | 115.9563 | 0 | 0 | 0 | 0 | -63.4563 | 52.5 | 426.59 | 3000 | 0 | 3000 | 2459.2575 | 0 | 154.6135
0 | 123.7106 | 0 | 0 | 0 | 0 | -71.2106 | 52.5 | 355.3793 | 3000 | 0 | 3000 | 2475.4798 | 0 | 148.2565
0 | 72.7491 | 0 | 0 | 0 | 0 | -20.2491 | 52.5 | 335.1303 | 3000 | 0 | 3000 | 2426.8129 | 0 | 141.0221
0 | 30.478 | 0 | 0 | 0 | 0 | 22.022 | 52.5 | 357.1522 | 3000 | 39.3503 | 3039.3503 | 2622.9786 | 0 | 148.9065
0 | 232.8692 | 0 | 0 | 0 | 0 | -180.3692 | 52.5 | 176.783 | 3000 | 0 | 3000 | 2610.6654 | 0 | 147.4504
0 | 50.9246 | 0 | 0 | 0 | 0 | 1.5754 | 52.5 | 178.3585 | 3000 | 2.8151 | 3002.8151 | 2797.333 | 0 | 158.6927
0 | 37.2336 | 0 | 0 | 0 | 0 | 15.2664 | 52.5 | 193.6249 | 3000 | 27.2791 | 3027.2791 | 2919.1306 | 0 | 168.3755
0 | 41.1381 | 0 | 0 | 0 | 0 | 11.3619 | 52.5 | 204.9868 | 3000 | 20.3022 | 3020.3022 | 2993.2651 | 0 | 180.9129
0 | 35.4527 | 0 | 0 | 0 | 0 | 17.0473 | 52.5 | 222.0341 | 3000 | 30.4613 | 3030.4613 | 3030.4613 | 0 | 200.9802
0 | 34.5234 | 0 | 0 | 0 | 0 | 17.9766 | 52.5 | 240.0108 | 3000 | 32.1219 | 3032.1219 | 3032.1219 | 0 | 204.1831
0 | 32.6866 | 0 | 0 | 0 | 0 | 19.8134 | 52.5 | 259.8241 | 3000 | 35.4039 | 3035.4039 | 3035.4039 | 0 | 179.3317
0 | 30.9781 | 0 | 0 | 0 | 0 | 21.5219 | 52.5 | 281.346 | 3000 | 38.4567 | 3038.4567 | 3038.4567 | 0 | 164.3805
0 | 32.3478 | 0 | 0 | 0 | 0 | 20.1522 | 52.5 | 301.4982 | 3000 | 36.0092 | 3036.0092 | 3036.0092 | 0 | 156.5974
0 | 29.6562 | 0 | 0 | 0 | 0 | 22.8438 | 52.5 | 324.3419 | 3000 | 40.8188 | 3040.8188 | 3040.8188 | 0 | 153.8654
0 | 36.6968 | 0 | 0 | 0 | 0 | 15.8032 | 52.5 | 340.1451 | 3000 | 28.2382 | 3028.2382 | 3028.2382 | 0 | 151.4725
0 | 33.0205 | 0 | 0 | 0 | 0 | 19.4795 | 52.5 | 359.6247 | 3000 | 34.8073 | 3034.8073 | 3034.8073 | 0 | 145.6708
0 | 33.309 | 0 | 0 | 0 | 0 | 19.191 | 52.5 | 378.8157 | 3000 | 34.2918 | 3034.2918 | 3034.2918 | 0 | 144.4019
0 | 20.1257 | 0 | 0 | 0 | 0 | 32.3743 | 52.5 | 411.19 | 3000 | 57.8486 | 3057.8486 | 3057.8486 | 0 | 150.2321
0 | 30.8564 | 0 | 0 | 0 | 0 | 21.6436 | 52.5 | 432.8336 | 3000 | 38.6742 | 3038.6742 | 3038.6742 | 0 | 157.5856
0 | 47.7076 | 0 | 0 | 0 | 0 | 4.7924 | 52.5 | 437.626 | 3000 | 8.5633 | 3008.5633 | 2986.9336 | 0 | 178.2303
0 | 247.8476 | 0 | 0 | 0 | 0 | -195.3476 | 52.5 | 242.2784 | 3000 | 0 | 3000 | 2913.4812 | 0 | 199.9813
0 | 55.5066 | 0 | 0 | 0 | 0 | -55.5066 | 0 | 186.7717 | 0 | 0 | 0 | 0 | 183.8525 | 0
0 | 48.1782 | 0 | 0 | 0 | 0 | 4.3218 | 52.5 | 191.0935 | 3000 | 7.7225 | 3007.7225 | 2780.6106 | 0 | 173.7882
0 | 71.2078 | 0 | 0 | 0 | 0 | -71.2078 | 0 | 119.8857 | 0 | 0 | 0 | 0 | 248.7416 | 0
0 | 121.7947 | 0 | 0 | 0 | 0 | -69.2947 | 52.5 | 50.591 | 3000 | 0 | 3000 | 2621.4802 | 0 | 170.7894
0 | 93.3893 | 0 | 0 | 0 | 0 | -40.8893 | 52.5 | 9.7018 | 3000 | 0 | 3000 | 2599.8505 | 0 | 155.991
0 | 45.2389 | 0 | 0 | 0 | 0 | 7.2611 | 52.5 | 16.9629 | 3000 | 12.9747 | 3012.9747 | 2693.9366 | 0 | 151.7225
0 | 37.9067 | 0 | 0 | 0 | 0 | 14.5933 | 52.5 | 31.5561 | 3000 | 26.0762 | 3026.0762 | 2777.3346 | 0 | 148.8374
0 | 36.1322 | 0 | 0 | 0 | 0 | 16.3678 | 52.5 | 47.9239 | 3000 | 29.2471 | 3029.2471 | 2899.4689 | 0 | 154.5417
0 | 42.6163 | 0 | 0 | 0 | 0 | 9.8837 | 52.5 | 57.8076 | 3000 | 17.6608 | 3017.6608 | 2920.3271 | 0 | 155.0694
0 | 52.5267 | 0 | 0 | 0 | 0 | -0.026716 | 52.5 | 57.7809 | 3000 | 0 | 3000 | 2891.8515 | 0 | 159.2832
0 | 54.3084 | 0 | 0 | 0 | 0 | -1.8084 | 52.5 | 55.9725 | 3000 | 0 | 3000 | 2945.9257 | 0 | 177.4331
0 | 45.9725 | 0 | 0 | 0 | 0 | 6.5275 | 52.5 | 62.5 | 3000 | 11.6638 | 3011.6638 | 3006.2564 | 0 | 196.9098
0 | 29.5584 | 0 | 0 | 0 | 0 | 22.9416 | 52.5 | 85.4416 | 3000 | 40.9936 | 3040.9936 | 3040.9936 | 0 | 194.4107
0 | 28.6757 | 0 | 0 | 0 | 0 | 23.8243 | 52.5 | 109.266 | 3000 | 42.5709 | 3042.5709 | 3042.5709 | 0 | 178.9336
0 | 34.0943 | 0 | 0 | 0 | 0 | 18.4057 | 52.5 | 127.6717 | 3000 | 32.8885 | 3032.8885 | 3032.8885 | 0 | 162.1685
0 | 20.8262 | 0 | 0 | 0 | 0 | 31.6738 | 52.5 | 159.3454 | 3000 | 56.5968 | 3056.5968 | 3056.5968 | 0 | 158.3317
0 | 28.4394 | 0 | 0 | 0 | 0 | 24.0606 | 52.5 | 183.406 | 3000 | 42.993 | 3042.993 | 3042.993 | 0 | 153.2451
0 | 28.9868 | 0 | 0 | 0 | 0 | 23.5132 | 52.5 | 206.9192 | 3000 | 42.015 | 3042.015 | 3042.015 | 0 | 151.7965
0 | 22.4855 | 0 | 0 | 0 | 0 | 30.0145 | 52.5 | 236.9337 | 3000 | 53.632 | 3053.632 | 3053.632 | 0 | 151.1242
0 | 31.7433 | 0 | 0 | 0 | 0 | 20.7567 | 52.5 | 257.6904 | 3000 | 37.0895 | 3037.0895 | 3037.0895 | 0 | 148.0885
0 | 36.3142 | 0 | 0 | 0 | 0 | 16.1858 | 52.5 | 273.8762 | 3000 | 28.9218 | 3028.9218 | 3028.9218 | 0 | 154.9899
0 | 60.568 | 0 | 0 | 0 | 0 | -8.068 | 52.5 | 265.8082 | 3000 | 0 | 3000 | 3000 | 0 | 160.59
0 | 111.2129 | 0 | 0 | 0 | 0 | -58.7129 | 52.5 | 207.0953 | 3000 | 0 | 3000 | 2962.148 | 0 | 177.2549
0 | 57.2827 | 0 | 0 | 0 | 0 | -4.7827 | 52.5 | 202.3126 | 3000 | 0 | 3000 | 2859.4069 | 0 | 191.6946
0 | 91.4128 | 0 | 0 | 0 | 0 | -82.3284 | 9.0845 | 119.9842 | 519.1128 | 0 | 519.1128 | 0 | 0 | 0
0 | 104.3029 | 0 | 0 | 0 | 0 | -51.8029 | 52.5 | 68.1814 | 3000 | 0 | 3000 | 2178.0714 | 0 | 149.5028
0 | 83.962 | 0 | 0 | 0 | 0 | -31.462 | 52.5 | 36.7194 | 3000 | 0 | 3000 | 2324.0718 | 0 | 143.1163
0 | 47.0464 | 0 | 0 | 0 | 0 | 5.4536 | 52.5 | 42.173 | 3000 | 9.7449 | 3009.7449 | 2425.743 | 0 | 139.8441
0 | 44.8454 | 0 | 0 | 0 | 0 | 7.6546 | 52.5 | 49.8277 | 3000 | 13.6778 | 3013.6778 | 2591.8986 | 0 | 142.2952
0 | 34.6798 | 0 | 0 | 0 | 0 | 17.8202 | 52.5 | 67.6479 | 3000 | 31.8423 | 3031.8423 | 2566.8037 | 0 | 140.4555
0 | 42.8916 | 0 | 0 | 0 | 0 | 9.6084 | 52.5 | 77.2563 | 3000 | 17.169 | 3017.169 | 2730.5755 | 0 | 146.195
0 | 43.6349 | 0 | 0 | 0 | 0 | 8.8651 | 52.5 | 86.1214 | 3000 | 15.8408 | 3015.8408 | 2675.173 | 0 | 142.6937
0 | 39.8137 | 0 | 0 | 0 | 0 | 12.6863 | 52.5 | 98.8077 | 3000 | 22.6687 | 3022.6687 | 2741.4826 | 0 | 147.0531
0 | 39.7734 | 0 | 0 | 0 | 0 | 12.7266 | 52.5 | 111.5344 | 3000 | 22.7408 | 3022.7408 | 2876.7403 | 0 | 160.9824
0 | 40.2237 | 0 | 0 | 0 | 0 | 12.2763 | 52.5 | 123.8107 | 3000 | 21.9362 | 3021.9362 | 3000.3065 | 0 | 178.0682
0 | 39.8185 | 0 | 0 | 0 | 0 | 12.6815 | 52.5 | 136.4922 | 3000 | 22.6601 | 3022.6601 | 3022.6601 | 0 | 188.1001
0 | 32.7615 | 0 | 0 | 0 | 0 | 19.7385 | 52.5 | 156.2306 | 3000 | 35.27 | 3035.27 | 3035.27 | 0 | 188.0046
0 | 208.7306 | 0 | 0 | 0 | 0 | -156.2306 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 170.97
0 | 23.5815 | 0 | 0 | 0 | 0 | 28.9185 | 52.5 | 28.9185 | 3000 | 51.6735 | 3051.6735 | 3051.6735 | 0 | 171.9008
0 | 31.6688 | 0 | 0 | 0 | 0 | 20.8312 | 52.5 | 49.7497 | 3000 | 37.2226 | 3037.2226 | 3037.2226 | 0 | 168.0495
0 | 24.7377 | 0 | 0 | 0 | 0 | 27.7623 | 52.5 | 77.512 | 3000 | 49.6076 | 3049.6076 | 3049.6076 | 0 | 172.7603
0 | 23.1437 | 0 | 0 | 0 | 0 | 29.3563 | 52.5 | 106.8683 | 3000 | 52.4558 | 3052.4558 | 3052.4558 | 0 | 167.4577
0 | 24.685 | 0 | 0 | 0 | 0 | 27.815 | 52.5 | 134.6834 | 3000 | 49.7018 | 3049.7018 | 3049.7018 | 0 | 162.5796
0 | 24.9693 | 0 | 0 | 0 | 0 | 27.5307 | 52.5 | 162.214 | 3000 | 49.1937 | 3049.1937 | 3049.1937 | 0 | 155.8138
0 | 25.5009 | 0 | 0 | 0 | 0 | 26.9991 | 52.5 | 189.2132 | 3000 | 48.2439 | 3048.2439 | 3048.2439 | 0 | 155.8567
0 | 43.0031 | 0 | 0 | 0 | 0 | 9.4969 | 52.5 | 198.7101 | 3000 | 16.9697 | 3016.9697 | 3016.9697 | 0 | 157.697
0 | 90.0744 | 0 | 0 | 0 | 0 | -37.5744 | 52.5 | 161.1356 | 3000 | 0 | 3000 | 2983.7777 | 0 | 161.7208
0 | 97.5382 | 0 | 0 | 0 | 0 | -45.0382 | 52.5 | 116.0974 | 3000 | 0 | 3000 | 2945.9257 | 0 | 168.0061
0 | 49.4252 | 0 | 0 | 0 | 0 | 3.0748 | 52.5 | 119.1722 | 3000 | 5.4943 | 3005.4943 | 2924.3829 | 0 | 172.7141
0 | 49.1478 | 0 | 0 | 0 | 0 | 3.3522 | 52.5 | 122.5244 | 3000 | 5.99 | 3005.99 | 2816.7301 | 0 | 173.2571
0 | 175.0244 | 0 | 0 | 0 | 0 | -122.5244 | 52.5 | 0 | 3000 | 0 | 3000 | 2794.5178 | 0 | 161.2996
0 | 42.2617 | 0 | 0 | 0 | 0 | 10.2383 | 52.5 | 10.2383 | 3000 | 18.2944 | 3018.2944 | 2596.5152 | 0 | 145.1712
0 | 47.076 | 0 | 0 | 0 | 0 | 5.424 | 52.5 | 15.6622 | 3000 | 9.6919 | 3009.6919 | 2133.689 | 0 | 112.8081
0 | 35.4137 | 0 | 0 | 0 | 0 | 17.0863 | 52.5 | 32.7486 | 3000 | 30.531 | 3030.531 | 2446.5291 | 0 | 129.3969
0 | 46.5585 | 0 | 0 | 0 | 0 | 5.9415 | 52.5 | 38.6901 | 3000 | 10.6167 | 3010.6167 | 2507.7262 | 0 | 124.3832
0 | 38.9944 | 0 | 0 | 0 | 0 | 13.5056 | 52.5 | 52.1957 | 3000 | 24.1328 | 3024.1328 | 2667.2427 | 0 | 136.5628
0 | 48.735 | 0 | 0 | 0 | 0 | 3.765 | 52.5 | 55.9607 | 3000 | 6.7275 | 3006.7275 | 2644.4301 | 0 | 138.5152
0 | 40.7964 | 0 | 0 | 0 | 0 | 11.7036 | 52.5 | 67.6644 | 3000 | 20.9128 | 3020.9128 | 2804.6158 | 0 | 150.3274
0 | 39.9117 | 0 | 0 | 0 | 0 | 12.5883 | 52.5 | 80.2526 | 3000 | 22.4936 | 3022.4936 | 2963.0119 | 0 | 167.7657
0 | 43.5411 | 0 | 0 | 0 | 0 | 8.9589 | 52.5 | 89.2116 | 3000 | 16.0084 | 3016.0084 | 3016.0084 | 0 | 174.657
0 | 30.3588 | 0 | 0 | 0 | 0 | -30.3588 | 0 | 58.8528 | 0 | 0 | 0 | 0 | 0 | 0
0 | 26.706 | 0 | 0 | 0 | 0 | 25.794 | 52.5 | 84.6468 | 3000 | 46.0905 | 3046.0905 | 3046.0905 | 0 | 190.076
0 | 54.4894 | 0 | 0 | 0 | 0 | -1.9894 | 52.5 | 82.6574 | 3000 | 0 | 3000 | 3000 | 0 | 189
0 | 131.0121 | 0 | 0 | 0 | 0 | -78.5121 | 52.5 | 4.1454 | 3000 | 0 | 3000 | 3000 | 0 | 181.59
0 | 56.6454 | 0 | 0 | 0 | 0 | -4.1454 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 170.34
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 160.89
0 | 47.8682 | 0 | 0 | 0 | 0 | 4.6318 | 52.5 | 4.6318 | 3000 | 8.2764 | 3008.2764 | 3008.2764 | 0 | 157.6337
0 | 27.0205 | 0 | 0 | 0 | 0 | 25.4795 | 52.5 | 30.1113 | 3000 | 45.5285 | 3045.5285 | 3045.5285 | 0 | 153.7992
0 | 33.4085 | 0 | 0 | 0 | 0 | 19.0915 | 52.5 | 49.2028 | 3000 | 34.114 | 3034.114 | 3034.114 | 0 | 153.6475
0 | 27.5147 | 0 | 0 | 0 | 0 | 24.9853 | 52.5 | 74.1881 | 3000 | 44.6454 | 3044.6454 | 3044.6454 | 0 | 155.7945
0 | 28.4989 | 0 | 0 | 0 | 0 | 24.0011 | 52.5 | 98.1892 | 3000 | 42.8868 | 3042.8868 | 2967.1828 | 0 | 153.3737
0 | 25.4537 | 0 | 0 | 0 | 0 | 27.0463 | 52.5 | 125.2355 | 3000 | 48.3281 | 3048.3281 | 2740.1048 | 0 | 149.1439
0 | 35.6411 | 0 | 0 | 0 | 0 | 16.8589 | 52.5 | 142.0944 | 3000 | 30.1247 | 3030.1247 | 2435.3079 | 0 | 135.1839
0 | 72.9708 | 0 | 0 | 0 | 0 | -20.4708 | 52.5 | 121.6237 | 3000 | 0 | 3000 | 2129.4045 | 0 | 118.5227
0 | 131.2678 | 0 | 0 | 0 | 0 | -78.7678 | 52.5 | 42.8559 | 3000 | 0 | 3000 | 1875.2556 | 0 | 96.8194
0 | 95.3559 | 0 | 0 | 0 | 0 | -42.8559 | 52.5 | 0 | 3000 | 0 | 3000 | 1734.6625 | 0 | 86.7158
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1680.5882 | 0 | 83.4916
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1713.0328 | 0 | 79.656
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1815.7739 | 0 | 78.1327
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2015.8486 | 0 | 88.5361
0 | 46.5807 | 0 | 0 | 0 | 0 | 5.9193 | 52.5 | 5.9193 | 3000 | 10.5771 | 3010.5771 | 2313.0192 | 0 | 107.3241
0 | 45.4417 | 0 | 0 | 0 | 0 | 7.0583 | 52.5 | 12.9777 | 3000 | 12.6123 | 3012.6123 | 2634.0925 | 0 | 131.3622
0 | 45.7615 | 0 | 0 | 0 | 0 | 6.7385 | 52.5 | 19.7162 | 3000 | 12.0409 | 3012.0409 | 2898.4849 | 0 | 167.8223
0 | 39.3742 | 0 | 0 | 0 | 0 | 13.1258 | 52.5 | 32.842 | 3000 | 23.454 | 3023.454 | 3018.0466 | 0 | 186.0626
0 | 25.5003 | 0 | 0 | 0 | 0 | 26.9997 | 52.5 | 59.8417 | 3000 | 48.2449 | 3048.2449 | 3048.2449 | 0 | 197.069
0 | 29.4128 | 0 | 0 | 0 | 0 | 23.0872 | 52.5 | 82.9289 | 3000 | 41.2538 | 3041.2538 | 3041.2538 | 0 | 186.3376
0 | 28.8686 | 0 | 0 | 0 | 0 | 23.6314 | 52.5 | 106.5603 | 3000 | 42.2262 | 3042.2262 | 3042.2262 | 0 | 184.2068
0 | 32.1671 | 0 | 0 | 0 | 0 | 20.3329 | 52.5 | 126.8932 | 3000 | 36.3321 | 3036.3321 | 3036.3321 | 0 | 179.174
0 | 40.8928 | 0 | 0 | 0 | 0 | 11.6072 | 52.5 | 138.5004 | 3000 | 20.7405 | 3020.7405 | 3020.7405 | 0 | 162.6367
0 | 24.8095 | 0 | 0 | 0 | 0 | 27.6905 | 52.5 | 166.1909 | 3000 | 49.4792 | 3049.4792 | 3049.4792 | 0 | 160.7076
0 | 41.294 | 0 | 0 | 0 | 0 | 11.206 | 52.5 | 177.3969 | 3000 | 20.0237 | 3020.0237 | 3020.0237 | 0 | 156.2258
0 | 29.9235 | 0 | 0 | 0 | 0 | 22.5765 | 52.5 | 199.9735 | 3000 | 40.3413 | 3040.3413 | 3040.3413 | 0 | 155.9695
0 | 30.6357 | 0 | 0 | 0 | 0 | 21.8643 | 52.5 | 221.8377 | 3000 | 39.0685 | 3039.0685 | 3039.0685 | 0 | 158.6394
0 | 35.7296 | 0 | 0 | 0 | 0 | 16.7704 | 52.5 | 238.6081 | 3000 | 29.9665 | 3029.9665 | 3029.9665 | 0 | 171.4961
0 | 21.7726 | 0 | 0 | 0 | 0 | 30.7274 | 52.5 | 269.3355 | 3000 | 54.9058 | 3054.9058 | 2968.3869 | 0 | 207.6684
0 | 21.8193 | 0 | 0 | 0 | 0 | -15.763 | 6.0563 | 253.5725 | 346.0752 | 0 | 346.0752 | 0 | 0 | 0
0 | 50.1134 | 0 | 0 | 0 | 0 | -37.9061 | 12.2073 | 215.6664 | 697.5579 | 0 | 697.5579 | 0 | 0 | 0
0 | 37.0913 | 0 | 0 | 0 | 0 | -19.9633 | 17.128 | 195.7031 | 978.744 | 0 | 978.744 | 0 | 0 | 0
0 | 31.3352 | 0 | 0 | 0 | 0 | 21.1648 | 52.5 | 216.8679 | 3000 | 37.8187 | 3037.8187 | 1853.5926 | 0 | 118.8153
0 | 33.9102 | 0 | 0 | 0 | 0 | 18.5898 | 52.5 | 235.4577 | 3000 | 33.2175 | 3033.2175 | 1713.8058 | 0 | 101.8001
0 | 36.4707 | 0 | 0 | 0 | 0 | 16.0293 | 52.5 | 251.487 | 3000 | 28.6422 | 3028.6422 | 1665.971 | 0 | 93.2944
0 | 36.7607 | 0 | 0 | 0 | 0 | 15.7393 | 52.5 | 267.2263 | 3000 | 28.1241 | 3028.1241 | 1730.342 | 0 | 96.0513
0 | 54.8145 | 0 | 0 | 0 | 0 | -2.3145 | 52.5 | 264.9119 | 3000 | 0 | 3000 | 1810.3664 | 0 | 98.2124
0 | 244.0418 | 0 | 0 | 0 | 0 | -191.5418 | 52.5 | 73.3701 | 3000 | 0 | 3000 | 2069.9229 | 0 | 114.1976
0 | 52.2409 | 0 | 0 | 0 | 0 | 0.25911 | 52.5 | 73.6292 | 3000 | 0.463 | 3000.463 | 2319.1274 | 0 | 126.9258
0 | 35.2419 | 0 | 0 | 0 | 0 | 17.2581 | 52.5 | 90.8874 | 3000 | 30.838 | 3030.838 | 2722.6148 | 0 | 157.476
0 | 43.3045 | 0 | 0 | 0 | 0 | 9.1955 | 52.5 | 100.0829 | 3000 | 16.4312 | 3016.4312 | 2902.8752 | 0 | 174.3177
0 | 26.9121 | 0 | 0 | 0 | 0 | 25.5879 | 52.5 | 125.6707 | 3000 | 45.7221 | 3045.7221 | 3040.3147 | 0 | 192.9384
0 | 20.0163 | 0 | 0 | 0 | 0 | 32.4837 | 52.5 | 158.1545 | 3000 | 58.0441 | 3058.0441 | 3058.0441 | 0 | 188.3144
0 | 24.8923 | 0 | 0 | 0 | 0 | 27.6077 | 52.5 | 185.7622 | 3000 | 49.3313 | 3049.3313 | 3049.3313 | 0 | 179.2397
0 | 21.5522 | 0 | 0 | 0 | 0 | 30.9478 | 52.5 | 216.71 | 3000 | 55.2996 | 3055.2996 | 3055.2996 | 0 | 175.2825
0 | 24.9351 | 0 | 0 | 0 | 0 | 27.5649 | 52.5 | 244.2749 | 3000 | 49.2549 | 3049.2549 | 3049.2549 | 0 | 159.9029
0 | 30.6189 | 0 | 0 | 0 | 0 | 21.8811 | 52.5 | 266.156 | 3000 | 39.0986 | 3039.0986 | 3039.0986 | 0 | 151.1952
0 | 26.6618 | 0 | 0 | 0 | 0 | 25.8382 | 52.5 | 291.9942 | 3000 | 46.1695 | 3046.1695 | 3046.1695 | 0 | 151.3642
0 | 33.368 | 0 | 0 | 0 | 0 | 19.132 | 52.5 | 311.1262 | 3000 | 34.1863 | 3034.1863 | 3034.1863 | 0 | 153.5298
0 | 30.4894 | 0 | 0 | 0 | 0 | 22.0106 | 52.5 | 333.1368 | 3000 | 39.33 | 3039.33 | 3039.33 | 0 | 151.8449
0 | 31.2634 | 0 | 0 | 0 | 0 | 21.2366 | 52.5 | 354.3734 | 3000 | 37.947 | 3037.947 | 3037.947 | 0 | 152.2619
0 | 31.2964 | 0 | 0 | 0 | 0 | 21.2036 | 52.5 | 375.577 | 3000 | 37.888 | 3037.888 | 3037.888 | 0 | 159.398
0 | 225.7896 | 0 | 0 | 0 | 0 | -173.2896 | 52.5 | 202.2874 | 3000 | 0 | 3000 | 2918.8886 | 0 | 181.5549
0 | 32.0331 | 0 | 0 | 0 | 0 | 20.4669 | 52.5 | 222.7543 | 3000 | 36.5716 | 3036.5716 | 2706.7187 | 0 | 181.5667
0 | 55.3564 | 0 | 0 | 0 | 0 | -44.7578 | 10.5986 | 177.9965 | 605.6316 | 0 | 605.6316 | 0 | 0 | 0
0 | 63.7434 | 0 | 0 | 0 | 0 | -11.2434 | 52.5 | 166.7531 | 3000 | 0 | 3000 | 1994.2189 | 0 | 128.5673
0 | 55.5224 | 0 | 0 | 0 | 0 | -3.0224 | 52.5 | 163.7307 | 3000 | 0 | 3000 | 1810.3664 | 0 | 112.4419
0 | 37.6789 | 0 | 0 | 0 | 0 | 14.8211 | 52.5 | 178.5518 | 3000 | 26.4833 | 3026.4833 | 1647.5899 | 0 | 98.5094
0 | 39.8337 | 0 | 0 | 0 | 0 | 12.6663 | 52.5 | 191.2181 | 3000 | 22.6329 | 3022.6329 | 1611.295 | 0 | 91.4732
0 | 44.431 | 0 | 0 | 0 | 0 | 8.069 | 52.5 | 199.2871 | 3000 | 14.4182 | 3014.4182 | 1662.5619 | 0 | 93.0037
0 | 44.5212 | 0 | 0 | 0 | 0 | 7.9788 | 52.5 | 207.2659 | 3000 | 14.257 | 3014.257 | 1759.7344 | 0 | 96.0639
0 | 31.113 | 0 | 0 | 0 | 0 | 21.387 | 52.5 | 228.6529 | 3000 | 38.2158 | 3038.2158 | 1967.5456 | 0 | 103.06
0 | 50.5501 | 0 | 0 | 0 | 0 | 1.9499 | 52.5 | 230.6028 | 3000 | 3.4842 | 3003.4842 | 2197.7778 | 0 | 115.1416
0 | 52.232 | 0 | 0 | 0 | 0 | 0.26804 | 52.5 | 230.8708 | 3000 | 0.47896 | 3000.479 | 2578.6998 | 0 | 143.6594
0 | 77.9983 | 0 | 0 | 0 | 0 | -25.4983 | 52.5 | 205.3725 | 3000 | 0 | 3000 | 2864.8144 | 0 | 169.2819
0 | 74.0535 | 0 | 0 | 0 | 0 | -21.5535 | 52.5 | 183.819 | 3000 | 0 | 3000 | 2994.5926 | 0 | 185.6947
0 | 70.8004 | 0 | 0 | 0 | 0 | -18.3004 | 52.5 | 165.5186 | 3000 | 0 | 3000 | 3000 | 0 | 182.82
0 | 111.9604 | 0 | 0 | 0 | 0 | -59.4604 | 52.5 | 106.0582 | 3000 | 0 | 3000 | 3000 | 0 | 173.28
0 | 80.8167 | 0 | 0 | 0 | 0 | -28.3167 | 52.5 | 77.7415 | 3000 | 0 | 3000 | 3000 | 0 | 171.03
0 | 28.8989 | 0 | 0 | 0 | 0 | 23.6011 | 52.5 | 101.3426 | 3000 | 42.172 | 3042.172 | 3042.172 | 0 | 164.4902
0 | 36.5467 | 0 | 0 | 0 | 0 | 15.9533 | 52.5 | 117.2959 | 3000 | 28.5065 | 3028.5065 | 3028.5065 | 0 | 155.9681
0 | 22.9338 | 0 | 0 | 0 | 0 | 29.5662 | 52.5 | 146.8621 | 3000 | 52.8308 | 3052.8308 | 3052.8308 | 0 | 159.2967
0 | 34.6197 | 0 | 0 | 0 | 0 | 17.8803 | 52.5 | 164.7424 | 3000 | 31.9497 | 3031.9497 | 3031.9497 | 0 | 156.2667
0 | 31.9934 | 0 | 0 | 0 | 0 | 20.5066 | 52.5 | 185.2489 | 3000 | 36.6425 | 3036.6425 | 3036.6425 | 0 | 154.2007
0 | 33.8615 | 0 | 0 | 0 | 0 | 18.6385 | 52.5 | 203.8874 | 3000 | 33.3045 | 3033.3045 | 3033.3045 | 0 | 156.6095
0 | 28.1053 | 0 | 0 | 0 | 0 | 24.3947 | 52.5 | 228.2821 | 3000 | 43.59 | 3043.59 | 3043.59 | 0 | 162.9842
0 | 34.4314 | 0 | 0 | 0 | 0 | 18.0686 | 52.5 | 246.3507 | 3000 | 32.2861 | 3032.2861 | 2907.9154 | 0 | 180.2617
0 | 43.6092 | 0 | 0 | 0 | 0 | 8.8908 | 52.5 | 255.2414 | 3000 | 15.8866 | 3015.8866 | 2610.3297 | 0 | 181.2352
0 | 82.0077 | 0 | 0 | 0 | 0 | -68.6649 | 13.3428 | 186.5765 | 762.447 | 0 | 762.447 | 0 | 0 | 0
0 | 68.6855 | 0 | 0 | 0 | 0 | -16.1855 | 52.5 | 170.391 | 3000 | 0 | 3000 | 1945.5521 | 0 | 127.6088
0 | 54.6015 | 0 | 0 | 0 | 0 | -2.1015 | 52.5 | 168.2895 | 3000 | 0 | 3000 | 1734.6625 | 0 | 103.5247
0 | 102.4862 | 0 | 0 | 0 | 0 | -49.9862 | 52.5 | 118.3033 | 3000 | 0 | 3000 | 1588.662 | 0 | 89.5052
0 | 61.3371 | 0 | 0 | 0 | 0 | -8.8371 | 52.5 | 109.4662 | 3000 | 0 | 3000 | 1550.81 | 0 | 79.8667
0 | 50.7133 | 0 | 0 | 0 | 0 | 1.7867 | 52.5 | 111.2529 | 3000 | 3.1926 | 3003.1926 | 1618.8917 | 0 | 84.8461
0 | 51.7079 | 0 | 0 | 0 | 0 | 0.79209 | 52.5 | 112.045 | 3000 | 1.4154 | 3001.4154 | 1725.263 | 0 | 91.6805
0 | 52.7399 | 0 | 0 | 0 | 0 | -0.23987 | 52.5 | 111.8051 | 3000 | 0 | 3000 | 1896.8853 | 0 | 99.7762
0 | 46.8004 | 0 | 0 | 0 | 0 | 5.6996 | 52.5 | 117.5047 | 3000 | 10.1844 | 3010.1844 | 2182.8483 | 0 | 115.9529
0 | 42.991 | 0 | 0 | 0 | 0 | 9.509 | 52.5 | 127.0137 | 3000 | 16.9913 | 3016.9913 | 2557.3602 | 0 | 147.3039
0 | 49.1318 | 0 | 0 | 0 | 0 | 3.3682 | 52.5 | 130.3819 | 3000 | 6.0186 | 3006.0186 | 2849.2032 | 0 | 175.226
0 | 47.9858 | 0 | 0 | 0 | 0 | 4.5142 | 52.5 | 134.8961 | 3000 | 8.0663 | 3008.0663 | 2997.2515 | 0 | 186.429
0 | 35.0971 | 0 | 0 | 0 | 0 | 17.4029 | 52.5 | 152.299 | 3000 | 31.0967 | 3031.0967 | 3031.0967 | 0 | 187.8371
0 | 30.3096 | 0 | 0 | 0 | 0 | 22.1904 | 52.5 | 174.4894 | 3000 | 39.6513 | 3039.6513 | 3039.6513 | 0 | 181.0416
0 | 37.6852 | 0 | 0 | 0 | 0 | 14.8148 | 52.5 | 189.3042 | 3000 | 26.4721 | 3026.4721 | 3026.4721 | 0 | 174.3248
0 | 29.4385 | 0 | 0 | 0 | 0 | 23.0615 | 52.5 | 212.3658 | 3000 | 41.2079 | 3041.2079 | 3041.2079 | 0 | 164.9247
0 | 23.708 | 0 | 0 | 0 | 0 | 28.792 | 52.5 | 241.1578 | 3000 | 51.4475 | 3051.4475 | 3051.4475 | 0 | 160.201
0 | 25.6287 | 0 | 0 | 0 | 0 | 26.8713 | 52.5 | 268.0291 | 3000 | 48.0154 | 3048.0154 | 3048.0154 | 0 | 158.7102
0 | 23.7159 | 0 | 0 | 0 | 0 | 28.7841 | 52.5 | 296.8131 | 3000 | 51.4333 | 3051.4333 | 3051.4333 | 0 | 158.8881
0 | 25.3371 | 0 | 0 | 0 | 0 | 27.1629 | 52.5 | 323.976 | 3000 | 48.5365 | 3048.5365 | 3048.5365 | 0 | 157.0606
0 | 31.0478 | 0 | 0 | 0 | 0 | 21.4522 | 52.5 | 345.4282 | 3000 | 38.3322 | 3038.3322 | 3038.3322 | 0 | 158.2971
0 | 71.1884 | 0 | 0 | 0 | 0 | -18.6884 | 52.5 | 326.7398 | 3000 | 0 | 3000 | 3000 | 0 | 161.61
0 | 87.2451 | 0 | 0 | 0 | 0 | -34.7451 | 52.5 | 291.9947 | 3000 | 0 | 3000 | 2875.6292 | 0 | 180.9058
0 | 32.3268 | 0 | 0 | 0 | 0 | -25.3242 | 7.0026 | 266.6706 | 400.1495 | 0 | 400.1495 | 0 | 0 | 0
0 | 57.8075 | 0 | 0 | 0 | 0 | -44.654 | 13.1536 | 222.0166 | 751.6321 | 0 | 751.6321 | 0 | 0 | 0
0 | 38.887 | 0 | 0 | 0 | 0 | 13.613 | 52.5 | 235.6296 | 3000 | 24.3247 | 3024.3247 | 1991.5064 | 0 | 132.8335
0 | 45.1295 | 0 | 0 | 0 | 0 | 7.3705 | 52.5 | 243.0001 | 3000 | 13.17 | 3013.17 | 1796.4993 | 0 | 114.1675
0 | 109.8033 | 0 | 0 | 0 | 0 | -57.3033 | 52.5 | 185.6968 | 3000 | 0 | 3000 | 2194.2936 | 0 | 133.808
0 | 97.4037 | 0 | 0 | 0 | 0 | -44.9037 | 52.5 | 140.7931 | 3000 | 0 | 3000 | 2291.6273 | 0 | 135.0914
0 | 54.9958 | 0 | 0 | 0 | 0 | -2.4958 | 52.5 | 138.2973 | 3000 | 0 | 3000 | 2340.2941 | 0 | 128.3885
0 | 49.9718 | 0 | 0 | 0 | 0 | 2.5282 | 52.5 | 140.8256 | 3000 | 4.5176 | 3004.5176 | 2112.2925 | 0 | 113.8526
0 | 37.466 | 0 | 0 | 0 | 0 | 15.034 | 52.5 | 155.8596 | 3000 | 26.8638 | 3026.8638 | 2221.1575 | 0 | 120.5644
0 | 38.856 | 0 | 0 | 0 | 0 | 13.644 | 52.5 | 169.5036 | 3000 | 24.38 | 3024.38 | 2391.7112 | 0 | 129.1524
0 | 36.2409 | 0 | 0 | 0 | 0 | 16.2591 | 52.5 | 185.7627 | 3000 | 29.0529 | 3029.0529 | 2747.8668 | 0 | 161.9043
0 | 39.7466 | 0 | 0 | 0 | 0 | 12.7534 | 52.5 | 198.5161 | 3000 | 22.7886 | 3022.7886 | 2947.0847 | 0 | 184.7527
0 | 43.168 | 0 | 0 | 0 | 0 | 9.332 | 52.5 | 207.8481 | 3000 | 16.675 | 3016.675 | 3011.2676 | 0 | 207.8377
0 | 24.0548 | 0 | 0 | 0 | 0 | 28.4452 | 52.5 | 236.2932 | 3000 | 50.8277 | 3050.8277 | 3050.8277 | 0 | 207.4258
0 | 24.5732 | 0 | 0 | 0 | 0 | 27.9268 | 52.5 | 264.22 | 3000 | 49.9015 | 3049.9015 | 3049.9015 | 0 | 195.2547
0 | 30.5812 | 0 | 0 | 0 | 0 | 21.9188 | 52.5 | 286.1388 | 3000 | 39.1659 | 3039.1659 | 3039.1659 | 0 | 189.0361
0 | 25.1417 | 0 | 0 | 0 | 0 | 27.3583 | 52.5 | 313.497 | 3000 | 48.8856 | 3048.8856 | 3048.8856 | 0 | 180.0367
0 | 29.0126 | 0 | 0 | 0 | 0 | 23.4874 | 52.5 | 336.9845 | 3000 | 41.9689 | 3041.9689 | 3041.9689 | 0 | 166.0611
0 | 237.7834 | 0 | 0 | 0 | 0 | -185.2834 | 52.5 | 151.7011 | 3000 | 0 | 3000 | 3000 | 0 | 162.03
0 | 30.311 | 0 | 0 | 0 | 0 | 22.189 | 52.5 | 173.8901 | 3000 | 39.6488 | 3039.6488 | 3039.6488 | 0 | 160.9494
0 | 223.4418 | 0 | 0 | 0 | 0 | -170.9418 | 52.5 | 2.9483 | 3000 | 0 | 3000 | 3000 | 0 | 156.66
0 | 36.9463 | 0 | 0 | 0 | 0 | 15.5537 | 52.5 | 18.502 | 3000 | 27.7924 | 3027.7924 | 3027.7924 | 0 | 158.9591
0 | 46.7813 | 0 | 0 | 0 | 0 | 5.7187 | 52.5 | 24.2207 | 3000 | 10.2186 | 3010.2186 | 3010.2186 | 0 | 168.7228
0 | 76.7207 | 0 | 0 | 0 | 0 | -24.2207 | 52.5 | 0 | 3000 | 0 | 3000 | 2951.3332 | 0 | 190.7151
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 286.5935 | 0
0 | 10.9771 | 0 | 0 | 0 | 0 | 0 | 10.9771 | 0 | 627.2613 | 0 | 627.2613 | 0 | 0 | 0
0 | 37.1638 | 0 | 0 | 0 | 0 | 15.3362 | 52.5 | 15.3362 | 3000 | 27.4038 | 3027.4038 | 2346.0682 | 0 | 156.1308
0 | 59.4843 | 0 | 0 | 0 | 0 | -6.9843 | 52.5 | 8.3519 | 3000 | 0 | 3000 | 2210.5159 | 0 | 141.4067
0 | 60.8519 | 0 | 0 | 0 | 0 | -8.3519 | 52.5 | 0 | 3000 | 0 | 3000 | 2291.6273 | 0 | 142.058
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2524.1466 | 0 | 151.7012
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2464.6649 | 0 | 145.6863
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2599.8505 | 0 | 148.4775
0 | 34.0527 | 0 | 0 | 0 | 0 | 18.4473 | 52.5 | 18.4473 | 3000 | 32.9629 | 3032.9629 | 2627.406 | 0 | 146.2677
0 | 43.1372 | 0 | 0 | 0 | 0 | 9.3628 | 52.5 | 27.8101 | 3000 | 16.7301 | 3016.7301 | 2649.0252 | 0 | 141.9083
0 | 45.6278 | 0 | 0 | 0 | 0 | 6.8722 | 52.5 | 34.6823 | 3000 | 12.2796 | 3012.2796 | 2720.2787 | 0 | 154.3214
0 | 45.6317 | 0 | 0 | 0 | 0 | 6.8683 | 52.5 | 41.5506 | 3000 | 12.2727 | 3012.2727 | 2931.1613 | 0 | 180.0612
0 | 38.3372 | 0 | 0 | 0 | 0 | 14.1628 | 52.5 | 55.7134 | 3000 | 25.3071 | 3025.3071 | 3014.4922 | 0 | 191.2092
0 | 31.047 | 0 | 0 | 0 | 0 | 21.453 | 52.5 | 77.1664 | 3000 | 38.3336 | 3038.3336 | 3038.3336 | 0 | 191.6581
0 | 19.8084 | 0 | 0 | 0 | 0 | 32.6916 | 52.5 | 109.858 | 3000 | 58.4156 | 3058.4156 | 3058.4156 | 0 | 184.606
0 | 25.8036 | 0 | 0 | 0 | 0 | 26.6964 | 52.5 | 136.5545 | 3000 | 47.703 | 3047.703 | 3047.703 | 0 | 183.6851
0 | 28.5413 | 0 | 0 | 0 | 0 | 23.9587 | 52.5 | 160.5132 | 3000 | 42.8111 | 3042.8111 | 3042.8111 | 0 | 177.3046
0 | 34.3987 | 0 | 0 | 0 | 0 | 18.1013 | 52.5 | 178.6145 | 3000 | 32.3447 | 3032.3447 | 3032.3447 | 0 | 181.2736
0 | 29.4832 | 0 | 0 | 0 | 0 | 23.0168 | 52.5 | 201.6313 | 3000 | 41.1279 | 3041.1279 | 3041.1279 | 0 | 177.8147
0 | 36.2673 | 0 | 0 | 0 | 0 | 16.2327 | 52.5 | 217.864 | 3000 | 29.0057 | 3029.0057 | 3029.0057 | 0 | 173.7438
0 | 23.5957 | 0 | 0 | 0 | 0 | 28.9043 | 52.5 | 246.7683 | 3000 | 51.6481 | 3051.6481 | 3051.6481 | 0 | 168.1763
0 | 21.7174 | 0 | 0 | 0 | 0 | 30.7826 | 52.5 | 277.5509 | 3000 | 55.0044 | 3055.0044 | 3055.0044 | 0 | 166.345
0 | 38.6022 | 0 | 0 | 0 | 0 | 13.8978 | 52.5 | 291.4486 | 3000 | 24.8334 | 3024.8334 | 3019.426 | 0 | 168.8765
0 | 34.6248 | 0 | 0 | 0 | 0 | 17.8752 | 52.5 | 309.3238 | 3000 | 31.9405 | 3031.9405 | 2875.1252 | 0 | 168.9999
0 | 82.4578 | 0 | 0 | 0 | 0 | -29.9578 | 52.5 | 279.366 | 3000 | 0 | 3000 | 2567.406 | 0 | 154.3011
0 | 79.1585 | 0 | 0 | 0 | 0 | -26.6585 | 52.5 | 252.7075 | 3000 | 0 | 3000 | 2226.7382 | 0 | 138.6813
0 | 46.8254 | 0 | 0 | 0 | 0 | 5.6746 | 52.5 | 258.382 | 3000 | 10.1397 | 3010.1397 | 2025.9883 | 0 | 125.5302
0 | 54.5313 | 0 | 0 | 0 | 0 | -2.0313 | 52.5 | 256.3507 | 3000 | 0 | 3000 | 1940.1447 | 0 | 111.4613
0 | 49.0517 | 0 | 0 | 0 | 0 | 3.4483 | 52.5 | 259.7991 | 3000 | 6.1617 | 3006.1617 | 2270.7519 | 0 | 124.5507
0 | 57.755 | 0 | 0 | 0 | 0 | -5.255 | 52.5 | 254.5441 | 3000 | 0 | 3000 | 1821.1813 | 0 | 97.5607
0 | 40.7614 | 0 | 0 | 0 | 0 | 11.7386 | 52.5 | 266.2827 | 3000 | 20.9753 | 3020.9753 | 2442.3808 | 0 | 129.495
0 | 53.0703 | 0 | 0 | 0 | 0 | -0.57031 | 52.5 | 265.7124 | 3000 | 0 | 3000 | 2372.7387 | 0 | 123.6434
0 | 56.93 | 0 | 0 | 0 | 0 | -4.43 | 52.5 | 261.2824 | 3000 | 0 | 3000 | 2470.0723 | 0 | 127.0111
0 | 54.1174 | 0 | 0 | 0 | 0 | -1.6174 | 52.5 | 259.665 | 3000 | 0 | 3000 | 2313.257 | 0 | 117.1665
0 | 44.0496 | 0 | 0 | 0 | 0 | 8.4504 | 52.5 | 268.1154 | 3000 | 15.0998 | 3015.0998 | 2793.3954 | 0 | 147.5751
0 | 48.7104 | 0 | 0 | 0 | 0 | 3.7896 | 52.5 | 271.905 | 3000 | 6.7715 | 3006.7715 | 2936.4749 | 0 | 170.4036
0 | 39.3939 | 0 | 0 | 0 | 0 | 13.1061 | 52.5 | 285.0111 | 3000 | 23.4189 | 3023.4189 | 3012.604 | 0 | 184.04
0 | 29.1357 | 0 | 0 | 0 | 0 | 23.3643 | 52.5 | 308.3754 | 3000 | 41.7489 | 3041.7489 | 3041.7489 | 0 | 186.3984
0 | 31.2682 | 0 | 0 | 0 | 0 | 21.2318 | 52.5 | 329.6072 | 3000 | 37.9384 | 3037.9384 | 3037.9384 | 0 | 184.0079
0 | 29.6909 | 0 | 0 | 0 | 0 | 22.8091 | 52.5 | 352.4163 | 3000 | 40.7568 | 3040.7568 | 3040.7568 | 0 | 182.567
0 | 27.4234 | 0 | 0 | 0 | 0 | 25.0766 | 52.5 | 377.4929 | 3000 | 44.8086 | 3044.8086 | 3044.8086 | 0 | 181.5924
0 | 28.8353 | 0 | 0 | 0 | 0 | 23.6647 | 52.5 | 401.1576 | 3000 | 42.2857 | 3042.2857 | 3042.2857 | 0 | 166.1088
0 | 29.1477 | 0 | 0 | 0 | 0 | 23.3523 | 52.5 | 424.5099 | 3000 | 41.7274 | 3041.7274 | 3041.7274 | 0 | 167.295
0 | 30.5527 | 0 | 0 | 0 | 0 | 21.9473 | 52.5 | 446.4572 | 3000 | 39.2169 | 3039.2169 | 3039.2169 | 0 | 166.2452
0 | 35.0441 | 0 | 0 | 0 | 0 | 17.4559 | 52.5 | 463.9131 | 3000 | 31.1914 | 3031.1914 | 3031.1914 | 0 | 156.4398
0 | 23.0923 | 0 | 0 | 0 | 0 | 29.4077 | 52.5 | 493.3208 | 3000 | 52.5477 | 3052.5477 | 3052.5477 | 0 | 159.4346
0 | 32.8738 | 0 | 0 | 0 | 0 | 19.6262 | 52.5 | 512.947 | 3000 | 35.0694 | 3035.0694 | 3029.662 | 0 | 165.7225
0 | 29.8721 | 0 | 0 | 0 | 0 | 22.6279 | 52.5 | 535.5749 | 3000 | 40.4331 | 3040.4331 | 2937.692 | 0 | 153.8176
0 | 33.2339 | 0 | 0 | 0 | 0 | 19.2661 | 52.5 | 554.841 | 3000 | 34.4259 | 3034.4259 | 2785.6844 | 0 | 148.1427
0 | 41.1658 | 0 | 0 | 0 | 0 | 11.3342 | 52.5 | 566.1752 | 3000 | 20.2527 | 3020.2527 | 2301.0652 | 0 | 127.387
0 | 50.5666 | 0 | 0 | 0 | 0 | 1.9334 | 52.5 | 568.1087 | 3000 | 3.4548 | 3003.4548 | 2003.0811 | 0 | 109.6887
0 | 45.8236 | 0 | 0 | 0 | 0 | 6.6764 | 52.5 | 574.7851 | 3000 | 11.9299 | 3011.9299 | 1762.8147 | 0 | 91.8426
0 | 57.7658 | 0 | 0 | 0 | 0 | -5.2658 | 52.5 | 569.5193 | 3000 | 0 | 3000 | 1713.0328 | 0 | 93.5316
0 | 45.164 | 0 | 0 | 0 | 0 | 7.336 | 52.5 | 576.8553 | 3000 | 13.1085 | 3013.1085 | 1536.8815 | 0 | 76.8441
0 | 40.409 | 0 | 0 | 0 | 0 | 12.091 | 52.5 | 588.9463 | 3000 | 21.6049 | 3021.6049 | 1610.267 | 0 | 87.1154
0 | 36.1296 | 0 | 0 | 0 | 0 | 16.3704 | 52.5 | 605.3167 | 3000 | 29.2517 | 3029.2517 | 1823.3959 | 0 | 91.1698
0 | 48.3022 | 0 | 0 | 0 | 0 | 4.1978 | 52.5 | 609.5145 | 3000 | 7.5009 | 3007.5009 | 2196.3872 | 0 | 121.3065
0 | 45.0692 | 0 | 0 | 0 | 0 | 7.4308 | 52.5 | 616.9452 | 3000 | 13.2778 | 3013.2778 | 2407.6461 | 0 | 131.6982
0 | 48.3344 | 0 | 0 | 0 | 0 | 4.1656 | 52.5 | 621.1109 | 3000 | 7.4434 | 3007.4434 | 2704.6276 | 0 | 136.5837
0 | 21.8228 | 0 | 0 | 0 | 0 | 30.6772 | 52.5 | 651.788 | 3000 | 54.8161 | 3054.8161 | 2979.1121 | 0 | 169.4221
0 | 37.1682 | 0 | 0 | 0 | 0 | 15.3318 | 52.5 | 667.1198 | 3000 | 27.3959 | 3027.3959 | 3016.581 | 0 | 180.0899
0 | 25.8092 | 0 | 0 | 0 | 0 | 26.6908 | 52.5 | 693.8107 | 3000 | 47.693 | 3047.693 | 3047.693 | 0 | 188.1646
0 | 224.5988 | 0 | 0 | 0 | 0 | -172.0988 | 52.5 | 521.7119 | 3000 | 0 | 3000 | 3000 | 0 | 174.84
0 | 29.9883 | 0 | 0 | 0 | 0 | 22.5117 | 52.5 | 544.2236 | 3000 | 40.2255 | 3040.2255 | 3040.2255 | 0 | 186.001
0 | 23.9003 | 0 | 0 | 0 | 0 | 28.5997 | 52.5 | 572.8233 | 3000 | 51.1038 | 3051.1038 | 3051.1038 | 0 | 183.3713
0 | 39.3494 | 0 | 0 | 0 | 0 | 13.1506 | 52.5 | 585.9739 | 3000 | 23.4984 | 3023.4984 | 3023.4984 | 0 | 183.3449
0 | 30.1971 | 0 | 0 | 0 | 0 | 22.3029 | 52.5 | 608.2768 | 3000 | 39.8524 | 3039.8524 | 3039.8524 | 0 | 172.086
0 | 25.9938 | 0 | 0 | 0 | 0 | 26.5062 | 52.5 | 634.783 | 3000 | 47.3631 | 3047.3631 | 3047.3631 | 0 | 169.7991
0 | 30.267 | 0 | 0 | 0 | 0 | 22.233 | 52.5 | 657.0161 | 3000 | 39.7275 | 3039.7275 | 3039.7275 | 0 | 163.8413
0 | 28.3972 | 0 | 0 | 0 | 0 | 24.1028 | 52.5 | 681.1188 | 3000 | 43.0684 | 3043.0684 | 3043.0684 | 0 | 161.2522
0 | 30.3701 | 0 | 0 | 0 | 0 | 22.1299 | 52.5 | 703.2487 | 3000 | 39.5432 | 3039.5432 | 3034.1357 | 0 | 174.7662
0 | 38.3005 | 0 | 0 | 0 | 0 | 14.1995 | 52.5 | 717.4482 | 3000 | 25.3726 | 3025.3726 | 2895.5944 | 0 | 188.8796
0 | 48.6458 | 0 | 0 | 0 | 0 | -41.8324 | 6.8134 | 675.6158 | 389.3346 | 0 | 389.3346 | 0 | 0 | 0
0 | 53.3945 | 0 | 0 | 0 | 0 | -40.7141 | 12.6804 | 634.9017 | 724.595 | 0 | 724.595 | 0 | 0 | 0
0 | 33.3378 | 0 | 0 | 0 | 0 | 19.1622 | 52.5 | 654.0639 | 3000 | 34.2403 | 3034.2403 | 2033.8666 | 0 | 142.0452
0 | 48.1086 | 0 | 0 | 0 | 0 | 4.3914 | 52.5 | 658.4552 | 3000 | 7.8468 | 3007.8468 | 1807.3984 | 0 | 110.2513
0 | 48.8877 | 0 | 0 | 0 | 0 | 3.6123 | 52.5 | 662.0675 | 3000 | 6.4547 | 3006.4547 | 1643.7835 | 0 | 92.4628
0 | 246.6632 | 0 | 0 | 0 | 0 | -194.1632 | 52.5 | 467.9043 | 3000 | 0 | 3000 | 1588.662 | 0 | 80.8629
0 | 29.8429 | 0 | 0 | 0 | 0 | 22.6571 | 52.5 | 490.5614 | 3000 | 40.4853 | 3040.4853 | 1661.5918 | 0 | 85.572
0 | 54.1599 | 0 | 0 | 0 | 0 | -1.6599 | 52.5 | 488.9015 | 3000 | 0 | 3000 | 1734.6625 | 0 | 93.6718
0 | 41.3008 | 0 | 0 | 0 | 0 | 11.1992 | 52.5 | 500.1007 | 3000 | 20.0116 | 3020.0116 | 1987.1933 | 0 | 103.8507
0 | 41.9413 | 0 | 0 | 0 | 0 | 10.5587 | 52.5 | 510.6594 | 3000 | 18.867 | 3018.867 | 2218.568 | 0 | 114.6112
0 | 35.1935 | 0 | 0 | 0 | 0 | 17.3065 | 52.5 | 527.9659 | 3000 | 30.9245 | 3030.9245 | 2571.2933 | 0 | 143.8896
0 | 39.1245 | 0 | 0 | 0 | 0 | 13.3755 | 52.5 | 541.3414 | 3000 | 23.9002 | 3023.9002 | 2867.0848 | 0 | 177.7879
0 | 47.6156 | 0 | 0 | 0 | 0 | 4.8844 | 52.5 | 546.2259 | 3000 | 8.7278 | 3008.7278 | 2992.5056 | 0 | 192.3283
0 | 31.5275 | 0 | 0 | 0 | 0 | 20.9725 | 52.5 | 567.1984 | 3000 | 37.4752 | 3037.4752 | 3037.4752 | 0 | 193.0619
0 | 22.653 | 0 | 0 | 0 | 0 | 29.847 | 52.5 | 597.0454 | 3000 | 53.3326 | 3053.3326 | 3053.3326 | 0 | 185.3373
0 | 30.235 | 0 | 0 | 0 | 0 | 22.265 | 52.5 | 619.3104 | 3000 | 39.7847 | 3039.7847 | 3039.7847 | 0 | 174.5748
0 | 27.1721 | 0 | 0 | 0 | 0 | 25.3279 | 52.5 | 644.6384 | 3000 | 45.2576 | 3045.2576 | 3045.2576 | 0 | 157.1353
0 | 34.8835 | 0 | 0 | 0 | 0 | 17.6165 | 52.5 | 662.2548 | 3000 | 31.4783 | 3031.4783 | 3031.4783 | 0 | 157.0306
0 | 24.8109 | 0 | 0 | 0 | 0 | 27.6891 | 52.5 | 689.9439 | 3000 | 49.4767 | 3049.4767 | 3049.4767 | 0 | 154.9439
0 | 33.2945 | 0 | 0 | 0 | 0 | 19.2055 | 52.5 | 709.1494 | 3000 | 34.3177 | 3034.3177 | 3034.3177 | 0 | 156.7529
0 | 76.8946 | 0 | 0 | 0 | 0 | -24.3946 | 52.5 | 684.7547 | 3000 | 0 | 3000 | 3000 | 0 | 153.09
0 | 116.3982 | 0 | 0 | 0 | 0 | -63.8982 | 52.5 | 620.8566 | 3000 | 0 | 3000 | 3000 | 0 | 150.18
0 | 94.3791 | 0 | 0 | 0 | 0 | -41.8791 | 52.5 | 578.9775 | 3000 | 0 | 3000 | 2989.1851 | 0 | 156.6931
0 | 95.381 | 0 | 0 | 0 | 0 | -42.881 | 52.5 | 536.0965 | 3000 | 0 | 3000 | 2810.7401 | 0 | 172.0735
0 | 96.1956 | 0 | 0 | 0 | 0 | -43.6956 | 52.5 | 492.4009 | 3000 | 0 | 3000 | 2540.3689 | 0 | 170.3571
0 | 105.7974 | 0 | 0 | 0 | 0 | -53.2974 | 52.5 | 439.1035 | 3000 | 0 | 3000 | 2221.3308 | 0 | 149.1846
0 | 117.395 | 0 | 0 | 0 | 0 | -64.895 | 52.5 | 374.2085 | 3000 | 0 | 3000 | 1945.5521 | 0 | 119.8849
0 | 94.9888 | 0 | 0 | 0 | 0 | -42.4888 | 52.5 | 331.7196 | 3000 | 0 | 3000 | 1734.6625 | 0 | 96.6554
0 | 81.1987 | 0 | 0 | 0 | 0 | -28.6987 | 52.5 | 303.021 | 3000 | 0 | 3000 | 1594.0694 | 0 | 81.9352
0 | 131.3214 | 0 | 0 | 0 | 0 | -78.8214 | 52.5 | 224.1996 | 3000 | 0 | 3000 | 1561.6249 | 0 | 78.7059
0 | 147.9199 | 0 | 0 | 0 | 0 | -95.4199 | 52.5 | 128.7797 | 3000 | 0 | 3000 | 1615.6991 | 0 | 82.0614
0 | 107.8365 | 0 | 0 | 0 | 0 | -55.3365 | 52.5 | 73.4432 | 3000 | 0 | 3000 | 1734.6625 | 0 | 87.7739
0 | 34.4729 | 0 | 0 | 0 | 0 | 18.0271 | 52.5 | 91.4703 | 3000 | 32.212 | 3032.212 | 1972.3567 | 0 | 102.3061
0 | 47.5199 | 0 | 0 | 0 | 0 | 4.9801 | 52.5 | 96.4504 | 3000 | 8.8988 | 3008.8988 | 2365.4152 | 0 | 128.3947
0 | 56.7185 | 0 | 0 | 0 | 0 | -4.2185 | 52.5 | 92.2319 | 3000 | 0 | 3000 | 2697.1842 | 0 | 160.4825
0 | 37.2309 | 0 | 0 | 0 | 0 | 15.2691 | 52.5 | 107.501 | 3000 | 27.2838 | 3027.2838 | 2919.1353 | 0 | 188.9848
0 | 49.7598 | 0 | 0 | 0 | 0 | 2.7402 | 52.5 | 110.2411 | 3000 | 4.8963 | 3004.8963 | 2994.0815 | 0 | 203.4478
0 | 27.588 | 0 | 0 | 0 | 0 | 24.912 | 52.5 | 135.1532 | 3000 | 44.5145 | 3044.5145 | 3044.5145 | 0 | 198.8677
0 | 28.3881 | 0 | 0 | 0 | 0 | 24.1119 | 52.5 | 159.2651 | 3000 | 43.0848 | 3043.0848 | 3043.0848 | 0 | 191.5318
0 | 35.7501 | 0 | 0 | 0 | 0 | 16.7499 | 52.5 | 176.015 | 3000 | 29.9299 | 3029.9299 | 3029.9299 | 0 | 178.4629
0 | 24.4065 | 0 | 0 | 0 | 0 | 28.0935 | 52.5 | 204.1085 | 3000 | 50.1993 | 3050.1993 | 3050.1993 | 0 | 164.1007
0 | 23.8449 | 0 | 0 | 0 | 0 | 28.6551 | 52.5 | 232.7636 | 3000 | 51.2029 | 3051.2029 | 3051.2029 | 0 | 147.9833
0 | 30.7341 | 0 | 0 | 0 | 0 | 21.7659 | 52.5 | 254.5295 | 3000 | 38.8927 | 3038.8927 | 3038.8927 | 0 | 147.9941
0 | 29.3453 | 0 | 0 | 0 | 0 | 23.1547 | 52.5 | 277.6842 | 3000 | 41.3743 | 3041.3743 | 3041.3743 | 0 | 152.1295
0 | 33.1973 | 0 | 0 | 0 | 0 | 19.3027 | 52.5 | 296.9869 | 3000 | 34.4913 | 3034.4913 | 3034.4913 | 0 | 151.7853
0 | 41.7012 | 0 | 0 | 0 | 0 | 10.7988 | 52.5 | 307.7857 | 3000 | 19.2961 | 3019.2961 | 3019.2961 | 0 | 152.0518
0 | 73.4936 | 0 | 0 | 0 | 0 | -20.9936 | 52.5 | 286.792 | 3000 | 0 | 3000 | 2989.1851 | 0 | 158.2475
0 | 98.9362 | 0 | 0 | 0 | 0 | -46.4362 | 52.5 | 240.3559 | 3000 | 0 | 3000 | 2902.6663 | 0 | 179.4428
0 | 104.2478 | 0 | 0 | 0 | 0 | -51.7478 | 52.5 | 188.608 | 3000 | 0 | 3000 | 2680.9619 | 0 | 175.4153
0 | 95.6681 | 0 | 0 | 0 | 0 | -43.1681 | 52.5 | 145.4399 | 3000 | 0 | 3000 | 2302.4421 | 0 | 154.7932
0 | 92.899 | 0 | 0 | 0 | 0 | -40.399 | 52.5 | 105.0409 | 3000 | 0 | 3000 | 2037.4783 | 0 | 133.2511
0 | 108.2684 | 0 | 0 | 0 | 0 | -55.7684 | 52.5 | 49.2725 | 3000 | 0 | 3000 | 1896.8853 | 0 | 119.5227
0 | 101.7725 | 0 | 0 | 0 | 0 | -49.2725 | 52.5 | 0 | 3000 | 0 | 3000 | 1685.9957 | 0 | 102.93
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1815.7739 | 0 | 109.6183
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2302.4421 | 0 | 130.9859
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2491.702 | 0 | 127.3758
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2637.7025 | 0 | 132.017
0 | 46.9968 | 0 | 0 | 0 | 0 | 5.5032 | 52.5 | 5.5032 | 3000 | 9.8335 | 3009.8335 | 2696.2028 | 0 | 136.1313
0 | 58.0032 | 0 | 0 | 0 | 0 | -5.5032 | 52.5 | 0 | 3000 | 0 | 3000 | 2843.1847 | 0 | 152.7643
0 | 49.8575 | 0 | 0 | 0 | 0 | 2.6425 | 52.5 | 2.6425 | 3000 | 4.7218 | 3004.7218 | 2939.8327 | 0 | 179.5944
0 | 47.3336 | 0 | 0 | 0 | 0 | 5.1664 | 52.5 | 7.809 | 3000 | 9.2317 | 3009.2317 | 2993.0095 | 0 | 193.0192
0 | 24.4986 | 0 | 0 | 0 | 0 | 28.0014 | 52.5 | 35.8104 | 3000 | 50.0348 | 3050.0348 | 3050.0348 | 0 | 192.4267
0 | 24.0518 | 0 | 0 | 0 | 0 | 28.4482 | 52.5 | 64.2586 | 3000 | 50.8332 | 3050.8332 | 3050.8332 | 0 | 182.5314
0 | 25.7981 | 0 | 0 | 0 | 0 | 26.7019 | 52.5 | 90.9605 | 3000 | 47.7128 | 3047.7128 | 3047.7128 | 0 | 170.7633
0 | 26.153 | 0 | 0 | 0 | 0 | 26.347 | 52.5 | 117.3075 | 3000 | 47.0785 | 3047.0785 | 3047.0785 | 0 | 159.3317
0 | 23.2091 | 0 | 0 | 0 | 0 | 29.2909 | 52.5 | 146.5984 | 3000 | 52.3389 | 3052.3389 | 3052.3389 | 0 | 161.5603
0 | 26.5265 | 0 | 0 | 0 | 0 | 25.9735 | 52.5 | 172.5719 | 3000 | 46.4112 | 3046.4112 | 3046.4112 | 0 | 159.3273
0 | 32.6301 | 0 | 0 | 0 | 0 | 19.8699 | 52.5 | 192.4418 | 3000 | 35.5049 | 3035.5049 | 3035.5049 | 0 | 158.5748
0 | 41.3332 | 0 | 0 | 0 | 0 | 11.1668 | 52.5 | 203.6086 | 3000 | 19.9536 | 3019.9536 | 3019.9536 | 0 | 151.0581
0 | 35.22 | 0 | 0 | 0 | 0 | 17.28 | 52.5 | 220.8886 | 3000 | 30.8771 | 3030.8771 | 3030.8771 | 0 | 151.7257
0 | 84.1796 | 0 | 0 | 0 | 0 | -31.6796 | 52.5 | 189.209 | 3000 | 0 | 3000 | 2983.7777 | 0 | 158.3491
0 | 73.7574 | 0 | 0 | 0 | 0 | -21.2574 | 52.5 | 167.9516 | 3000 | 0 | 3000 | 2826.9624 | 0 | 177.5898
0 | 84.5468 | 0 | 0 | 0 | 0 | -32.0468 | 52.5 | 135.9048 | 3000 | 0 | 3000 | 2540.3689 | 0 | 170.0777
0 | 98.5812 | 0 | 0 | 0 | 0 | -84.576 | 14.0052 | 51.3288 | 800.2989 | 0 | 800.2989 | 0 | 0 | 0
0 | 100.9695 | 0 | 0 | 0 | 0 | -48.4695 | 52.5 | 2.8593 | 3000 | 0 | 3000 | 1918.515 | 0 | 124.5692
0 | 55.3593 | 0 | 0 | 0 | 0 | -2.8593 | 52.5 | 0 | 3000 | 0 | 3000 | 1713.0328 | 0 | 102.0454
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1815.7739 | 0 | 100.5757
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1621.1066 | 0 | 85.5782
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1610.2917 | 0 | 84.3793
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1826.5887 | 0 | 93.156
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2151.0342 | 0 | 107.5517
0 | 45.0743 | 0 | 0 | 0 | 0 | 7.4257 | 52.5 | 7.4257 | 3000 | 13.2687 | 3013.2687 | 2348.1554 | 0 | 117.4078
0 | 44.8688 | 0 | 0 | 0 | 0 | 7.6312 | 52.5 | 15.0569 | 3000 | 13.636 | 3013.636 | 2564.8197 | 0 | 139.5262
0 | 41.8293 | 0 | 0 | 0 | 0 | 10.6707 | 52.5 | 25.7276 | 3000 | 19.0672 | 3019.0672 | 2856.8444 | 0 | 171.6678
0 | 40.3717 | 0 | 0 | 0 | 0 | 12.1283 | 52.5 | 37.8559 | 3000 | 21.6717 | 3021.6717 | 3005.4494 | 0 | 193.2804
0 | 25.5982 | 0 | 0 | 0 | 0 | 26.9018 | 52.5 | 64.7577 | 3000 | 48.0699 | 3048.0699 | 3048.0699 | 0 | 192.6075
0 | 117.2577 | 0 | 0 | 0 | 0 | -64.7577 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 182.43
0 | 37.888 | 0 | 0 | 0 | 0 | 14.612 | 52.5 | 14.612 | 3000 | 26.1097 | 3026.1097 | 3026.1097 | 0 | 176.0893
0 | 25.6795 | 0 | 0 | 0 | 0 | 26.8205 | 52.5 | 41.4325 | 3000 | 47.9246 | 3047.9246 | 3047.9246 | 0 | 172.6649
0 | 23.3622 | 0 | 0 | 0 | 0 | 29.1378 | 52.5 | 70.5703 | 3000 | 52.0654 | 3052.0654 | 3052.0654 | 0 | 168.7487
0 | 21.3957 | 0 | 0 | 0 | 0 | 31.1043 | 52.5 | 101.6746 | 3000 | 55.5793 | 3055.5793 | 3055.5793 | 0 | 168.9124
0 | 28.451 | 0 | 0 | 0 | 0 | 24.049 | 52.5 | 125.7236 | 3000 | 42.9724 | 3042.9724 | 3042.9724 | 0 | 157.3217
0 | 29.2376 | 0 | 0 | 0 | 0 | 23.2624 | 52.5 | 148.986 | 3000 | 41.5668 | 3041.5668 | 3041.5668 | 0 | 149.3409
0 | 23.5652 | 0 | 0 | 0 | 0 | 28.9348 | 52.5 | 177.9208 | 3000 | 51.7027 | 3051.7027 | 3051.7027 | 0 | 143.6436
0 | 35.8353 | 0 | 0 | 0 | 0 | 16.6647 | 52.5 | 194.5856 | 3000 | 29.7777 | 3029.7777 | 3013.5554 | 0 | 150.3764
0 | 62.4589 | 0 | 0 | 0 | 0 | -9.9589 | 52.5 | 184.6267 | 3000 | 0 | 3000 | 2805.3327 | 0 | 155.2471
0 | 111.6206 | 0 | 0 | 0 | 0 | -59.1206 | 52.5 | 125.5061 | 3000 | 0 | 3000 | 2524.1466 | 0 | 146.3248
0 | 118.0028 | 0 | 0 | 0 | 0 | -65.5028 | 52.5 | 60.0033 | 3000 | 0 | 3000 | 2194.2936 | 0 | 141.2247
0 | 82.5103 | 0 | 0 | 0 | 0 | -30.0103 | 52.5 | 29.993 | 3000 | 0 | 3000 | 1918.515 | 0 | 114.1325
0 | 30.8706 | 0 | 0 | 0 | 0 | 21.6294 | 52.5 | 51.6224 | 3000 | 38.6488 | 3038.6488 | 1740.8668 | 0 | 98.5157
0 | 61.2979 | 0 | 0 | 0 | 0 | -8.7979 | 52.5 | 42.8245 | 3000 | 0 | 3000 | 1556.2175 | 0 | 87.7551
0 | 95.3245 | 0 | 0 | 0 | 0 | -42.8245 | 52.5 | 0 | 3000 | 0 | 3000 | 1518.3655 | 0 | 87.0023
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1572.4397 | 0 | 88.8586
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1675.1808 | 0 | 94.6645
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1886.0704 | 0 | 103.1115
0 | 41.5799 | 0 | 0 | 0 | 0 | 10.9201 | 52.5 | 10.9201 | 3000 | 19.5127 | 3019.5127 | 2246.2509 | 0 | 101.3059
0 | 43.6729 | 0 | 0 | 0 | 0 | 8.8271 | 52.5 | 19.7472 | 3000 | 15.7729 | 3015.7729 | 2529.1046 | 0 | 146.2581
0 | 48.3077 | 0 | 0 | 0 | 0 | 4.1923 | 52.5 | 23.9395 | 3000 | 7.4911 | 3007.4911 | 2829.0461 | 0 | 178.145
0 | 56.4081 | 0 | 0 | 0 | 0 | -3.9081 | 52.5 | 20.0314 | 3000 | 0 | 3000 | 2978.3703 | 0 | 199.6104
0 | 29.9284 | 0 | 0 | 0 | 0 | 22.5716 | 52.5 | 42.6031 | 3000 | 40.3325 | 3040.3325 | 3040.3325 | 0 | 176.9474
0 | 32.3459 | 0 | 0 | 0 | 0 | 20.1541 | 52.5 | 62.7571 | 3000 | 36.0126 | 3036.0126 | 3036.0126 | 0 | 183.8002
0 | 32.2542 | 0 | 0 | 0 | 0 | 20.2458 | 52.5 | 83.0029 | 3000 | 36.1765 | 3036.1765 | 3036.1765 | 0 | 179.3773
0 | 33.2158 | 0 | 0 | 0 | 0 | 19.2842 | 52.5 | 102.2871 | 3000 | 34.4583 | 3034.4583 | 3034.4583 | 0 | 174.0869
0 | 26.4251 | 0 | 0 | 0 | 0 | 26.0749 | 52.5 | 128.362 | 3000 | 46.5924 | 3046.5924 | 3046.5924 | 0 | 170.8834
0 | 20.4741 | 0 | 0 | 0 | 0 | 32.0259 | 52.5 | 160.3879 | 3000 | 57.2261 | 3057.2261 | 3057.2261 | 0 | 142.375
0 | 21.4293 | 0 | 0 | 0 | 0 | 31.0707 | 52.5 | 191.4586 | 3000 | 55.5192 | 3055.5192 | 3055.5192 | 0 | 137.4984
0 | 27.4835 | 0 | 0 | 0 | 0 | 25.0165 | 52.5 | 216.4751 | 3000 | 44.7011 | 3044.7011 | 3044.7011 | 0 | 144.6233
0 | 17.8485 | 0 | 0 | 0 | 0 | 34.6515 | 52.5 | 251.1266 | 3000 | 61.9176 | 3061.9176 | 3061.9176 | 0 | 145.4411
0 | 42.713 | 0 | 0 | 0 | 0 | 9.787 | 52.5 | 260.9136 | 3000 | 17.488 | 3017.488 | 2995.8583 | 0 | 147.7857
0 | 69.8571 | 0 | 0 | 0 | 0 | -17.3571 | 52.5 | 243.5565 | 3000 | 0 | 3000 | 2799.9253 | 0 | 153.7719
0 | 66.8401 | 0 | 0 | 0 | 0 | -14.3401 | 52.5 | 229.2164 | 3000 | 0 | 3000 | 2502.5169 | 0 | 137.8887
0 | 44.7823 | 0 | 0 | 0 | 0 | 7.7177 | 52.5 | 236.9341 | 3000 | 13.7905 | 3013.7905 | 2186.4544 | 0 | 123.0974
0 | 39.4739 | 0 | 0 | 0 | 0 | 13.0261 | 52.5 | 249.9602 | 3000 | 23.276 | 3023.276 | 1930.9761 | 0 | 101.7624
0 | 50.6529 | 0 | 0 | 0 | 0 | 1.8471 | 52.5 | 251.8073 | 3000 | 3.3006 | 3003.3006 | 1689.2962 | 0 | 77.7583
0 | 50.2611 | 0 | 0 | 0 | 0 | 2.2389 | 52.5 | 254.0462 | 3000 | 4.0005 | 3004.0005 | 1554.8106 | 0 | 67.4477
0 | 38.442 | 0 | 0 | 0 | 0 | 14.058 | 52.5 | 268.1042 | 3000 | 25.1198 | 3025.1198 | 1548.8927 | 0 | 64.9141
0 | 245.9601 | 0 | 0 | 0 | 0 | -193.4601 | 52.5 | 74.6442 | 3000 | 0 | 3000 | 1567.0323 | 0 | 59.2338
0 | 44.0844 | 0 | 0 | 0 | 0 | 8.4156 | 52.5 | 83.0597 | 3000 | 15.0375 | 3015.0375 | 1695.6257 | 0 | 61.0934
0 | 46.8459 | 0 | 0 | 0 | 0 | 5.6541 | 52.5 | 88.7138 | 3000 | 10.1031 | 3010.1031 | 1923.2107 | 0 | 93.6604
0 | 40.7497 | 0 | 0 | 0 | 0 | 11.7503 | 52.5 | 100.4641 | 3000 | 20.9962 | 3020.9962 | 2269.3641 | 0 | 122.9088
0 | 31.9219 | 0 | 0 | 0 | 0 | 20.5781 | 52.5 | 121.0422 | 3000 | 36.7702 | 3036.7702 | 2555.5094 | 0 | 147.734
0 | 43.9623 | 0 | 0 | 0 | 0 | 8.5377 | 52.5 | 129.5799 | 3000 | 15.2558 | 3015.2558 | 2836.8108 | 0 | 166.7761
0 | 46.6616 | 0 | 0 | 0 | 0 | 5.8384 | 52.5 | 135.4184 | 3000 | 10.4325 | 3010.4325 | 2983.3954 | 0 | 192.3992
0 | 24.796 | 0 | 0 | 0 | 0 | -24.796 | 0 | 110.6224 | 0 | 0 | 0 | 0 | 0 | 0
0 | 24.5879 | 0 | 0 | 0 | 0 | 27.9121 | 52.5 | 138.5345 | 3000 | 49.8751 | 3049.8751 | 3049.8751 | 0 | 178.1432
0 | 27.4403 | 0 | 0 | 0 | 0 | 25.0597 | 52.5 | 163.5942 | 3000 | 44.7784 | 3044.7784 | 3044.7784 | 0 | 175.0748
0 | 32.3417 | 0 | 0 | 0 | 0 | 20.1583 | 52.5 | 183.7525 | 3000 | 36.0202 | 3036.0202 | 3036.0202 | 0 | 171.1405
0 | 30.4274 | 0 | 0 | 0 | 0 | 22.0726 | 52.5 | 205.8251 | 3000 | 39.4409 | 3039.4409 | 3039.4409 | 0 | 157.899
0 | 28.5102 | 0 | 0 | 0 | 0 | 23.9898 | 52.5 | 229.815 | 3000 | 42.8667 | 3042.8667 | 3042.8667 | 0 | 149.1613
0 | 35.0055 | 0 | 0 | 0 | 0 | 17.4945 | 52.5 | 247.3095 | 3000 | 31.2604 | 3031.2604 | 3031.2604 | 0 | 145.5005
0 | 59.05 | 0 | 0 | 0 | 0 | -6.55 | 52.5 | 240.7595 | 3000 | 0 | 3000 | 3000 | 0 | 152.1
0 | 84.1503 | 0 | 0 | 0 | 0 | -31.6503 | 52.5 | 209.1092 | 3000 | 0 | 3000 | 3000 | 0 | 160.41
0 | 82.2169 | 0 | 0 | 0 | 0 | -29.7169 | 52.5 | 179.3922 | 3000 | 0 | 3000 | 2978.3703 | 0 | 165.0017
0 | 100.5643 | 0 | 0 | 0 | 0 | -48.0643 | 52.5 | 131.3279 | 3000 | 0 | 3000 | 2789.1104 | 0 | 141.4079
0 | 78.4627 | 0 | 0 | 0 | 0 | -25.9627 | 52.5 | 105.3652 | 3000 | 0 | 3000 | 2480.8872 | 0 | 128.9069
0 | 83.5162 | 0 | 0 | 0 | 0 | -31.0162 | 52.5 | 74.349 | 3000 | 0 | 3000 | 2145.6268 | 0 | 105.1357
0 | 83.1833 | 0 | 0 | 0 | 0 | -30.6833 | 52.5 | 43.6657 | 3000 | 0 | 3000 | 1864.4407 | 0 | 88.0575
0 | 89.2404 | 0 | 0 | 0 | 0 | -36.7404 | 52.5 | 6.9254 | 3000 | 0 | 3000 | 1653.5511 | 0 | 72.9216
0 | 59.4254 | 0 | 0 | 0 | 0 | -6.9254 | 52.5 | 0 | 3000 | 0 | 3000 | 1502.1432 | 0 | 66.1694
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1475.1061 | 0 | 62.6478
0 | 36.5895 | 0 | 0 | 0 | 0 | 15.9105 | 52.5 | 15.9105 | 3000 | 28.43 | 3028.43 | 1552.2029 | 0 | 38.8051
0 | 58.4808 | 0 | 0 | 0 | 0 | -5.9808 | 52.5 | 9.9298 | 3000 | 0 | 3000 | 1642.7363 | 0 | 34.941
0 | 33.9157 | 0 | 0 | 0 | 0 | 18.5843 | 52.5 | 28.5141 | 3000 | 33.2077 | 3033.2077 | 1903.0558 | 0 | 47.0055
0 | 34.1579 | 0 | 0 | 0 | 0 | 18.3421 | 52.5 | 46.8562 | 3000 | 32.775 | 3032.775 | 2248.6983 | 0 | 84.1013
0 | 32.8172 | 0 | 0 | 0 | 0 | 19.6828 | 52.5 | 66.539 | 3000 | 35.1706 | 3035.1706 | 2537.6875 | 0 | 137.0097
0 | 62.8554 | 0 | 0 | 0 | 0 | -10.3554 | 52.5 | 56.1836 | 3000 | 0 | 3000 | 2816.1475 | 0 | 169.7292
0 | 38.7269 | 0 | 0 | 0 | 0 | 13.7731 | 52.5 | 69.9568 | 3000 | 24.6107 | 3024.6107 | 2997.5736 | 0 | 194.2428
0 | 29.4923 | 0 | 0 | 0 | 0 | 23.0077 | 52.5 | 92.9645 | 3000 | 41.1118 | 3041.1118 | 3041.1118 | 0 | 185.7511
0 | 27.2716 | 0 | 0 | 0 | 0 | 25.2284 | 52.5 | 118.1929 | 3000 | 45.0798 | 3045.0798 | 3045.0798 | 0 | 180.1469
0 | 27.0386 | 0 | 0 | 0 | 0 | 25.4614 | 52.5 | 143.6543 | 3000 | 45.4962 | 3045.4962 | 3045.4962 | 0 | 171.7051
0 | 25.7662 | 0 | 0 | 0 | 0 | 26.7338 | 52.5 | 170.3881 | 3000 | 47.7697 | 3047.7697 | 3047.7697 | 0 | 162.568
0 | 27.2754 | 0 | 0 | 0 | 0 | 25.2246 | 52.5 | 195.6127 | 3000 | 45.073 | 3045.073 | 3045.073 | 0 | 130.2987
0 | 32.7591 | 0 | 0 | 0 | 0 | 19.7409 | 52.5 | 215.3536 | 3000 | 35.2744 | 3035.2744 | 3035.2744 | 0 | 103.7457
0 | 24.8575 | 0 | 0 | 0 | 0 | 27.6425 | 52.5 | 242.9961 | 3000 | 49.3934 | 3049.3934 | 3049.3934 | 0 | 85.383
0 | 21.7247 | 0 | 0 | 0 | 0 | 30.7753 | 52.5 | 273.7714 | 3000 | 54.9914 | 3054.9914 | 3054.9914 | 0 | 76.4053
0 | 33.118 | 0 | 0 | 0 | 0 | 19.382 | 52.5 | 293.1534 | 3000 | 34.6331 | 3034.6331 | 3034.6331 | 0 | 129.5788
0 | 28.3461 | 0 | 0 | 0 | 0 | 24.1539 | 52.5 | 317.3073 | 3000 | 43.1598 | 3043.1598 | 3021.5301 | 0 | 115.9059
0 | 24.5429 | 0 | 0 | 0 | 0 | 27.9571 | 52.5 | 345.2644 | 3000 | 49.9557 | 3049.9557 | 2839.0661 | 0 | 119.2408
0 | 29.8963 | 0 | 0 | 0 | 0 | 22.6037 | 52.5 | 367.8681 | 3000 | 40.3898 | 3040.3898 | 2532.0918 | 0 | 119.0083
0 | 49.0575 | 0 | 0 | 0 | 0 | 3.4425 | 52.5 | 371.3106 | 3000 | 6.1512 | 3006.1512 | 2168.0003 | 0 | 86.5032
0 | 39.517 | 0 | 0 | 0 | 0 | 12.983 | 52.5 | 384.2936 | 3000 | 23.1989 | 3023.1989 | 1909.2693 | 0 | 81.5258
0 | 32.0403 | 0 | 0 | 0 | 0 | 20.4597 | 52.5 | 404.7533 | 3000 | 36.5588 | 3036.5588 | 1819.8881 | 0 | 109.0113
0 | 54.3799 | 0 | 0 | 0 | 0 | -1.8799 | 52.5 | 402.8733 | 3000 | 0 | 3000 | 1572.4397 | 0 | 110.0236
0 | 49.2301 | 0 | 0 | 0 | 0 | 3.2699 | 52.5 | 406.1432 | 3000 | 5.8428 | 3005.8428 | 1513.3935 | 0 | 85.5219
0 | 41.3523 | 0 | 0 | 0 | 0 | 11.1477 | 52.5 | 417.2909 | 3000 | 19.9195 | 3019.9195 | 1576.137 | 0 | 83.6771
0 | 63.5676 | 0 | 0 | 0 | 0 | -11.0676 | 52.5 | 406.2234 | 3000 | 0 | 3000 | 1691.4031 | 0 | 87.0396
0 | 51.1049 | 0 | 0 | 0 | 0 | 1.3951 | 52.5 | 407.6185 | 3000 | 2.4929 | 3002.4929 | 1904.7856 | 0 | 92.6678
0 | 53.6804 | 0 | 0 | 0 | 0 | -1.1804 | 52.5 | 406.4381 | 3000 | 0 | 3000 | 2215.9233 | 0 | 117.4439
0 | 36.7659 | 0 | 0 | 0 | 0 | 15.7341 | 52.5 | 422.1722 | 3000 | 28.1148 | 3028.1148 | 2568.4837 | 0 | 147.6878
0 | 50.2826 | 0 | 0 | 0 | 0 | 2.2174 | 52.5 | 424.3896 | 3000 | 3.9622 | 3003.9622 | 2879.5915 | 0 | 176.9221
0 | 44.8628 | 0 | 0 | 0 | 0 | 7.6372 | 52.5 | 432.0269 | 3000 | 13.6467 | 3013.6467 | 2986.6096 | 0 | 195.1152
0 | 25.6437 | 0 | 0 | 0 | 0 | 26.8563 | 52.5 | 458.8831 | 3000 | 47.9886 | 3047.9886 | 3047.9886 | 0 | 207.2632
0 | 31.7519 | 0 | 0 | 0 | 0 | -31.7519 | 0 | 427.1312 | 0 | 0 | 0 | 0 | 0 | 0
0 | 32.5171 | 0 | 0 | 0 | 0 | 19.9829 | 52.5 | 447.1141 | 3000 | 35.7067 | 3035.7067 | 3035.7067 | 0 | 204.6066
0 | 29.2977 | 0 | 0 | 0 | 0 | 23.2023 | 52.5 | 470.3163 | 3000 | 41.4594 | 3041.4594 | 3041.4594 | 0 | 175.9788
0 | 230.3591 | 0 | 0 | 0 | 0 | -177.8591 | 52.5 | 292.4573 | 3000 | 0 | 3000 | 3000 | 0 | 164.1
0 | 28.7379 | 0 | 0 | 0 | 0 | 23.7621 | 52.5 | 316.2194 | 3000 | 42.4598 | 3042.4598 | 3042.4598 | 0 | 160.9461
0 | 26.5907 | 0 | 0 | 0 | 0 | 25.9093 | 52.5 | 342.1287 | 3000 | 46.2964 | 3046.2964 | 3046.2964 | 0 | 160.7226
0 | 23.5654 | 0 | 0 | 0 | 0 | 28.9346 | 52.5 | 371.0633 | 3000 | 51.7023 | 3051.7023 | 3051.7023 | 0 | 161.8928
0 | 65.8353 | 0 | 0 | 0 | 0 | -13.3353 | 52.5 | 357.728 | 3000 | 0 | 3000 | 3000 | 0 | 158.25
0 | 125.7765 | 0 | 0 | 0 | 0 | -73.2765 | 52.5 | 284.4515 | 3000 | 0 | 3000 | 2967.5554 | 0 | 158.4081
0 | 129.7718 | 0 | 0 | 0 | 0 | -77.2718 | 52.5 | 207.1798 | 3000 | 0 | 3000 | 2762.0733 | 0 | 147.7709
0 | 100.8098 | 0 | 0 | 0 | 0 | -48.3098 | 52.5 | 158.8699 | 3000 | 0 | 3000 | 2464.6649 | 0 | 152.0205
0 | 127.7595 | 0 | 0 | 0 | 0 | -75.2595 | 52.5 | 83.6104 | 3000 | 0 | 3000 | 2140.2194 | 0 | 136.974
0 | 103.2934 | 0 | 0 | 0 | 0 | -83.6104 | 19.683 | 0 | 1124.7444 | 0 | 1124.7444 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1658.9585 | 0 | 95.2242
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1539.9952 | 0 | 90.7211
0 | 38.5056 | 0 | 0 | 0 | 0 | 13.9944 | 52.5 | 13.9944 | 3000 | 25.0061 | 3025.0061 | 1667.7424 | 0 | 91.5591
0 | 47.4918 | 0 | 0 | 0 | 0 | 5.0082 | 52.5 | 19.0026 | 3000 | 8.949 | 3008.949 | 1505.6848 | 0 | 81.5479
0 | 41.5787 | 0 | 0 | 0 | 0 | 10.9213 | 52.5 | 29.9239 | 3000 | 19.5149 | 3019.5149 | 1673.0661 | 0 | 88.9067
0 | 44.7666 | 0 | 0 | 0 | 0 | 7.7334 | 52.5 | 37.6573 | 3000 | 13.8186 | 3013.8186 | 2002.6301 | 0 | 97.428
0 | 53.2316 | 0 | 0 | 0 | 0 | -0.7316 | 52.5 | 36.9257 | 3000 | 0 | 3000 | 2610.6654 | 0 | 137.5037
0 | 38.0528 | 0 | 0 | 0 | 0 | 14.4472 | 52.5 | 51.373 | 3000 | 25.8153 | 3025.8153 | 2593.2213 | 0 | 143.8719
0 | 43.0221 | 0 | 0 | 0 | 0 | 9.4779 | 52.5 | 60.8509 | 3000 | 16.9358 | 3016.9358 | 2849.3056 | 0 | 170.5879
0 | 25.4277 | 0 | 0 | 0 | 0 | 27.0723 | 52.5 | 87.9233 | 3000 | 48.3747 | 3048.3747 | 3021.3375 | 0 | 187.2021
0 | 27.8726 | 0 | 0 | 0 | 0 | 24.6274 | 52.5 | 112.5507 | 3000 | 44.006 | 3044.006 | 3044.006 | 0 | 198.1648
0 | 25.9174 | 0 | 0 | 0 | 0 | -25.9174 | 0 | 86.6332 | 0 | 0 | 0 | 0 | 0 | 0
0 | 32.1845 | 0 | 0 | 0 | 0 | 20.3155 | 52.5 | 106.9487 | 3000 | 36.301 | 3036.301 | 3036.301 | 0 | 179.5668
0 | 33.6507 | 0 | 0 | 0 | 0 | 18.8493 | 52.5 | 125.798 | 3000 | 33.6812 | 3033.6812 | 3033.6812 | 0 | 169.0367
0 | 27.2574 | 0 | 0 | 0 | 0 | 25.2426 | 52.5 | 151.0406 | 3000 | 45.1052 | 3045.1052 | 3045.1052 | 0 | 161.3906
0 | 27.9183 | 0 | 0 | 0 | 0 | 24.5817 | 52.5 | 175.6223 | 3000 | 43.9242 | 3043.9242 | 3043.9242 | 0 | 149.5784
0 | 27.4783 | 0 | 0 | 0 | 0 | 25.0217 | 52.5 | 200.644 | 3000 | 44.7104 | 3044.7104 | 3044.7104 | 0 | 149.343
0 | 35.312 | 0 | 0 | 0 | 0 | 17.188 | 52.5 | 217.832 | 3000 | 30.7127 | 3030.7127 | 3030.7127 | 0 | 145.1711
0 | 38.1336 | 0 | 0 | 0 | 0 | 14.3664 | 52.5 | 232.1984 | 3000 | 25.6709 | 3025.6709 | 3025.6709 | 0 | 144.0219
0 | 75.9118 | 0 | 0 | 0 | 0 | -23.4118 | 52.5 | 208.7866 | 3000 | 0 | 3000 | 2983.7777 | 0 | 140.9835
0 | 69.45 | 0 | 0 | 0 | 0 | -16.95 | 52.5 | 191.8366 | 3000 | 0 | 3000 | 2832.3698 | 0 | 154.6191
0 | 48.8707 | 0 | 0 | 0 | 0 | 3.6293 | 52.5 | 195.466 | 3000 | 6.4851 | 3006.4851 | 2682.0396 | 0 | 156.0411
0 | 29.3875 | 0 | 0 | 0 | 0 | 23.1125 | 52.5 | 218.5785 | 3000 | 41.299 | 3041.299 | 2630.3347 | 0 | 171.4978
0 | 57.3433 | 0 | 0 | 0 | 0 | -4.8433 | 52.5 | 213.7352 | 3000 | 0 | 3000 | 2567.406 | 0 | 146.2651
0 | 94.4774 | 0 | 0 | 0 | 0 | -41.9774 | 52.5 | 171.7578 | 3000 | 0 | 3000 | 1923.9224 | 0 | 105.1424
0 | 114.4355 | 0 | 0 | 0 | 0 | -61.9355 | 52.5 | 109.8223 | 3000 | 0 | 3000 | 1567.0323 | 0 | 83.9303
0 | 71.3031 | 0 | 0 | 0 | 0 | -18.8031 | 52.5 | 91.0192 | 3000 | 0 | 3000 | 1691.4031 | 0 | 80.8491
0 | 39.3689 | 0 | 0 | 0 | 0 | 13.1311 | 52.5 | 104.1503 | 3000 | 23.4635 | 3023.4635 | 1677.0146 | 0 | 79.6917
0 | 54.4442 | 0 | 0 | 0 | 0 | -1.9442 | 52.5 | 102.2061 | 3000 | 0 | 3000 | 1691.4031 | 0 | 78.8194
0 | 41.5914 | 0 | 0 | 0 | 0 | 10.9086 | 52.5 | 113.1147 | 3000 | 19.4922 | 3019.4922 | 2035.3409 | 0 | 95.661
0 | 41.0446 | 0 | 0 | 0 | 0 | 11.4554 | 52.5 | 124.5701 | 3000 | 20.4693 | 3020.4693 | 2485.1342 | 0 | 121.6225
0 | 47.21 | 0 | 0 | 0 | 0 | 5.29 | 52.5 | 129.8601 | 3000 | 9.4525 | 3009.4525 | 2609.303 | 0 | 144.451
0 | 41.2494 | 0 | 0 | 0 | 0 | 11.2506 | 52.5 | 141.1107 | 3000 | 20.1033 | 3020.1033 | 2938.9919 | 0 | 177.4563
0 | 54.135 | 0 | 0 | 0 | 0 | -1.635 | 52.5 | 139.4757 | 3000 | 0 | 3000 | 2989.1851 | 0 | 183.7751
0 | 27.6688 | 0 | 0 | 0 | 0 | 24.8312 | 52.5 | 164.3069 | 3000 | 44.3701 | 3044.3701 | 3044.3701 | 0 | 180.7138
0 | 30.4731 | 0 | 0 | 0 | 0 | 22.0269 | 52.5 | 186.3339 | 3000 | 39.3592 | 3039.3592 | 3039.3592 | 0 | 176.4956
0 | 33.34 | 0 | 0 | 0 | 0 | 19.16 | 52.5 | 205.4939 | 3000 | 34.2364 | 3034.2364 | 3034.2364 | 0 | 162.7868
0 | 20.1008 | 0 | 0 | 0 | 0 | 32.3992 | 52.5 | 237.8931 | 3000 | 57.893 | 3057.893 | 3057.893 | 0 | 158.8575
0 | 28.9348 | 0 | 0 | 0 | 0 | 23.5652 | 52.5 | 261.4583 | 3000 | 42.108 | 3042.108 | 3042.108 | 0 | 163.9696
0 | 31.876 | 0 | 0 | 0 | 0 | 20.624 | 52.5 | 282.0823 | 3000 | 36.8524 | 3036.8524 | 3036.8524 | 0 | 153.2396
0 | 29.4347 | 0 | 0 | 0 | 0 | 23.0653 | 52.5 | 305.1477 | 3000 | 41.2147 | 3041.2147 | 3041.2147 | 0 | 147.286
0 | 27.7845 | 0 | 0 | 0 | 0 | 24.7155 | 52.5 | 329.8632 | 3000 | 44.1633 | 3044.1633 | 3044.1633 | 0 | 150.747
0 | 31.7987 | 0 | 0 | 0 | 0 | 20.7013 | 52.5 | 350.5645 | 3000 | 36.9905 | 3036.9905 | 3036.9905 | 0 | 135.1157
0 | 34.8994 | 0 | 0 | 0 | 0 | 17.6006 | 52.5 | 368.1651 | 3000 | 31.45 | 3031.45 | 2993.598 | 0 | 152.6436
0 | 38.3048 | 0 | 0 | 0 | 0 | 14.1952 | 52.5 | 382.3603 | 3000 | 25.3649 | 3025.3649 | 2798.253 | 0 | 160.8995
0 | 64.9649 | 0 | 0 | 0 | 0 | -12.4649 | 52.5 | 369.8954 | 3000 | 0 | 3000 | 2616.0728 | 0 | 170.1232
0 | 55.137 | 0 | 0 | 0 | 0 | -2.637 | 52.5 | 367.2584 | 3000 | 0 | 3000 | 2280.8124 | 0 | 143.4175
0 | 53.4811 | 0 | 0 | 0 | 0 | -0.98107 | 52.5 | 366.2773 | 3000 | 0 | 3000 | 2459.2575 | 0 | 145.5389
0 | 44.5776 | 0 | 0 | 0 | 0 | 7.9224 | 52.5 | 374.1997 | 3000 | 14.1563 | 3014.1563 | 2078.6717 | 0 | 116.3225
0 | 41.9041 | 0 | 0 | 0 | 0 | 10.5959 | 52.5 | 384.7956 | 3000 | 18.9334 | 3018.9334 | 1791.4479 | 0 | 94.3197
0 | 43.5129 | 0 | 0 | 0 | 0 | 8.9871 | 52.5 | 393.7827 | 3000 | 16.0588 | 3016.0588 | 1496.5723 | 0 | 77.6721
0 | 37.6235 | 0 | 0 | 0 | 0 | 14.8765 | 52.5 | 408.6593 | 3000 | 26.5824 | 3026.5824 | 1717.9855 | 0 | 86.0711
0 | 40.4054 | 0 | 0 | 0 | 0 | 12.0946 | 52.5 | 420.7539 | 3000 | 21.6115 | 3021.6115 | 2107.7566 | 0 | 99.9077
0 | 46.8524 | 0 | 0 | 0 | 0 | 5.6476 | 52.5 | 426.4014 | 3000 | 10.0914 | 3010.0914 | 2366.6078 | 0 | 125.4539
0 | 49.537 | 0 | 0 | 0 | 0 | 2.963 | 52.5 | 429.3644 | 3000 | 5.2945 | 3005.2945 | 2718.7009 | 0 | 134.032
0 | 36.7648 | 0 | 0 | 0 | 0 | 15.7352 | 52.5 | 445.0997 | 3000 | 28.1168 | 3028.1168 | 2849.6718 | 0 | 158.2138
0 | 53.3516 | 0 | 0 | 0 | 0 | -0.85159 | 52.5 | 444.2481 | 3000 | 0 | 3000 | 2924.296 | 0 | 179.0254
0 | 54.4131 | 0 | 0 | 0 | 0 | -54.4131 | 0 | 389.8349 | 0 | 0 | 0 | 0 | 21.6297 | 0
0 | 27.9035 | 0 | 0 | 0 | 0 | -27.9035 | 0 | 361.9314 | 0 | 0 | 0 | 0 | 0 | 0
0 | 38.4676 | 0 | 0 | 0 | 0 | 14.0324 | 52.5 | 375.9638 | 3000 | 25.074 | 3025.074 | 3025.074 | 0 | 192.183
0 | 30.9226 | 0 | 0 | 0 | 0 | 21.5774 | 52.5 | 397.5412 | 3000 | 38.556 | 3038.556 | 3038.556 | 0 | 173.8358
0 | 30.8572 | 0 | 0 | 0 | 0 | 21.6428 | 52.5 | 419.184 | 3000 | 38.6727 | 3038.6727 | 3038.6727 | 0 | 164.2099
0 | 28.9299 | 0 | 0 | 0 | 0 | 23.5701 | 52.5 | 442.754 | 3000 | 42.1166 | 3042.1166 | 3042.1166 | 0 | 158.1901
0 | 30.7212 | 0 | 0 | 0 | 0 | 21.7788 | 52.5 | 464.5328 | 3000 | 38.9159 | 3038.9159 | 3038.9159 | 0 | 151.9458
0 | 31.8203 | 0 | 0 | 0 | 0 | 20.6797 | 52.5 | 485.2125 | 3000 | 36.9518 | 3036.9518 | 3036.9518 | 0 | 147.0188
0 | 234.8485 | 0 | 0 | 0 | 0 | -182.3485 | 52.5 | 302.864 | 3000 | 0 | 3000 | 3000 | 0 | 147.87
0 | 32.5077 | 0 | 0 | 0 | 0 | 19.9923 | 52.5 | 322.8563 | 3000 | 35.7236 | 3035.7236 | 3035.7236 | 0 | 153.5773
0 | 51.2439 | 0 | 0 | 0 | 0 | 1.2561 | 52.5 | 324.1124 | 3000 | 2.2445 | 3002.2445 | 2996.8371 | 0 | 161.5895
0 | 284.8111 | 0 | 0 | 0 | 0 | -232.3111 | 52.5 | 91.8013 | 3000 | 0 | 3000 | 2956.7406 | 0 | 177.6705
0 | 40.1033 | 0 | 0 | 0 | 0 | 12.3967 | 52.5 | 104.198 | 3000 | 22.1513 | 3022.1513 | 2903.188 | 0 | 199.1587
0 | 50.975 | 0 | 0 | 0 | 0 | -50.975 | 0 | 53.223 | 0 | 0 | 0 | 0 | 259.5564 | 0
0 | 36.4372 | 0 | 0 | 0 | 0 | 16.0628 | 52.5 | 69.2858 | 3000 | 28.7021 | 3028.7021 | 2633.9601 | 0 | 178.9512
0 | 39.1344 | 0 | 0 | 0 | 0 | 13.3656 | 52.5 | 82.6514 | 3000 | 23.8825 | 3023.8825 | 2391.2138 | 0 | 155.2615
0 | 45.1181 | 0 | 0 | 0 | 0 | 7.3819 | 52.5 | 90.0334 | 3000 | 13.1905 | 3013.1905 | 2321.0401 | 0 | 143.7652
0 | 36.2219 | 0 | 0 | 0 | 0 | 16.2781 | 52.5 | 106.3115 | 3000 | 29.0868 | 3029.0868 | 2234.1953 | 0 | 131.7282
0 | 41.8394 | 0 | 0 | 0 | 0 | 10.6606 | 52.5 | 116.972 | 3000 | 19.049 | 3019.049 | 2224.1575 | 0 | 127.1328
0 | 45.3301 | 0 | 0 | 0 | 0 | 7.1699 | 52.5 | 124.1419 | 3000 | 12.8116 | 3012.8116 | 2477.4765 | 0 | 137.1283
0 | 50.7271 | 0 | 0 | 0 | 0 | 1.7729 | 52.5 | 125.9148 | 3000 | 3.1679 | 3003.1679 | 2575.9813 | 0 | 142.6578
0 | 41.39 | 0 | 0 | 0 | 0 | 11.11 | 52.5 | 137.0248 | 3000 | 19.852 | 3019.852 | 2679.1842 | 0 | 149.6592
0 | 27.5622 | 0 | 0 | 0 | 0 | 24.9378 | 52.5 | 161.9625 | 3000 | 44.5605 | 3044.5605 | 2768.7818 | 0 | 164.521
0 | 49.6709 | 0 | 0 | 0 | 0 | 2.8291 | 52.5 | 164.7916 | 3000 | 5.0552 | 3005.0552 | 2740.0914 | 0 | 163.5287
0 | 49.957 | 0 | 0 | 0 | 0 | 2.543 | 52.5 | 167.3346 | 3000 | 4.5441 | 3004.5441 | 2961.2847 | 0 | 188.7819
0 | 31.513 | 0 | 0 | 0 | 0 | 20.987 | 52.5 | 188.3217 | 3000 | 37.501 | 3037.501 | 3037.501 | 0 | 194.3089
0 | 27.109 | 0 | 0 | 0 | 0 | 25.391 | 52.5 | 213.7127 | 3000 | 45.3703 | 3045.3703 | 3045.3703 | 0 | 185.8894
0 | 29.5314 | 0 | 0 | 0 | 0 | 22.9686 | 52.5 | 236.6813 | 3000 | 41.0419 | 3041.0419 | 3041.0419 | 0 | 173.2482
0 | 28.9069 | 0 | 0 | 0 | 0 | 23.5931 | 52.5 | 260.2744 | 3000 | 42.1577 | 3042.1577 | 3042.1577 | 0 | 158.3443
0 | 28.3339 | 0 | 0 | 0 | 0 | 24.1661 | 52.5 | 284.4404 | 3000 | 43.1816 | 3043.1816 | 3043.1816 | 0 | 143.0904
0 | 24.8894 | 0 | 0 | 0 | 0 | 27.6106 | 52.5 | 312.0511 | 3000 | 49.3365 | 3049.3365 | 3049.3365 | 0 | 137.5251
0 | 28.1113 | 0 | 0 | 0 | 0 | 24.3887 | 52.5 | 336.4398 | 3000 | 43.5794 | 3043.5794 | 3043.5794 | 0 | 134.0697
0 | 26.0904 | 0 | 0 | 0 | 0 | 26.4096 | 52.5 | 362.8493 | 3000 | 47.1904 | 3047.1904 | 3047.1904 | 0 | 131.1511
0 | 22.664 | 0 | 0 | 0 | 0 | 29.836 | 52.5 | 392.6853 | 3000 | 53.313 | 3053.313 | 3053.313 | 0 | 138.4372
0 | 33.2894 | 0 | 0 | 0 | 0 | 19.2106 | 52.5 | 411.8959 | 3000 | 34.3267 | 3034.3267 | 2985.6599 | 0 | 133.25
0 | 20.0539 | 0 | 0 | 0 | 0 | 32.4461 | 52.5 | 444.342 | 3000 | 57.9769 | 3057.9769 | 3003.9027 | 0 | 131.9014
0 | 32.9126 | 0 | 0 | 0 | 0 | 19.5874 | 52.5 | 463.9294 | 3000 | 35.0001 | 3035.0001 | 2910.6293 | 0 | 145.1531
0 | 49.0166 | 0 | 0 | 0 | 0 | 3.4834 | 52.5 | 467.4129 | 3000 | 6.2245 | 3006.2245 | 2854.8165 | 0 | 157.0149
0 | 51.6873 | 0 | 0 | 0 | 0 | 0.81273 | 52.5 | 468.2256 | 3000 | 1.4522 | 3001.4522 | 2817.5998 | 0 | 156.3768
0 | 56.1362 | 0 | 0 | 0 | 0 | -3.6362 | 52.5 | 464.5894 | 3000 | 0 | 3000 | 2745.851 | 0 | 137.018
0 | 29.5491 | 0 | 0 | 0 | 0 | 22.9509 | 52.5 | 487.5402 | 3000 | 41.0101 | 3041.0101 | 2511.0825 | 0 | 128.9943
0 | 49.7408 | 0 | 0 | 0 | 0 | 2.7592 | 52.5 | 490.2995 | 3000 | 4.9304 | 3004.9304 | 2301.9651 | 0 | 104.6934
0 | 42.6723 | 0 | 0 | 0 | 0 | 9.8277 | 52.5 | 500.1272 | 3000 | 17.5609 | 3017.5609 | 1990.1501 | 0 | 89.5568
0 | 42.3841 | 0 | 0 | 0 | 0 | 10.1159 | 52.5 | 510.243 | 3000 | 18.0757 | 3018.0757 | 2131.2579 | 0 | 95.6935
0 | 33.1655 | 0 | 0 | 0 | 0 | 19.3345 | 52.5 | 529.5775 | 3000 | 34.5481 | 3034.5481 | 2347.8051 | 0 | 106.7547
0 | 49.2043 | 0 | 0 | 0 | 0 | 3.2957 | 52.5 | 532.8732 | 3000 | 5.889 | 3005.889 | 2632.7767 | 0 | 130.691
0 | 47.1686 | 0 | 0 | 0 | 0 | 5.3314 | 52.5 | 538.2047 | 3000 | 9.5265 | 3009.5265 | 2760.785 | 0 | 145.4382
0 | 43.9588 | 0 | 0 | 0 | 0 | 8.5412 | 52.5 | 546.7458 | 3000 | 15.2619 | 3015.2619 | 2917.9283 | 0 | 162.6453
0 | 49.1704 | 0 | 0 | 0 | 0 | 3.3296 | 52.5 | 550.0754 | 3000 | 5.9496 | 3005.9496 | 2989.7273 | 0 | 164.7639
0 | 27.8229 | 0 | 0 | 0 | 0 | 24.6771 | 52.5 | 574.7525 | 3000 | 44.0947 | 3044.0947 | 3044.0947 | 0 | 163.1026
0 | 34.9627 | 0 | 0 | 0 | 0 | 17.5373 | 52.5 | 592.2898 | 3000 | 31.3368 | 3031.3368 | 3031.3368 | 0 | 160.964
0 | 35.8089 | 0 | 0 | 0 | 0 | 16.6911 | 52.5 | 608.9809 | 3000 | 29.8247 | 3029.8247 | 3029.8247 | 0 | 155.6118
0 | 27.281 | 0 | 0 | 0 | 0 | 25.219 | 52.5 | 634.1999 | 3000 | 45.0631 | 3045.0631 | 3045.0631 | 0 | 141.8086
0 | 29.0352 | 0 | 0 | 0 | 0 | 23.4648 | 52.5 | 657.6647 | 3000 | 41.9285 | 3041.9285 | 3041.9285 | 0 | 159.0929
0 | 31.7842 | 0 | 0 | 0 | 0 | 20.7158 | 52.5 | 678.3805 | 3000 | 37.0163 | 3037.0163 | 3037.0163 | 0 | 156.8923
0 | 31.8115 | 0 | 0 | 0 | 0 | 20.6885 | 52.5 | 699.069 | 3000 | 36.9676 | 3036.9676 | 3036.9676 | 0 | 136.6635
0 | 35.617 | 0 | 0 | 0 | 0 | 16.883 | 52.5 | 715.9519 | 3000 | 30.1676 | 3030.1676 | 3030.1676 | 0 | 133.3274
0 | 28.5386 | 0 | 0 | 0 | 0 | 23.9614 | 52.5 | 739.9133 | 3000 | 42.8158 | 3042.8158 | 3042.8158 | 0 | 145.1423
0 | 29.7924 | 0 | 0 | 0 | 0 | 22.7076 | 52.5 | 762.621 | 3000 | 40.5755 | 3040.5755 | 3008.131 | 0 | 147.3984
0 | 26.8432 | 0 | 0 | 0 | 0 | 25.6568 | 52.5 | 788.2778 | 3000 | 45.8454 | 3045.8454 | 2829.5483 | 0 | 156.5589
0 | 34.6043 | 0 | 0 | 0 | 0 | 17.8957 | 52.5 | 806.1734 | 3000 | 31.9772 | 3031.9772 | 2621.0128 | 0 | 142.0065
0 | 62.217 | 0 | 0 | 0 | 0 | -9.717 | 52.5 | 796.4564 | 3000 | 0 | 3000 | 2361.9238 | 0 | 111.1285
0 | 55.4332 | 0 | 0 | 0 | 0 | -2.9332 | 52.5 | 793.5232 | 3000 | 0 | 3000 | 2486.2946 | 0 | 133.514
0 | 57.9908 | 0 | 0 | 0 | 0 | -5.4908 | 52.5 | 788.0324 | 3000 | 0 | 3000 | 1977.9966 | 0 | 107.2074
0 | 51.4282 | 0 | 0 | 0 | 0 | 1.0718 | 52.5 | 789.1042 | 3000 | 1.9151 | 3001.9151 | 2374.6538 | 0 | 124.1944
0 | 45.7814 | 0 | 0 | 0 | 0 | 6.7186 | 52.5 | 795.8228 | 3000 | 12.0053 | 3012.0053 | 2579.4113 | 0 | 134.9032
0 | 46.0492 | 0 | 0 | 0 | 0 | 6.4508 | 52.5 | 802.2737 | 3000 | 11.5268 | 3011.5268 | 2741.1555 | 0 | 149.9412
0 | 44.4036 | 0 | 0 | 0 | 0 | 8.0964 | 52.5 | 810.3701 | 3000 | 14.4672 | 3014.4672 | 2641.3548 | 0 | 138.1429
0 | 49.2176 | 0 | 0 | 0 | 0 | 3.2824 | 52.5 | 813.6524 | 3000 | 5.8651 | 3005.8651 | 2816.6053 | 0 | 140.4641
0 | 44.712 | 0 | 0 | 0 | 0 | 7.788 | 52.5 | 821.4404 | 3000 | 13.9161 | 3013.9161 | 2705.6929 | 0 | 134.5271
0 | 41.1546 | 0 | 0 | 0 | 0 | 11.3454 | 52.5 | 832.7858 | 3000 | 20.2728 | 3020.2728 | 2755.3089 | 0 | 144.5711
0 | 36.2809 | 0 | 0 | 0 | 0 | 16.2191 | 52.5 | 849.0049 | 3000 | 28.9814 | 3028.9814 | 2850.5363 | 0 | 162.6516
0 | 37.3018 | 0 | 0 | 0 | 0 | 15.1982 | 52.5 | 864.2031 | 3000 | 27.1571 | 3027.1571 | 2973.0828 | 0 | 183.1122
0 | 28.4767 | 0 | 0 | 0 | 0 | 24.0233 | 52.5 | 888.2264 | 3000 | 42.9264 | 3042.9264 | 3042.9264 | 0 | 198.3988
0 | 28.2576 | 0 | 0 | 0 | 0 | 24.2424 | 52.5 | 912.4688 | 3000 | 43.318 | 3043.318 | 3043.318 | 0 | 185.8554
0 | 23.8476 | 0 | 0 | 0 | 0 | 28.6524 | 52.5 | 941.1212 | 3000 | 51.198 | 3051.198 | 3051.198 | 0 | 191.4932
0 | 29.2909 | 0 | 0 | 0 | 0 | 23.2091 | 52.5 | 964.3303 | 3000 | 41.4716 | 3041.4716 | 3041.4716 | 0 | 181.15
0 | 29.1779 | 0 | 0 | 0 | 0 | 23.3221 | 52.5 | 987.6524 | 3000 | 41.6735 | 3041.6735 | 3041.6735 | 0 | 162.8208
0 | 225.6725 | 0 | 0 | 0 | 0 | -173.1725 | 52.5 | 814.4799 | 3000 | 0 | 3000 | 3000 | 0 | 153.66
0 | 38.6293 | 0 | 0 | 0 | 0 | 13.8707 | 52.5 | 828.3507 | 3000 | 24.7852 | 3024.7852 | 3024.7852 | 0 | 152.9634
0 | 36.773 | 0 | 0 | 0 | 0 | 15.727 | 52.5 | 844.0776 | 3000 | 28.102 | 3028.102 | 3028.102 | 0 | 151.4354
0 | 35.116 | 0 | 0 | 0 | 0 | 17.384 | 52.5 | 861.4616 | 3000 | 31.0629 | 3031.0629 | 3031.0629 | 0 | 149.0677
0 | 229.0689 | 0 | 0 | 0 | 0 | -176.5689 | 52.5 | 684.8927 | 3000 | 0 | 3000 | 2972.9629 | 0 | 153.3157
0 | 30.8317 | 0 | 0 | 0 | 0 | 21.6683 | 52.5 | 706.561 | 3000 | 38.7184 | 3038.7184 | 2833.2362 | 0 | 175.1507
0 | 19.5387 | 0 | 0 | 0 | 0 | 32.9613 | 52.5 | 739.5223 | 3000 | 58.8974 | 3058.8974 | 2485.7103 | 0 | 168.4566
0 | 42.2189 | 0 | 0 | 0 | 0 | -26.8889 | 15.3301 | 712.6334 | 876.0029 | 0 | 876.0029 | 0 | 0 | 0
0 | 52.696 | 0 | 0 | 0 | 0 | -0.196 | 52.5 | 712.4374 | 3000 | 0 | 3000 | 1956.3669 | 0 | 129.7071
0 | 44.0884 | 0 | 0 | 0 | 0 | 8.4116 | 52.5 | 720.849 | 3000 | 15.0304 | 3015.0304 | 1782.1374 | 0 | 110.4747
0 | 47.5549 | 0 | 0 | 0 | 0 | 4.9451 | 52.5 | 725.7941 | 3000 | 8.8363 | 3008.8363 | 1592.0909 | 0 | 96.4966
0 | 32.1113 | 0 | 0 | 0 | 0 | 20.3887 | 52.5 | 746.1828 | 3000 | 36.4318 | 3036.4318 | 1776.5018 | 0 | 104.9202
0 | 42.7932 | 0 | 0 | 0 | 0 | 9.7068 | 52.5 | 755.8896 | 3000 | 17.3447 | 3017.3447 | 2125.1195 | 0 | 123.2569
0 | 45.5208 | 0 | 0 | 0 | 0 | 6.9792 | 52.5 | 762.8687 | 3000 | 12.4709 | 3012.4709 | 2006.6898 | 0 | 111.7124
0 | 33.4888 | 0 | 0 | 0 | 0 | 19.0112 | 52.5 | 781.88 | 3000 | 33.9706 | 3033.9706 | 2504.0429 | 0 | 136.245
0 | 40.5246 | 0 | 0 | 0 | 0 | 11.9754 | 52.5 | 793.8554 | 3000 | 21.3985 | 3021.3985 | 2810.5089 | 0 | 153.1446
0 | 38.1068 | 0 | 0 | 0 | 0 | 14.3932 | 52.5 | 808.2486 | 3000 | 25.7187 | 3025.7187 | 2885.1257 | 0 | 167.0776
0 | 58.467 | 0 | 0 | 0 | 0 | -5.967 | 52.5 | 802.2816 | 3000 | 0 | 3000 | 2945.9257 | 0 | 183.4428
0 | 43.7442 | 0 | 0 | 0 | 0 | 8.7558 | 52.5 | 811.0373 | 3000 | 15.6454 | 3015.6454 | 3004.8306 | 0 | 187.0808
0 | 34.8203 | 0 | 0 | 0 | 0 | 17.6797 | 52.5 | 828.7171 | 3000 | 31.5913 | 3031.5913 | 3031.5913 | 0 | 194.2341
0 | 33.822 | 0 | 0 | 0 | 0 | 18.678 | 52.5 | 847.3951 | 3000 | 33.3751 | 3033.3751 | 3033.3751 | 0 | 187.4929
0 | 28.356 | 0 | 0 | 0 | 0 | 24.144 | 52.5 | 871.539 | 3000 | 43.142 | 3043.142 | 3043.142 | 0 | 182.1625
0 | 28.7617 | 0 | 0 | 0 | 0 | 23.7383 | 52.5 | 895.2773 | 3000 | 42.4172 | 3042.4172 | 3042.4172 | 0 | 162.5564
0 | 24.5714 | 0 | 0 | 0 | 0 | 27.9286 | 52.5 | 923.2059 | 3000 | 49.9048 | 3049.9048 | 3049.9048 | 0 | 149.4453
0 | 27.0398 | 0 | 0 | 0 | 0 | 25.4602 | 52.5 | 948.6662 | 3000 | 45.4941 | 3045.4941 | 3045.4941 | 0 | 155.5334
0 | 39.3868 | 0 | 0 | 0 | 0 | 13.1132 | 52.5 | 961.7794 | 3000 | 23.4315 | 3023.4315 | 3023.4315 | 0 | 151.1716
0 | 33.3134 | 0 | 0 | 0 | 0 | 19.1866 | 52.5 | 980.966 | 3000 | 34.284 | 3034.284 | 3034.284 | 0 | 152.4424
0 | 31.9566 | 0 | 0 | 0 | 0 | 20.5434 | 52.5 | 1001.5095 | 3000 | 36.7084 | 3036.7084 | 3036.7084 | 0 | 150.1349
0 | 49.3431 | 0 | 0 | 0 | 0 | 3.1569 | 52.5 | 1004.6664 | 3000 | 5.641 | 3005.641 | 2989.4188 | 0 | 155.4797
0 | 46.9345 | 0 | 0 | 0 | 0 | 5.5655 | 52.5 | 1010.2319 | 3000 | 9.9448 | 3009.9448 | 2966.6854 | 0 | 179.8405
0 | 107.1494 | 0 | 0 | 0 | 0 | -54.6494 | 52.5 | 955.5825 | 3000 | 0 | 3000 | 2935.1109 | 0 | 197.0633
0 | 84.9361 | 0 | 0 | 0 | 0 | -84.9361 | 0 | 870.6464 | 0 | 0 | 0 | 0 | 140.5931 | 0
0 | 41.8091 | 0 | 0 | 0 | 0 | 10.6909 | 52.5 | 881.3373 | 3000 | 19.1032 | 3019.1032 | 2775.7691 | 0 | 184.5054
0 | 46.0542 | 0 | 0 | 0 | 0 | 6.4458 | 52.5 | 887.7831 | 3000 | 11.5178 | 3011.5178 | 2741.1465 | 0 | 171.1298
0 | 52.9502 | 0 | 0 | 0 | 0 | -0.45018 | 52.5 | 887.3329 | 3000 | 0 | 3000 | 2670.1471 | 0 | 159.8083
0 | 68.5083 | 0 | 0 | 0 | 0 | -16.0083 | 52.5 | 871.3246 | 3000 | 0 | 3000 | 2551.1837 | 0 | 142.4836
0 | 47.5412 | 0 | 0 | 0 | 0 | 4.9588 | 52.5 | 876.2834 | 3000 | 8.8607 | 3008.8607 | 2500.5627 | 0 | 128.754
0 | 38.3889 | 0 | 0 | 0 | 0 | 14.1111 | 52.5 | 890.3945 | 3000 | 25.2147 | 3025.2147 | 2354.6939 | 0 | 117.6876
0 | 29.7089 | 0 | 0 | 0 | 0 | 22.7911 | 52.5 | 913.1856 | 3000 | 40.7247 | 3040.7247 | 1872.7209 | 0 | 93.5237
0 | 34.6184 | 0 | 0 | 0 | 0 | 17.8816 | 52.5 | 931.0672 | 3000 | 31.952 | 3031.952 | 2210.0234 | 0 | 111.2526
0 | 56.5072 | 0 | 0 | 0 | 0 | -4.0072 | 52.5 | 927.06 | 3000 | 0 | 3000 | 2443.0352 | 0 | 137.5429
0 | 51.6042 | 0 | 0 | 0 | 0 | 0.8958 | 52.5 | 927.9558 | 3000 | 1.6007 | 3001.6007 | 2715.0071 | 0 | 168.5748
0 | 39.7925 | 0 | 0 | 0 | 0 | 12.7075 | 52.5 | 940.6633 | 3000 | 22.7066 | 3022.7066 | 2968.6323 | 0 | 206.0231
0 | 30.8053 | 0 | 0 | 0 | 0 | 21.6947 | 52.5 | 962.358 | 3000 | 38.7655 | 3038.7655 | 3038.7655 | 0 | 202.868
0 | 36.3017 | 0 | 0 | 0 | 0 | 16.1983 | 52.5 | 978.5563 | 3000 | 28.9443 | 3028.9443 | 3028.9443 | 0 | 192.974
0 | 25.1732 | 0 | 0 | 0 | 0 | 27.3268 | 52.5 | 1005.8831 | 3000 | 48.8293 | 3048.8293 | 3048.8293 | 0 | 186.8323
0 | 35.3307 | 0 | 0 | 0 | 0 | 17.1693 | 52.5 | 1023.0524 | 3000 | 30.6793 | 3030.6793 | 3030.6793 | 0 | 177.022
0 | 28.1138 | 0 | 0 | 0 | 0 | 24.3862 | 52.5 | 1047.4386 | 3000 | 43.575 | 3043.575 | 3043.575 | 0 | 161.3095
0 | 34.7291 | 0 | 0 | 0 | 0 | 17.7709 | 52.5 | 1065.2095 | 3000 | 31.7542 | 3031.7542 | 3031.7542 | 0 | 152.1941
0 | 32.3645 | 0 | 0 | 0 | 0 | 20.1355 | 52.5 | 1085.345 | 3000 | 35.9795 | 3035.9795 | 3035.9795 | 0 | 144.6341
0 | 37.4725 | 0 | 0 | 0 | 0 | 15.0275 | 52.5 | 1100.3726 | 3000 | 26.8522 | 3026.8522 | 3026.8522 | 0 | 139.7195
0 | 35.5988 | 0 | 0 | 0 | 0 | 16.9012 | 52.5 | 1117.2737 | 3000 | 30.2001 | 3030.2001 | 3030.2001 | 0 | 146.3587
0 | 59.6167 | 0 | 0 | 0 | 0 | -7.1167 | 52.5 | 1110.1571 | 3000 | 0 | 3000 | 2978.3703 | 0 | 136.1115
0 | 85.0423 | 0 | 0 | 0 | 0 | -32.5423 | 52.5 | 1077.6147 | 3000 | 0 | 3000 | 2902.6663 | 0 | 133.4646
0 | 98.1944 | 0 | 0 | 0 | 0 | -45.6944 | 52.5 | 1031.9203 | 3000 | 0 | 3000 | 2789.1104 | 0 | 139.3997
0 | 50.4896 | 0 | 0 | 0 | 0 | 2.0104 | 52.5 | 1033.9307 | 3000 | 3.5923 | 3003.5923 | 2695.3691 | 0 | 146.8976
0 | 34.3162 | 0 | 0 | 0 | 0 | 18.1838 | 52.5 | 1052.1145 | 3000 | 32.492 | 3032.492 | 2621.5277 | 0 | 136.4505
0 | 58.5479 | 0 | 0 | 0 | 0 | -6.0479 | 52.5 | 1046.0666 | 3000 | 0 | 3000 | 2464.6649 | 0 | 128.0393
0 | 79.0817 | 0 | 0 | 0 | 0 | -26.5817 | 52.5 | 1019.4849 | 3000 | 0 | 3000 | 2351.109 | 0 | 112.5946
0 | 57.2571 | 0 | 0 | 0 | 0 | -4.7571 | 52.5 | 1014.7278 | 3000 | 0 | 3000 | 2069.9229 | 0 | 120.6972
0 | 58.911 | 0 | 0 | 0 | 0 | -6.411 | 52.5 | 1008.3167 | 3000 | 0 | 3000 | 1896.8853 | 0 | 129.5004
0 | 247.8403 | 0 | 0 | 0 | 0 | -195.3403 | 52.5 | 812.9765 | 3000 | 0 | 3000 | 1826.5887 | 0 | 115.5683
0 | 39.1638 | 0 | 0 | 0 | 0 | 13.3362 | 52.5 | 826.3126 | 3000 | 23.83 | 3023.83 | 1845.0113 | 0 | 105.4608
0 | 40.2442 | 0 | 0 | 0 | 0 | 12.2558 | 52.5 | 838.5684 | 3000 | 21.8995 | 3021.8995 | 2135.0817 | 0 | 112.4334
0 | 51.5317 | 0 | 0 | 0 | 0 | 0.96829 | 52.5 | 839.5367 | 3000 | 1.7302 | 3001.7302 | 2444.7654 | 0 | 122.4827
0 | 36.9729 | 0 | 0 | 0 | 0 | 15.5271 | 52.5 | 855.0639 | 3000 | 27.7449 | 3027.7449 | 2741.1514 | 0 | 136.1256
0 | 58.3213 | 0 | 0 | 0 | 0 | -5.8213 | 52.5 | 849.2425 | 3000 | 0 | 3000 | 2918.8886 | 0 | 158.7875
0 | 112.2404 | 0 | 0 | 0 | 0 | -59.7404 | 52.5 | 789.5021 | 3000 | 0 | 3000 | 3000 | 0 | 164.7
0 | 93.3463 | 0 | 0 | 0 | 0 | -93.3463 | 0 | 696.1558 | 0 | 0 | 0 | 0 | 0 | 0
0 | 65.7723 | 0 | 0 | 0 | 0 | -13.2723 | 52.5 | 682.8835 | 3000 | 0 | 3000 | 3000 | 0 | 201.03
0 | 66.3046 | 0 | 0 | 0 | 0 | -13.8046 | 52.5 | 669.0788 | 3000 | 0 | 3000 | 3000 | 0 | 169.77
0 | 44.2076 | 0 | 0 | 0 | 0 | 8.2924 | 52.5 | 677.3712 | 3000 | 14.8174 | 3014.8174 | 3014.8174 | 0 | 152.2483
0 | 52.7197 | 0 | 0 | 0 | 0 | -0.21972 | 52.5 | 677.1515 | 3000 | 0 | 3000 | 3000 | 0 | 154.92
0 | 45.656 | 0 | 0 | 0 | 0 | 6.844 | 52.5 | 683.9955 | 3000 | 12.2293 | 3012.2293 | 3012.2293 | 0 | 153.0514
0 | 30.3282 | 0 | 0 | 0 | 0 | 22.1718 | 52.5 | 706.1673 | 3000 | 39.6181 | 3039.6181 | 3039.6181 | 0 | 150.3091
0 | 28.0303 | 0 | 0 | 0 | 0 | 24.4697 | 52.5 | 730.637 | 3000 | 43.724 | 3043.724 | 3043.724 | 0 | 127.7451
0 | 40.3334 | 0 | 0 | 0 | 0 | 12.1666 | 52.5 | 742.8036 | 3000 | 21.7401 | 3021.7401 | 2983.8881 | 0 | 140.0339
0 | 59.1732 | 0 | 0 | 0 | 0 | -6.6732 | 52.5 | 736.1304 | 3000 | 0 | 3000 | 2843.1847 | 0 | 161.3507
0 | 54.1651 | 0 | 0 | 0 | 0 | -1.6651 | 52.5 | 734.4653 | 3000 | 0 | 3000 | 2659.3322 | 0 | 160.9428
0 | 83.4725 | 0 | 0 | 0 | 0 | -30.9725 | 52.5 | 703.4928 | 3000 | 0 | 3000 | 2340.2941 | 0 | 145.5195
0 | 121.6567 | 0 | 0 | 0 | 0 | -69.1567 | 52.5 | 634.3361 | 3000 | 0 | 3000 | 2129.4045 | 0 | 124.1443
0 | 109.4594 | 0 | 0 | 0 | 0 | -56.9594 | 52.5 | 577.3767 | 3000 | 0 | 3000 | 2221.3308 | 0 | 134.2794
0 | 45.3936 | 0 | 0 | 0 | 0 | 7.1064 | 52.5 | 584.483 | 3000 | 12.6981 | 3012.6981 | 2661.2155 | 0 | 157.0117
0 | 41.4695 | 0 | 0 | 0 | 0 | 11.0305 | 52.5 | 595.5136 | 3000 | 19.7101 | 3019.7101 | 2916.969 | 0 | 165.5088
0 | 240.1729 | 0 | 0 | 0 | 0 | -187.6729 | 52.5 | 407.8407 | 3000 | 0 | 3000 | 2821.555 | 0 | 159.8975
0 | 31.7276 | 0 | 0 | 0 | 0 | 20.7724 | 52.5 | 428.6131 | 3000 | 37.1176 | 3037.1176 | 2636.9681 | 0 | 144.3476
0 | 41.4522 | 0 | 0 | 0 | 0 | 11.0478 | 52.5 | 439.6609 | 3000 | 19.7409 | 3019.7409 | 2689.888 | 0 | 139.8742
0 | 33.9905 | 0 | 0 | 0 | 0 | 18.5095 | 52.5 | 458.1703 | 3000 | 33.0739 | 3033.0739 | 2822.1844 | 0 | 148.1082
0 | 32.9452 | 0 | 0 | 0 | 0 | 19.5548 | 52.5 | 477.7251 | 3000 | 34.9417 | 3034.9417 | 2629.3849 | 0 | 145.6942
0 | 47.7878 | 0 | 0 | 0 | 0 | 4.7122 | 52.5 | 482.4373 | 3000 | 8.42 | 3008.42 | 2759.6785 | 0 | 168.2852
0 | 33.0885 | 0 | 0 | 0 | 0 | 19.4115 | 52.5 | 501.8488 | 3000 | 34.6858 | 3034.6858 | 3002.2412 | 0 | 186.6794
0 | 37.4514 | 0 | 0 | 0 | 0 | 15.0486 | 52.5 | 516.8974 | 3000 | 26.8898 | 3026.8898 | 3026.8898 | 0 | 192.3891
0 | 55.4938 | 0 | 0 | 0 | 0 | -2.9938 | 52.5 | 513.9036 | 3000 | 0 | 3000 | 3000 | 0 | 185.88
0 | 94.2637 | 0 | 0 | 0 | 0 | -41.7637 | 52.5 | 472.1399 | 3000 | 0 | 3000 | 3000 | 0 | 179.16
0 | 20.9654 | 0 | 0 | 0 | 0 | 31.5346 | 52.5 | 503.6745 | 3000 | 56.3482 | 3056.3482 | 3056.3482 | 0 | 173.3255
0 | 30.0745 | 0 | 0 | 0 | 0 | 22.4255 | 52.5 | 526.1 | 3000 | 40.0714 | 3040.0714 | 3040.0714 | 0 | 146.805
0 | 35.7548 | 0 | 0 | 0 | 0 | 16.7452 | 52.5 | 542.8452 | 3000 | 29.9215 | 3029.9215 | 3029.9215 | 0 | 151.1931
0 | 57.1262 | 0 | 0 | 0 | 0 | -4.6262 | 52.5 | 538.219 | 3000 | 0 | 3000 | 3000 | 0 | 145.8
0 | 39.8886 | 0 | 0 | 0 | 0 | 12.6114 | 52.5 | 550.8304 | 3000 | 22.5348 | 3022.5348 | 3022.5348 | 0 | 143.51
0 | 33.9634 | 0 | 0 | 0 | 0 | 18.5366 | 52.5 | 569.367 | 3000 | 33.1225 | 3033.1225 | 3033.1225 | 0 | 145.8932
0 | 32.6672 | 0 | 0 | 0 | 0 | 19.8328 | 52.5 | 589.1998 | 3000 | 35.4386 | 3035.4386 | 2970.5495 | 0 | 151.3792
0 | 32.7868 | 0 | 0 | 0 | 0 | 19.7132 | 52.5 | 608.9129 | 3000 | 35.2248 | 3035.2248 | 2727.0015 | 0 | 155.3027
0 | 35.8228 | 0 | 0 | 0 | 0 | 16.6772 | 52.5 | 625.5902 | 3000 | 29.8 | 3029.8 | 2499.8723 | 0 | 154.9671
0 | 43.992 | 0 | 0 | 0 | 0 | 8.508 | 52.5 | 634.0981 | 3000 | 15.2026 | 3015.2026 | 2425.7932 | 0 | 157.9191
0 | 59.0232 | 0 | 0 | 0 | 0 | -6.5232 | 52.5 | 627.5749 | 3000 | 0 | 3000 | 2280.8124 | 0 | 143.5543
0 | 53.9422 | 0 | 0 | 0 | 0 | -1.4422 | 52.5 | 626.1326 | 3000 | 0 | 3000 | 2113.1823 | 0 | 130.806
0 | 50.5934 | 0 | 0 | 0 | 0 | 1.9066 | 52.5 | 628.0393 | 3000 | 3.4069 | 3003.4069 | 1905.6996 | 0 | 117.1434
0 | 34.8632 | 0 | 0 | 0 | 0 | 17.6368 | 52.5 | 645.6761 | 3000 | 31.5147 | 3031.5147 | 1749.9549 | 0 | 102.7224
0 | 35.9926 | 0 | 0 | 0 | 0 | 16.5074 | 52.5 | 662.1836 | 3000 | 29.4966 | 3029.4966 | 2169.716 | 0 | 122.0248
0 | 30.1847 | 0 | 0 | 0 | 0 | 22.3153 | 52.5 | 684.4989 | 3000 | 39.8745 | 3039.8745 | 2515.3542 | 0 | 135.9549
0 | 53.6088 | 0 | 0 | 0 | 0 | -1.1088 | 52.5 | 683.39 | 3000 | 0 | 3000 | 2534.9614 | 0 | 128.2944
0 | 41.2553 | 0 | 0 | 0 | 0 | 11.2447 | 52.5 | 694.6347 | 3000 | 20.0927 | 3020.0927 | 2701.0547 | 0 | 136.3222
0 | 57.232 | 0 | 0 | 0 | 0 | -4.732 | 52.5 | 689.9027 | 3000 | 0 | 3000 | 2821.555 | 0 | 152.0536
0 | 44.7911 | 0 | 0 | 0 | 0 | 7.7089 | 52.5 | 697.6116 | 3000 | 13.7748 | 3013.7748 | 2975.9228 | 0 | 169.6574
0 | 60.6375 | 0 | 0 | 0 | 0 | -8.1375 | 52.5 | 689.4741 | 3000 | 0 | 3000 | 2994.5926 | 0 | 176.5612
0 | 100.3173 | 0 | 0 | 0 | 0 | -47.8173 | 52.5 | 641.6568 | 3000 | 0 | 3000 | 3000 | 0 | 178.71
0 | 112.7788 | 0 | 0 | 0 | 0 | -60.2788 | 52.5 | 581.378 | 3000 | 0 | 3000 | 3000 | 0 | 179.76
0 | 141.8245 | 0 | 0 | 0 | 0 | -89.3245 | 52.5 | 492.0534 | 3000 | 0 | 3000 | 3000 | 0 | 181.11
0 | 311.7593 | 0 | 0 | 0 | 0 | -259.2593 | 52.5 | 232.7941 | 3000 | 0 | 3000 | 3000 | 0 | 171.03
0 | 33.077 | 0 | 0 | 0 | 0 | 19.423 | 52.5 | 252.2171 | 3000 | 34.7063 | 3034.7063 | 3034.7063 | 0 | 166.0591
0 | 28.869 | 0 | 0 | 0 | 0 | 23.631 | 52.5 | 275.8481 | 3000 | 42.2255 | 3042.2255 | 3042.2255 | 0 | 164.7365
0 | 23.6218 | 0 | 0 | 0 | 0 | 28.8782 | 52.5 | 304.7263 | 3000 | 51.6015 | 3051.6015 | 3051.6015 | 0 | 154.289
0 | 39.5183 | 0 | 0 | 0 | 0 | 12.9817 | 52.5 | 317.708 | 3000 | 23.1965 | 3023.1965 | 3023.1965 | 0 | 150.8575
0 | 22.3698 | 0 | 0 | 0 | 0 | 30.1302 | 52.5 | 347.8381 | 3000 | 53.8386 | 3053.8386 | 3053.8386 | 0 | 152.6309
0 | 47.1762 | 0 | 0 | 0 | 0 | 5.3238 | 52.5 | 353.162 | 3000 | 9.513 | 3009.513 | 2944.6239 | 0 | 145.7883
0 | 90.4549 | 0 | 0 | 0 | 0 | -37.9549 | 52.5 | 315.2071 | 3000 | 0 | 3000 | 2794.5178 | 0 | 141.3747
0 | 105.4279 | 0 | 0 | 0 | 0 | -52.9279 | 52.5 | 262.2791 | 3000 | 0 | 3000 | 2561.9986 | 0 | 143.1389
0 | 91.2107 | 0 | 0 | 0 | 0 | -38.7107 | 52.5 | 223.5684 | 3000 | 0 | 3000 | 2464.6649 | 0 | 147.8799
0 | 94.7733 | 0 | 0 | 0 | 0 | -42.2733 | 52.5 | 181.2951 | 3000 | 0 | 3000 | 2367.3312 | 0 | 142.2056
0 | 75.1217 | 0 | 0 | 0 | 0 | -22.6217 | 52.5 | 158.6735 | 3000 | 0 | 3000 | 2248.3679 | 0 | 131.7993
0 | 97.8113 | 0 | 0 | 0 | 0 | -45.3113 | 52.5 | 113.3622 | 3000 | 0 | 3000 | 2329.4793 | 0 | 134.2945
0 | 39.9538 | 0 | 0 | 0 | 0 | 12.5462 | 52.5 | 125.9083 | 3000 | 22.4183 | 3022.4183 | 2319.453 | 0 | 128.8688
0 | 42.2441 | 0 | 0 | 0 | 0 | 10.2559 | 52.5 | 136.1642 | 3000 | 18.326 | 3018.326 | 2218.027 | 0 | 115.293
0 | 58.7056 | 0 | 0 | 0 | 0 | -6.2056 | 52.5 | 129.9587 | 3000 | 0 | 3000 | 2156.4417 | 0 | 107.7143
0 | 54.5197 | 0 | 0 | 0 | 0 | -2.0197 | 52.5 | 127.939 | 3000 | 0 | 3000 | 1929.3298 | 0 | 96.6787
0 | 44.4811 | 0 | 0 | 0 | 0 | 8.0189 | 52.5 | 135.9579 | 3000 | 14.3287 | 3014.3287 | 2057.2144 | 0 | 108.0038
0 | 50.9393 | 0 | 0 | 0 | 0 | 1.5607 | 52.5 | 137.5186 | 3000 | 2.7888 | 3002.7888 | 2478.2685 | 0 | 134.3222
0 | 52.5841 | 0 | 0 | 0 | 0 | -0.084148 | 52.5 | 137.4345 | 3000 | 0 | 3000 | 2605.258 | 0 | 145.9726
0 | 43.8718 | 0 | 0 | 0 | 0 | 8.6282 | 52.5 | 146.0627 | 3000 | 15.4174 | 3015.4174 | 2950.5283 | 0 | 175.645
0 | 31.1653 | 0 | 0 | 0 | 0 | 21.3347 | 52.5 | 167.3973 | 3000 | 38.1222 | 3038.1222 | 3038.1222 | 0 | 181.7101
0 | 23.1699 | 0 | 0 | 0 | 0 | 29.3301 | 52.5 | 196.7274 | 3000 | 52.409 | 3052.409 | 3052.409 | 0 | 184.6707
0 | 30.0371 | 0 | 0 | 0 | 0 | 22.4629 | 52.5 | 219.1903 | 3000 | 40.1381 | 3040.1381 | 3040.1381 | 0 | 185.2052
0 | 29.6256 | 0 | 0 | 0 | 0 | 22.8744 | 52.5 | 242.0647 | 3000 | 40.8736 | 3040.8736 | 3040.8736 | 0 | 180.3238
0 | 30.519 | 0 | 0 | 0 | 0 | 21.981 | 52.5 | 264.0457 | 3000 | 39.2772 | 3039.2772 | 3039.2772 | 0 | 152.5413
0 | 34.9608 | 0 | 0 | 0 | 0 | 17.5392 | 52.5 | 281.5849 | 3000 | 31.3401 | 3031.3401 | 3031.3401 | 0 | 142.5336
0 | 31.6446 | 0 | 0 | 0 | 0 | 20.8554 | 52.5 | 302.4403 | 3000 | 37.2659 | 3037.2659 | 3037.2659 | 0 | 136.677
0 | 23.73 | 0 | 0 | 0 | 0 | 28.77 | 52.5 | 331.2103 | 3000 | 51.4081 | 3051.4081 | 3051.4081 | 0 | 143.7213
0 | 27.9507 | 0 | 0 | 0 | 0 | 24.5493 | 52.5 | 355.7596 | 3000 | 43.8664 | 3043.8664 | 3043.8664 | 0 | 143.3661
0 | 36.7125 | 0 | 0 | 0 | 0 | 15.7875 | 52.5 | 371.547 | 3000 | 28.2101 | 3028.2101 | 2963.321 | 0 | 158.7451
0 | 31.1482 | 0 | 0 | 0 | 0 | 21.3518 | 52.5 | 392.8989 | 3000 | 38.1529 | 3038.1529 | 2897.5599 | 0 | 144.878
0 | 27.025 | 0 | 0 | 0 | 0 | 25.475 | 52.5 | 418.3739 | 3000 | 45.5205 | 3045.5205 | 2845.4458 | 0 | 144.1503
0 | 46.2218 | 0 | 0 | 0 | 0 | 6.2782 | 52.5 | 424.6521 | 3000 | 11.2183 | 3011.2183 | 2556.9946 | 0 | 125.1137
0 | 41.0139 | 0 | 0 | 0 | 0 | 11.4861 | 52.5 | 436.1383 | 3000 | 20.5242 | 3020.5242 | 2598.745 | 0 | 134.7709
0 | 37.2341 | 0 | 0 | 0 | 0 | 15.2659 | 52.5 | 451.4041 | 3000 | 27.278 | 3027.278 | 2432.4613 | 0 | 128.9204
0 | 35.7948 | 0 | 0 | 0 | 0 | 16.7052 | 52.5 | 468.1093 | 3000 | 29.8499 | 3029.8499 | 2418.8109 | 0 | 120.6987
0 | 44.8377 | 0 | 0 | 0 | 0 | 7.6623 | 52.5 | 475.7717 | 3000 | 13.6916 | 3013.6916 | 2516.2085 | 0 | 139.1463
0 | 43.231 | 0 | 0 | 0 | 0 | 9.269 | 52.5 | 485.0407 | 3000 | 16.5625 | 3016.5625 | 2427.1532 | 0 | 133.7847
0 | 43.005 | 0 | 0 | 0 | 0 | 9.495 | 52.5 | 494.5356 | 3000 | 16.9662 | 3016.9662 | 2487.0386 | 0 | 111.9167
0 | 37.8524 | 0 | 0 | 0 | 0 | 14.6476 | 52.5 | 509.1833 | 3000 | 26.1734 | 3026.1734 | 1836.5398 | 0 | 82.4606
0 | 43.1661 | 0 | 0 | 0 | 0 | 9.3339 | 52.5 | 518.5172 | 3000 | 16.6785 | 3016.6785 | 2454.3063 | 0 | 123.4516
0 | 38.3186 | 0 | 0 | 0 | 0 | 14.1814 | 52.5 | 532.6986 | 3000 | 25.3403 | 3025.3403 | 2668.4502 | 0 | 146.8448
0 | 44.3074 | 0 | 0 | 0 | 0 | 8.1926 | 52.5 | 540.8912 | 3000 | 14.6391 | 3014.6391 | 2809.1569 | 0 | 154.5036
0 | 45.9198 | 0 | 0 | 0 | 0 | 6.5802 | 52.5 | 547.4714 | 3000 | 11.7579 | 3011.7579 | 2946.8688 | 0 | 163.787
0 | 29.2695 | 0 | 0 | 0 | 0 | 23.2305 | 52.5 | 570.7019 | 3000 | 41.5099 | 3041.5099 | 3041.5099 | 0 | 182.4906
0 | 34.2272 | 0 | 0 | 0 | 0 | -34.2272 | 0 | 536.4747 | 0 | 0 | 0 | 0 | 0 | 0
0 | 49.2563 | 0 | 0 | 0 | 0 | -49.2563 | 0 | 487.2184 | 0 | 0 | 0 | 0 | 0 | 0
0 | 72.5819 | 0 | 0 | 0 | 0 | -20.0819 | 52.5 | 467.1365 | 3000 | 0 | 3000 | 3000 | 0 | 201.06
0 | 69.2488 | 0 | 0 | 0 | 0 | -16.7488 | 52.5 | 450.3877 | 3000 | 0 | 3000 | 3000 | 0 | 201.99
0 | 23.9899 | 0 | 0 | 0 | 0 | 28.5101 | 52.5 | 478.8978 | 3000 | 50.9437 | 3050.9437 | 3050.9437 | 0 | 175.9174
0 | 34.5008 | 0 | 0 | 0 | 0 | 17.9992 | 52.5 | 496.897 | 3000 | 32.1622 | 3032.1622 | 3032.1622 | 0 | 166.4657
0 | 34.3204 | 0 | 0 | 0 | 0 | 18.1796 | 52.5 | 515.0767 | 3000 | 32.4846 | 3032.4846 | 3032.4846 | 0 | 165.4524
0 | 38.3073 | 0 | 0 | 0 | 0 | 14.1927 | 52.5 | 529.2693 | 3000 | 25.3604 | 3025.3604 | 3025.3604 | 0 | 154.8682
0 | 29.348 | 0 | 0 | 0 | 0 | 23.152 | 52.5 | 552.4213 | 3000 | 41.3695 | 3041.3695 | 3003.5176 | 0 | 154.2306
0 | 27.1474 | 0 | 0 | 0 | 0 | 25.3526 | 52.5 | 577.7739 | 3000 | 45.3017 | 3045.3017 | 2920.9309 | 0 | 177.7386
0 | 29.4211 | 0 | 0 | 0 | 0 | 23.0789 | 52.5 | 600.8528 | 3000 | 41.2389 | 3041.2389 | 2781.6825 | 0 | 185.3435
0 | 40.9652 | 0 | 0 | 0 | 0 | 11.5348 | 52.5 | 612.3876 | 3000 | 20.6112 | 3020.6112 | 2517.7206 | 0 | 160.7313
0 | 51.2949 | 0 | 0 | 0 | 0 | 1.2051 | 52.5 | 613.5926 | 3000 | 2.1533 | 3002.1533 | 2050.4465 | 0 | 123.4779
0 | 42.3024 | 0 | 0 | 0 | 0 | 10.1976 | 52.5 | 623.7903 | 3000 | 18.2218 | 3018.2218 | 1698.8101 | 0 | 102.6421
0 | 32.2865 | 0 | 0 | 0 | 0 | 20.2135 | 52.5 | 644.0038 | 3000 | 36.1189 | 3036.1189 | 2365.5981 | 0 | 144.7983
0 | 51.0258 | 0 | 0 | 0 | 0 | 1.4742 | 52.5 | 645.4779 | 3000 | 2.6341 | 3002.6341 | 2570.0401 | 0 | 156.4383
0 | 40.0968 | 0 | 0 | 0 | 0 | 12.4032 | 52.5 | 657.8811 | 3000 | 22.1628 | 3022.1628 | 2627.4208 | 0 | 155.517
0 | 55.0581 | 0 | 0 | 0 | 0 | -2.5581 | 52.5 | 655.323 | 3000 | 0 | 3000 | 2816.1475 | 0 | 160.7457
0 | 43.7795 | 0 | 0 | 0 | 0 | 8.7205 | 52.5 | 664.0435 | 3000 | 15.5824 | 3015.5824 | 2664.0998 | 0 | 149.4294
0 | 43.505 | 0 | 0 | 0 | 0 | 8.995 | 52.5 | 673.0385 | 3000 | 16.0728 | 3016.0728 | 2891.702 | 0 | 162.398
0 | 45.1122 | 0 | 0 | 0 | 0 | 7.3878 | 52.5 | 680.4263 | 3000 | 13.2009 | 3013.2009 | 2883.4227 | 0 | 169.7471
0 | 43.561 | 0 | 0 | 0 | 0 | 8.939 | 52.5 | 689.3652 | 3000 | 15.9728 | 3015.9728 | 2891.602 | 0 | 179.8287
0 | 42.5532 | 0 | 0 | 0 | 0 | 9.9468 | 52.5 | 699.3121 | 3000 | 17.7737 | 3017.7737 | 2979.9217 | 0 | 206.8066
0 | 20.6664 | 0 | 0 | 0 | 0 | -20.6664 | 0 | 678.6457 | 0 | 0 | 0 | 0 | 0 | 0
0 | 32.2939 | 0 | 0 | 0 | 0 | -32.2939 | 0 | 646.3518 | 0 | 0 | 0 | 0 | 0 | 0
0 | 35.2163 | 0 | 0 | 0 | 0 | -35.2163 | 0 | 611.1355 | 0 | 0 | 0 | 0 | 0 | 0
0 | 28.7523 | 0 | 0 | 0 | 0 | 23.7477 | 52.5 | 634.8832 | 3000 | 42.434 | 3042.434 | 3042.434 | 0 | 183.55
0 | 22.7348 | 0 | 0 | 0 | 0 | 29.7652 | 52.5 | 664.6484 | 3000 | 53.1864 | 3053.1864 | 3053.1864 | 0 | 175.0086
0 | 33.8677 | 0 | 0 | 0 | 0 | 18.6323 | 52.5 | 683.2807 | 3000 | 33.2934 | 3033.2934 | 3033.2934 | 0 | 169.8038
0 | 28.8998 | 0 | 0 | 0 | 0 | 23.6002 | 52.5 | 706.8809 | 3000 | 42.1705 | 3042.1705 | 3042.1705 | 0 | 169.7531
0 | 28.916 | 0 | 0 | 0 | 0 | 23.584 | 52.5 | 730.4649 | 3000 | 42.1416 | 3042.1416 | 3042.1416 | 0 | 167.409
0 | 39.4906 | 0 | 0 | 0 | 0 | 13.0094 | 52.5 | 743.4743 | 3000 | 23.246 | 3023.246 | 3023.246 | 0 | 166.3692
0 | 105.6811 | 0 | 0 | 0 | 0 | -53.1811 | 52.5 | 690.2932 | 3000 | 0 | 3000 | 2924.296 | 0 | 168.7611
0 | 91.9264 | 0 | 0 | 0 | 0 | -39.4264 | 52.5 | 650.8667 | 3000 | 0 | 3000 | 2724.2213 | 0 | 181.4059
0 | 239.8236 | 0 | 0 | 0 | 0 | -230.3606 | 9.463 | 420.5061 | 540.7425 | 0 | 540.7425 | 0 | 0 | 0
0 | 42.8161 | 0 | 0 | 0 | 0 | -26.0666 | 16.7495 | 394.4396 | 957.1143 | 0 | 957.1143 | 0 | 0 | 0
0 | 38.3199 | 0 | 0 | 0 | 0 | -27.3429 | 10.9771 | 367.0967 | 627.2613 | 0 | 627.2613 | 0 | 0 | 0
0 | 62.9478 | 0 | 0 | 0 | 0 | -45.1574 | 17.7904 | 321.9393 | 1016.5959 | 0 | 1016.5959 | 0 | 0 | 0
0 | 117.7546 | 0 | 0 | 0 | 0 | -108.0077 | 9.7469 | 213.9316 | 556.9648 | 0 | 556.9648 | 0 | 0 | 0
0 | 101.4157 | 0 | 0 | 0 | 0 | -48.9157 | 52.5 | 165.0159 | 3000 | 0 | 3000 | 2075.3303 | 0 | 143.3431
0 | 49.0927 | 0 | 0 | 0 | 0 | 3.4073 | 52.5 | 168.4233 | 3000 | 6.0885 | 3006.0885 | 2043.5668 | 0 | 130.6657
0 | 45.1959 | 0 | 0 | 0 | 0 | 7.3041 | 52.5 | 175.7274 | 3000 | 13.0515 | 3013.0515 | 1845.0476 | 0 | 116.238
0 | 37.0808 | 0 | 0 | 0 | 0 | 15.4192 | 52.5 | 191.1465 | 3000 | 27.552 | 3027.552 | 2654.4397 | 0 | 163.9647
0 | 37.1706 | 0 | 0 | 0 | 0 | 15.3294 | 52.5 | 206.476 | 3000 | 27.3917 | 3027.3917 | 2794.8724 | 0 | 173.5616
0 | 28.15 | 0 | 0 | 0 | 0 | 24.35 | 52.5 | 230.826 | 3000 | 43.5102 | 3043.5102 | 2762.3241 | 0 | 176.623
0 | 48.9978 | 0 | 0 | 0 | 0 | -48.9978 | 0 | 181.8282 | 0 | 0 | 0 | 0 | 86.5188 | 0
0 | 40.7898 | 0 | 0 | 0 | 0 | -40.7898 | 0 | 141.0384 | 0 | 0 | 0 | 0 | 75.704 | 0
0 | 25.1473 | 0 | 0 | 0 | 0 | -25.1473 | 0 | 115.8911 | 0 | 0 | 0 | 0 | 0 | 0
0 | 26.441 | 0 | 0 | 0 | 0 | -26.441 | 0 | 89.4501 | 0 | 0 | 0 | 0 | 0 | 0
0 | 40.0005 | 0 | 0 | 0 | 0 | 12.4995 | 52.5 | 101.9496 | 3000 | 22.3349 | 3022.3349 | 3022.3349 | 0 | 199.4137
0 | 154.4496 | 0 | 0 | 0 | 0 | -101.9496 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 180
0 | 26.2838 | 0 | 0 | 0 | 0 | 26.2162 | 52.5 | 26.2162 | 3000 | 46.8449 | 3046.8449 | 3046.8449 | 0 | 180.3123
0 | 33.5557 | 0 | 0 | 0 | 0 | 18.9443 | 52.5 | 45.1605 | 3000 | 33.851 | 3033.851 | 3033.851 | 0 | 163.919
0 | 33.1054 | 0 | 0 | 0 | 0 | 19.3946 | 52.5 | 64.5551 | 3000 | 34.6555 | 3034.6555 | 3034.6555 | 0 | 154.646
0 | 28.838 | 0 | 0 | 0 | 0 | 23.662 | 52.5 | 88.2171 | 3000 | 42.2808 | 3042.2808 | 3042.2808 | 0 | 154.5174
0 | 33.983 | 0 | 0 | 0 | 0 | 18.517 | 52.5 | 106.7341 | 3000 | 33.0875 | 3033.0875 | 3033.0875 | 0 | 151.897
0 | 60.3636 | 0 | 0 | 0 | 0 | -7.8636 | 52.5 | 98.8706 | 3000 | 0 | 3000 | 2962.148 | 0 | 152.1655
0 | 84.5471 | 0 | 0 | 0 | 0 | -32.0471 | 52.5 | 66.8234 | 3000 | 0 | 3000 | 2859.4069 | 0 | 167.7614
0 | 55.2681 | 0 | 0 | 0 | 0 | -2.7681 | 52.5 | 64.0553 | 3000 | 0 | 3000 | 2740.4436 | 0 | 175.635
0 | 101.5939 | 0 | 0 | 0 | 0 | -49.0939 | 52.5 | 14.9615 | 3000 | 0 | 3000 | 2464.6649 | 0 | 157.5414
0 | 67.4615 | 0 | 0 | 0 | 0 | -14.9615 | 52.5 | 0 | 3000 | 0 | 3000 | 2226.7382 | 0 | 136.2764
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1994.2189 | 0 | 118.9751
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2232.1456 | 0 | 130.5805
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2313.257 | 0 | 133.8682
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2616.0728 | 0 | 139.1489
0 | 45.4511 | 0 | 0 | 0 | 0 | 7.0489 | 52.5 | 7.0489 | 3000 | 12.5954 | 3012.5954 | 2623.2608 | 0 | 133.2092
0 | 47.8587 | 0 | 0 | 0 | 0 | 4.6413 | 52.5 | 11.6902 | 3000 | 8.2935 | 3008.2935 | 2878.5153 | 0 | 143.6379
0 | 46.1266 | 0 | 0 | 0 | 0 | 6.3734 | 52.5 | 18.0636 | 3000 | 11.3885 | 3011.3885 | 2914.0548 | 0 | 143.896
0 | 44.3667 | 0 | 0 | 0 | 0 | 8.1333 | 52.5 | 26.1969 | 3000 | 14.5331 | 3014.5331 | 2857.7178 | 0 | 144.1719
0 | 42.1928 | 0 | 0 | 0 | 0 | 10.3072 | 52.5 | 36.5041 | 3000 | 18.4175 | 3018.4175 | 2931.8987 | 0 | 153.4849
0 | 56.5058 | 0 | 0 | 0 | 0 | -4.0058 | 52.5 | 32.4983 | 3000 | 0 | 3000 | 2940.5183 | 0 | 159.3467
0 | 31.1073 | 0 | 0 | 0 | 0 | 21.3927 | 52.5 | 53.8911 | 3000 | 38.226 | 3038.226 | 3032.8186 | 0 | 165.6222
0 | 38.5394 | 0 | 0 | 0 | 0 | 13.9606 | 52.5 | 67.8516 | 3000 | 24.9457 | 3024.9457 | 3024.9457 | 0 | 160.3524
0 | 23.0926 | 0 | 0 | 0 | 0 | 29.4074 | 52.5 | 97.2591 | 3000 | 52.5472 | 3052.5472 | 3052.5472 | 0 | 183.1528
0 | 27.8588 | 0 | 0 | 0 | 0 | 24.6412 | 52.5 | 121.9003 | 3000 | 44.0305 | 3044.0305 | 3044.0305 | 0 | 168
0 | 27.4101 | 0 | 0 | 0 | 0 | 25.0899 | 52.5 | 146.9901 | 3000 | 44.8322 | 3044.8322 | 3044.8322 | 0 | 148.9532
0 | 34.387 | 0 | 0 | 0 | 0 | 18.113 | 52.5 | 165.1031 | 3000 | 32.3655 | 3032.3655 | 3032.3655 | 0 | 142.5515
0 | 35.4315 | 0 | 0 | 0 | 0 | 17.0685 | 52.5 | 182.1716 | 3000 | 30.4991 | 3030.4991 | 3030.4991 | 0 | 137.1604
0 | 29.9941 | 0 | 0 | 0 | 0 | 22.5059 | 52.5 | 204.6775 | 3000 | 40.2151 | 3040.2151 | 3040.2151 | 0 | 138.9074
0 | 37.8367 | 0 | 0 | 0 | 0 | 14.6633 | 52.5 | 219.3408 | 3000 | 26.2014 | 3026.2014 | 3026.2014 | 0 | 145.5603
0 | 41.951 | 0 | 0 | 0 | 0 | 10.549 | 52.5 | 229.8899 | 3000 | 18.8497 | 3018.8497 | 2970.1829 | 0 | 154.6574
0 | 64.0388 | 0 | 0 | 0 | 0 | -11.5388 | 52.5 | 218.351 | 3000 | 0 | 3000 | 2707.999 | 0 | 165.1609
0 | 28.7638 | 0 | 0 | 0 | 0 | 23.7362 | 52.5 | 242.0873 | 3000 | 42.4135 | 3042.4135 | 2436.7818 | 0 | 158.1959
0 | 54.4324 | 0 | 0 | 0 | 0 | -1.9324 | 52.5 | 240.1548 | 3000 | 0 | 3000 | 2053.7006 | 0 | 143.0608
0 | 47.4684 | 0 | 0 | 0 | 0 | 5.0316 | 52.5 | 245.1864 | 3000 | 8.9908 | 3008.9908 | 1970.7652 | 0 | 132.4157
0 | 41.7464 | 0 | 0 | 0 | 0 | 10.7536 | 52.5 | 255.94 | 3000 | 19.2152 | 3019.2152 | 1975.5821 | 0 | 128.3141
0 | 57.2135 | 0 | 0 | 0 | 0 | -4.7135 | 52.5 | 251.2265 | 3000 | 0 | 3000 | 1583.2546 | 0 | 102.8007
0 | 51.9434 | 0 | 0 | 0 | 0 | 0.55665 | 52.5 | 251.7832 | 3000 | 0.99465 | 3000.9947 | 2092.5472 | 0 | 134.0276
0 | 48.8094 | 0 | 0 | 0 | 0 | 3.6906 | 52.5 | 255.4738 | 3000 | 6.5946 | 3006.5946 | 2071.1101 | 0 | 129.9829
0 | 50.4418 | 0 | 0 | 0 | 0 | 2.0582 | 52.5 | 257.532 | 3000 | 3.6777 | 3003.6777 | 2051.9709 | 0 | 124.6777
0 | 29.1015 | 0 | 0 | 0 | 0 | 23.3985 | 52.5 | 280.9305 | 3000 | 41.8101 | 3041.8101 | 2490.2527 | 0 | 150.2369
0 | 42.334 | 0 | 0 | 0 | 0 | 10.166 | 52.5 | 291.0965 | 3000 | 18.1653 | 3018.1653 | 2709.942 | 0 | 164.0599
0 | 40.5246 | 0 | 0 | 0 | 0 | 11.9754 | 52.5 | 303.0719 | 3000 | 21.3984 | 3021.3984 | 2869.9905 | 0 | 190.5961
0 | 36.3756 | 0 | 0 | 0 | 0 | 16.1244 | 52.5 | 319.1963 | 3000 | 28.8122 | 3028.8122 | 2823.33 | 0 | 186.4809
0 | 46.2132 | 0 | 0 | 0 | 0 | -46.2132 | 0 | 272.9831 | 0 | 0 | 0 | 0 | 48.6668 | 0
0 | 23.6266 | 0 | 0 | 0 | 0 | -23.6266 | 0 | 249.3565 | 0 | 0 | 0 | 0 | 0 | 0
0 | 26.3198 | 0 | 0 | 0 | 0 | 26.1802 | 52.5 | 275.5367 | 3000 | 46.7805 | 3046.7805 | 3046.7805 | 0 | 197.7361
0 | 34.5423 | 0 | 0 | 0 | 0 | 17.9577 | 52.5 | 293.4944 | 3000 | 32.088 | 3032.088 | 3032.088 | 0 | 194.2659
0 | 35.2714 | 0 | 0 | 0 | 0 | 17.2286 | 52.5 | 310.723 | 3000 | 30.7853 | 3030.7853 | 3030.7853 | 0 | 178.8163
0 | 30.3634 | 0 | 0 | 0 | 0 | 22.1366 | 52.5 | 332.8596 | 3000 | 39.5552 | 3039.5552 | 3039.5552 | 0 | 167.4795
0 | 31.254 | 0 | 0 | 0 | 0 | 21.246 | 52.5 | 354.1056 | 3000 | 37.9638 | 3037.9638 | 3037.9638 | 0 | 163.5336
0 | 22.678 | 0 | 0 | 0 | 0 | 29.822 | 52.5 | 383.9276 | 3000 | 53.2879 | 3053.2879 | 3053.2879 | 0 | 160.4197
0 | 29.542 | 0 | 0 | 0 | 0 | 22.958 | 52.5 | 406.8856 | 3000 | 41.023 | 3041.023 | 3041.023 | 0 | 158.8934
0 | 25.5182 | 0 | 0 | 0 | 0 | 26.9818 | 52.5 | 433.8674 | 3000 | 48.2129 | 3048.2129 | 3042.8055 | 0 | 158.7432
0 | 32.19 | 0 | 0 | 0 | 0 | 20.31 | 52.5 | 454.1774 | 3000 | 36.2912 | 3036.2912 | 3014.6615 | 0 | 162.852
0 | 28.6023 | 0 | 0 | 0 | 0 | 23.8977 | 52.5 | 478.0751 | 3000 | 42.7021 | 3042.7021 | 2999.4427 | 0 | 187.8551
0 | 35.8033 | 0 | 0 | 0 | 0 | 16.6967 | 52.5 | 494.7718 | 3000 | 29.8347 | 3029.8347 | 2916.2788 | 0 | 202.9147
0 | 37.8764 | 0 | 0 | 0 | 0 | -37.8764 | 0 | 456.8954 | 0 | 0 | 0 | 0 | 108.1485 | 0
0 | 45.0943 | 0 | 0 | 0 | 0 | 7.4057 | 52.5 | 464.3012 | 3000 | 13.2331 | 3013.2331 | 2645.5281 | 0 | 180.0811
0 | 45.3448 | 0 | 0 | 0 | 0 | 7.1552 | 52.5 | 471.4564 | 3000 | 12.7854 | 3012.7854 | 2358.487 | 0 | 154.2686
0 | 59.5533 | 0 | 0 | 0 | 0 | -7.0533 | 52.5 | 464.4031 | 3000 | 0 | 3000 | 2410.5907 | 0 | 149.2879
0 | 48.3723 | 0 | 0 | 0 | 0 | 4.1277 | 52.5 | 468.5308 | 3000 | 7.3756 | 3007.3756 | 2088.1133 | 0 | 125.5165
0 | 55.8668 | 0 | 0 | 0 | 0 | -3.3668 | 52.5 | 465.1639 | 3000 | 0 | 3000 | 2551.1837 | 0 | 145.3664
0 | 37.9081 | 0 | 0 | 0 | 0 | 14.5919 | 52.5 | 479.7558 | 3000 | 26.0738 | 3026.0738 | 2598.8872 | 0 | 145.3817
0 | 48.4091 | 0 | 0 | 0 | 0 | 4.0909 | 52.5 | 483.8467 | 3000 | 7.3098 | 3007.3098 | 2331.3817 | 0 | 123.5632
0 | 46.1277 | 0 | 0 | 0 | 0 | 6.3723 | 52.5 | 490.219 | 3000 | 11.3865 | 3011.3865 | 2102.939 | 0 | 110.1519
0 | 44.38 | 0 | 0 | 0 | 0 | 8.12 | 52.5 | 498.339 | 3000 | 14.5093 | 3014.5093 | 2484.5817 | 0 | 143.3604
0 | 63.9841 | 0 | 0 | 0 | 0 | -11.4841 | 52.5 | 486.8549 | 3000 | 0 | 3000 | 2745.851 | 0 | 175.4599
0 | 49.5699 | 0 | 0 | 0 | 0 | 2.9301 | 52.5 | 489.785 | 3000 | 5.2356 | 3005.2356 | 2924.1242 | 0 | 191.4717
0 | 33.7142 | 0 | 0 | 0 | 0 | 18.7858 | 52.5 | 508.5707 | 3000 | 33.5677 | 3033.5677 | 3028.1603 | 0 | 202.3114
0 | 29.1689 | 0 | 0 | 0 | 0 | 23.3311 | 52.5 | 531.9019 | 3000 | 41.6896 | 3041.6896 | 3041.6896 | 0 | 202.1203
0 | 37.6114 | 0 | 0 | 0 | 0 | 14.8886 | 52.5 | 546.7905 | 3000 | 26.604 | 3026.604 | 3026.604 | 0 | 200.4217
0 | 22.2857 | 0 | 0 | 0 | 0 | 30.2143 | 52.5 | 577.0048 | 3000 | 53.9889 | 3053.9889 | 3053.9889 | 0 | 193.8367
0 | 30.2751 | 0 | 0 | 0 | 0 | 22.2249 | 52.5 | 599.2297 | 3000 | 39.713 | 3039.713 | 3039.713 | 0 | 179.5254
0 | 32.299 | 0 | 0 | 0 | 0 | 20.201 | 52.5 | 619.4307 | 3000 | 36.0965 | 3036.0965 | 3036.0965 | 0 | 166.9853
0 | 24.7165 | 0 | 0 | 0 | 0 | 27.7835 | 52.5 | 647.2142 | 3000 | 49.6454 | 3049.6454 | 3049.6454 | 0 | 161.4482
0 | 28.9627 | 0 | 0 | 0 | 0 | 23.5373 | 52.5 | 670.7515 | 3000 | 42.0581 | 3042.0581 | 3042.0581 | 0 | 167.5566
0 | 27.4901 | 0 | 0 | 0 | 0 | 25.0099 | 52.5 | 695.7614 | 3000 | 44.6893 | 3044.6893 | 3044.6893 | 0 | 158.2021
0 | 28.6333 | 0 | 0 | 0 | 0 | 23.8667 | 52.5 | 719.6282 | 3000 | 42.6467 | 3042.6467 | 2977.7576 | 0 | 153.7118
0 | 24.4047 | 0 | 0 | 0 | 0 | 28.0953 | 52.5 | 747.7235 | 3000 | 50.2026 | 3050.2026 | 2758.2016 | 0 | 143.8678
0 | 33.8486 | 0 | 0 | 0 | 0 | 18.6514 | 52.5 | 766.3749 | 3000 | 33.3276 | 3033.3276 | 2519.6222 | 0 | 135.1777
0 | 45.6095 | 0 | 0 | 0 | 0 | 6.8905 | 52.5 | 773.2654 | 3000 | 12.3124 | 3012.3124 | 2130.9021 | 0 | 120.5025
0 | 48.4276 | 0 | 0 | 0 | 0 | 4.0724 | 52.5 | 777.3378 | 3000 | 7.2769 | 3007.2769 | 1801.4211 | 0 | 103.4016
0 | 34.6197 | 0 | 0 | 0 | 0 | 17.8803 | 52.5 | 795.2181 | 3000 | 31.9497 | 3031.9497 | 1642.2414 | 0 | 101.1292
0 | 52.5037 | 0 | 0 | 0 | 0 | -0.0037336 | 52.5 | 795.2144 | 3000 | 0 | 3000 | 1923.9224 | 0 | 115.8778
0 | 50.4524 | 0 | 0 | 0 | 0 | 2.0476 | 52.5 | 797.262 | 3000 | 3.6588 | 3003.6588 | 1851.8772 | 0 | 101.6125
0 | 41.4997 | 0 | 0 | 0 | 0 | 11.0003 | 52.5 | 808.2623 | 3000 | 19.656 | 3019.656 | 1759.726 | 0 | 89.9044
0 | 37.5756 | 0 | 0 | 0 | 0 | 14.9244 | 52.5 | 823.1866 | 3000 | 26.6679 | 3026.6679 | 2015.4793 | 0 | 97.1259
0 | 247.1778 | 0 | 0 | 0 | 0 | -194.6778 | 52.5 | 628.5088 | 3000 | 0 | 3000 | 2032.0709 | 0 | 95.0806
0 | 45.0508 | 0 | 0 | 0 | 0 | 7.4492 | 52.5 | 635.958 | 3000 | 13.3107 | 3013.3107 | 1996.7148 | 0 | 93.2466
0 | 42.7086 | 0 | 0 | 0 | 0 | 9.7914 | 52.5 | 645.7495 | 3000 | 17.496 | 3017.496 | 2292.901 | 0 | 113.4069
0 | 41.9515 | 0 | 0 | 0 | 0 | 10.5485 | 52.5 | 656.298 | 3000 | 18.8488 | 3018.8488 | 2651.1439 | 0 | 138.8139
0 | 40.2993 | 0 | 0 | 0 | 0 | 12.2007 | 52.5 | 668.4987 | 3000 | 21.801 | 3021.801 | 2897.4302 | 0 | 159.0689
0 | 36.0371 | 0 | 0 | 0 | 0 | 16.4629 | 52.5 | 684.9615 | 3000 | 29.417 | 3029.417 | 3024.0096 | 0 | 159.9096
0 | 28.4702 | 0 | 0 | 0 | 0 | 24.0298 | 52.5 | 708.9913 | 3000 | 42.9381 | 3042.9381 | 3042.9381 | 0 | 183.5196
0 | 19.6979 | 0 | 0 | 0 | 0 | -19.6979 | 0 | 689.2934 | 0 | 0 | 0 | 0 | 0 | 0
0 | 35.1541 | 0 | 0 | 0 | 0 | 17.3459 | 52.5 | 706.6393 | 3000 | 30.9949 | 3030.9949 | 3030.9949 | 0 | 205.8349
0 | 34.0425 | 0 | 0 | 0 | 0 | 18.4575 | 52.5 | 725.0969 | 3000 | 32.9811 | 3032.9811 | 3032.9811 | 0 | 178.218
0 | 29.2721 | 0 | 0 | 0 | 0 | 23.2279 | 52.5 | 748.3248 | 3000 | 41.5052 | 3041.5052 | 3041.5052 | 0 | 169.716
0 | 236.1635 | 0 | 0 | 0 | 0 | -183.6635 | 52.5 | 564.6612 | 3000 | 0 | 3000 | 3000 | 0 | 166.5
0 | 34.8963 | 0 | 0 | 0 | 0 | 17.6037 | 52.5 | 582.2649 | 3000 | 31.4554 | 3031.4554 | 3031.4554 | 0 | 166.3663
0 | 34.6622 | 0 | 0 | 0 | 0 | 17.8378 | 52.5 | 600.1027 | 3000 | 31.8738 | 3031.8738 | 3026.4663 | 0 | 167.7873
0 | 41.4656 | 0 | 0 | 0 | 0 | 11.0344 | 52.5 | 611.1371 | 3000 | 19.717 | 3019.717 | 2906.1611 | 0 | 152.2828
0 | 31.7986 | 0 | 0 | 0 | 0 | 20.7014 | 52.5 | 631.8384 | 3000 | 36.9906 | 3036.9906 | 2642.2486 | 0 | 113.8809
0 | 26.4196 | 0 | 0 | 0 | 0 | 26.0804 | 52.5 | 657.9189 | 3000 | 46.6022 | 3046.6022 | 2327.4147 | 0 | 128.9155
0 | 49.7204 | 0 | 0 | 0 | 0 | 2.7796 | 52.5 | 660.6984 | 3000 | 4.9668 | 3004.9668 | 1939.704 | 0 | 107.77
0 | 43.6806 | 0 | 0 | 0 | 0 | 8.8194 | 52.5 | 669.5179 | 3000 | 15.7591 | 3015.7591 | 2172.2008 | 0 | 120.7744
0 | 41.8515 | 0 | 0 | 0 | 0 | 10.6485 | 52.5 | 680.1664 | 3000 | 19.0274 | 3019.0274 | 2521.5443 | 0 | 135.9112
0 | 54.0813 | 0 | 0 | 0 | 0 | -1.5813 | 52.5 | 678.585 | 3000 | 0 | 3000 | 1848.2184 | 0 | 98.3252
0 | 48.1586 | 0 | 0 | 0 | 0 | 4.3414 | 52.5 | 682.9264 | 3000 | 7.7575 | 3007.7575 | 1396.3448 | 0 | 75.4026
0 | 47.9748 | 0 | 0 | 0 | 0 | 4.5252 | 52.5 | 687.4516 | 3000 | 8.086 | 3008.086 | 1834.6747 | 0 | 96.137
0 | 28.1194 | 0 | 0 | 0 | 0 | 24.3806 | 52.5 | 711.8323 | 3000 | 43.5649 | 3043.5649 | 2048.5987 | 0 | 102.4299
0 | 42.5324 | 0 | 0 | 0 | 0 | 9.9676 | 52.5 | 721.7998 | 3000 | 17.8107 | 3017.8107 | 2120.1781 | 0 | 105.7969
0 | 66.9833 | 0 | 0 | 0 | 0 | -14.4833 | 52.5 | 707.3165 | 3000 | 0 | 3000 | 2242.9605 | 0 | 124.5516
0 | 39.6152 | 0 | 0 | 0 | 0 | 12.8848 | 52.5 | 720.2013 | 3000 | 23.0234 | 3023.0234 | 2352.5027 | 0 | 113.3906
0 | 33.444 | 0 | 0 | 0 | 0 | 19.056 | 52.5 | 739.2573 | 3000 | 34.0506 | 3034.0506 | 2633.9011 | 0 | 147.1824
0 | 45.6159 | 0 | 0 | 0 | 0 | 6.8841 | 52.5 | 746.1414 | 3000 | 12.301 | 3012.301 | 2877.1154 | 0 | 152.4296
0 | 18.8309 | 0 | 0 | 0 | 0 | 33.6691 | 52.5 | 779.8106 | 3000 | 60.1622 | 3060.1622 | 3054.7548 | 0 | 168.0115
0 | 31.8212 | 0 | 0 | 0 | 0 | 20.6788 | 52.5 | 800.4893 | 3000 | 36.9502 | 3036.9502 | 3036.9502 | 0 | 169.6744
0 | 37.8884 | 0 | 0 | 0 | 0 | 14.6116 | 52.5 | 815.101 | 3000 | 26.1091 | 3026.1091 | 3026.1091 | 0 | 178.843
0 | 26.9283 | 0 | 0 | 0 | 0 | 25.5717 | 52.5 | 840.6726 | 3000 | 45.6932 | 3045.6932 | 3045.6932 | 0 | 179.97
0 | 31.9539 | 0 | 0 | 0 | 0 | 20.5461 | 52.5 | 861.2187 | 3000 | 36.7131 | 3036.7131 | 3036.7131 | 0 | 182.0206
0 | 26.09 | 0 | 0 | 0 | 0 | 26.41 | 52.5 | 887.6287 | 3000 | 47.1912 | 3047.1912 | 3047.1912 | 0 | 175.4877
0 | 33.0964 | 0 | 0 | 0 | 0 | 19.4036 | 52.5 | 907.0323 | 3000 | 34.6716 | 3034.6716 | 3034.6716 | 0 | 166.6035
0 | 32.3257 | 0 | 0 | 0 | 0 | 20.1743 | 52.5 | 927.2066 | 3000 | 36.0489 | 3036.0489 | 3036.0489 | 0 | 157.2673
0 | 26.3403 | 0 | 0 | 0 | 0 | 26.1597 | 52.5 | 953.3663 | 3000 | 46.7439 | 3046.7439 | 3041.3364 | 0 | 139.9015
0 | 23.4858 | 0 | 0 | 0 | 0 | 29.0142 | 52.5 | 982.3805 | 3000 | 51.8445 | 3051.8445 | 2938.2886 | 0 | 149.0594
0 | 26.3001 | 0 | 0 | 0 | 0 | 26.1999 | 52.5 | 1008.5804 | 3000 | 46.8158 | 3046.8158 | 2733.1851 | 0 | 167.1616
0 | 19.1906 | 0 | 0 | 0 | 0 | 33.3094 | 52.5 | 1041.8898 | 3000 | 59.5195 | 3059.5195 | 2443.073 | 0 | 166.1534
0 | 49.1833 | 0 | 0 | 0 | 0 | 3.3167 | 52.5 | 1045.2065 | 3000 | 5.9264 | 3005.9264 | 1978.5156 | 0 | 134.5588
0 | 52.3162 | 0 | 0 | 0 | 0 | 0.18379 | 52.5 | 1045.3903 | 3000 | 0.32841 | 3000.3284 | 1675.5092 | 0 | 104.3172
0 | 44.7166 | 0 | 0 | 0 | 0 | 7.7834 | 52.5 | 1053.1737 | 3000 | 13.9079 | 3013.9079 | 1499.8289 | 0 | 82.4906
0 | 44.9177 | 0 | 0 | 0 | 0 | 7.5823 | 52.5 | 1060.7561 | 3000 | 13.5486 | 3013.5486 | 1402.1359 | 0 | 72.4904
0 | 44.961 | 0 | 0 | 0 | 0 | 7.539 | 52.5 | 1068.2951 | 3000 | 13.4713 | 3013.4713 | 1353.3917 | 0 | 67.2636
0 | 36.818 | 0 | 0 | 0 | 0 | 15.682 | 52.5 | 1083.9771 | 3000 | 28.0216 | 3028.0216 | 1622.0911 | 0 | 77.4386
0 | 47.0736 | 0 | 0 | 0 | 0 | 5.4264 | 52.5 | 1089.4035 | 3000 | 9.6962 | 3009.6962 | 1868.7295 | 0 | 86.5782
0 | 37.4478 | 0 | 0 | 0 | 0 | 15.0522 | 52.5 | 1104.4557 | 3000 | 26.8962 | 3026.8962 | 1880.5221 | 0 | 86.4664
0 | 34.2474 | 0 | 0 | 0 | 0 | 18.2526 | 52.5 | 1122.7082 | 3000 | 32.615 | 3032.615 | 2005.2042 | 0 | 94.3649
0 | 45.5989 | 0 | 0 | 0 | 0 | 6.9011 | 52.5 | 1129.6093 | 3000 | 12.3313 | 3012.3313 | 2298.5512 | 0 | 123.9839
0 | 40.4498 | 0 | 0 | 0 | 0 | 12.0502 | 52.5 | 1141.6595 | 3000 | 21.5321 | 3021.5321 | 2643.0123 | 0 | 154.8805
0 | 41.0042 | 0 | 0 | 0 | 0 | 11.4958 | 52.5 | 1153.1553 | 3000 | 20.5415 | 3020.5415 | 2896.1707 | 0 | 185.2101
0 | 37.5856 | 0 | 0 | 0 | 0 | 14.9144 | 52.5 | 1168.0697 | 3000 | 26.65 | 3026.65 | 3021.2425 | 0 | 200.0365
0 | 29.9874 | 0 | 0 | 0 | 0 | 22.5126 | 52.5 | 1190.5823 | 3000 | 40.227 | 3040.227 | 3040.227 | 0 | 190.3486
0 | 39.0391 | 0 | 0 | 0 | 0 | 13.4609 | 52.5 | 1204.0431 | 3000 | 24.0528 | 3024.0528 | 3024.0528 | 0 | 187.1284
0 | 29.3784 | 0 | 0 | 0 | 0 | 23.1216 | 52.5 | 1227.1648 | 3000 | 41.3153 | 3041.3153 | 3041.3153 | 0 | 171.1044
0 | 28.5255 | 0 | 0 | 0 | 0 | 23.9745 | 52.5 | 1251.1393 | 3000 | 42.8393 | 3042.8393 | 3042.8393 | 0 | 162.305
0 | 28.1665 | 0 | 0 | 0 | 0 | 24.3335 | 52.5 | 1275.4728 | 3000 | 43.4807 | 3043.4807 | 3043.4807 | 0 | 154.7001
0 | 36.3729 | 0 | 0 | 0 | 0 | 16.1271 | 52.5 | 1291.5999 | 3000 | 28.8169 | 3028.8169 | 3028.8169 | 0 | 152.4101
0 | 32.7378 | 0 | 0 | 0 | 0 | 19.7622 | 52.5 | 1311.3621 | 3000 | 35.3125 | 3035.3125 | 3035.3125 | 0 | 151.6442
0 | 59.9177 | 0 | 0 | 0 | 0 | -7.4177 | 52.5 | 1303.9443 | 3000 | 0 | 3000 | 2994.5926 | 0 | 151.5264
0 | 128.6758 | 0 | 0 | 0 | 0 | -76.1758 | 52.5 | 1227.7686 | 3000 | 0 | 3000 | 2881.0366 | 0 | 154.971
0 | 140.7127 | 0 | 0 | 0 | 0 | -88.2127 | 52.5 | 1139.5559 | 3000 | 0 | 3000 | 2610.6654 | 0 | 165.0463
0 | 117.5569 | 0 | 0 | 0 | 0 | -65.0569 | 52.5 | 1074.499 | 3000 | 0 | 3000 | 2329.4793 | 0 | 162.1551
0 | 146.6242 | 0 | 0 | 0 | 0 | -130.5371 | 16.0871 | 943.9619 | 919.2623 | 0 | 919.2623 | 0 | 0 | 0
0 | 150.224 | 0 | 0 | 0 | 0 | -97.724 | 52.5 | 846.238 | 3000 | 0 | 3000 | 1756.2922 | 0 | 108.855
0 | 131.974 | 0 | 0 | 0 | 0 | -79.474 | 52.5 | 766.764 | 3000 | 0 | 3000 | 1729.2551 | 0 | 96.3368
0 | 136.7568 | 0 | 0 | 0 | 0 | -84.2568 | 52.5 | 682.5072 | 3000 | 0 | 3000 | 1431.8467 | 0 | 73.4537
0 | 106.3568 | 0 | 0 | 0 | 0 | -53.8568 | 52.5 | 628.6504 | 3000 | 0 | 3000 | 1377.7724 | 0 | 67.8691
0 | 33.9278 | 0 | 0 | 0 | 0 | 18.5722 | 52.5 | 647.2226 | 3000 | 33.186 | 3033.186 | 1410.9585 | 0 | 69.137
0 | 46.6286 | 0 | 0 | 0 | 0 | 5.8714 | 52.5 | 653.0939 | 3000 | 10.4914 | 3010.4914 | 1658.6351 | 0 | 81.0077
0 | 44.7529 | 0 | 0 | 0 | 0 | 7.7471 | 52.5 | 660.8411 | 3000 | 13.8431 | 3013.8431 | 1824.2095 | 0 | 89.4592
0 | 53.5317 | 0 | 0 | 0 | 0 | -1.0317 | 52.5 | 659.8093 | 3000 | 0 | 3000 | 2199.7011 | 0 | 109.8311
0 | 47.5055 | 0 | 0 | 0 | 0 | 4.9945 | 52.5 | 664.8039 | 3000 | 8.9246 | 3008.9246 | 2370.8484 | 0 | 123.9954
0 | 48.2181 | 0 | 0 | 0 | 0 | 4.2819 | 52.5 | 669.0858 | 3000 | 7.6512 | 3007.6512 | 2666.9834 | 0 | 157.2187
0 | 43.964 | 0 | 0 | 0 | 0 | 8.536 | 52.5 | 677.6218 | 3000 | 15.2527 | 3015.2527 | 2890.8819 | 0 | 181.8654
0 | 28.3414 | 0 | 0 | 0 | 0 | 24.1586 | 52.5 | 701.7804 | 3000 | 43.1682 | 3043.1682 | 3037.7608 | 0 | 192.2599
0 | 29.3919 | 0 | 0 | 0 | 0 | 23.1081 | 52.5 | 724.8885 | 3000 | 41.2911 | 3041.2911 | 3041.2911 | 0 | 192.2704
0 | 39.1619 | 0 | 0 | 0 | 0 | 13.3381 | 52.5 | 738.2266 | 3000 | 23.8334 | 3023.8334 | 3023.8334 | 0 | 182.0045
0 | 31.5045 | 0 | 0 | 0 | 0 | 20.9955 | 52.5 | 759.2221 | 3000 | 37.5162 | 3037.5162 | 3037.5162 | 0 | 168.1569
0 | 32.6561 | 0 | 0 | 0 | 0 | 19.8439 | 52.5 | 779.066 | 3000 | 35.4585 | 3035.4585 | 3035.4585 | 0 | 158.1474
0 | 31.8005 | 0 | 0 | 0 | 0 | 20.6995 | 52.5 | 799.7656 | 3000 | 36.9873 | 3036.9873 | 3036.9873 | 0 | 153.9145
0 | 29.3276 | 0 | 0 | 0 | 0 | 23.1724 | 52.5 | 822.9379 | 3000 | 41.406 | 3041.406 | 3041.406 | 0 | 153.8039
0 | 36.5272 | 0 | 0 | 0 | 0 | 15.9728 | 52.5 | 838.9108 | 3000 | 28.5413 | 3028.5413 | 3028.5413 | 0 | 152.7596
0 | 45.4041 | 0 | 0 | 0 | 0 | 7.0959 | 52.5 | 846.0067 | 3000 | 12.6794 | 3012.6794 | 3007.272 | 0 | 148.4991
0 | 62.6768 | 0 | 0 | 0 | 0 | -10.1768 | 52.5 | 835.8299 | 3000 | 0 | 3000 | 2881.0366 | 0 | 147.5379
0 | 57.4704 | 0 | 0 | 0 | 0 | -4.9704 | 52.5 | 830.8595 | 3000 | 0 | 3000 | 2599.8505 | 0 | 153.6512
0 | 29.6982 | 0 | 0 | 0 | 0 | 22.8018 | 52.5 | 853.6612 | 3000 | 40.7437 | 3040.7437 | 2289.1116 | 0 | 151.0585
0 | 46.9642 | 0 | 0 | 0 | 0 | -30.4986 | 16.4656 | 823.1626 | 940.892 | 0 | 940.892 | 0 | 0 | 0
0 | 55.0486 | 0 | 0 | 0 | 0 | -2.5486 | 52.5 | 820.614 | 3000 | 0 | 3000 | 1675.1808 | 0 | 105.2349
0 | 37.2176 | 0 | 0 | 0 | 0 | 15.2824 | 52.5 | 835.8964 | 3000 | 27.3076 | 3027.3076 | 1513.2285 | 0 | 90.5516
0 | 41.7937 | 0 | 0 | 0 | 0 | 10.7063 | 52.5 | 846.6026 | 3000 | 19.1307 | 3019.1307 | 1386.0883 | 0 | 77.5378
0 | 31.8298 | 0 | 0 | 0 | 0 | 20.6702 | 52.5 | 867.2728 | 3000 | 36.9348 | 3036.9348 | 1360.633 | 0 | 73.1612
0 | 34.5191 | 0 | 0 | 0 | 0 | 17.9809 | 52.5 | 885.2537 | 3000 | 32.1295 | 3032.1295 | 1566.7173 | 0 | 79.3856
0 | 45.2469 | 0 | 0 | 0 | 0 | 7.2531 | 52.5 | 892.5068 | 3000 | 12.9603 | 3012.9603 | 1774.6599 | 0 | 89.7446
0 | 52.0297 | 0 | 0 | 0 | 0 | 0.47034 | 52.5 | 892.9771 | 3000 | 0.84043 | 3000.8404 | 1973.4296 | 0 | 97.2506
0 | 40.8392 | 0 | 0 | 0 | 0 | 11.6608 | 52.5 | 904.638 | 3000 | 20.8363 | 3020.8363 | 2166.4632 | 0 | 109.4497
0 | 49.3277 | 0 | 0 | 0 | 0 | 3.1723 | 52.5 | 907.8103 | 3000 | 5.6686 | 3005.6686 | 2421.6666 | 0 | 133.1917
0 | 44.3988 | 0 | 0 | 0 | 0 | 8.1012 | 52.5 | 915.9115 | 3000 | 14.4758 | 3014.4758 | 2668.4005 | 0 | 157.7292
0 | 43.3462 | 0 | 0 | 0 | 0 | 9.1538 | 52.5 | 925.0653 | 3000 | 16.3566 | 3016.3566 | 2864.9487 | 0 | 174.1889
0 | 33.8248 | 0 | 0 | 0 | 0 | 18.6752 | 52.5 | 943.7405 | 3000 | 33.3701 | 3033.3701 | 3027.9627 | 0 | 179.7701
0 | 23.1677 | 0 | 0 | 0 | 0 | 29.3323 | 52.5 | 973.0728 | 3000 | 52.413 | 3052.413 | 3052.413 | 0 | 177.742
0 | 29.8839 | 0 | 0 | 0 | 0 | 22.6161 | 52.5 | 995.689 | 3000 | 40.412 | 3040.412 | 3040.412 | 0 | 177.8641
0 | 230.6124 | 0 | 0 | 0 | 0 | -178.1124 | 52.5 | 817.5765 | 3000 | 0 | 3000 | 3000 | 0 | 161.73
0 | 37.8818 | 0 | 0 | 0 | 0 | 14.6182 | 52.5 | 832.1947 | 3000 | 26.1207 | 3026.1207 | 3026.1207 | 0 | 149.793
0 | 32.8581 | 0 | 0 | 0 | 0 | 19.6419 | 52.5 | 851.8366 | 3000 | 35.0974 | 3035.0974 | 3035.0974 | 0 | 150.2373
0 | 26.7949 | 0 | 0 | 0 | 0 | 25.7051 | 52.5 | 877.5417 | 3000 | 45.9316 | 3045.9316 | 3045.9316 | 0 | 149.2811
0 | 30.9979 | 0 | 0 | 0 | 0 | 21.5021 | 52.5 | 899.0437 | 3000 | 38.4213 | 3038.4213 | 3038.4213 | 0 | 143.0185
0 | 28.6788 | 0 | 0 | 0 | 0 | 23.8212 | 52.5 | 922.865 | 3000 | 42.5654 | 3042.5654 | 3037.158 | 0 | 146.0569
0 | 31.281 | 0 | 0 | 0 | 0 | 21.219 | 52.5 | 944.084 | 3000 | 37.9155 | 3037.9155 | 2994.6561 | 0 | 149.8825
0 | 42.6652 | 0 | 0 | 0 | 0 | 9.8348 | 52.5 | 953.9187 | 3000 | 17.5734 | 3017.5734 | 2920.2398 | 0 | 168.4978
0 | 61.8929 | 0 | 0 | 0 | 0 | -9.3929 | 52.5 | 944.5259 | 3000 | 0 | 3000 | 2789.1104 | 0 | 173.5106
0 | 63.0743 | 0 | 0 | 0 | 0 | -10.5743 | 52.5 | 933.9515 | 3000 | 0 | 3000 | 2675.5545 | 0 | 172.0382
0 | 60.7076 | 0 | 0 | 0 | 0 | -8.2076 | 52.5 | 925.7439 | 3000 | 0 | 3000 | 2237.553 | 0 | 134.3874
0 | 135.3766 | 0 | 0 | 0 | 0 | -82.8766 | 52.5 | 842.8673 | 3000 | 0 | 3000 | 1918.515 | 0 | 113.6336
0 | 101.2465 | 0 | 0 | 0 | 0 | -48.7465 | 52.5 | 794.1208 | 3000 | 0 | 3000 | 1518.3655 | 0 | 89.4773
0 | 66.6185 | 0 | 0 | 0 | 0 | -14.1185 | 52.5 | 780.0023 | 3000 | 0 | 3000 | 1642.7363 | 0 | 93.1431
0 | 44.3954 | 0 | 0 | 0 | 0 | 8.1046 | 52.5 | 788.1069 | 3000 | 14.4819 | 3014.4819 | 1770.7741 | 0 | 97.3395
0 | 29.4771 | 0 | 0 | 0 | 0 | 23.0229 | 52.5 | 811.1298 | 3000 | 41.1389 | 3041.1389 | 2040.7652 | 0 | 109.936
0 | 52.1493 | 0 | 0 | 0 | 0 | 0.35074 | 52.5 | 811.4805 | 3000 | 0.62672 | 3000.6267 | 2535.5882 | 0 | 134.3101
0 | 31.7932 | 0 | 0 | 0 | 0 | 20.7068 | 52.5 | 832.1873 | 3000 | 37.0003 | 3037.0003 | 2577.3691 | 0 | 131.1881
0 | 37.5659 | 0 | 0 | 0 | 0 | 14.9341 | 52.5 | 847.1214 | 3000 | 26.6853 | 3026.6853 | 2842.8328 | 0 | 153.6551
0 | 45.0684 | 0 | 0 | 0 | 0 | 7.4316 | 52.5 | 854.553 | 3000 | 13.2792 | 3013.2792 | 2915.9455 | 0 | 163.2055
0 | 47.0179 | 0 | 0 | 0 | 0 | 5.4821 | 52.5 | 860.0351 | 3000 | 9.7957 | 3009.7957 | 2950.314 | 0 | 170.5282
0 | 40.1616 | 0 | 0 | 0 | 0 | 12.3384 | 52.5 | 872.3735 | 3000 | 22.0472 | 3022.0472 | 3022.0472 | 0 | 170.9874
0 | 229.0694 | 0 | 0 | 0 | 0 | -176.5694 | 52.5 | 695.8041 | 3000 | 0 | 3000 | 3000 | 0 | 169.14
0 | 31.2023 | 0 | 0 | 0 | 0 | 21.2977 | 52.5 | 717.1018 | 3000 | 38.0562 | 3038.0562 | 3038.0562 | 0 | 169.6147
0 | 28.3914 | 0 | 0 | 0 | 0 | 24.1086 | 52.5 | 741.2104 | 3000 | 43.0788 | 3043.0788 | 3043.0788 | 0 | 157.6011
0 | 58.7772 | 0 | 0 | 0 | 0 | -6.2772 | 52.5 | 734.9333 | 3000 | 0 | 3000 | 3000 | 0 | 152.1
0 | 118.9531 | 0 | 0 | 0 | 0 | -66.4531 | 52.5 | 668.4801 | 3000 | 0 | 3000 | 3000 | 0 | 150.54
0 | 87.1981 | 0 | 0 | 0 | 0 | -34.6981 | 52.5 | 633.782 | 3000 | 0 | 3000 | 3000 | 0 | 147.75
0 | 29.003 | 0 | 0 | 0 | 0 | 23.497 | 52.5 | 657.279 | 3000 | 41.986 | 3041.986 | 3041.986 | 0 | 148.4185
0 | 36.5343 | 0 | 0 | 0 | 0 | 15.9657 | 52.5 | 673.2447 | 3000 | 28.5286 | 3028.5286 | 3028.5286 | 0 | 148.3979
0 | 42.9382 | 0 | 0 | 0 | 0 | 9.5618 | 52.5 | 682.8065 | 3000 | 17.0856 | 3017.0856 | 2968.4188 | 0 | 151.6565
0 | 80.6629 | 0 | 0 | 0 | 0 | -28.1629 | 52.5 | 654.6436 | 3000 | 0 | 3000 | 2848.5921 | 0 | 159.8915
0 | 84.8779 | 0 | 0 | 0 | 0 | -32.3779 | 52.5 | 622.2657 | 3000 | 0 | 3000 | 2772.8881 | 0 | 171.1149
0 | 87.0637 | 0 | 0 | 0 | 0 | -34.5637 | 52.5 | 587.702 | 3000 | 0 | 3000 | 2605.258 | 0 | 171.6604
0 | 97.4079 | 0 | 0 | 0 | 0 | -44.9079 | 52.5 | 542.7941 | 3000 | 0 | 3000 | 2313.257 | 0 | 148.4417
0 | 42.8937 | 0 | 0 | 0 | 0 | 9.6063 | 52.5 | 552.4004 | 3000 | 17.1652 | 3017.1652 | 2422.3484 | 0 | 148.4173
0 | 40.2407 | 0 | 0 | 0 | 0 | 12.2593 | 52.5 | 564.6597 | 3000 | 21.9057 | 3021.9057 | 2529.83 | 0 | 154.3955
0 | 46.6707 | 0 | 0 | 0 | 0 | 5.8293 | 52.5 | 570.489 | 3000 | 10.4162 | 3010.4162 | 2431.8217 | 0 | 145.5688
0 | 45.5196 | 0 | 0 | 0 | 0 | 6.9804 | 52.5 | 577.4694 | 3000 | 12.4731 | 3012.4731 | 2412.2489 | 0 | 136.5333
0 | 39.8653 | 0 | 0 | 0 | 0 | 12.6347 | 52.5 | 590.1041 | 3000 | 22.5766 | 3022.5766 | 2671.094 | 0 | 144.6397
0 | 48.4605 | 0 | 0 | 0 | 0 | 4.0395 | 52.5 | 594.1436 | 3000 | 7.218 | 3007.218 | 2780.1062 | 0 | 148.7079
0 | 49.2971 | 0 | 0 | 0 | 0 | 3.2029 | 52.5 | 597.3465 | 3000 | 5.7231 | 3005.7231 | 2708.3147 | 0 | 146.3573
0 | 43.3388 | 0 | 0 | 0 | 0 | 9.1612 | 52.5 | 606.5077 | 3000 | 16.3699 | 3016.3699 | 2859.5546 | 0 | 164.5102
0 | 30.9929 | 0 | 0 | 0 | 0 | 21.5071 | 52.5 | 628.0148 | 3000 | 38.4304 | 3038.4304 | 2968.1339 | 0 | 188.061
0 | 48.9254 | 0 | 0 | 0 | 0 | 3.5746 | 52.5 | 631.5895 | 3000 | 6.3874 | 3006.3874 | 2979.3503 | 0 | 201.4339
0 | 32.7926 | 0 | 0 | 0 | 0 | 19.7074 | 52.5 | 651.2969 | 3000 | 35.2145 | 3035.2145 | 3029.8071 | 0 | 204.6635
0 | 53.2163 | 0 | 0 | 0 | 0 | -0.7163 | 52.5 | 650.5806 | 3000 | 0 | 3000 | 3000 | 0 | 191.49
0 | 99.1263 | 0 | 0 | 0 | 0 | -46.6263 | 52.5 | 603.9543 | 3000 | 0 | 3000 | 3000 | 0 | 189.96
0 | 110.3036 | 0 | 0 | 0 | 0 | -57.8036 | 52.5 | 546.1507 | 3000 | 0 | 3000 | 3000 | 0 | 175.41
0 | 101.9978 | 0 | 0 | 0 | 0 | -49.4978 | 52.5 | 496.6529 | 3000 | 0 | 3000 | 3000 | 0 | 157.11
0 | 59.4274 | 0 | 0 | 0 | 0 | -6.9274 | 52.5 | 489.7255 | 3000 | 0 | 3000 | 3000 | 0 | 148.17
0 | 34.9719 | 0 | 0 | 0 | 0 | 17.5281 | 52.5 | 507.2536 | 3000 | 31.3203 | 3031.3203 | 3031.3203 | 0 | 151.1113
0 | 27.702 | 0 | 0 | 0 | 0 | 24.798 | 52.5 | 532.0516 | 3000 | 44.3108 | 3044.3108 | 3044.3108 | 0 | 149.5061
0 | 28.499 | 0 | 0 | 0 | 0 | 24.001 | 52.5 | 556.0526 | 3000 | 42.8867 | 3042.8867 | 3037.4792 | 0 | 151.145
0 | 41.6417 | 0 | 0 | 0 | 0 | 10.8583 | 52.5 | 566.9109 | 3000 | 19.4024 | 3019.4024 | 2905.8465 | 0 | 140.7011
0 | 108.2222 | 0 | 0 | 0 | 0 | -55.7222 | 52.5 | 511.1887 | 3000 | 0 | 3000 | 2626.8877 | 0 | 128.5073
0 | 95.2996 | 0 | 0 | 0 | 0 | -42.7996 | 52.5 | 468.3891 | 3000 | 0 | 3000 | 2318.6644 | 0 | 118.8084
0 | 83.8941 | 0 | 0 | 0 | 0 | -31.3941 | 52.5 | 436.9951 | 3000 | 0 | 3000 | 2107.7748 | 0 | 113.7988
0 | 94.2167 | 0 | 0 | 0 | 0 | -41.7167 | 52.5 | 395.2784 | 3000 | 0 | 3000 | 1994.2189 | 0 | 104.7364
0 | 92.5897 | 0 | 0 | 0 | 0 | -40.0897 | 52.5 | 355.1887 | 3000 | 0 | 3000 | 1723.8476 | 0 | 86.3992
0 | 52.6935 | 0 | 0 | 0 | 0 | -0.19352 | 52.5 | 354.9951 | 3000 | 0 | 3000 | 1880.663 | 0 | 93.6382
0 | 47.7061 | 0 | 0 | 0 | 0 | 4.7939 | 52.5 | 359.789 | 3000 | 8.566 | 3008.566 | 1483.6721 | 0 | 72.5516
0 | 47.4102 | 0 | 0 | 0 | 0 | 5.0898 | 52.5 | 364.8788 | 3000 | 9.0948 | 3009.0948 | 1835.6835 | 0 | 88.2046
0 | 45.2859 | 0 | 0 | 0 | 0 | 7.2141 | 52.5 | 372.0929 | 3000 | 12.8907 | 3012.8907 | 1709.7012 | 0 | 80.9714
0 | 29.3491 | 0 | 0 | 0 | 0 | 23.1509 | 52.5 | 395.2438 | 3000 | 41.3675 | 3041.3675 | 1857.1414 | 0 | 89.6071
0 | 41.282 | 0 | 0 | 0 | 0 | 11.218 | 52.5 | 406.4617 | 3000 | 20.045 | 3020.045 | 2219.7461 | 0 | 108.9895
0 | 41.4267 | 0 | 0 | 0 | 0 | 11.0733 | 52.5 | 417.5351 | 3000 | 19.7866 | 3019.7866 | 2619.6371 | 0 | 131.9249
0 | 41.2549 | 0 | 0 | 0 | 0 | 11.2451 | 52.5 | 428.7802 | 3000 | 20.0935 | 3020.0935 | 2619.944 | 0 | 151.6948
0 | 51.5355 | 0 | 0 | 0 | 0 | 0.96445 | 52.5 | 429.7446 | 3000 | 1.7234 | 3001.7234 | 2877.3526 | 0 | 172.4397
0 | 36.409 | 0 | 0 | 0 | 0 | 16.091 | 52.5 | 445.8356 | 3000 | 28.7525 | 3028.7525 | 3017.9377 | 0 | 181.5893
0 | 31.4456 | 0 | 0 | 0 | 0 | 21.0544 | 52.5 | 466.8901 | 3000 | 37.6215 | 3037.6215 | 3037.6215 | 0 | 181.4979
0 | 29.7903 | 0 | 0 | 0 | 0 | 22.7097 | 52.5 | 489.5998 | 3000 | 40.5792 | 3040.5792 | 3040.5792 | 0 | 182.3131
0 | 25.2184 | 0 | 0 | 0 | 0 | 27.2816 | 52.5 | 516.8814 | 3000 | 48.7487 | 3048.7487 | 3048.7487 | 0 | 173.7787
0 | 29.6094 | 0 | 0 | 0 | 0 | 22.8906 | 52.5 | 539.7721 | 3000 | 40.9025 | 3040.9025 | 3040.9025 | 0 | 166.2157
0 | 26.4012 | 0 | 0 | 0 | 0 | 26.0988 | 52.5 | 565.8709 | 3000 | 46.6351 | 3046.6351 | 3046.6351 | 0 | 155.4393
0 | 28.4328 | 0 | 0 | 0 | 0 | 24.0672 | 52.5 | 589.9381 | 3000 | 43.0049 | 3043.0049 | 3043.0049 | 0 | 152.1502
0 | 29.4942 | 0 | 0 | 0 | 0 | 23.0058 | 52.5 | 612.9439 | 3000 | 41.1083 | 3041.1083 | 3041.1083 | 0 | 149.1055
0 | 33.0559 | 0 | 0 | 0 | 0 | 19.4441 | 52.5 | 632.388 | 3000 | 34.7441 | 3034.7441 | 3023.9292 | 0 | 148.7168
0 | 37.4552 | 0 | 0 | 0 | 0 | 15.0448 | 52.5 | 647.4328 | 3000 | 26.883 | 3026.883 | 2929.5493 | 0 | 143.2843
0 | 236.0842 | 0 | 0 | 0 | 0 | -183.5842 | 52.5 | 463.8486 | 3000 | 0 | 3000 | 2724.2213 | 0 | 131.7706
0 | 31.5798 | 0 | 0 | 0 | 0 | 20.9202 | 52.5 | 484.7688 | 3000 | 37.3816 | 3037.3816 | 2550.7133 | 0 | 125.087
0 | 32.0556 | 0 | 0 | 0 | 0 | 20.4444 | 52.5 | 505.2132 | 3000 | 36.5314 | 3036.5314 | 2209.1953 | 0 | 110.6144
0 | 38.4168 | 0 | 0 | 0 | 0 | 14.0832 | 52.5 | 519.2964 | 3000 | 25.1649 | 3025.1649 | 1916.6427 | 0 | 95.8705
0 | 32.7043 | 0 | 0 | 0 | 0 | 19.7957 | 52.5 | 539.0921 | 3000 | 35.3723 | 3035.3723 | 1840.3314 | 0 | 90.3235
0 | 42.3379 | 0 | 0 | 0 | 0 | 10.1621 | 52.5 | 549.2543 | 3000 | 18.1583 | 3018.1583 | 1731.1911 | 0 | 85.0015
0 | 47.5299 | 0 | 0 | 0 | 0 | 4.9701 | 52.5 | 554.2243 | 3000 | 8.8809 | 3008.8809 | 1429.9127 | 0 | 69.7797
0 | 48.0037 | 0 | 0 | 0 | 0 | 4.4963 | 52.5 | 558.7206 | 3000 | 8.0343 | 3008.0343 | 1867.0675 | 0 | 83.3459
0 | 45.1027 | 0 | 0 | 0 | 0 | 7.3973 | 52.5 | 566.1179 | 3000 | 13.218 | 3013.218 | 1569.4355 | 0 | 66.5598
0 | 40.3975 | 0 | 0 | 0 | 0 | 12.1025 | 52.5 | 578.2204 | 3000 | 21.6256 | 3021.6256 | 1988.8073 | 0 | 84.5044
0 | 44.5115 | 0 | 0 | 0 | 0 | 7.9885 | 52.5 | 586.2089 | 3000 | 14.2743 | 3014.2743 | 2322.1239 | 0 | 105.1458
0 | 40.676 | 0 | 0 | 0 | 0 | 11.824 | 52.5 | 598.0329 | 3000 | 21.128 | 3021.128 | 2983.276 | 0 | 147.5827
0 | 55.555 | 0 | 0 | 0 | 0 | -3.055 | 52.5 | 594.9779 | 3000 | 0 | 3000 | 2983.7777 | 0 | 158.9757
0 | 33.9009 | 0 | 0 | 0 | 0 | 18.5991 | 52.5 | 613.577 | 3000 | 33.2341 | 3033.2341 | 3027.8267 | 0 | 173.4339
0 | 34.7351 | 0 | 0 | 0 | 0 | 17.7649 | 52.5 | 631.3418 | 3000 | 31.7434 | 3031.7434 | 3031.7434 | 0 | 173.8402
0 | 32.4057 | 0 | 0 | 0 | 0 | 20.0943 | 52.5 | 651.4361 | 3000 | 35.9059 | 3035.9059 | 3035.9059 | 0 | 172.1662
0 | 29.8794 | 0 | 0 | 0 | 0 | 22.6206 | 52.5 | 674.0568 | 3000 | 40.42 | 3040.42 | 3040.42 | 0 | 177.3477
0 | 34.188 | 0 | 0 | 0 | 0 | 18.312 | 52.5 | 692.3687 | 3000 | 32.7211 | 3032.7211 | 3032.7211 | 0 | 163.585
0 | 23.0481 | 0 | 0 | 0 | 0 | 29.4519 | 52.5 | 721.8206 | 3000 | 52.6266 | 3052.6266 | 3052.6266 | 0 | 159.6524
0 | 30.6216 | 0 | 0 | 0 | 0 | 21.8784 | 52.5 | 743.699 | 3000 | 39.0938 | 3039.0938 | 3039.0938 | 0 | 151.9547
0 | 32.3765 | 0 | 0 | 0 | 0 | 20.1235 | 52.5 | 763.8225 | 3000 | 35.958 | 3035.958 | 3035.958 | 0 | 150.4317
0 | 39.7977 | 0 | 0 | 0 | 0 | 12.7023 | 52.5 | 776.5248 | 3000 | 22.6973 | 3022.6973 | 3022.6973 | 0 | 150.8326
0 | 37.0851 | 0 | 0 | 0 | 0 | 15.4149 | 52.5 | 791.9397 | 3000 | 27.5444 | 3027.5444 | 3022.137 | 0 | 147.3896
0 | 29.8198 | 0 | 0 | 0 | 0 | 22.6802 | 52.5 | 814.6199 | 3000 | 40.5264 | 3040.5264 | 2964.8225 | 0 | 151.3245
0 | 35.7167 | 0 | 0 | 0 | 0 | 16.7833 | 52.5 | 831.4032 | 3000 | 29.9895 | 3029.9895 | 2883.989 | 0 | 181.1145
0 | 32.5085 | 0 | 0 | 0 | 0 | -32.5085 | 0 | 798.8947 | 0 | 0 | 0 | 0 | 259.5564 | 0
0 | 30.8435 | 0 | 0 | 0 | 0 | -24.7872 | 6.0563 | 774.1075 | 346.0752 | 0 | 346.0752 | 0 | 0 | 0
0 | 40.026 | 0 | 0 | 0 | 0 | -30.563 | 9.463 | 743.5445 | 540.7425 | 0 | 540.7425 | 0 | 0 | 0
0 | 42.6697 | 0 | 0 | 0 | 0 | -20.9994 | 21.6703 | 722.5451 | 1238.3004 | 0 | 1238.3004 | 0 | 0 | 0
0 | 56.4883 | 0 | 0 | 0 | 0 | -37.7516 | 18.7367 | 684.7935 | 1070.6702 | 0 | 1070.6702 | 0 | 0 | 0
0 | 62.8589 | 0 | 0 | 0 | 0 | -10.3589 | 52.5 | 674.4345 | 3000 | 0 | 3000 | 2021.256 | 0 | 135.4039
0 | 43.9801 | 0 | 0 | 0 | 0 | 8.5199 | 52.5 | 682.9544 | 3000 | 15.224 | 3015.224 | 1852.6276 | 0 | 120.9581
0 | 50.7985 | 0 | 0 | 0 | 0 | 1.7015 | 52.5 | 684.6559 | 3000 | 3.0403 | 3003.0403 | 2110.8151 | 0 | 132.1159
0 | 45.1892 | 0 | 0 | 0 | 0 | 7.3108 | 52.5 | 691.9668 | 3000 | 13.0635 | 3013.0635 | 2304.6908 | 0 | 139.7334
0 | 25.0289 | 0 | 0 | 0 | 0 | 27.4711 | 52.5 | 719.4379 | 3000 | 49.0872 | 3049.0872 | 2405.6036 | 0 | 142.8207
0 | 49.8665 | 0 | 0 | 0 | 0 | 2.6335 | 52.5 | 722.0713 | 3000 | 4.7056 | 3004.7056 | 2566.7042 | 0 | 156.8
0 | 48.8867 | 0 | 0 | 0 | 0 | 3.6133 | 52.5 | 725.6846 | 3000 | 6.4565 | 3006.4565 | 2800.9743 | 0 | 176.2093
0 | 41.5016 | 0 | 0 | 0 | 0 | 10.9984 | 52.5 | 736.683 | 3000 | 19.6527 | 3019.6527 | 2970.9858 | 0 | 191.3018
0 | 36.6741 | 0 | 0 | 0 | 0 | 15.8259 | 52.5 | 752.5089 | 3000 | 28.2788 | 3028.2788 | 3017.464 | 0 | 184.6084
0 | 28.9616 | 0 | 0 | 0 | 0 | 23.5384 | 52.5 | 776.0473 | 3000 | 42.06 | 3042.06 | 3042.06 | 0 | 184.9572
0 | 33.7395 | 0 | 0 | 0 | 0 | 18.7605 | 52.5 | 794.8078 | 3000 | 33.5225 | 3033.5225 | 3033.5225 | 0 | 179.4935
0 | 26.6979 | 0 | 0 | 0 | 0 | 25.8021 | 52.5 | 820.6099 | 3000 | 46.105 | 3046.105 | 3046.105 | 0 | 160.4079
0 | 26.6732 | 0 | 0 | 0 | 0 | 25.8268 | 52.5 | 846.4367 | 3000 | 46.149 | 3046.149 | 3046.149 | 0 | 152.9167
0 | 32.8984 | 0 | 0 | 0 | 0 | 19.6016 | 52.5 | 866.0383 | 3000 | 35.0255 | 3035.0255 | 3035.0255 | 0 | 150.0517
0 | 23.7404 | 0 | 0 | 0 | 0 | 28.7596 | 52.5 | 894.7979 | 3000 | 51.3896 | 3051.3896 | 3051.3896 | 0 | 146.8329
0 | 31.559 | 0 | 0 | 0 | 0 | 20.941 | 52.5 | 915.739 | 3000 | 37.4189 | 3037.4189 | 3037.4189 | 0 | 141.2096
0 | 33.4525 | 0 | 0 | 0 | 0 | 19.0475 | 52.5 | 934.7865 | 3000 | 34.0354 | 3034.0354 | 3028.628 | 0 | 143.4661
0 | 36.0945 | 0 | 0 | 0 | 0 | 16.4055 | 52.5 | 951.192 | 3000 | 29.3145 | 3029.3145 | 3002.2774 | 0 | 147.8622
0 | 28.9339 | 0 | 0 | 0 | 0 | 23.5661 | 52.5 | 974.7581 | 3000 | 42.1095 | 3042.1095 | 2960.9981 | 0 | 164.3946
0 | 24.7975 | 0 | 0 | 0 | 0 | 27.7025 | 52.5 | 1002.4607 | 3000 | 49.5007 | 3049.5007 | 2935.9448 | 0 | 190.6015
0 | 42.5631 | 0 | 0 | 0 | 0 | -42.5631 | 0 | 959.8975 | 0 | 0 | 0 | 0 | 194.6673 | 0
0 | 43.4421 | 0 | 0 | 0 | 0 | -43.4421 | 0 | 916.4555 | 0 | 0 | 0 | 0 | 275.7787 | 0
0 | 39.7577 | 0 | 0 | 0 | 0 | 12.7423 | 52.5 | 929.1978 | 3000 | 22.7689 | 3022.7689 | 2611.8045 | 0 | 176.349
0 | 52.7402 | 0 | 0 | 0 | 0 | -0.24021 | 52.5 | 928.9576 | 3000 | 0 | 3000 | 2643.1099 | 0 | 174.8417
0 | 50.3283 | 0 | 0 | 0 | 0 | 2.1717 | 52.5 | 931.1292 | 3000 | 3.8805 | 3003.8805 | 2674.0275 | 0 | 173.4107
0 | 47.6919 | 0 | 0 | 0 | 0 | 4.8081 | 52.5 | 935.9373 | 3000 | 8.5914 | 3008.5914 | 2711.183 | 0 | 166.1142
0 | 34.6744 | 0 | 0 | 0 | 0 | 17.8256 | 52.5 | 953.7629 | 3000 | 31.852 | 3031.852 | 2783.1104 | 0 | 164.0644
0 | 251.4478 | 0 | 0 | 0 | 0 | -198.9478 | 52.5 | 754.8151 | 3000 | 0 | 3000 | 2821.555 | 0 | 158.4021
0 | 35.4781 | 0 | 0 | 0 | 0 | 17.0219 | 52.5 | 771.837 | 3000 | 30.4159 | 3030.4159 | 2851.9709 | 0 | 158.3414
0 | 38.4082 | 0 | 0 | 0 | 0 | 14.0918 | 52.5 | 785.9288 | 3000 | 25.1801 | 3025.1801 | 2922.4391 | 0 | 167.8941
0 | 42.9915 | 0 | 0 | 0 | 0 | 9.5085 | 52.5 | 795.4373 | 3000 | 16.9903 | 3016.9903 | 2984.5458 | 0 | 181.9081
0 | 35.7009 | 0 | 0 | 0 | 0 | 16.7991 | 52.5 | 812.2364 | 3000 | 30.0178 | 3030.0178 | 3013.7956 | 0 | 186.7348
0 | 29.3203 | 0 | 0 | 0 | 0 | 23.1797 | 52.5 | 835.4161 | 3000 | 41.4191 | 3041.4191 | 3036.0117 | 0 | 181.766
0 | 30.6894 | 0 | 0 | 0 | 0 | 21.8106 | 52.5 | 857.2267 | 3000 | 38.9726 | 3038.9726 | 3038.9726 | 0 | 179.6337
0 | 32.04 | 0 | 0 | 0 | 0 | 20.46 | 52.5 | 877.6867 | 3000 | 36.5594 | 3036.5594 | 3036.5594 | 0 | 171.5352
0 | 29.9065 | 0 | 0 | 0 | 0 | 22.5935 | 52.5 | 900.2802 | 3000 | 40.3716 | 3040.3716 | 3040.3716 | 0 | 152.5658
0 | 30.9515 | 0 | 0 | 0 | 0 | 21.5485 | 52.5 | 921.8288 | 3000 | 38.5044 | 3038.5044 | 3038.5044 | 0 | 144.8151
0 | 29.2278 | 0 | 0 | 0 | 0 | 23.2722 | 52.5 | 945.1009 | 3000 | 41.5842 | 3041.5842 | 3041.5842 | 0 | 144.4753
0 | 30.8129 | 0 | 0 | 0 | 0 | 21.6871 | 52.5 | 966.788 | 3000 | 38.752 | 3038.752 | 3038.752 | 0 | 135.7107
0 | 26.1858 | 0 | 0 | 0 | 0 | 26.3142 | 52.5 | 993.1022 | 3000 | 47.02 | 3047.02 | 3047.02 | 0 | 134.0689
0 | 45.444 | 0 | 0 | 0 | 0 | 7.056 | 52.5 | 1000.1582 | 3000 | 12.6081 | 3012.6081 | 3007.2007 | 0 | 134.1512
0 | 60.5766 | 0 | 0 | 0 | 0 | -8.0766 | 52.5 | 992.0816 | 3000 | 0 | 3000 | 2967.5554 | 0 | 142.7097
0 | 80.7938 | 0 | 0 | 0 | 0 | -28.2938 | 52.5 | 963.7878 | 3000 | 0 | 3000 | 2918.8886 | 0 | 153.5335
0 | 50.1859 | 0 | 0 | 0 | 0 | 2.3141 | 52.5 | 966.1019 | 3000 | 4.1351 | 3004.1351 | 2771.6158 | 0 | 170.7315
0 | 57.6724 | 0 | 0 | 0 | 0 | -5.1724 | 52.5 | 960.9295 | 3000 | 0 | 3000 | 2410.5907 | 0 | 157.5321
0 | 51.4598 | 0 | 0 | 0 | 0 | 1.0402 | 52.5 | 961.9697 | 3000 | 1.8587 | 3001.8587 | 1914.9662 | 0 | 121.3514
0 | 98.6346 | 0 | 0 | 0 | 0 | -46.1346 | 52.5 | 915.8351 | 3000 | 0 | 3000 | 1707.6254 | 0 | 103.7724
0 | 81.8815 | 0 | 0 | 0 | 0 | -29.3815 | 52.5 | 886.4535 | 3000 | 0 | 3000 | 1356.1427 | 0 | 77.8562
0 | 58.9091 | 0 | 0 | 0 | 0 | -6.4091 | 52.5 | 880.0445 | 3000 | 0 | 3000 | 1329.1056 | 0 | 74.4166
0 | 47.9897 | 0 | 0 | 0 | 0 | 4.5103 | 52.5 | 884.5548 | 3000 | 8.0593 | 3008.0593 | 1704.8698 | 0 | 91.4663
0 | 40.1196 | 0 | 0 | 0 | 0 | 12.3804 | 52.5 | 896.9352 | 3000 | 22.1221 | 3022.1221 | 1545.8951 | 0 | 80.3711
0 | 40.3141 | 0 | 0 | 0 | 0 | 12.1859 | 52.5 | 909.1211 | 3000 | 21.7746 | 3021.7746 | 1778.0668 | 0 | 90.717
0 | 44.5415 | 0 | 0 | 0 | 0 | 7.9585 | 52.5 | 917.0796 | 3000 | 14.2208 | 3014.2208 | 2008.4397 | 0 | 101.848
0 | 63.0969 | 0 | 0 | 0 | 0 | -10.5969 | 52.5 | 906.4828 | 3000 | 0 | 3000 | 2269.9976 | 0 | 122.5799
0 | 46.5804 | 0 | 0 | 0 | 0 | 5.9196 | 52.5 | 912.4024 | 3000 | 10.5776 | 3010.5776 | 2669.9098 | 0 | 154.4543
0 | 50.336 | 0 | 0 | 0 | 0 | 2.164 | 52.5 | 914.5664 | 3000 | 3.8668 | 3003.8668 | 2911.9405 | 0 | 181.9089
0 | 26.7798 | 0 | 0 | 0 | 0 | 25.7202 | 52.5 | 940.2866 | 3000 | 45.9586 | 3045.9586 | 3035.1437 | 0 | 194.2188
0 | 27.5845 | 0 | 0 | 0 | 0 | 24.9155 | 52.5 | 965.2021 | 3000 | 44.5207 | 3044.5207 | 3044.5207 | 0 | 192.231
0 | 32.4132 | 0 | 0 | 0 | 0 | 20.0868 | 52.5 | 985.2889 | 3000 | 35.8924 | 3035.8924 | 3035.8924 | 0 | 192.6274
0 | 35.1967 | 0 | 0 | 0 | 0 | 17.3033 | 52.5 | 1002.5922 | 3000 | 30.9187 | 3030.9187 | 3030.9187 | 0 | 170.2164
0 | 29.8266 | 0 | 0 | 0 | 0 | 22.6734 | 52.5 | 1025.2656 | 3000 | 40.5143 | 3040.5143 | 3040.5143 | 0 | 154.4581
0 | 25.5663 | 0 | 0 | 0 | 0 | 26.9337 | 52.5 | 1052.1993 | 3000 | 48.1269 | 3048.1269 | 3048.1269 | 0 | 147.2855
0 | 30.5039 | 0 | 0 | 0 | 0 | 21.9961 | 52.5 | 1074.1954 | 3000 | 39.3042 | 3039.3042 | 3039.3042 | 0 | 143.9718
0 | 227.158 | 0 | 0 | 0 | 0 | -174.658 | 52.5 | 899.5374 | 3000 | 0 | 3000 | 3000 | 0 | 138.45
0 | 41.9549 | 0 | 0 | 0 | 0 | 10.5451 | 52.5 | 910.0825 | 3000 | 18.8426 | 3018.8426 | 3008.0278 | 0 | 137.527
0 | 74.8221 | 0 | 0 | 0 | 0 | -22.3221 | 52.5 | 887.7604 | 3000 | 0 | 3000 | 2826.9624 | 0 | 137.7296
0 | 84.3253 | 0 | 0 | 0 | 0 | -31.8253 | 52.5 | 855.935 | 3000 | 0 | 3000 | 2572.8134 | 0 | 139.395
0 | 40.7297 | 0 | 0 | 0 | 0 | 11.7703 | 52.5 | 867.7054 | 3000 | 21.032 | 3021.032 | 2307.2519 | 0 | 142.5189
0 | 61.1006 | 0 | 0 | 0 | 0 | -8.6006 | 52.5 | 859.1048 | 3000 | 0 | 3000 | 1967.1818 | 0 | 122.0833
0 | 70.0453 | 0 | 0 | 0 | 0 | -17.5453 | 52.5 | 841.5594 | 3000 | 0 | 3000 | 1750.8848 | 0 | 97.8044
0 | 79.7031 | 0 | 0 | 0 | 0 | -27.2031 | 52.5 | 814.3563 | 3000 | 0 | 3000 | 1610.2917 | 0 | 81.8833
0 | 57.97 | 0 | 0 | 0 | 0 | -5.47 | 52.5 | 808.8863 | 3000 | 0 | 3000 | 1588.662 | 0 | 80.3863
0 | 81.6758 | 0 | 0 | 0 | 0 | -29.1758 | 52.5 | 779.7105 | 3000 | 0 | 3000 | 1437.2541 | 0 | 72.6676
0 | 52.6056 | 0 | 0 | 0 | 0 | -0.10558 | 52.5 | 779.6049 | 3000 | 0 | 3000 | 1529.1803 | 0 | 77.5906
0 | 38.3091 | 0 | 0 | 0 | 0 | 14.1909 | 52.5 | 793.7958 | 3000 | 25.3572 | 3025.3572 | 1711.3528 | 0 | 86.5089
0 | 37.2129 | 0 | 0 | 0 | 0 | 15.2871 | 52.5 | 809.0829 | 3000 | 27.3161 | 3027.3161 | 1843.09 | 0 | 95.3983
0 | 47.2863 | 0 | 0 | 0 | 0 | 5.2137 | 52.5 | 814.2966 | 3000 | 9.3162 | 3009.3162 | 1960.2757 | 0 | 103.0517
0 | 52.4271 | 0 | 0 | 0 | 0 | 0.072898 | 52.5 | 814.3695 | 3000 | 0.13026 | 3000.1303 | 2291.7576 | 0 | 133.0136
0 | 51.9714 | 0 | 0 | 0 | 0 | 0.52863 | 52.5 | 814.8982 | 3000 | 0.94459 | 3000.9446 | 2568.3506 | 0 | 163.2187
0 | 39.3758 | 0 | 0 | 0 | 0 | 13.1242 | 52.5 | 828.0224 | 3000 | 23.4512 | 3023.4512 | 2888.2656 | 0 | 194.6113
0 | 33.1127 | 0 | 0 | 0 | 0 | 19.3873 | 52.5 | 847.4097 | 3000 | 34.6425 | 3034.6425 | 3023.8277 | 0 | 211.5167
0 | 34.2423 | 0 | 0 | 0 | 0 | 18.2577 | 52.5 | 865.6674 | 3000 | 32.6241 | 3032.6241 | 3032.6241 | 0 | 203.1252
0 | 22.7174 | 0 | 0 | 0 | 0 | 29.7826 | 52.5 | 895.4499 | 3000 | 53.2175 | 3053.2175 | 3053.2175 | 0 | 196.6577
0 | 32.5334 | 0 | 0 | 0 | 0 | 19.9666 | 52.5 | 915.4165 | 3000 | 35.6776 | 3035.6776 | 3035.6776 | 0 | 182.3835
0 | 32.7497 | 0 | 0 | 0 | 0 | 19.7503 | 52.5 | 935.1668 | 3000 | 35.2911 | 3035.2911 | 3035.2911 | 0 | 166.6375
0 | 23.0275 | 0 | 0 | 0 | 0 | 29.4725 | 52.5 | 964.6393 | 3000 | 52.6634 | 3052.6634 | 3052.6634 | 0 | 153.3658
0 | 33.8662 | 0 | 0 | 0 | 0 | 18.6338 | 52.5 | 983.2731 | 3000 | 33.2962 | 3033.2962 | 3033.2962 | 0 | 151.4525
0 | 23.7753 | 0 | 0 | 0 | 0 | 28.7247 | 52.5 | 1011.9978 | 3000 | 51.3273 | 3051.3273 | 3051.3273 | 0 | 149.1184
0 | 36.5353 | 0 | 0 | 0 | 0 | 15.9647 | 52.5 | 1027.9626 | 3000 | 28.5269 | 3028.5269 | 3017.712 | 0 | 149.256
0 | 48.1827 | 0 | 0 | 0 | 0 | 4.3173 | 52.5 | 1032.2799 | 3000 | 7.7145 | 3007.7145 | 2888.7511 | 0 | 144.3798
0 | 86.2951 | 0 | 0 | 0 | 0 | -33.7951 | 52.5 | 998.4848 | 3000 | 0 | 3000 | 2589.0357 | 0 | 142.8112
0 | 55.8365 | 0 | 0 | 0 | 0 | -3.3365 | 52.5 | 995.1483 | 3000 | 0 | 3000 | 2367.3312 | 0 | 153.261
0 | 69.2993 | 0 | 0 | 0 | 0 | -16.7993 | 52.5 | 978.349 | 3000 | 0 | 3000 | 2161.8491 | 0 | 142.5739
0 | 30.7046 | 0 | 0 | 0 | 0 | 21.7954 | 52.5 | 1000.1444 | 3000 | 38.9455 | 3038.9455 | 1757.3857 | 0 | 107.0951
0 | 52.4874 | 0 | 0 | 0 | 0 | 0.012582 | 52.5 | 1000.157 | 3000 | 0.022482 | 3000.0225 | 1502.1657 | 0 | 88.2973
0 | 78.7198 | 0 | 0 | 0 | 0 | -26.2198 | 52.5 | 973.9372 | 3000 | 0 | 3000 | 1334.513 | 0 | 72.7843
0 | 109.1924 | 0 | 0 | 0 | 0 | -56.6924 | 52.5 | 917.2448 | 3000 | 0 | 3000 | 1366.9576 | 0 | 71.7379
0 | 22.9209 | 0 | 0 | 0 | 0 | 29.5791 | 52.5 | 946.8239 | 3000 | 60.5249 | 3060.5249 | 1497.779 | 0 | 76.1621
0 | 38.8197 | 0 | 0 | 0 | 0 | 13.6803 | 52.5 | 960.5043 | 3000 | 24.4449 | 3024.4449 | 1559.0327 | 0 | 78.4973
0 | 43.723 | 0 | 0 | 0 | 0 | 8.777 | 52.5 | 969.2813 | 3000 | 15.6834 | 3015.6834 | 1723.3088 | 0 | 86.1654
0 | 41.8988 | 0 | 0 | 0 | 0 | 10.6012 | 52.5 | 979.8825 | 3000 | 18.9429 | 3018.9429 | 1959.0876 | 0 | 98.1111
0 | 28.6869 | 0 | 0 | 0 | 0 | 23.8131 | 52.5 | 1003.6955 | 3000 | 42.5508 | 3042.5508 | 2269.289 | 0 | 117.1861
0 | 49.9528 | 0 | 0 | 0 | 0 | 2.5472 | 52.5 | 1006.2427 | 3000 | 4.5515 | 3004.5515 | 2550.3278 | 0 | 144.4506
0 | 48.6797 | 0 | 0 | 0 | 0 | 3.8203 | 52.5 | 1010.0631 | 3000 | 6.8264 | 3006.8264 | 2828.3814 | 0 | 169.3635
0 | 27.8005 | 0 | 0 | 0 | 0 | 24.6995 | 52.5 | 1034.7626 | 3000 | 44.1348 | 3044.1348 | 3027.9125 | 0 | 183.3401
0 | 34.2164 | 0 | 0 | 0 | 0 | 18.2836 | 52.5 | 1053.0462 | 3000 | 32.6704 | 3032.6704 | 3032.6704 | 0 | 183.5069
0 | 23.9287 | 0 | 0 | 0 | 0 | 28.5713 | 52.5 | 1081.6175 | 3000 | 51.0532 | 3051.0532 | 3051.0532 | 0 | 183.2463
0 | 34.513 | 0 | 0 | 0 | 0 | 17.987 | 52.5 | 1099.6046 | 3000 | 32.1404 | 3032.1404 | 3032.1404 | 0 | 172.4985
0 | 31.7143 | 0 | 0 | 0 | 0 | 20.7857 | 52.5 | 1120.3903 | 3000 | 37.1413 | 3037.1413 | 3037.1413 | 0 | 173.0259
0 | 30.101 | 0 | 0 | 0 | 0 | 22.399 | 52.5 | 1142.7893 | 3000 | 40.0241 | 3040.0241 | 3040.0241 | 0 | 158.5373
0 | 31.2331 | 0 | 0 | 0 | 0 | 21.2669 | 52.5 | 1164.0561 | 3000 | 38.0011 | 3038.0011 | 3038.0011 | 0 | 152.1127
0 | 32.3385 | 0 | 0 | 0 | 0 | 20.1615 | 52.5 | 1184.2176 | 3000 | 36.0259 | 3036.0259 | 3036.0259 | 0 | 148.8563
0 | 33.2009 | 0 | 0 | 0 | 0 | 19.2991 | 52.5 | 1203.5167 | 3000 | 34.4849 | 3034.4849 | 3023.6701 | 0 | 147.676
0 | 32.7384 | 0 | 0 | 0 | 0 | 19.7616 | 52.5 | 1223.2783 | 3000 | 35.3114 | 3035.3114 | 2975.8297 | 0 | 143.1077
0 | 51.9141 | 0 | 0 | 0 | 0 | 0.58591 | 52.5 | 1223.8642 | 3000 | 1.047 | 3001.047 | 2800.9722 | 0 | 137.3877
0 | 25.3458 | 0 | 0 | 0 | 0 | 27.1542 | 52.5 | 1251.0184 | 3000 | 48.5209 | 3048.5209 | 2615.9269 | 0 | 131.0841
0 | 44.6891 | 0 | 0 | 0 | 0 | 7.8109 | 52.5 | 1258.8293 | 3000 | 13.957 | 3013.957 | 2365.066 | 0 | 124.639
0 | 41.3678 | 0 | 0 | 0 | 0 | 11.1322 | 52.5 | 1269.9615 | 3000 | 19.8917 | 3019.8917 | 2489.9641 | 0 | 130.8725
0 | 50.3746 | 0 | 0 | 0 | 0 | 2.1254 | 52.5 | 1272.0869 | 3000 | 3.7979 | 3003.7979 | 2436.0182 | 0 | 125.0165
0 | 50.0911 | 0 | 0 | 0 | 0 | 2.4089 | 52.5 | 1274.4958 | 3000 | 4.3043 | 3004.3043 | 1863.3376 | 0 | 93.5395
0 | 28.3548 | 0 | 0 | 0 | 0 | 24.1452 | 52.5 | 1298.641 | 3000 | 43.1442 | 3043.1442 | 2021.1408 | 0 | 99.521
0 | 39.0443 | 0 | 0 | 0 | 0 | 13.4557 | 52.5 | 1312.0967 | 3000 | 24.0435 | 3024.0435 | 1742.4837 | 0 | 83.6566
0 | 48.228 | 0 | 0 | 0 | 0 | 4.272 | 52.5 | 1316.3686 | 3000 | 7.6334 | 3007.6334 | 1850.4444 | 0 | 85.8976
0 | 48.6793 | 0 | 0 | 0 | 0 | 3.8207 | 52.5 | 1320.1893 | 3000 | 6.8271 | 3006.8271 | 1914.5272 | 0 | 88.7383
0 | 36.9527 | 0 | 0 | 0 | 0 | 15.5473 | 52.5 | 1335.7367 | 3000 | 27.781 | 3027.781 | 2308.5934 | 0 | 108.6886
0 | 36.0815 | 0 | 0 | 0 | 0 | 16.4185 | 52.5 | 1352.1551 | 3000 | 29.3376 | 3029.3376 | 2299.3352 | 0 | 113.1043
0 | 38.779 | 0 | 0 | 0 | 0 | 13.721 | 52.5 | 1365.8762 | 3000 | 24.5176 | 3024.5176 | 2618.9607 | 0 | 137.4431
0 | 40.3255 | 0 | 0 | 0 | 0 | 12.1745 | 52.5 | 1378.0506 | 3000 | 21.7542 | 3021.7542 | 2929.828 | 0 | 164.4219
0 | 31.6481 | 0 | 0 | 0 | 0 | 20.8519 | 52.5 | 1398.9026 | 3000 | 37.2596 | 3037.2596 | 3031.8522 | 0 | 180.3042
0 | 26.1659 | 0 | 0 | 0 | 0 | 26.3341 | 52.5 | 1425.2366 | 3000 | 47.0555 | 3047.0555 | 3047.0555 | 0 | 181.9397
0 | 25.216 | 0 | 0 | 0 | 0 | 27.284 | 52.5 | 1452.5206 | 3000 | 48.7529 | 3048.7529 | 3048.7529 | 0 | 181.3093
0 | 25.5734 | 0 | 0 | 0 | 0 | 26.9266 | 52.5 | 1479.4472 | 3000 | 48.1143 | 3048.1143 | 3048.1143 | 0 | 169.4142
0 | 25.4696 | 0 | 0 | 0 | 0 | 20.5528 | 46.0224 | 1500 | 2629.8518 | 36.725 | 2666.5768 | 2666.5768 | 0 | 137.062
0 | 32.045 | 0 | 0 | 0 | 0 | -6.3949e-14 | 32.045 | 1500 | 1831.1425 | 0 | 1831.1425 | 1831.1425 | 0 | 87.9681
0 | 31.7061 | 0 | 0 | 0 | 0 | 4.2633e-14 | 31.7061 | 1500 | 1811.7799 | 7.6179e-14 | 1811.7799 | 1811.7799 | 0 | 80.3887
0 | 38.6412 | 0 | 0 | 0 | 0 | -9.9476e-14 | 38.6412 | 1500 | 2208.0701 | 0 | 2208.0701 | 2208.0701 | 0 | 94.5275
0 | 28.5821 | 0 | 0 | 0 | 0 | 5.3291e-14 | 28.5821 | 1500 | 1633.2612 | 9.5223e-14 | 1633.2612 | 1622.4463 | 0 | 61.6692
0 | 30.9078 | 0 | 0 | 0 | 0 | -3.5527e-14 | 30.9078 | 1500 | 1766.1583 | 0 | 1766.1583 | 1701.2692 | 0 | 56.3971
0 | 25.3358 | 0 | 0 | 0 | 0 | 0 | 25.3358 | 1500 | 1447.7583 | 0 | 1447.7583 | 1209.8316 | 0 | 35.8473
0 | 24.2277 | 0 | 0 | 0 | 0 | 1.5987e-14 | 24.2277 | 1500 | 1384.4419 | 2.8567e-14 | 1384.4419 | 897.7736 | 0 | 30.2101
0 | 39.9358 | 0 | 0 | 0 | 0 | 0 | 39.9358 | 1500 | 2282.046 | 6.3482e-15 | 2282.046 | 1589.8956 | 0 | 62.9281
0 | 42.3781 | 0 | 0 | 0 | 0 | 0 | 42.3781 | 1500 | 2421.6071 | 1.2696e-14 | 2421.6071 | 1437.4557 | 0 | 62.2418
0 | 27.8804 | 0 | 0 | 0 | 0 | 5.862e-14 | 27.8804 | 1500 | 1593.1645 | 1.0475e-13 | 1593.1645 | 814.4952 | 0 | 27.4403
0 | 241.7726 | 0 | 0 | 0 | 0 | -189.2726 | 52.5 | 1310.7274 | 3000 | 0 | 3000 | 2140.2194 | 0 | 92.6715
0 | 41.5862 | 0 | 0 | 0 | 0 | 10.9138 | 52.5 | 1321.6412 | 3000 | 19.5016 | 3019.5016 | 2051.5724 | 0 | 90.4743
0 | 42.3199 | 0 | 0 | 0 | 0 | 10.1801 | 52.5 | 1331.8213 | 3000 | 18.1904 | 3018.1904 | 2034.0391 | 0 | 86.2433
0 | 53.8096 | 0 | 0 | 0 | 0 | -1.3096 | 52.5 | 1330.5117 | 3000 | 0 | 3000 | 2302.4421 | 0 | 69.9942
0 | 46.9096 | 0 | 0 | 0 | 0 | 5.5904 | 52.5 | 1336.1021 | 3000 | 9.9893 | 3009.9893 | 2355.6908 | 0 | 47.1138
0 | 37.8807 | 0 | 0 | 0 | 0 | 14.6193 | 52.5 | 1350.7215 | 3000 | 26.1228 | 3026.1228 | 2479.9728 | 0 | 48.7811
0 | 39.4771 | 0 | 0 | 0 | 0 | 13.0229 | 52.5 | 1363.7444 | 3000 | 23.2703 | 3023.2703 | 2693.4173 | 0 | 125.8903
0 | 33.8975 | 0 | 0 | 0 | 0 | 18.6025 | 52.5 | 1382.3469 | 3000 | 33.2402 | 3033.2402 | 2881.8322 | 0 | 138.3568
0 | 50.6423 | 0 | 0 | 0 | 0 | 1.8577 | 52.5 | 1384.2046 | 3000 | 3.3195 | 3003.3195 | 2954.6527 | 0 | 152.5487
0 | 27.042 | 0 | 0 | 0 | 0 | 25.458 | 52.5 | 1409.6626 | 3000 | 45.4901 | 3045.4901 | 3040.0827 | 0 | 158.5707
0 | 28.7612 | 0 | 0 | 0 | 0 | 23.7388 | 52.5 | 1433.4014 | 3000 | 42.4181 | 3042.4181 | 3042.4181 | 0 | 156.9584
0 | 29.4056 | 0 | 0 | 0 | 0 | 23.0944 | 52.5 | 1456.4959 | 3000 | 41.2667 | 3041.2667 | 3041.2667 | 0 | 156.2299
0 | 36.5164 | 0 | 0 | 0 | 0 | 15.9836 | 52.5 | 1472.4795 | 3000 | 28.5606 | 3028.5606 | 3028.5606 | 0 | 143.7052
0 | 31.7437 | 0 | 0 | 0 | 0 | 20.7563 | 52.5 | 1493.2358 | 3000 | 37.0888 | 3037.0888 | 3037.0888 | 0 | 146.4788
0 | 25.8722 | 0 | 0 | 0 | 0 | 6.7642 | 32.6364 | 1500 | 1864.9354 | 12.0866 | 1877.022 | 1877.022 | 0 | 79.5857
0 | 19.5028 | 0 | 0 | 0 | 0 | 0 | 19.5028 | 1500 | 1114.4476 | 6.3482e-15 | 1114.4476 | 1114.4476 | 0 | 45.28
0 | 32.8111 | 0 | 0 | 0 | 0 | 1.0658e-13 | 32.8111 | 1500 | 1874.9212 | 1.9045e-13 | 1874.9212 | 1874.9212 | 0 | 71.7157
0 | 25.2329 | 0 | 0 | 0 | 0 | -1.1013e-13 | 25.2329 | 1500 | 1441.8809 | 0 | 1441.8809 | 1425.6586 | 0 | 54.9021
0 | 37.4751 | 0 | 0 | 0 | 0 | 0 | 37.4751 | 1500 | 2141.4348 | 2.5393e-14 | 2141.4348 | 1990.0269 | 0 | 87.0836
0 | 31.5778 | 0 | 0 | 0 | 0 | 4.2633e-14 | 31.5778 | 1500 | 1804.4472 | 7.6179e-14 | 1804.4472 | 1480.0017 | 0 | 76.4421
0 | 25.9243 | 0 | 0 | 0 | 0 | 2.4869e-14 | 25.9243 | 1500 | 1481.3905 | 4.4438e-14 | 1481.3905 | 697.3138 | 0 | 42.6547
0 | 37.595 | 0 | 0 | 0 | 0 | -3.5527e-14 | 37.595 | 1500 | 2148.2845 | 0 | 2148.2845 | 1164.1331 | 0 | 67.9272
0 | 33.1692 | 0 | 0 | 0 | 0 | -8.5265e-14 | 33.1692 | 1500 | 1895.3856 | 0 | 1895.3856 | 575.9739 | 0 | 33.0436
0 | 249.1828 | 0 | 0 | 0 | 0 | -196.6828 | 52.5 | 1303.3172 | 3000 | 0 | 3000 | 1669.7734 | 0 | 91.4034
0 | 45.1439 | 0 | 0 | 0 | 0 | 7.3561 | 52.5 | 1310.6734 | 3000 | 13.1444 | 3013.1444 | 2007.3633 | 0 | 108.9396
0 | 35.6953 | 0 | 0 | 0 | 0 | 16.8047 | 52.5 | 1327.478 | 3000 | 30.0277 | 3030.0277 | 2375.7293 | 0 | 125.9849
0 | 40.4766 | 0 | 0 | 0 | 0 | 12.0234 | 52.5 | 1339.5014 | 3000 | 21.4842 | 3021.4842 | 2248.2224 | 0 | 119.1558
0 | 57.4336 | 0 | 0 | 0 | 0 | -4.9336 | 52.5 | 1334.5678 | 3000 | 0 | 3000 | 2486.2946 | 0 | 127.8701
0 | 43.5589 | 0 | 0 | 0 | 0 | 8.9411 | 52.5 | 1343.5089 | 3000 | 15.9766 | 3015.9766 | 2502.2712 | 0 | 127.3406
0 | 26.4795 | 0 | 0 | 0 | 0 | 26.0205 | 52.5 | 1369.5294 | 3000 | 46.4952 | 3046.4952 | 2813.9759 | 0 | 141.9932
0 | 43.7299 | 0 | 0 | 0 | 0 | 8.7701 | 52.5 | 1378.2996 | 3000 | 15.671 | 3015.671 | 2561.4473 | 0 | 133.8869
0 | 43.388 | 0 | 0 | 0 | 0 | 9.112 | 52.5 | 1387.4116 | 3000 | 16.2819 | 3016.2819 | 2659.3918 | 0 | 147.5431
0 | 41.3555 | 0 | 0 | 0 | 0 | 11.1445 | 52.5 | 1398.5561 | 3000 | 19.9138 | 3019.9138 | 2863.0985 | 0 | 172.9025
0 | 19.5089 | 0 | 0 | 0 | 0 | 32.9911 | 52.5 | 1431.5472 | 3000 | 58.9507 | 3058.9507 | 3048.1359 | 0 | 192.0326
0 | 33.3631 | 0 | 0 | 0 | 0 | 19.1369 | 52.5 | 1450.6841 | 3000 | 34.195 | 3034.195 | 3034.195 | 0 | 184.1756
0 | 23.3456 | 0 | 0 | 0 | 0 | 29.1544 | 52.5 | 1479.8385 | 3000 | 52.0951 | 3052.0951 | 3052.0951 | 0 | 176.3806
0 | 33.7885 | 0 | 0 | 0 | 0 | 18.7115 | 52.5 | 1498.55 | 3000 | 33.435 | 3033.435 | 3033.435 | 0 | 162.7135
0 | 31.8329 | 0 | 0 | 0 | 0 | 1.45 | 33.2828 | 1500 | 1901.8753 | 2.5909 | 1904.4662 | 1904.4662 | 0 | 93.4522
0 | 32.5621 | 0 | 0 | 0 | 0 | 0 | 32.5621 | 1500 | 1860.694 | 7.6179e-14 | 1860.694 | 1860.694 | 0 | 89.4994
0 | 24.4048 | 0 | 0 | 0 | 0 | 8.5265e-14 | 24.4048 | 1500 | 1394.5625 | 1.5236e-13 | 1394.5625 | 1394.5625 | 0 | 66.5346
0 | 27.8719 | 0 | 0 | 0 | 0 | 7.4607e-14 | 27.8719 | 1500 | 1592.682 | 1.3331e-13 | 1592.682 | 1592.682 | 0 | 76.9106
0 | 43.9114 | 0 | 0 | 0 | 0 | 0 | 43.9114 | 1500 | 2509.2254 | 0 | 2509.2254 | 2498.4106 | 0 | 120.2235
0 | 89.6304 | 0 | 0 | 0 | 0 | -37.1304 | 52.5 | 1462.8696 | 3000 | 0 | 3000 | 2956.7406 | 0 | 146.2108
0 | 123.0683 | 0 | 0 | 0 | 0 | -70.5683 | 52.5 | 1392.3013 | 3000 | 0 | 3000 | 2945.9257 | 0 | 180.379
0 | 111.3279 | 0 | 0 | 0 | 0 | -58.8279 | 52.5 | 1333.4734 | 3000 | 0 | 3000 | 2967.5554 | 0 | 194.3155
0 | 65.0524 | 0 | 0 | 0 | 0 | -65.0524 | 0 | 1268.421 | 0 | 0 | 0 | 0 | 140.5931 | 0
0 | 44.5486 | 0 | 0 | 0 | 0 | -44.5486 | 0 | 1223.8724 | 0 | 0 | 0 | 0 | 216.297 | 0
0 | 45.9095 | 0 | 0 | 0 | 0 | 6.5905 | 52.5 | 1230.4629 | 3000 | 11.7763 | 3011.7763 | 2773.8496 | 0 | 182.131
0 | 34.1668 | 0 | 0 | 0 | 0 | 18.3332 | 52.5 | 1248.7961 | 3000 | 32.759 | 3032.759 | 2675.8689 | 0 | 168.7938
0 | 34.6028 | 0 | 0 | 0 | 0 | 17.8972 | 52.5 | 1266.6933 | 3000 | 31.98 | 3031.98 | 2069.4583 | 0 | 124.064
0 | 57.9939 | 0 | 0 | 0 | 0 | -5.4939 | 52.5 | 1261.1995 | 3000 | 0 | 3000 | 1777.9219 | 0 | 106.4975
0 | 39.8515 | 0 | 0 | 0 | 0 | 12.6485 | 52.5 | 1273.8479 | 3000 | 22.6011 | 3022.6011 | 2671.1185 | 0 | 147.4725
0 | 43.0627 | 0 | 0 | 0 | 0 | 9.4373 | 52.5 | 1283.2852 | 3000 | 16.8632 | 3016.8632 | 1794.7851 | 0 | 98.085
0 | 43.6824 | 0 | 0 | 0 | 0 | 8.8176 | 52.5 | 1292.1028 | 3000 | 15.7559 | 3015.7559 | 2291.1609 | 0 | 125.2578
0 | 37.8312 | 0 | 0 | 0 | 0 | 14.6688 | 52.5 | 1306.7716 | 3000 | 26.2112 | 3026.2112 | 2290.8013 | 0 | 130.9651
0 | 41.3411 | 0 | 0 | 0 | 0 | 11.1589 | 52.5 | 1317.9305 | 3000 | 19.9394 | 3019.9394 | 2754.9756 | 0 | 157.8326
0 | 38.8975 | 0 | 0 | 0 | 0 | 13.6025 | 52.5 | 1331.533 | 3000 | 24.3059 | 3024.3059 | 2829.6386 | 0 | 163.1004
0 | 29.3553 | 0 | 0 | 0 | 0 | 23.1447 | 52.5 | 1354.6776 | 3000 | 41.3564 | 3041.3564 | 3019.7267 | 0 | 175.4461
0 | 27.2934 | 0 | 0 | 0 | 0 | 25.2066 | 52.5 | 1379.8843 | 3000 | 45.0409 | 3045.0409 | 3045.0409 | 0 | 172.9279
0 | 38.7809 | 0 | 0 | 0 | 0 | 13.7191 | 52.5 | 1393.6033 | 3000 | 24.5142 | 3024.5142 | 3024.5142 | 0 | 162.6281
0 | 27.3134 | 0 | 0 | 0 | 0 | 25.1866 | 52.5 | 1418.7899 | 3000 | 45.005 | 3045.005 | 3045.005 | 0 | 149.4184
0 | 28.9982 | 0 | 0 | 0 | 0 | 23.5018 | 52.5 | 1442.2917 | 3000 | 41.9946 | 3041.9946 | 3041.9946 | 0 | 150.2745
0 | 24.7892 | 0 | 0 | 0 | 0 | 27.7108 | 52.5 | 1470.0026 | 3000 | 49.5156 | 3049.5156 | 3049.5156 | 0 | 146.5902
0 | 25.8895 | 0 | 0 | 0 | 0 | 26.6105 | 52.5 | 1496.613 | 3000 | 47.5494 | 3047.5494 | 3047.5494 | 0 | 138.8768
0 | 32.2775 | 0 | 0 | 0 | 0 | 3.387 | 35.6645 | 1500 | 2037.9715 | 6.0521 | 2044.0236 | 2044.0236 | 0 | 93.6163
0 | 43.8929 | 0 | 0 | 0 | 0 | 0 | 43.8929 | 1500 | 2508.1674 | 7.6179e-14 | 2508.1674 | 2481.1302 | 0 | 118.7965
0 | 98.343 | 0 | 0 | 0 | 0 | -45.843 | 52.5 | 1454.157 | 3000 | 0 | 3000 | 2794.5178 | 0 | 134.4163
0 | 41.9294 | 0 | 0 | 0 | 0 | 10.5706 | 52.5 | 1464.7276 | 3000 | 18.8882 | 3018.8882 | 2586.2942 | 0 | 144.9618
0 | 35.2141 | 0 | 0 | 0 | 0 | 17.2859 | 52.5 | 1482.0135 | 3000 | 30.8876 | 3030.8876 | 2252.2184 | 0 | 141.1465
0 | 45.8561 | 0 | 0 | 0 | 0 | 6.6439 | 52.5 | 1488.6574 | 3000 | 11.8717 | 3011.8717 | 1924.9792 | 0 | 126.3171
0 | 49.3999 | 0 | 0 | 0 | 0 | 3.1001 | 52.5 | 1491.7574 | 3000 | 5.5394 | 3005.5394 | 1615.8312 | 0 | 101.4742
0 | 50.3631 | 0 | 0 | 0 | 0 | 2.1369 | 52.5 | 1493.8943 | 3000 | 3.8184 | 3003.8184 | 1451.8873 | 0 | 88.5216
0 | 54.9211 | 0 | 0 | 0 | 0 | -2.4211 | 52.5 | 1491.4733 | 3000 | 0 | 3000 | 1296.6611 | 0 | 77.3458
0 | 35.0341 | 0 | 0 | 0 | 0 | 8.5267 | 43.5608 | 1500 | 2489.1894 | 15.2361 | 2504.4255 | 757.8271 | 0 | 42.355
0 | 30.2268 | 0 | 0 | 0 | 0 | 8.1712e-14 | 30.2268 | 1500 | 1727.2457 | 1.4601e-13 | 1727.2457 | 23.9067 | 0 | 1.3125
0 | 36.2832 | 0 | 0 | 0 | 0 | 8.5265e-14 | 36.2832 | 1500 | 2073.3232 | 1.5236e-13 | 2073.3232 | 543.0218 | 0 | 29.8228
0 | 45.2231 | 0 | 0 | 0 | 0 | 3.5527e-14 | 45.2231 | 1500 | 2584.1777 | 6.3482e-14 | 2584.1777 | 1205.2843 | 0 | 64.2296
0 | 41.9095 | 0 | 0 | 0 | 0 | 0 | 41.9095 | 1500 | 2394.8259 | 0 | 2394.8259 | 1367.4151 | 0 | 75.4129
0 | 46.1062 | 0 | 0 | 0 | 0 | 0 | 46.1062 | 1500 | 2634.6421 | 0 | 2634.6421 | 1915.4545 | 0 | 115.387
0 | 39.1654 | 0 | 0 | 0 | 0 | -6.3949e-14 | 39.1654 | 1500 | 2238.025 | 0 | 2238.025 | 1859.5052 | 0 | 120.1798
0 | 43.9703 | 0 | 0 | 0 | 0 | 8.5265e-14 | 43.9703 | 1500 | 2512.588 | 1.5236e-13 | 2512.588 | 2371.995 | 0 | 158.6627
0 | 32.7437 | 0 | 0 | 0 | 0 | -1.0658e-13 | 32.7437 | 1500 | 1871.0689 | 0 | 1871.0689 | 1860.2541 | 0 | 124.637
0 | 30.24 | 0 | 0 | 0 | 0 | -3.908e-14 | 30.24 | 1500 | 1727.9978 | 0 | 1727.9978 | 1727.9978 | 0 | 107.3605
0 | 27.4799 | 0 | 0 | 0 | 0 | -4.9738e-14 | 27.4799 | 1500 | 1570.2783 | 0 | 1570.2783 | 1570.2783 | 0 | 87.5744
0 | 31.0566 | 0 | 0 | 0 | 0 | -7.816e-14 | 31.0566 | 1500 | 1774.6617 | 0 | 1774.6617 | 1774.6617 | 0 | 87.9345
0 | 29.1846 | 0 | 0 | 0 | 0 | 5.3291e-14 | 29.1846 | 1500 | 1667.6908 | 9.5223e-14 | 1667.6908 | 1667.6908 | 0 | 78.5482
0 | 37.3406 | 0 | 0 | 0 | 0 | -1.0658e-13 | 37.3406 | 1500 | 2133.7468 | 0 | 2133.7468 | 2133.7468 | 0 | 94.525
0 | 27.8151 | 0 | 0 | 0 | 0 | 0 | 27.8151 | 1500 | 1589.4371 | 0 | 1589.4371 | 1589.4371 | 0 | 72.6532
0 | 30.5539 | 0 | 0 | 0 | 0 | 9.2371e-14 | 30.5539 | 1500 | 1745.938 | 1.6505e-13 | 1745.938 | 1745.938 | 0 | 72.9104
0 | 32.7279 | 0 | 0 | 0 | 0 | 7.816e-14 | 32.7279 | 1500 | 1870.1661 | 1.3966e-13 | 1870.1661 | 1864.7587 | 0 | 71.5321
0 | 64.357 | 0 | 0 | 0 | 0 | -11.857 | 52.5 | 1488.143 | 3000 | 0 | 3000 | 2983.7777 | 0 | 104.9395
0 | 99.9523 | 0 | 0 | 0 | 0 | -47.4523 | 52.5 | 1440.6907 | 3000 | 0 | 3000 | 2945.9257 | 0 | 117.513
0 | 65.75 | 0 | 0 | 0 | 0 | -13.25 | 52.5 | 1427.4407 | 3000 | 0 | 3000 | 2886.4441 | 0 | 133.8733
0 | 66.9361 | 0 | 0 | 0 | 0 | -14.4361 | 52.5 | 1413.0046 | 3000 | 0 | 3000 | 2794.5178 | 0 | 129.6097
0 | 104.7083 | 0 | 0 | 0 | 0 | -52.2083 | 52.5 | 1360.7963 | 3000 | 0 | 3000 | 2783.703 | 0 | 133.924
0 | 63.3909 | 0 | 0 | 0 | 0 | -10.8909 | 52.5 | 1349.9054 | 3000 | 0 | 3000 | 2691.7768 | 0 | 137.469
0 | 46.5957 | 0 | 0 | 0 | 0 | 5.9043 | 52.5 | 1355.8097 | 3000 | 10.5502 | 3010.5502 | 2594.1784 | 0 | 132.4069
0 | 49.046 | 0 | 0 | 0 | 0 | 3.454 | 52.5 | 1359.2637 | 3000 | 6.1718 | 3006.1718 | 2541.1333 | 0 | 130.8938
0 | 37.183 | 0 | 0 | 0 | 0 | 15.317 | 52.5 | 1374.5807 | 3000 | 27.3695 | 3027.3695 | 2302.7745 | 0 | 116.3131
0 | 40.9511 | 0 | 0 | 0 | 0 | 11.5489 | 52.5 | 1386.1296 | 3000 | 20.6364 | 3020.6364 | 2182.4855 | 0 | 108.7751
0 | 53.7467 | 0 | 0 | 0 | 0 | -1.2467 | 52.5 | 1384.8829 | 3000 | 0 | 3000 | 2199.7011 | 0 | 102.0221
0 | 46.1212 | 0 | 0 | 0 | 0 | 6.3788 | 52.5 | 1391.2617 | 3000 | 11.398 | 3011.398 | 2432.8035 | 0 | 109.2329
0 | 34.5376 | 0 | 0 | 0 | 0 | 17.9624 | 52.5 | 1409.2241 | 3000 | 32.0964 | 3032.0964 | 2734.688 | 0 | 120.5997
0 | 37.9147 | 0 | 0 | 0 | 0 | 14.5853 | 52.5 | 1423.8094 | 3000 | 26.062 | 3026.062 | 2885.469 | 0 | 142.8019
0 | 40.8289 | 0 | 0 | 0 | 0 | 11.6711 | 52.5 | 1435.4805 | 3000 | 20.8547 | 3020.8547 | 2972.1878 | 0 | 152.0869
0 | 36.1802 | 0 | 0 | 0 | 0 | 16.3198 | 52.5 | 1451.8003 | 3000 | 29.1614 | 3029.1614 | 3018.3466 | 0 | 157.0144
0 | 33.1545 | 0 | 0 | 0 | 0 | 19.3455 | 52.5 | 1471.1458 | 3000 | 34.5678 | 3034.5678 | 3034.5678 | 0 | 160.8624
0 | 32.9589 | 0 | 0 | 0 | 0 | 19.5411 | 52.5 | 1490.6869 | 3000 | 34.9173 | 3034.9173 | 3034.9173 | 0 | 167.9523
0 | 25.182 | 0 | 0 | 0 | 0 | 9.3131 | 34.4951 | 1500 | 1971.1512 | 16.6413 | 1987.7925 | 1987.7925 | 0 | 102.749
0 | 30.5857 | 0 | 0 | 0 | 0 | -7.816e-14 | 30.5857 | 1500 | 1747.757 | 0 | 1747.757 | 1747.757 | 0 | 82.1795
0 | 32.9188 | 0 | 0 | 0 | 0 | 0 | 32.9188 | 1500 | 1881.0748 | 1.2696e-14 | 1881.0748 | 1881.0748 | 0 | 83.689
0 | 27.5558 | 0 | 0 | 0 | 0 | -3.5527e-14 | 27.5558 | 1500 | 1574.6159 | 0 | 1574.6159 | 1574.6159 | 0 | 68.3068
0 | 26.3904 | 0 | 0 | 0 | 0 | 0 | 26.3904 | 1500 | 1508.0219 | 0 | 1508.0219 | 1508.0219 | 0 | 65.7498
0 | 38.9956 | 0 | 0 | 0 | 0 | -8.5265e-14 | 38.9956 | 1500 | 2228.3183 | 0 | 2228.3183 | 2217.5035 | 0 | 97.7254
0 | 62.3274 | 0 | 0 | 0 | 0 | -9.8274 | 52.5 | 1490.1726 | 3000 | 0 | 3000 | 2918.8886 | 0 | 128.6354
0 | 113.9892 | 0 | 0 | 0 | 0 | -61.4892 | 52.5 | 1428.6833 | 3000 | 0 | 3000 | 2778.2956 | 0 | 138.9148
0 | 275.3719 | 0 | 0 | 0 | 0 | -222.8719 | 52.5 | 1205.8114 | 3000 | 0 | 3000 | 2670.1471 | 0 | 149.6617
0 | 40.5689 | 0 | 0 | 0 | 0 | 11.9311 | 52.5 | 1217.7425 | 3000 | 21.3193 | 3021.3193 | 2269.6872 | 0 | 128.2146
0 | 46.8206 | 0 | 0 | 0 | 0 | 5.6794 | 52.5 | 1223.4219 | 3000 | 10.1484 | 3010.1484 | 2020.5895 | 0 | 110.6879
0 | 41.0102 | 0 | 0 | 0 | 0 | 11.4898 | 52.5 | 1234.9117 | 3000 | 20.5308 | 3020.5308 | 1668.6745 | 0 | 86.7711
0 | 37.7932 | 0 | 0 | 0 | 0 | 14.7068 | 52.5 | 1249.6185 | 3000 | 26.2791 | 3026.2791 | 2020.498 | 0 | 102.2978
0 | 41.6839 | 0 | 0 | 0 | 0 | 10.8161 | 52.5 | 1260.4346 | 3000 | 19.3269 | 3019.3269 | 1797.2488 | 0 | 88.3707
0 | 47.716 | 0 | 0 | 0 | 0 | 4.784 | 52.5 | 1265.2186 | 3000 | 8.5483 | 3008.5483 | 1970.3227 | 0 | 89.6694
0 | 243.4264 | 0 | 0 | 0 | 0 | -190.9264 | 52.5 | 1074.2922 | 3000 | 0 | 3000 | 1880.663 | 0 | 84.6298
0 | 39.1566 | 0 | 0 | 0 | 0 | 13.3434 | 52.5 | 1087.6355 | 3000 | 23.8428 | 3023.8428 | 2283.0256 | 0 | 100.7727
0 | 36.482 | 0 | 0 | 0 | 0 | 16.018 | 52.5 | 1103.6535 | 3000 | 28.622 | 3028.622 | 2168.8414 | 0 | 105.2105
0 | 39.3159 | 0 | 0 | 0 | 0 | 13.1841 | 52.5 | 1116.8376 | 3000 | 23.5582 | 3023.5582 | 2293.5558 | 0 | 119.3566
0 | 43.9321 | 0 | 0 | 0 | 0 | 8.5679 | 52.5 | 1125.4055 | 3000 | 15.3097 | 3015.3097 | 2593.5305 | 0 | 144.2003
0 | 52.2583 | 0 | 0 | 0 | 0 | 0.24173 | 52.5 | 1125.6472 | 3000 | 0.43193 | 3000.4319 | 2865.2463 | 0 | 174.207
0 | 39.4351 | 0 | 0 | 0 | 0 | 13.0649 | 52.5 | 1138.7121 | 3000 | 23.3452 | 3023.3452 | 3001.7155 | 0 | 186.8868
0 | 21.0495 | 0 | 0 | 0 | 0 | 31.4505 | 52.5 | 1170.1626 | 3000 | 56.1979 | 3056.1979 | 3056.1979 | 0 | 183.9526
0 | 36.1539 | 0 | 0 | 0 | 0 | 16.3461 | 52.5 | 1186.5087 | 3000 | 29.2083 | 3029.2083 | 3029.2083 | 0 | 178.6627
0 | 33.9292 | 0 | 0 | 0 | 0 | 18.5708 | 52.5 | 1205.0795 | 3000 | 33.1835 | 3033.1835 | 3033.1835 | 0 | 166.8251
0 | 36.547 | 0 | 0 | 0 | 0 | 15.953 | 52.5 | 1221.0325 | 3000 | 28.5059 | 3028.5059 | 3028.5059 | 0 | 147.2762
0 | 28.4102 | 0 | 0 | 0 | 0 | 24.0898 | 52.5 | 1245.1223 | 3000 | 43.0453 | 3043.0453 | 3043.0453 | 0 | 140.0714
0 | 30.0504 | 0 | 0 | 0 | 0 | 22.4496 | 52.5 | 1267.572 | 3000 | 40.1145 | 3040.1145 | 3040.1145 | 0 | 131.4241
0 | 30.167 | 0 | 0 | 0 | 0 | 22.333 | 52.5 | 1289.9049 | 3000 | 39.9061 | 3039.9061 | 3039.9061 | 0 | 129.5608
0 | 36.481 | 0 | 0 | 0 | 0 | 16.019 | 52.5 | 1305.9239 | 3000 | 28.6238 | 3028.6238 | 3012.4015 | 0 | 127.3945
0 | 68.1943 | 0 | 0 | 0 | 0 | -15.6943 | 52.5 | 1290.2296 | 3000 | 0 | 3000 | 2837.7772 | 0 | 119.1866
0 | 58.4733 | 0 | 0 | 0 | 0 | -5.9733 | 52.5 | 1284.2563 | 3000 | 0 | 3000 | 2572.8134 | 0 | 112.6892
0 | 29.4824 | 0 | 0 | 0 | 0 | 23.0176 | 52.5 | 1307.2739 | 3000 | 41.1293 | 3041.1293 | 2365.2012 | 0 | 110.0055
0 | 44.4537 | 0 | 0 | 0 | 0 | 8.0463 | 52.5 | 1315.3201 | 3000 | 14.3776 | 3014.3776 | 2068.0782 | 0 | 97.5306
0 | 46.5278 | 0 | 0 | 0 | 0 | 5.9722 | 52.5 | 1321.2923 | 3000 | 10.6715 | 3010.6715 | 1777.7785 | 0 | 88.3378
0 | 47.4838 | 0 | 0 | 0 | 0 | 5.0162 | 52.5 | 1326.3085 | 3000 | 8.9632 | 3008.9632 | 1586.8104 | 0 | 77.4839
0 | 46.818 | 0 | 0 | 0 | 0 | 5.682 | 52.5 | 1331.9905 | 3000 | 10.153 | 3010.153 | 1474.4443 | 0 | 70.39
0 | 29.6957 | 0 | 0 | 0 | 0 | 22.8043 | 52.5 | 1354.7948 | 3000 | 40.7482 | 3040.7482 | 1532.0766 | 0 | 72.0842
0 | 44.1217 | 0 | 0 | 0 | 0 | 8.3783 | 52.5 | 1363.1731 | 3000 | 14.9709 | 3014.9709 | 1506.2993 | 0 | 67.7835
0 | 41.7695 | 0 | 0 | 0 | 0 | 10.7305 | 52.5 | 1373.9035 | 3000 | 19.1739 | 3019.1739 | 1602.4285 | 0 | 71.949
0 | 49.9801 | 0 | 0 | 0 | 0 | 2.5199 | 52.5 | 1376.4234 | 3000 | 4.5027 | 3004.5027 | 1749.98 | 0 | 77.8741
0 | 49.3504 | 0 | 0 | 0 | 0 | 3.1496 | 52.5 | 1379.5731 | 3000 | 5.628 | 3005.628 | 1983.6246 | 0 | 84.4429
0 | 47.4717 | 0 | 0 | 0 | 0 | 5.0283 | 52.5 | 1384.6014 | 3000 | 8.985 | 3008.985 | 2408.7608 | 0 | 106.2023
0 | 39.3771 | 0 | 0 | 0 | 0 | 13.1229 | 52.5 | 1397.7243 | 3000 | 23.4488 | 3023.4488 | 2704.4108 | 0 | 140.2778
0 | 37.7305 | 0 | 0 | 0 | 0 | 14.7695 | 52.5 | 1412.4938 | 3000 | 26.3912 | 3026.3912 | 2842.5387 | 0 | 156.766
0 | 24.7697 | 0 | 0 | 0 | 0 | 27.7303 | 52.5 | 1440.2241 | 3000 | 49.5504 | 3049.5504 | 3027.9207 | 0 | 171.9859
0 | 28.356 | 0 | 0 | 0 | 0 | 24.144 | 52.5 | 1464.3681 | 3000 | 43.1421 | 3043.1421 | 3043.1421 | 0 | 170.2334
0 | 23.4645 | 0 | 0 | 0 | 0 | 29.0355 | 52.5 | 1493.4037 | 3000 | 51.8826 | 3051.8826 | 3051.8826 | 0 | 168.9522
0 | 26.5969 | 0 | 0 | 0 | 0 | 6.5963 | 33.1932 | 1500 | 1896.7551 | 11.7868 | 1908.5419 | 1908.5419 | 0 | 100.3893
0 | 28.734 | 0 | 0 | 0 | 0 | 0 | 28.734 | 1500 | 1641.9437 | 0 | 1641.9437 | 1641.9437 | 0 | 71.4081
0 | 34.99 | 0 | 0 | 0 | 0 | 0 | 34.99 | 1500 | 1999.4291 | 0 | 1999.4291 | 1999.4291 | 0 | 87.9549
0 | 28.1898 | 0 | 0 | 0 | 0 | -6.0396e-14 | 28.1898 | 1500 | 1610.8473 | 0 | 1610.8473 | 1610.8473 | 0 | 74.9366
0 | 41.1431 | 0 | 0 | 0 | 0 | 0 | 41.1431 | 1500 | 2351.0332 | 1.2696e-14 | 2351.0332 | 2351.0332 | 0 | 112.5675
0 | 19.8151 | 0 | 0 | 0 | 0 | -1.0658e-13 | 19.8151 | 1500 | 1132.2905 | 0 | 1132.2905 | 1110.6608 | 0 | 47.2031
0 | 19.7992 | 0 | 0 | 0 | 0 | -3.1974e-14 | 19.7992 | 1500 | 1131.3814 | 0 | 1131.3814 | 963.7512 | 0 | 38.0874
0 | 30.8269 | 0 | 0 | 0 | 0 | -8.5265e-14 | 30.8269 | 1500 | 1761.536 | 0 | 1761.536 | 1328.942 | 0 | 51.8022
0 | 33.2924 | 0 | 0 | 0 | 0 | 7.1054e-14 | 33.2924 | 1500 | 1902.4245 | 1.2696e-13 | 1902.4245 | 1215.6815 | 0 | 45.8798
0 | 55.5449 | 0 | 0 | 0 | 0 | -3.0449 | 52.5 | 1496.9551 | 3000 | 0 | 3000 | 2064.5154 | 0 | 87.7419
0 | 52.9374 | 0 | 0 | 0 | 0 | -0.43742 | 52.5 | 1496.5177 | 3000 | 0 | 3000 | 1810.3664 | 0 | 78.8234
0 | 45.9727 | 0 | 0 | 0 | 0 | 3.4823 | 49.4551 | 1500 | 2826.0049 | 6.2225 | 2832.2274 | 1393.8523 | 0 | 37.2995
0 | 45.4531 | 0 | 0 | 0 | 0 | -3.5527e-14 | 45.4531 | 1500 | 2597.3223 | 0 | 2597.3223 | 1029.1689 | 0 | 27.6846
0 | 47.3176 | 0 | 0 | 0 | 0 | 8.1712e-14 | 47.3176 | 1500 | 2703.8608 | 1.4601e-13 | 2703.8608 | 1087.0406 | 0 | 25.9911
0 | 21.4808 | 0 | 0 | 0 | 0 | 3.5527e-15 | 21.4808 | 1500 | 1227.4715 | 0 | 1227.4715 | 0 | 319.0522 | 0
0 | 45.5389 | 0 | 0 | 0 | 0 | 7.4607e-14 | 45.5389 | 1500 | 2602.2251 | 1.3331e-13 | 2602.2251 | 1250.3688 | 0 | 7.4772
0 | 39.744 | 0 | 0 | 0 | 0 | 6.0396e-14 | 39.744 | 1500 | 2271.085 | 1.0792e-13 | 2271.085 | 1211.2297 | 0 | 17.5871
0 | 52.9596 | 0 | 0 | 0 | 0 | -0.45956 | 52.5 | 1499.5404 | 3000 | 0 | 3000 | 2188.8862 | 0 | 40.4944
0 | 45.5699 | 0 | 0 | 0 | 0 | 0.45956 | 46.0295 | 1500 | 2630.2544 | 0.82117 | 2631.0755 | 1987.5919 | 0 | 89.9783
0 | 40.8027 | 0 | 0 | 0 | 0 | -1.0658e-13 | 40.8027 | 1500 | 2331.5823 | 0 | 2331.5823 | 1855.7289 | 0 | 86.7368
0 | 47.6522 | 0 | 0 | 0 | 0 | 0 | 47.6522 | 1500 | 2722.9835 | 0 | 2722.9835 | 2533.7236 | 0 | 132.7925
0 | 25.7166 | 0 | 0 | 0 | 0 | -5.3291e-14 | 25.7166 | 1500 | 1469.5185 | 0 | 1469.5185 | 1458.7036 | 0 | 77.5009
0 | 23.747 | 0 | 0 | 0 | 0 | -1.0658e-13 | 23.747 | 1500 | 1356.9693 | 0 | 1356.9693 | 1356.9693 | 0 | 70.7524
0 | 23.3517 | 0 | 0 | 0 | 0 | -4.9738e-14 | 23.3517 | 1500 | 1334.3857 | 0 | 1334.3857 | 1334.3857 | 0 | 69.5482
0 | 26.1737 | 0 | 0 | 0 | 0 | 0 | 26.1737 | 1500 | 1495.6404 | 1.9045e-14 | 1495.6404 | 1495.6404 | 0 | 67.0795
0 | 29.798 | 0 | 0 | 0 | 0 | -6.7502e-14 | 29.798 | 1500 | 1702.7441 | 0 | 1702.7441 | 1702.7441 | 0 | 71.1747
0 | 27.4331 | 0 | 0 | 0 | 0 | 0 | 27.4331 | 1500 | 1567.6085 | 0 | 1567.6085 | 1567.6085 | 0 | 60.3686
0 | 28.031 | 0 | 0 | 0 | 0 | 4.6185e-14 | 28.031 | 1500 | 1601.771 | 8.2527e-14 | 1601.771 | 1601.771 | 0 | 57.3114
0 | 23.8687 | 0 | 0 | 0 | 0 | 8.8818e-14 | 23.8687 | 1500 | 1363.9276 | 1.5871e-13 | 1363.9276 | 1363.9276 | 0 | 47.5192
0 | 23.9385 | 0 | 0 | 0 | 0 | -9.2371e-14 | 23.9385 | 1500 | 1367.9135 | 0 | 1367.9135 | 1362.5061 | 0 | 46.7748
0 | 22.4551 | 0 | 0 | 0 | 0 | 1.0303e-13 | 22.4551 | 1500 | 1283.1469 | 1.841e-13 | 1283.1469 | 1164.1835 | 0 | 45.2518
0 | 29.192 | 0 | 0 | 0 | 0 | -3.5527e-14 | 29.192 | 1500 | 1668.1134 | 0 | 1668.1134 | 1397.7422 | 0 | 75.7856
0 | 26.5923 | 0 | 0 | 0 | 0 | 4.2633e-14 | 26.5923 | 1500 | 1519.5582 | 7.6179e-14 | 1519.5582 | 984.2231 | 0 | 58.6991
0 | 49.4262 | 0 | 0 | 0 | 0 | 0 | 49.4262 | 1500 | 2824.3566 | 2.5393e-14 | 2824.3566 | 2121.3913 | 0 | 127.3259
0 | 45.791 | 0 | 0 | 0 | 0 | -4.2633e-14 | 45.791 | 1500 | 2616.6264 | 0 | 2616.6264 | 1740.6235 | 0 | 98.8848
0 | 40.591 | 0 | 0 | 0 | 0 | 3.908e-14 | 40.591 | 1500 | 2319.4855 | 6.983e-14 | 2319.4855 | 1508.3717 | 0 | 81.9951
0 | 28.6744 | 0 | 0 | 0 | 0 | 0 | 28.6744 | 1500 | 1638.5372 | 3.8089e-14 | 1638.5372 | 1000.461 | 0 | 52.7343
0 | 48.2117 | 0 | 0 | 0 | 0 | 0 | 48.2117 | 1500 | 2754.9541 | 0 | 2754.9541 | 2106.063 | 0 | 107.9357
0 | 44.586 | 0 | 0 | 0 | 0 | -9.2371e-14 | 44.586 | 1500 | 2547.7734 | 0 | 2547.7734 | 1969.1789 | 0 | 99.3648
0 | 33.551 | 0 | 0 | 0 | 0 | -5.3291e-14 | 33.551 | 1500 | 1917.1972 | 0 | 1917.1972 | 1354.825 | 0 | 68.0529
0 | 39.3682 | 0 | 0 | 0 | 0 | 8.5265e-14 | 39.3682 | 1500 | 2249.6127 | 1.5236e-13 | 2249.6127 | 1990.0563 | 0 | 100.8561
0 | 28.5336 | 0 | 0 | 0 | 0 | -8.8818e-14 | 28.5336 | 1500 | 1630.4897 | 0 | 1630.4897 | 1387.1556 | 0 | 70.3149
0 | 39.2726 | 0 | 0 | 0 | 0 | -4.9738e-14 | 39.2726 | 1500 | 2244.1472 | 0 | 2244.1472 | 1779.1087 | 0 | 101.5871
0 | 43.0496 | 0 | 0 | 0 | 0 | -8.5265e-14 | 43.0496 | 1500 | 2459.9755 | 0 | 2459.9755 | 2313.975 | 0 | 139.8104
0 | 228.7791 | 0 | 0 | 0 | 0 | -176.2791 | 52.5 | 1323.7209 | 3000 | 0 | 3000 | 2929.7035 | 0 | 191.8956
0 | 33.6075 | 0 | 0 | 0 | 0 | 18.8925 | 52.5 | 1342.6133 | 3000 | 33.7583 | 3033.7583 | 3012.1286 | 0 | 192.716
0 | 23.2956 | 0 | 0 | 0 | 0 | 29.2044 | 52.5 | 1371.8177 | 3000 | 52.1844 | 3052.1844 | 3052.1844 | 0 | 192.6539
0 | 28.4988 | 0 | 0 | 0 | 0 | 24.0012 | 52.5 | 1395.819 | 3000 | 42.887 | 3042.887 | 3042.887 | 0 | 185.4944
0 | 24.6176 | 0 | 0 | 0 | 0 | 27.8824 | 52.5 | 1423.7013 | 3000 | 49.8221 | 3049.8221 | 3049.8221 | 0 | 172.01
0 | 26.784 | 0 | 0 | 0 | 0 | 25.716 | 52.5 | 1449.4173 | 3000 | 45.9511 | 3045.9511 | 3045.9511 | 0 | 151.5056
0 | 24.1695 | 0 | 0 | 0 | 0 | 28.3305 | 52.5 | 1477.7478 | 3000 | 50.6228 | 3050.6228 | 3050.6228 | 0 | 146.3994
0 | 39.3794 | 0 | 0 | 0 | 0 | 13.1206 | 52.5 | 1490.8684 | 3000 | 23.4448 | 3023.4448 | 3023.4448 | 0 | 141.6786
0 | 39.8862 | 0 | 0 | 0 | 0 | 9.1316 | 49.0178 | 1500 | 2801.0171 | 16.3169 | 2817.3341 | 2817.3341 | 0 | 129.5692
0 | 90.0641 | 0 | 0 | 0 | 0 | -37.5641 | 52.5 | 1462.4359 | 3000 | 0 | 3000 | 2978.3703 | 0 | 140.6684
0 | 116.4556 | 0 | 0 | 0 | 0 | -63.9556 | 52.5 | 1398.4803 | 3000 | 0 | 3000 | 2875.6292 | 0 | 138.8641
0 | 117.5406 | 0 | 0 | 0 | 0 | -65.0406 | 52.5 | 1333.4397 | 3000 | 0 | 3000 | 2594.4431 | 0 | 147.8833
0 | 99.5352 | 0 | 0 | 0 | 0 | -47.0352 | 52.5 | 1286.4044 | 3000 | 0 | 3000 | 2302.4421 | 0 | 131.009
0 | 131.508 | 0 | 0 | 0 | 0 | -79.008 | 52.5 | 1207.3964 | 3000 | 0 | 3000 | 2048.2932 | 0 | 142.766
0 | 134.2551 | 0 | 0 | 0 | 0 | -81.7551 | 52.5 | 1125.6413 | 3000 | 0 | 3000 | 1707.6254 | 0 | 105.7532
0 | 83.1877 | 0 | 0 | 0 | 0 | -30.6877 | 52.5 | 1094.9536 | 3000 | 0 | 3000 | 1512.9581 | 0 | 86.6017
0 | 73.903 | 0 | 0 | 0 | 0 | -21.403 | 52.5 | 1073.5506 | 3000 | 0 | 3000 | 1383.1799 | 0 | 77.4581
0 | 99.1064 | 0 | 0 | 0 | 0 | -46.6064 | 52.5 | 1026.9442 | 3000 | 0 | 3000 | 1956.3669 | 0 | 102.8266
0 | 89.4166 | 0 | 0 | 0 | 0 | -36.9166 | 52.5 | 990.0276 | 3000 | 0 | 3000 | 2291.6273 | 0 | 118.0188
0 | 60.8485 | 0 | 0 | 0 | 0 | -8.3485 | 52.5 | 981.6791 | 3000 | 0 | 3000 | 1929.3298 | 0 | 96.8331
0 | 47.1219 | 0 | 0 | 0 | 0 | 5.3781 | 52.5 | 987.0572 | 3000 | 9.6099 | 3009.6099 | 2090.3476 | 0 | 103.4095
0 | 54.7083 | 0 | 0 | 0 | 0 | -2.2083 | 52.5 | 984.8489 | 3000 | 0 | 3000 | 2232.1456 | 0 | 115.2903
0 | 42.1523 | 0 | 0 | 0 | 0 | 10.3477 | 52.5 | 995.1966 | 3000 | 18.49 | 3018.49 | 2407.4509 | 0 | 136.8877
0 | 20.2985 | 0 | 0 | 0 | 0 | 32.2015 | 52.5 | 1027.3981 | 3000 | 57.5398 | 3057.5398 | 2624.9458 | 0 | 157.838
0 | 35.4261 | 0 | 0 | 0 | 0 | 17.0739 | 52.5 | 1044.472 | 3000 | 30.5088 | 3030.5088 | 2949.3974 | 0 | 180.4146
0 | 37.2616 | 0 | 0 | 0 | 0 | 15.2384 | 52.5 | 1059.7104 | 3000 | 27.2289 | 3027.2289 | 3011.0066 | 0 | 179.8173
0 | 28.5476 | 0 | 0 | 0 | 0 | 23.9524 | 52.5 | 1083.6627 | 3000 | 42.7997 | 3042.7997 | 3042.7997 | 0 | 162.1204
0 | 225.4204 | 0 | 0 | 0 | 0 | -172.9204 | 52.5 | 910.7424 | 3000 | 0 | 3000 | 3000 | 0 | 146.49
0 | 28.6618 | 0 | 0 | 0 | 0 | 23.8382 | 52.5 | 934.5806 | 3000 | 42.5957 | 3042.5957 | 3042.5957 | 0 | 130.862
0 | 22.0222 | 0 | 0 | 0 | 0 | 30.4778 | 52.5 | 965.0584 | 3000 | 54.4598 | 3054.4598 | 3054.4598 | 0 | 129.7535
0 | 33.0071 | 0 | 0 | 0 | 0 | 19.4929 | 52.5 | 984.5513 | 3000 | 34.8313 | 3034.8313 | 3034.8313 | 0 | 124.6102
0 | 31.3048 | 0 | 0 | 0 | 0 | 21.1952 | 52.5 | 1005.7466 | 3000 | 37.873 | 3037.873 | 3037.873 | 0 | 120.1479
0 | 33.1471 | 0 | 0 | 0 | 0 | 19.3529 | 52.5 | 1025.0995 | 3000 | 34.581 | 3034.581 | 3034.581 | 0 | 119.9873
0 | 24.8334 | 0 | 0 | 0 | 0 | 27.6666 | 52.5 | 1052.766 | 3000 | 49.4365 | 3049.4365 | 3033.2142 | 0 | 122.2689
0 | 42.2895 | 0 | 0 | 0 | 0 | 10.2105 | 52.5 | 1062.9765 | 3000 | 18.2447 | 3018.2447 | 2974.9853 | 0 | 126.5261
0 | 70.0013 | 0 | 0 | 0 | 0 | -17.5013 | 52.5 | 1045.4751 | 3000 | 0 | 3000 | 2913.4812 | 0 | 150.5104
0 | 106.2198 | 0 | 0 | 0 | 0 | -53.7198 | 52.5 | 991.7554 | 3000 | 0 | 3000 | 2480.8872 | 0 | 147.0422
0 | 140.3093 | 0 | 0 | 0 | 0 | -87.8093 | 52.5 | 903.946 | 3000 | 0 | 3000 | 2437.6278 | 0 | 146.2333
0 | 118.0421 | 0 | 0 | 0 | 0 | -65.5421 | 52.5 | 838.4039 | 3000 | 0 | 3000 | 2545.7763 | 0 | 150.1244
0 | 105.5905 | 0 | 0 | 0 | 0 | -53.0905 | 52.5 | 785.3134 | 3000 | 0 | 3000 | 2161.8491 | 0 | 121.8851
0 | 109.1866 | 0 | 0 | 0 | 0 | -56.6866 | 52.5 | 728.6268 | 3000 | 0 | 3000 | 2123.9971 | 0 | 117.7969
0 | 107.5264 | 0 | 0 | 0 | 0 | -55.0264 | 52.5 | 673.6004 | 3000 | 0 | 3000 | 2188.8862 | 0 | 117.8715
0 | 100.1322 | 0 | 0 | 0 | 0 | -47.6322 | 52.5 | 625.9683 | 3000 | 0 | 3000 | 1864.4407 | 0 | 95.6831
0 | 47.4518 | 0 | 0 | 0 | 0 | 5.0482 | 52.5 | 631.0164 | 3000 | 9.0204 | 3009.0204 | 1765.3126 | 0 | 90.3664
0 | 39.7541 | 0 | 0 | 0 | 0 | 12.7459 | 52.5 | 643.7623 | 3000 | 22.7752 | 3022.7752 | 1919.6605 | 0 | 101.7612
0 | 51.0975 | 0 | 0 | 0 | 0 | 1.4025 | 52.5 | 645.1648 | 3000 | 2.5061 | 3002.5061 | 2012.9473 | 0 | 108.6992
0 | 43.6471 | 0 | 0 | 0 | 0 | 8.8529 | 52.5 | 654.0177 | 3000 | 15.819 | 3015.819 | 2404.7799 | 0 | 140.367
0 | 31.57 | 0 | 0 | 0 | 0 | 20.93 | 52.5 | 674.9477 | 3000 | 37.3991 | 3037.3991 | 2593.9902 | 0 | 164.1477
0 | 35.9198 | 0 | 0 | 0 | 0 | -35.9198 | 0 | 639.0279 | 0 | 0 | 0 | 0 | 210.8896 | 0
0 | 25.2131 | 0 | 0 | 0 | 0 | 27.2869 | 52.5 | 666.3148 | 3000 | 48.7581 | 3048.7581 | 3021.721 | 0 | 194.629
0 | 27.1905 | 0 | 0 | 0 | 0 | 25.3095 | 52.5 | 691.6243 | 3000 | 45.2246 | 3045.2246 | 3045.2246 | 0 | 177.293
0 | 27.6369 | 0 | 0 | 0 | 0 | 24.8631 | 52.5 | 716.4874 | 3000 | 44.4271 | 3044.4271 | 3044.4271 | 0 | 167.413
0 | 23.7851 | 0 | 0 | 0 | 0 | 28.7149 | 52.5 | 745.2023 | 3000 | 51.3097 | 3051.3097 | 3051.3097 | 0 | 143.6862
0 | 28.2094 | 0 | 0 | 0 | 0 | 24.2906 | 52.5 | 769.493 | 3000 | 43.4042 | 3043.4042 | 3043.4042 | 0 | 132.3881
0 | 27.3746 | 0 | 0 | 0 | 0 | 25.1254 | 52.5 | 794.6184 | 3000 | 44.8958 | 3044.8958 | 3044.8958 | 0 | 126.3632
0 | 26.3373 | 0 | 0 | 0 | 0 | 26.1627 | 52.5 | 820.7811 | 3000 | 46.7493 | 3046.7493 | 3046.7493 | 0 | 120.7731
0 | 29.0654 | 0 | 0 | 0 | 0 | 23.4346 | 52.5 | 844.2157 | 3000 | 41.8746 | 3041.8746 | 3041.8746 | 0 | 118.7244
0 | 21.1074 | 0 | 0 | 0 | 0 | 31.3926 | 52.5 | 875.6083 | 3000 | 56.0944 | 3056.0944 | 3050.6869 | 0 | 119.1598
0 | 34.8792 | 0 | 0 | 0 | 0 | 17.6208 | 52.5 | 893.2291 | 3000 | 31.4861 | 3031.4861 | 3004.449 | 0 | 127.8093
0 | 77.8871 | 0 | 0 | 0 | 0 | -25.3871 | 52.5 | 867.842 | 3000 | 0 | 3000 | 2929.7035 | 0 | 138.1648
0 | 100.0202 | 0 | 0 | 0 | 0 | -47.5202 | 52.5 | 820.3218 | 3000 | 0 | 3000 | 2810.7401 | 0 | 156.6425
0 | 125.2017 | 0 | 0 | 0 | 0 | -72.7017 | 52.5 | 747.6201 | 3000 | 0 | 3000 | 2783.703 | 0 | 161.2042
0 | 124.1778 | 0 | 0 | 0 | 0 | -71.6778 | 52.5 | 675.9423 | 3000 | 0 | 3000 | 2675.5545 | 0 | 146.9682
0 | 66.8391 | 0 | 0 | 0 | 0 | -14.3391 | 52.5 | 661.6032 | 3000 | 0 | 3000 | 2567.406 | 0 | 126.0853
0 | 46.8648 | 0 | 0 | 0 | 0 | 5.6352 | 52.5 | 667.2384 | 3000 | 10.0694 | 3010.0694 | 2469.3269 | 0 | 120.0587
0 | 61.8512 | 0 | 0 | 0 | 0 | -9.3512 | 52.5 | 657.8872 | 3000 | 0 | 3000 | 2459.2575 | 0 | 116.3475
0 | 33.8581 | 0 | 0 | 0 | 0 | 18.6419 | 52.5 | 676.5291 | 3000 | 33.3105 | 3033.3105 | 2276.271 | 0 | 106.9847
0 | 26.3421 | 0 | 0 | 0 | 0 | 26.1579 | 52.5 | 702.6869 | 3000 | 46.7406 | 3046.7406 | 2484.3684 | 0 | 116.7653
0 | 27.7706 | 0 | 0 | 0 | 0 | 24.7294 | 52.5 | 727.4163 | 3000 | 44.1881 | 3044.1881 | 2406.112 | 0 | 114.3625
0 | 54.6286 | 0 | 0 | 0 | 0 | -2.1286 | 52.5 | 725.2878 | 3000 | 0 | 3000 | 2524.1466 | 0 | 122.623
0 | 33.0389 | 0 | 0 | 0 | 0 | 19.4611 | 52.5 | 744.7488 | 3000 | 34.7743 | 3034.7743 | 2218.2531 | 0 | 112.5985
0 | 50.6022 | 0 | 0 | 0 | 0 | 1.8978 | 52.5 | 746.6467 | 3000 | 3.3912 | 3003.3912 | 2673.5383 | 0 | 154.3968
0 | 51.4047 | 0 | 0 | 0 | 0 | 1.0953 | 52.5 | 747.742 | 3000 | 1.9571 | 3001.9571 | 2774.8453 | 0 | 184.8602
0 | 30.5809 | 0 | 0 | 0 | 0 | -30.5809 | 0 | 717.1611 | 0 | 0 | 0 | 0 | 32.4446 | 0
0 | 31.9952 | 0 | 0 | 0 | 0 | 20.5048 | 52.5 | 737.6659 | 3000 | 36.6393 | 3036.6393 | 3036.6393 | 0 | 211.3501
0 | 28.3854 | 0 | 0 | 0 | 0 | 24.1146 | 52.5 | 761.7805 | 3000 | 43.0896 | 3043.0896 | 3043.0896 | 0 | 190.68
0 | 30.0901 | 0 | 0 | 0 | 0 | 22.4099 | 52.5 | 784.1904 | 3000 | 40.0435 | 3040.0435 | 3040.0435 | 0 | 171.4585
0 | 225.4308 | 0 | 0 | 0 | 0 | -172.9308 | 52.5 | 611.2595 | 3000 | 0 | 3000 | 3000 | 0 | 166.14
0 | 23.2696 | 0 | 0 | 0 | 0 | 29.2304 | 52.5 | 640.4899 | 3000 | 52.2308 | 3052.2308 | 3052.2308 | 0 | 149.7119
0 | 24.7776 | 0 | 0 | 0 | 0 | 27.7224 | 52.5 | 668.2123 | 3000 | 49.5362 | 3049.5362 | 3049.5362 | 0 | 144.731
0 | 31.0904 | 0 | 0 | 0 | 0 | 21.4096 | 52.5 | 689.6219 | 3000 | 38.2561 | 3038.2561 | 3038.2561 | 0 | 146.2616
0 | 47.4439 | 0 | 0 | 0 | 0 | 5.0561 | 52.5 | 694.678 | 3000 | 9.0346 | 3009.0346 | 2971.1826 | 0 | 139.913
0 | 107.2309 | 0 | 0 | 0 | 0 | -54.7309 | 52.5 | 639.9471 | 3000 | 0 | 3000 | 2826.9624 | 0 | 134.0263
0 | 103.9127 | 0 | 0 | 0 | 0 | -51.4127 | 52.5 | 588.5343 | 3000 | 0 | 3000 | 2594.4431 | 0 | 132.6279
0 | 112.4158 | 0 | 0 | 0 | 0 | -59.9158 | 52.5 | 528.6185 | 3000 | 0 | 3000 | 2226.7382 | 0 | 129.2399
0 | 136.1435 | 0 | 0 | 0 | 0 | -83.6435 | 52.5 | 444.975 | 3000 | 0 | 3000 | 2156.4417 | 0 | 142.6917
0 | 91.2104 | 0 | 0 | 0 | 0 | -38.7104 | 52.5 | 406.2645 | 3000 | 0 | 3000 | 1934.7372 | 0 | 117.6707
0 | 93.5102 | 0 | 0 | 0 | 0 | -41.0102 | 52.5 | 365.2544 | 3000 | 0 | 3000 | 1534.5878 | 0 | 80.1208
0 | 122.1647 | 0 | 0 | 0 | 0 | -69.6647 | 52.5 | 295.5897 | 3000 | 0 | 3000 | 1421.0318 | 0 | 68.7637
0 | 100.7609 | 0 | 0 | 0 | 0 | -48.2609 | 52.5 | 247.3288 | 3000 | 0 | 3000 | 1534.5878 | 0 | 69.1946
0 | 48.5776 | 0 | 0 | 0 | 0 | 3.9224 | 52.5 | 251.2512 | 3000 | 7.0088 | 3007.0088 | 1341.5218 | 0 | 57.283
0 | 43.6955 | 0 | 0 | 0 | 0 | 8.8045 | 52.5 | 260.0557 | 3000 | 15.7324 | 3015.7324 | 1550.3202 | 0 | 65.222
0 | 42.0141 | 0 | 0 | 0 | 0 | 10.4859 | 52.5 | 270.5416 | 3000 | 18.7369 | 3018.7369 | 2369.8459 | 0 | 100.0312
0 | 39.6236 | 0 | 0 | 0 | 0 | 12.8764 | 52.5 | 283.418 | 3000 | 23.0084 | 3023.0084 | 2887.8227 | 0 | 125.8224
0 | 49.0809 | 0 | 0 | 0 | 0 | 3.4191 | 52.5 | 286.8371 | 3000 | 6.1096 | 3006.1096 | 2843.8868 | 0 | 131.5866
0 | 60.3114 | 0 | 0 | 0 | 0 | -7.8114 | 52.5 | 279.0257 | 3000 | 0 | 3000 | 2935.1109 | 0 | 158.4666
0 | 34.6119 | 0 | 0 | 0 | 0 | 17.8881 | 52.5 | 296.9138 | 3000 | 31.9636 | 3031.9636 | 2983.2968 | 0 | 167.8999
0 | 27.8641 | 0 | 0 | 0 | 0 | 24.6359 | 52.5 | 321.5497 | 3000 | 44.0211 | 3044.0211 | 3022.3914 | 0 | 166.4431
0 | 33.0486 | 0 | 0 | 0 | 0 | 19.4514 | 52.5 | 341.0011 | 3000 | 34.7571 | 3034.7571 | 3034.7571 | 0 | 142.6943
0 | 32.3529 | 0 | 0 | 0 | 0 | 20.1471 | 52.5 | 361.1482 | 3000 | 36.0002 | 3036.0002 | 3036.0002 | 0 | 136.7414
0 | 26.9459 | 0 | 0 | 0 | 0 | 25.5541 | 52.5 | 386.7023 | 3000 | 45.6618 | 3045.6618 | 3045.6618 | 0 | 133.4
0 | 26.7567 | 0 | 0 | 0 | 0 | 25.7433 | 52.5 | 412.4456 | 3000 | 45.9998 | 3045.9998 | 3045.9998 | 0 | 175.4496
0 | 36.3011 | 0 | 0 | 0 | 0 | 16.1989 | 52.5 | 428.6445 | 3000 | 28.9453 | 3028.9453 | 3028.9453 | 0 | 151.4473
0 | 26.7721 | 0 | 0 | 0 | 0 | 25.7279 | 52.5 | 454.3724 | 3000 | 45.9723 | 3045.9723 | 3045.9723 | 0 | 128.2354
0 | 33.648 | 0 | 0 | 0 | 0 | 18.852 | 52.5 | 473.2244 | 3000 | 33.686 | 3033.686 | 3033.686 | 0 | 130.7519
0 | 33.0121 | 0 | 0 | 0 | 0 | 19.4879 | 52.5 | 492.7123 | 3000 | 34.8223 | 3034.8223 | 3029.4149 | 0 | 127.5384
0 | 67.0364 | 0 | 0 | 0 | 0 | -14.5364 | 52.5 | 478.1759 | 3000 | 0 | 3000 | 2978.3703 | 0 | 120.624
0 | 59.5147 | 0 | 0 | 0 | 0 | -7.0147 | 52.5 | 471.1611 | 3000 | 0 | 3000 | 2929.7035 | 0 | 112.7936
0 | 26.4023 | 0 | 0 | 0 | 0 | 26.0977 | 52.5 | 497.2589 | 3000 | 46.6332 | 3046.6332 | 2933.0772 | 0 | 123.4826
0 | 44.0966 | 0 | 0 | 0 | 0 | 8.4034 | 52.5 | 505.6623 | 3000 | 15.0158 | 3015.0158 | 2869.0153 | 0 | 123.6546
0 | 44.1806 | 0 | 0 | 0 | 0 | 8.3194 | 52.5 | 513.9817 | 3000 | 14.8657 | 3014.8657 | 2879.68 | 0 | 129.2976
0 | 51.8312 | 0 | 0 | 0 | 0 | 0.66878 | 52.5 | 514.6505 | 3000 | 1.195 | 3001.195 | 2887.6391 | 0 | 122.4359
0 | 51.6351 | 0 | 0 | 0 | 0 | 0.86494 | 52.5 | 515.5154 | 3000 | 1.5455 | 3001.5455 | 2677.1 | 0 | 110.2965
0 | 36.6206 | 0 | 0 | 0 | 0 | 15.8794 | 52.5 | 531.3948 | 3000 | 28.3743 | 3028.3743 | 2466.0021 | 0 | 92.7217
0 | 46.3276 | 0 | 0 | 0 | 0 | 6.1724 | 52.5 | 537.5672 | 3000 | 11.0292 | 3011.0292 | 2659.5466 | 0 | 101.5947
0 | 46.0903 | 0 | 0 | 0 | 0 | 6.4097 | 52.5 | 543.9769 | 3000 | 11.4533 | 3011.4533 | 2827.6009 | 0 | 99.2488
0 | 54.0052 | 0 | 0 | 0 | 0 | -1.5052 | 52.5 | 542.4717 | 3000 | 0 | 3000 | 2713.4065 | 0 | 85.4723
0 | 44.0114 | 0 | 0 | 0 | 0 | 8.4886 | 52.5 | 550.9603 | 3000 | 15.168 | 3015.168 | 2252.721 | 0 | 69.8344
0 | 41.97 | 0 | 0 | 0 | 0 | 10.53 | 52.5 | 561.4902 | 3000 | 18.8156 | 3018.8156 | 2418.5914 | 0 | 99.8878
0 | 35.0925 | 0 | 0 | 0 | 0 | 17.4075 | 52.5 | 578.8977 | 3000 | 31.1049 | 3031.1049 | 2706.6594 | 0 | 112.8677
0 | 49.5585 | 0 | 0 | 0 | 0 | 2.9415 | 52.5 | 581.8393 | 3000 | 5.2561 | 3005.2561 | 2810.5888 | 0 | 114.672
0 | 29.6558 | 0 | 0 | 0 | 0 | 22.8442 | 52.5 | 604.6835 | 3000 | 40.8196 | 3040.8196 | 3008.375 | 0 | 150.1179
0 | 31.3391 | 0 | 0 | 0 | 0 | 21.1609 | 52.5 | 625.8444 | 3000 | 37.8118 | 3037.8118 | 3037.8118 | 0 | 164.0418
0 | 28.4209 | 0 | 0 | 0 | 0 | 24.0791 | 52.5 | 649.9235 | 3000 | 43.0261 | 3043.0261 | 3043.0261 | 0 | 191.7106
0 | 24.9064 | 0 | 0 | 0 | 0 | 27.5936 | 52.5 | 677.5171 | 3000 | 49.3061 | 3049.3061 | 3049.3061 | 0 | 170.7611
0 | 26.987 | 0 | 0 | 0 | 0 | 25.513 | 52.5 | 703.0301 | 3000 | 45.5883 | 3045.5883 | 3045.5883 | 0 | 130.0466
0 | 27.9988 | 0 | 0 | 0 | 0 | 24.5012 | 52.5 | 727.5312 | 3000 | 43.7803 | 3043.7803 | 3043.7803 | 0 | 146.832
0 | 221.0422 | 0 | 0 | 0 | 0 | -168.5422 | 52.5 | 558.989 | 3000 | 0 | 3000 | 3000 | 0 | 154.29
0 | 17.4639 | 0 | 0 | 0 | 0 | 35.0361 | 52.5 | 594.0252 | 3000 | 62.6049 | 3062.6049 | 3062.6049 | 0 | 162.5937
0 | 26.3249 | 0 | 0 | 0 | 0 | 26.1751 | 52.5 | 620.2003 | 3000 | 46.7714 | 3046.7714 | 3014.3269 | 0 | 135.6447
0 | 23.5313 | 0 | 0 | 0 | 0 | 28.9687 | 52.5 | 649.1689 | 3000 | 51.7631 | 3051.7631 | 2862.5033 | 0 | 122.2289
0 | 32.0481 | 0 | 0 | 0 | 0 | 20.4519 | 52.5 | 669.6208 | 3000 | 36.5447 | 3036.5447 | 2668.8398 | 0 | 91.6746
0 | 21.8429 | 0 | 0 | 0 | 0 | 30.6571 | 52.5 | 700.2779 | 3000 | 54.7802 | 3054.7802 | 2487.0006 | 0 | 99.48
0 | 50.5488 | 0 | 0 | 0 | 0 | 1.9512 | 52.5 | 702.2291 | 3000 | 3.4865 | 3003.4865 | 2138.2985 | 0 | 88.8891
0 | 36.57 | 0 | 0 | 0 | 0 | 15.93 | 52.5 | 718.1591 | 3000 | 28.4648 | 3028.4648 | 1887.4981 | 0 | 85.4848
0 | 21.3533 | 0 | 0 | 0 | 0 | 31.1467 | 52.5 | 749.3058 | 3000 | 58.1717 | 3058.1717 | 1754.9822 | 0 | 79.1497
0 | 40.6071 | 0 | 0 | 0 | 0 | 11.8929 | 52.5 | 761.1987 | 3000 | 21.251 | 3021.251 | 1658.5798 | 0 | 70.755
0 | 28.1568 | 0 | 0 | 0 | 0 | 24.3432 | 52.5 | 785.5419 | 3000 | 44.8842 | 3044.8842 | 1390.2121 | 0 | 62.4205
0 | 34.4218 | 0 | 0 | 0 | 0 | 18.0782 | 52.5 | 803.6201 | 3000 | 32.3033 | 3032.3033 | 1534.4466 | 0 | 58.9227
0 | 38.6581 | 0 | 0 | 0 | 0 | 13.8419 | 52.5 | 817.462 | 3000 | 24.7336 | 3024.7336 | 1678.2847 | 0 | 56.1722
0 | 38.5624 | 0 | 0 | 0 | 0 | 13.9376 | 52.5 | 831.3996 | 3000 | 24.9046 | 3024.9046 | 2078.6052 | 0 | 68.4693
0 | 46.2937 | 0 | 0 | 0 | 0 | 6.2063 | 52.5 | 837.6059 | 3000 | 11.0898 | 3011.0898 | 2486.5696 | 0 | 108.1409
0 | 31.1307 | 0 | 0 | 0 | 0 | 21.3693 | 52.5 | 858.9752 | 3000 | 38.1842 | 3038.1842 | 2794.85 | 0 | 148.5183
0 | 50.574 | 0 | 0 | 0 | 0 | 1.926 | 52.5 | 860.9012 | 3000 | 3.4415 | 3003.4415 | 2922.3301 | 0 | 171.8622
0 | 41.8877 | 0 | 0 | 0 | 0 | 10.6123 | 52.5 | 871.5135 | 3000 | 18.9628 | 3018.9628 | 2991.9256 | 0 | 190.7951
0 | 29.5681 | 0 | 0 | 0 | 0 | -29.5681 | 0 | 841.9454 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 31.4787 | 0 | 0 | 0 | 0 | -31.4787 | 0 | 810.4666 | 0 | 0 | 0 | 0 | 0 | 0
0 | 27.5133 | 0 | 0 | 0 | 0 | 24.9867 | 52.5 | 835.4533 | 3000 | 44.6479 | 3044.6479 | 3044.6479 | 0 | 171.9922
0 | 29.1241 | 0 | 0 | 0 | 0 | 23.3759 | 52.5 | 858.8292 | 3000 | 41.7696 | 3041.7696 | 3041.7696 | 0 | 153.9135
0 | 33.6987 | 0 | 0 | 0 | 0 | 18.8013 | 52.5 | 877.6305 | 3000 | 33.5955 | 3033.5955 | 3033.5955 | 0 | 146.5833
0 | 33.1043 | 0 | 0 | 0 | 0 | 19.3957 | 52.5 | 897.0262 | 3000 | 34.6575 | 3034.6575 | 3034.6575 | 0 | 133.0394
0 | 26.7437 | 0 | 0 | 0 | 0 | 25.7563 | 52.5 | 922.7825 | 3000 | 46.023 | 3046.023 | 3046.023 | 0 | 130.3089
0 | 21.0322 | 0 | 0 | 0 | 0 | 31.4678 | 52.5 | 954.2503 | 3000 | 56.2288 | 3056.2288 | 3056.2288 | 0 | 128.3616
0 | 30.4131 | 0 | 0 | 0 | 0 | 22.0869 | 52.5 | 976.3372 | 3000 | 39.4664 | 3039.4664 | 3023.2441 | 0 | 127.0065
0 | 236.305 | 0 | 0 | 0 | 0 | -183.805 | 52.5 | 792.5322 | 3000 | 0 | 3000 | 2864.8144 | 0 | 116.9704
0 | 28.779 | 0 | 0 | 0 | 0 | 23.721 | 52.5 | 816.2531 | 3000 | 42.3862 | 3042.3862 | 2658.459 | 0 | 111.2299
0 | 27.4862 | 0 | 0 | 0 | 0 | 25.0138 | 52.5 | 841.267 | 3000 | 44.6964 | 3044.6964 | 2444.4722 | 0 | 110.0746
0 | 38.007 | 0 | 0 | 0 | 0 | 14.493 | 52.5 | 855.7599 | 3000 | 25.897 | 3025.897 | 2225.5981 | 0 | 108.0305
0 | 36.3029 | 0 | 0 | 0 | 0 | 16.1971 | 52.5 | 871.957 | 3000 | 28.942 | 3028.942 | 1741.9748 | 0 | 79.9915
0 | 39.0213 | 0 | 0 | 0 | 0 | 13.4787 | 52.5 | 885.4357 | 3000 | 24.0847 | 3024.0847 | 1574.8947 | 0 | 70.9648
0 | 57.9904 | 0 | 0 | 0 | 0 | -5.4904 | 52.5 | 879.9453 | 3000 | 0 | 3000 | 1399.4021 | 0 | 62.3434
0 | 41.4674 | 0 | 0 | 0 | 0 | 11.0326 | 52.5 | 890.9779 | 3000 | 19.7138 | 3019.7138 | 1456.9679 | 0 | 63.6549
0 | 42.1317 | 0 | 0 | 0 | 0 | 10.3683 | 52.5 | 901.3461 | 3000 | 18.5267 | 3018.5267 | 1434.1511 | 0 | 61.7115
0 | 44.3375 | 0 | 0 | 0 | 0 | 8.1625 | 52.5 | 909.5086 | 3000 | 14.5853 | 3014.5853 | 2068.2858 | 0 | 87.4885
0 | 49.9971 | 0 | 0 | 0 | 0 | 2.5029 | 52.5 | 912.0115 | 3000 | 4.4723 | 3004.4723 | 2085.21 | 0 | 88.5172
0 | 35.1343 | 0 | 0 | 0 | 0 | 17.3657 | 52.5 | 929.3772 | 3000 | 31.0302 | 3031.0302 | 2555.1768 | 0 | 110.077
0 | 42.0496 | 0 | 0 | 0 | 0 | 10.4504 | 52.5 | 939.8276 | 3000 | 18.6735 | 3018.6735 | 2445.4865 | 0 | 112.957
0 | 40.273 | 0 | 0 | 0 | 0 | 12.227 | 52.5 | 952.0546 | 3000 | 21.848 | 3021.848 | 2843.4029 | 0 | 146.4921
0 | 46.8537 | 0 | 0 | 0 | 0 | 5.6463 | 52.5 | 957.7009 | 3000 | 10.0891 | 3010.0891 | 3004.6817 | 0 | 165.2575
0 | 28.7741 | 0 | 0 | 0 | 0 | 23.7259 | 52.5 | 981.4267 | 3000 | 42.395 | 3042.395 | 3031.5801 | 0 | 169.8897
0 | 27.3437 | 0 | 0 | 0 | 0 | 25.1563 | 52.5 | 1006.583 | 3000 | 44.9509 | 3044.9509 | 3044.9509 | 0 | 167.1678
0 | 24.375 | 0 | 0 | 0 | 0 | 28.125 | 52.5 | 1034.708 | 3000 | 50.2556 | 3050.2556 | 3050.2556 | 0 | 167.7641
0 | 29.9671 | 0 | 0 | 0 | 0 | 22.5329 | 52.5 | 1057.2408 | 3000 | 40.2632 | 3040.2632 | 3040.2632 | 0 | 152.1956
0 | 34.4735 | 0 | 0 | 0 | 0 | 18.0265 | 52.5 | 1075.2674 | 3000 | 32.211 | 3032.211 | 3032.211 | 0 | 177.8392
0 | 33.5026 | 0 | 0 | 0 | 0 | 18.9974 | 52.5 | 1094.2648 | 3000 | 33.9458 | 3033.9458 | 3033.9458 | 0 | 134.1307
0 | 25.8952 | 0 | 0 | 0 | 0 | 26.6048 | 52.5 | 1120.8695 | 3000 | 47.5392 | 3047.5392 | 3047.5392 | 0 | 131.8975
0 | 27.5836 | 0 | 0 | 0 | 0 | 24.9164 | 52.5 | 1145.7859 | 3000 | 44.5223 | 3044.5223 | 3044.5223 | 0 | 128.2962
0 | 40.8063 | 0 | 0 | 0 | 0 | 11.6937 | 52.5 | 1157.4796 | 3000 | 20.8951 | 3020.8951 | 3015.4876 | 0 | 125.2332
0 | 79.9373 | 0 | 0 | 0 | 0 | -27.4373 | 52.5 | 1130.0423 | 3000 | 0 | 3000 | 2962.148 | 0 | 130.7196
0 | 116.3777 | 0 | 0 | 0 | 0 | -63.8777 | 52.5 | 1066.1646 | 3000 | 0 | 3000 | 2962.148 | 0 | 169.7903
0 | 107.3291 | 0 | 0 | 0 | 0 | -54.8291 | 52.5 | 1011.3355 | 3000 | 0 | 3000 | 2805.3327 | 0 | 174.127
0 | 94.9107 | 0 | 0 | 0 | 0 | -42.4107 | 52.5 | 968.9248 | 3000 | 0 | 3000 | 2735.0362 | 0 | 184.3688
0 | 52.2568 | 0 | 0 | 0 | 0 | 0.24318 | 52.5 | 969.168 | 3000 | 0.43453 | 3000.4345 | 2513.7663 | 0 | 163.4702
0 | 51.8283 | 0 | 0 | 0 | 0 | 0.6717 | 52.5 | 969.8397 | 3000 | 1.2002 | 3001.2002 | 2200.9013 | 0 | 147.9446
0 | 90.4193 | 0 | 0 | 0 | 0 | -37.9193 | 52.5 | 931.9203 | 3000 | 0 | 3000 | 1529.1803 | 0 | 104.5501
0 | 47.7366 | 0 | 0 | 0 | 0 | 4.7634 | 52.5 | 936.6838 | 3000 | 8.5116 | 3008.5116 | 1591.7662 | 0 | 99.2944
0 | 68.6866 | 0 | 0 | 0 | 0 | -16.1866 | 52.5 | 920.4972 | 3000 | 0 | 3000 | 1653.5511 | 0 | 100.4036
0 | 43.0419 | 0 | 0 | 0 | 0 | 9.4581 | 52.5 | 929.9553 | 3000 | 16.9004 | 3016.9004 | 1659.6366 | 0 | 99.5782
0 | 34.7634 | 0 | 0 | 0 | 0 | 17.7366 | 52.5 | 947.6919 | 3000 | 31.693 | 3031.693 | 1955.6154 | 0 | 119.6641
0 | 37.4477 | 0 | 0 | 0 | 0 | 15.0523 | 52.5 | 962.7443 | 3000 | 26.8965 | 3026.8965 | 2048.1526 | 0 | 131.3275
0 | 58.8117 | 0 | 0 | 0 | 0 | -49.0649 | 9.7469 | 913.6794 | 556.9648 | 0 | 556.9648 | 0 | 0 | 0
0 | 38.7773 | 0 | 0 | 0 | 0 | -33.3834 | 5.3939 | 880.296 | 308.2232 | 0 | 308.2232 | 0 | 0 | 0
0 | 39.0998 | 0 | 0 | 0 | 0 | -39.0998 | 0 | 841.1962 | 0 | 0 | 0 | 0 | 86.5188 | 0
0 | 71.8801 | 0 | 0 | 0 | 0 | -19.3801 | 52.5 | 821.8161 | 3000 | 0 | 3000 | 2972.9629 | 0 | 205.1344
0 | 94.2698 | 0 | 0 | 0 | 0 | -41.7698 | 52.5 | 780.0462 | 3000 | 0 | 3000 | 3000 | 0 | 198.75
0 | 95.4344 | 0 | 0 | 0 | 0 | -42.9344 | 52.5 | 737.1118 | 3000 | 0 | 3000 | 3000 | 0 | 183.3
0 | 27.8682 | 0 | 0 | 0 | 0 | 24.6318 | 52.5 | 761.7435 | 3000 | 44.0137 | 3044.0137 | 3044.0137 | 0 | 170.2517
0 | 28.7208 | 0 | 0 | 0 | 0 | 23.7792 | 52.5 | 785.5227 | 3000 | 42.4903 | 3042.4903 | 3042.4903 | 0 | 160.3088
0 | 23.6741 | 0 | 0 | 0 | 0 | 28.8259 | 52.5 | 814.3486 | 3000 | 51.508 | 3051.508 | 3051.508 | 0 | 154.5589
0 | 21.9597 | 0 | 0 | 0 | 0 | 30.5403 | 52.5 | 844.8889 | 3000 | 54.5714 | 3054.5714 | 3054.5714 | 0 | 147.9329
0 | 27.9857 | 0 | 0 | 0 | 0 | 24.5143 | 52.5 | 869.4031 | 3000 | 43.8037 | 3043.8037 | 3043.8037 | 0 | 146.2243
0 | 38.4724 | 0 | 0 | 0 | 0 | 14.0276 | 52.5 | 883.4308 | 3000 | 25.0655 | 3025.0655 | 3003.4358 | 0 | 143.0837
0 | 52.0726 | 0 | 0 | 0 | 0 | 0.42744 | 52.5 | 883.8582 | 3000 | 0.76377 | 3000.7638 | 2914.245 | 0 | 144.9545
0 | 126.2288 | 0 | 0 | 0 | 0 | -73.7288 | 52.5 | 810.1294 | 3000 | 0 | 3000 | 2707.999 | 0 | 166.9752
0 | 112.4821 | 0 | 0 | 0 | 0 | -102.5459 | 9.9361 | 707.5834 | 567.7796 | 0 | 567.7796 | 0 | 0 | 0
0 | 65.6407 | 0 | 0 | 0 | 0 | -53.7173 | 11.9234 | 653.8662 | 681.3356 | 0 | 681.3356 | 0 | 0 | 0
0 | 92.117 | 0 | 0 | 0 | 0 | -79.0581 | 13.0589 | 574.8081 | 746.2247 | 0 | 746.2247 | 0 | 0 | 0
0 | 85.5771 | 0 | 0 | 0 | 0 | -33.0771 | 52.5 | 541.731 | 3000 | 0 | 3000 | 2864.8144 | 0 | 192.8307
0 | 31.1031 | 0 | 0 | 0 | 0 | 21.3969 | 52.5 | 563.1279 | 3000 | 38.2334 | 3038.2334 | 2946.3071 | 0 | 193.101
0 | 35.8016 | 0 | 0 | 0 | 0 | 16.6984 | 52.5 | 579.8263 | 3000 | 29.8378 | 3029.8378 | 2927.0967 | 0 | 178.4944
0 | 39.4885 | 0 | 0 | 0 | 0 | 13.0115 | 52.5 | 592.8378 | 3000 | 23.2498 | 3023.2498 | 2936.731 | 0 | 170.0661
0 | 43.9611 | 0 | 0 | 0 | 0 | 8.5389 | 52.5 | 601.3767 | 3000 | 15.2579 | 3015.2579 | 2631.3307 | 0 | 142.2234
0 | 48.6892 | 0 | 0 | 0 | 0 | 3.8108 | 52.5 | 605.1875 | 3000 | 6.8094 | 3006.8094 | 2233.5476 | 0 | 109.6449
0 | 44.0043 | 0 | 0 | 0 | 0 | 8.4957 | 52.5 | 613.6832 | 3000 | 15.1807 | 3015.1807 | 2052.659 | 0 | 102.4277
0 | 33.1424 | 0 | 0 | 0 | 0 | 19.3576 | 52.5 | 633.0407 | 3000 | 34.5894 | 3034.5894 | 2342.439 | 0 | 133.847
0 | 59.8953 | 0 | 0 | 0 | 0 | -7.3953 | 52.5 | 625.6454 | 3000 | 0 | 3000 | 2605.258 | 0 | 165.4339
0 | 97.5381 | 0 | 0 | 0 | 0 | -45.0381 | 52.5 | 580.6073 | 3000 | 0 | 3000 | 2756.6659 | 0 | 183.1529
0 | 86.8164 | 0 | 0 | 0 | 0 | -34.3164 | 52.5 | 546.2909 | 3000 | 0 | 3000 | 2956.7406 | 0 | 193.8439
0 | 107.2753 | 0 | 0 | 0 | 0 | -54.7753 | 52.5 | 491.5156 | 3000 | 0 | 3000 | 3000 | 0 | 188.1
0 | 70.5421 | 0 | 0 | 0 | 0 | -18.0421 | 52.5 | 473.4735 | 3000 | 0 | 3000 | 3000 | 0 | 178.92
0 | 65.9281 | 0 | 0 | 0 | 0 | -13.4281 | 52.5 | 460.0454 | 3000 | 0 | 3000 | 3000 | 0 | 161.1
0 | 60.0061 | 0 | 0 | 0 | 0 | -7.5061 | 52.5 | 452.5393 | 3000 | 0 | 3000 | 3000 | 0 | 134.34
0 | 109.8183 | 0 | 0 | 0 | 0 | -57.3183 | 52.5 | 395.221 | 3000 | 0 | 3000 | 3000 | 0 | 130.02
0 | 57.3196 | 0 | 0 | 0 | 0 | -4.8196 | 52.5 | 390.4014 | 3000 | 0 | 3000 | 3000 | 0 | 126.96
0 | 21.6144 | 0 | 0 | 0 | 0 | 30.8856 | 52.5 | 421.287 | 3000 | 55.1884 | 3055.1884 | 3055.1884 | 0 | 129.3872
0 | 27.978 | 0 | 0 | 0 | 0 | 24.522 | 52.5 | 445.809 | 3000 | 43.8175 | 3043.8175 | 2995.1507 | 0 | 127.1441
0 | 37.6333 | 0 | 0 | 0 | 0 | 14.8667 | 52.5 | 460.6756 | 3000 | 26.5648 | 3026.5648 | 2794.0455 | 0 | 123.2174
0 | 277.6479 | 0 | 0 | 0 | 0 | -225.1479 | 52.5 | 235.5278 | 3000 | 0 | 3000 | 2578.2208 | 0 | 132.9331
0 | 85.7523 | 0 | 0 | 0 | 0 | -33.2523 | 52.5 | 202.2754 | 3000 | 0 | 3000 | 2378.1461 | 0 | 143.4498
0 | 71.3766 | 0 | 0 | 0 | 0 | -18.8766 | 52.5 | 183.3989 | 3000 | 0 | 3000 | 2313.257 | 0 | 137.6157
0 | 86.4753 | 0 | 0 | 0 | 0 | -33.9753 | 52.5 | 149.4236 | 3000 | 0 | 3000 | 1934.7372 | 0 | 99.4842
0 | 201.9236 | 0 | 0 | 0 | 0 | -149.4236 | 52.5 | 0 | 3000 | 0 | 3000 | 1875.2556 | 0 | 89.8247
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1594.0694 | 0 | 72.0201
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1977.9966 | 0 | 85.8846
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1869.8481 | 0 | 81.6376
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1826.5887 | 0 | 80.0959
0 | 40.1606 | 0 | 0 | 0 | 0 | 12.3394 | 52.5 | 12.3394 | 3000 | 22.0488 | 3022.0488 | 2189.3053 | 0 | 98.4093
0 | 42.3149 | 0 | 0 | 0 | 0 | 10.1851 | 52.5 | 22.5244 | 3000 | 18.1994 | 3018.1994 | 2618.0499 | 0 | 120.7183
0 | 46.3908 | 0 | 0 | 0 | 0 | 6.1092 | 52.5 | 28.6337 | 3000 | 10.9164 | 3010.9164 | 2421.507 | 0 | 117.879
0 | 46.1155 | 0 | 0 | 0 | 0 | 6.3845 | 52.5 | 35.0181 | 3000 | 11.4082 | 3011.4082 | 2741.0369 | 0 | 174.6315
0 | 35.0181 | 0 | 0 | 0 | 0 | -35.0181 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5188 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.0371 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 187.68
0 | 48.2545 | 0 | 0 | 0 | 0 | 4.2455 | 52.5 | 4.2455 | 3000 | 7.5861 | 3007.5861 | 3007.5861 | 0 | 168.515
0 | 40.4504 | 0 | 0 | 0 | 0 | 12.0496 | 52.5 | 16.2951 | 3000 | 21.5311 | 3021.5311 | 3021.5311 | 0 | 146.363
0 | 68.7951 | 0 | 0 | 0 | 0 | -16.2951 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 134.34
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 129.66
0 | 21.0403 | 0 | 0 | 0 | 0 | 31.4597 | 52.5 | 31.4597 | 3000 | 56.2144 | 3056.2144 | 3056.2144 | 0 | 131.3561
0 | 22.5944 | 0 | 0 | 0 | 0 | 29.9056 | 52.5 | 61.3653 | 3000 | 53.4373 | 3053.4373 | 3020.9928 | 0 | 129.8725
0 | 30.3718 | 0 | 0 | 0 | 0 | 22.1282 | 52.5 | 83.4936 | 3000 | 39.5402 | 3039.5402 | 2834.0581 | 0 | 126.2573
0 | 32.2804 | 0 | 0 | 0 | 0 | 20.2196 | 52.5 | 103.7131 | 3000 | 36.1297 | 3036.1297 | 2738.7213 | 0 | 148.603
0 | 21.5424 | 0 | 0 | 0 | 0 | 30.9576 | 52.5 | 134.6707 | 3000 | 55.3171 | 3055.3171 | 2563.2414 | 0 | 171.404
0 | 50.8983 | 0 | 0 | 0 | 0 | -41.7192 | 9.1791 | 92.9516 | 524.5202 | 0 | 524.5202 | 0 | 0 | 0
0 | 33.2445 | 0 | 0 | 0 | 0 | 19.2555 | 52.5 | 112.2071 | 3000 | 34.407 | 3034.407 | 2293.5898 | 0 | 146.8815
0 | 47.4793 | 0 | 0 | 0 | 0 | 5.0207 | 52.5 | 117.2278 | 3000 | 8.9714 | 3008.9714 | 2662.8962 | 0 | 154.2083
0 | 92.1646 | 0 | 0 | 0 | 0 | -39.6646 | 52.5 | 77.5632 | 3000 | 0 | 3000 | 2594.4431 | 0 | 145.3148
0 | 44.6058 | 0 | 0 | 0 | 0 | 7.8942 | 52.5 | 85.4575 | 3000 | 14.106 | 3014.106 | 2219.2145 | 0 | 110.7388
0 | 40.7558 | 0 | 0 | 0 | 0 | 11.7442 | 52.5 | 97.2017 | 3000 | 20.9853 | 3020.9853 | 1804.3146 | 0 | 86.6432
0 | 50.6899 | 0 | 0 | 0 | 0 | 1.8101 | 52.5 | 99.0118 | 3000 | 3.2344 | 3003.2344 | 1678.4152 | 0 | 81.0339
0 | 42.9951 | 0 | 0 | 0 | 0 | 9.5049 | 52.5 | 108.5166 | 3000 | 16.9839 | 3016.9839 | 2005.7954 | 0 | 98.4043
0 | 34.7204 | 0 | 0 | 0 | 0 | 17.7796 | 52.5 | 126.2963 | 3000 | 31.7698 | 3031.7698 | 2382.8788 | 0 | 122.337
0 | 45.2202 | 0 | 0 | 0 | 0 | 7.2798 | 52.5 | 133.576 | 3000 | 13.008 | 3013.008 | 2596.6363 | 0 | 163.0428
0 | 42.8211 | 0 | 0 | 0 | 0 | -37.0487 | 5.7724 | 96.5273 | 329.8529 | 0 | 329.8529 | 0 | 0 | 0
0 | 34.9597 | 0 | 0 | 0 | 0 | -34.9597 | 0 | 61.5676 | 0 | 0 | 0 | 0 | 194.6673 | 0
0 | 28.8081 | 0 | 0 | 0 | 0 | -28.8081 | 0 | 32.7596 | 0 | 0 | 0 | 0 | 54.0743 | 0
0 | 31.6171 | 0 | 0 | 0 | 0 | 20.8829 | 52.5 | 53.6425 | 3000 | 37.315 | 3037.315 | 3037.315 | 0 | 194.6008
0 | 35.0397 | 0 | 0 | 0 | 0 | 17.4603 | 52.5 | 71.1028 | 3000 | 31.1993 | 3031.1993 | 3031.1993 | 0 | 177.2948
0 | 68.4867 | 0 | 0 | 0 | 0 | -15.9867 | 52.5 | 55.1162 | 3000 | 0 | 3000 | 3000 | 0 | 158.82
0 | 105.6587 | 0 | 0 | 0 | 0 | -53.1587 | 52.5 | 1.9575 | 3000 | 0 | 3000 | 3000 | 0 | 144.87
0 | 54.4575 | 0 | 0 | 0 | 0 | -1.9575 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 139.41
0 | 39.2885 | 0 | 0 | 0 | 0 | 13.2115 | 52.5 | 13.2115 | 3000 | 23.6072 | 3023.6072 | 3023.6072 | 0 | 135.8204
0 | 33.6361 | 0 | 0 | 0 | 0 | 18.8639 | 52.5 | 32.0754 | 3000 | 33.7073 | 3033.7073 | 3033.7073 | 0 | 131.2382
0 | 30.3014 | 0 | 0 | 0 | 0 | 22.1986 | 52.5 | 54.274 | 3000 | 39.6659 | 3039.6659 | 3039.6659 | 0 | 129.125
0 | 36.3834 | 0 | 0 | 0 | 0 | 16.1166 | 52.5 | 70.3905 | 3000 | 28.7982 | 3028.7982 | 3007.1685 | 0 | 123.2338
0 | 65.9575 | 0 | 0 | 0 | 0 | -13.4575 | 52.5 | 56.933 | 3000 | 0 | 3000 | 2967.5554 | 0 | 123.6877
0 | 109.433 | 0 | 0 | 0 | 0 | -56.933 | 52.5 | 0 | 3000 | 0 | 3000 | 2908.0738 | 0 | 130.8342
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2853.9995 | 0 | 136.992
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2448.4426 | 0 | 134.6643
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2605.258 | 0 | 141.9866
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2048.2932 | 0 | 128.6328
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1918.515 | 0 | 106.7845
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1393.9947 | 0 | 57.1538
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1794.1442 | 0 | 70.5278
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1934.7372 | 0 | 76.2673
0 | 44.1302 | 0 | 0 | 0 | 0 | 8.3698 | 52.5 | 8.3698 | 3000 | 14.9558 | 3014.9558 | 2301.1756 | 0 | 91.8629
0 | 37.0705 | 0 | 0 | 0 | 0 | 15.4295 | 52.5 | 23.7993 | 3000 | 27.5704 | 3027.5704 | 2421.9388 | 0 | 114.7272
0 | 41.1766 | 0 | 0 | 0 | 0 | 11.3234 | 52.5 | 35.1227 | 3000 | 20.2334 | 3020.2334 | 2684.973 | 0 | 135.1615
0 | 34.5526 | 0 | 0 | 0 | 0 | 17.9474 | 52.5 | 53.0701 | 3000 | 32.0696 | 3032.0696 | 2831.9948 | 0 | 156.0429
0 | 24.1526 | 0 | 0 | 0 | 0 | 28.3474 | 52.5 | 81.4174 | 3000 | 50.653 | 3050.653 | 3029.0233 | 0 | 199.9761
0 | 22.5343 | 0 | 0 | 0 | 0 | 29.9657 | 52.5 | 111.3831 | 3000 | 53.5447 | 3053.5447 | 3053.5447 | 0 | 199.0606
0 | 25.9216 | 0 | 0 | 0 | 0 | 26.5784 | 52.5 | 137.9615 | 3000 | 47.492 | 3047.492 | 3047.492 | 0 | 176.1146
0 | 24.3711 | 0 | 0 | 0 | 0 | 28.1289 | 52.5 | 166.0904 | 3000 | 50.2626 | 3050.2626 | 3050.2626 | 0 | 150.4085
0 | 32.296 | 0 | 0 | 0 | 0 | 20.204 | 52.5 | 186.2944 | 3000 | 36.1018 | 3036.1018 | 3036.1018 | 0 | 137.1407
0 | 38.0922 | 0 | 0 | 0 | 0 | 14.4078 | 52.5 | 200.7022 | 3000 | 25.7449 | 3025.7449 | 3025.7449 | 0 | 131.4081
0 | 25.4865 | 0 | 0 | 0 | 0 | 27.0135 | 52.5 | 227.7157 | 3000 | 48.2695 | 3048.2695 | 3048.2695 | 0 | 138.5743
0 | 30.4873 | 0 | 0 | 0 | 0 | 22.0127 | 52.5 | 249.7284 | 3000 | 39.3337 | 3039.3337 | 3039.3337 | 0 | 130.2354
0 | 35.8835 | 0 | 0 | 0 | 0 | 16.6165 | 52.5 | 266.3449 | 3000 | 29.6915 | 3029.6915 | 3013.4692 | 0 | 129.8805
0 | 70.5091 | 0 | 0 | 0 | 0 | -18.0091 | 52.5 | 248.3357 | 3000 | 0 | 3000 | 2864.8144 | 0 | 122.5854
0 | 92.9656 | 0 | 0 | 0 | 0 | -40.4656 | 52.5 | 207.8701 | 3000 | 0 | 3000 | 2545.7763 | 0 | 112.0905
0 | 113.9884 | 0 | 0 | 0 | 0 | -61.4884 | 52.5 | 146.3817 | 3000 | 0 | 3000 | 2210.5159 | 0 | 107.0111
0 | 117.2883 | 0 | 0 | 0 | 0 | -64.7883 | 52.5 | 81.5934 | 3000 | 0 | 3000 | 1923.9224 | 0 | 91.5787
0 | 67.4848 | 0 | 0 | 0 | 0 | -14.9848 | 52.5 | 66.6086 | 3000 | 0 | 3000 | 1713.0328 | 0 | 79.7417
0 | 50.4463 | 0 | 0 | 0 | 0 | 2.0537 | 52.5 | 68.6623 | 3000 | 3.6697 | 3003.6697 | 1781.5916 | 0 | 77.232
0 | 101.7162 | 0 | 0 | 0 | 0 | -49.2162 | 52.5 | 19.4462 | 3000 | 0 | 3000 | 1664.366 | 0 | 71.5344
0 | 71.9462 | 0 | 0 | 0 | 0 | -19.4462 | 52.5 | 0 | 3000 | 0 | 3000 | 1280.4388 | 0 | 53.9961
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1994.2189 | 0 | 77.615
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2356.5164 | 0 | 96.4522
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1961.7744 | 0 | 83.395
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2091.5526 | 0 | 93.0323
0 | 39.304 | 0 | 0 | 0 | 0 | 13.196 | 52.5 | 13.196 | 3000 | 23.5794 | 3023.5794 | 2769.4304 | 0 | 136.256
0 | 38.1644 | 0 | 0 | 0 | 0 | 14.3356 | 52.5 | 27.5315 | 3000 | 25.6158 | 3025.6158 | 2609.2441 | 0 | 137.6376
0 | 42.6436 | 0 | 0 | 0 | 0 | 9.8564 | 52.5 | 37.3879 | 3000 | 17.6121 | 3017.6121 | 2920.2784 | 0 | 173.5813
0 | 30.109 | 0 | 0 | 0 | 0 | 22.391 | 52.5 | 59.7789 | 3000 | 40.0097 | 3040.0097 | 3007.5651 | 0 | 193.2661
0 | 28.7538 | 0 | 0 | 0 | 0 | 23.7462 | 52.5 | 83.5251 | 3000 | 42.4313 | 3042.4313 | 3042.4313 | 0 | 204.2993
0 | 29.8997 | 0 | 0 | 0 | 0 | 22.6003 | 52.5 | 106.1254 | 3000 | 40.3838 | 3040.3838 | 3040.3838 | 0 | 190.9361
0 | 25.2213 | 0 | 0 | 0 | 0 | 27.2787 | 52.5 | 133.4042 | 3000 | 48.7435 | 3048.7435 | 3048.7435 | 0 | 170.4552
0 | 32.2998 | 0 | 0 | 0 | 0 | 20.2002 | 52.5 | 153.6043 | 3000 | 36.095 | 3036.095 | 3036.095 | 0 | 145.9147
0 | 25.2521 | 0 | 0 | 0 | 0 | 27.2479 | 52.5 | 180.8522 | 3000 | 48.6884 | 3048.6884 | 3048.6884 | 0 | 138.0446
0 | 24.1092 | 0 | 0 | 0 | 0 | 28.3908 | 52.5 | 209.243 | 3000 | 50.7305 | 3050.7305 | 3050.7305 | 0 | 138.8082
0 | 23.1315 | 0 | 0 | 0 | 0 | 29.3685 | 52.5 | 238.6115 | 3000 | 52.4777 | 3052.4777 | 3052.4777 | 0 | 138.7656
0 | 25.3002 | 0 | 0 | 0 | 0 | 27.1998 | 52.5 | 265.8113 | 3000 | 48.6024 | 3048.6024 | 3016.1578 | 0 | 134.2793
0 | 59.0478 | 0 | 0 | 0 | 0 | -6.5478 | 52.5 | 259.2635 | 3000 | 0 | 3000 | 2778.2956 | 0 | 126.9403
0 | 112.7818 | 0 | 0 | 0 | 0 | -60.2818 | 52.5 | 198.9817 | 3000 | 0 | 3000 | 2513.3317 | 0 | 148.8395
0 | 120.7847 | 0 | 0 | 0 | 0 | -68.2847 | 52.5 | 130.697 | 3000 | 0 | 3000 | 2210.5159 | 0 | 145.4519
0 | 139.6144 | 0 | 0 | 0 | 0 | -87.1144 | 52.5 | 43.5826 | 3000 | 0 | 3000 | 1902.2927 | 0 | 121.7848
0 | 96.0826 | 0 | 0 | 0 | 0 | -43.5826 | 52.5 | 0 | 3000 | 0 | 3000 | 1653.5511 | 0 | 89.6059
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1464.2912 | 0 | 72.6874
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1421.0318 | 0 | 69.2043
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1366.9576 | 0 | 66.9673
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1621.1066 | 0 | 81.3147
0 | 51.9377 | 0 | 0 | 0 | 0 | 0.56234 | 52.5 | 0.56234 | 3000 | 1.0048 | 3001.0048 | 1573.4446 | 0 | 78.2946
0 | 46.3695 | 0 | 0 | 0 | 0 | 6.1305 | 52.5 | 6.6928 | 3000 | 10.9543 | 3010.9543 | 1610.4312 | 0 | 81.3268
0 | 51.5646 | 0 | 0 | 0 | 0 | 0.93536 | 52.5 | 7.6282 | 3000 | 1.6714 | 3001.6714 | 2017.52 | 0 | 109.2891
0 | 42.1493 | 0 | 0 | 0 | 0 | 10.3507 | 52.5 | 17.9789 | 3000 | 18.4953 | 3018.4953 | 2434.4934 | 0 | 145.9966
0 | 17.9789 | 0 | 0 | 0 | 0 | -17.9789 | 0 | 0 | 0 | 0 | 0 | 0 | 275.7787 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2228 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.0371 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 24.8912 | 0 | 0 | 0 | 0 | 27.6088 | 52.5 | 27.6088 | 3000 | 49.3332 | 3049.3332 | 3049.3332 | 0 | 188.0524
0 | 35.7015 | 0 | 0 | 0 | 0 | 16.7985 | 52.5 | 44.4072 | 3000 | 30.0167 | 3030.0167 | 3030.0167 | 0 | 163.9239
0 | 25.8582 | 0 | 0 | 0 | 0 | 26.6418 | 52.5 | 71.049 | 3000 | 47.6053 | 3047.6053 | 3047.6053 | 0 | 146.1936
0 | 33.2531 | 0 | 0 | 0 | 0 | 19.2469 | 52.5 | 90.2959 | 3000 | 34.3917 | 3034.3917 | 3034.3917 | 0 | 145.1956
0 | 26.9946 | 0 | 0 | 0 | 0 | 25.5054 | 52.5 | 115.8013 | 3000 | 45.5747 | 3045.5747 | 3045.5747 | 0 | 142.2588
0 | 31.3916 | 0 | 0 | 0 | 0 | 21.1084 | 52.5 | 136.9097 | 3000 | 37.7179 | 3037.7179 | 3037.7179 | 0 | 145.4156
0 | 29.7689 | 0 | 0 | 0 | 0 | 22.7311 | 52.5 | 159.6409 | 3000 | 40.6175 | 3040.6175 | 3018.9878 | 0 | 143.7038
0 | 40.9946 | 0 | 0 | 0 | 0 | 11.5054 | 52.5 | 171.1462 | 3000 | 20.5586 | 3020.5586 | 2896.1878 | 0 | 136.2077
0 | 63.1008 | 0 | 0 | 0 | 0 | -10.6008 | 52.5 | 160.5455 | 3000 | 0 | 3000 | 2653.9248 | 0 | 146.3905
0 | 37.1715 | 0 | 0 | 0 | 0 | 15.3285 | 52.5 | 175.874 | 3000 | 27.3901 | 3027.3901 | 2497.4624 | 0 | 166.6806
0 | 47.5243 | 0 | 0 | 0 | 0 | 4.9757 | 52.5 | 180.8497 | 3000 | 8.8909 | 3008.8909 | 2154.5177 | 0 | 139.505
0 | 83.1925 | 0 | 0 | 0 | 0 | -30.6925 | 52.5 | 150.1572 | 3000 | 0 | 3000 | 1929.3298 | 0 | 115.972
0 | 78.6708 | 0 | 0 | 0 | 0 | -26.1708 | 52.5 | 123.9864 | 3000 | 0 | 3000 | 1853.6259 | 0 | 101.8011
0 | 47.5736 | 0 | 0 | 0 | 0 | 4.9264 | 52.5 | 128.9128 | 3000 | 8.8028 | 3008.8028 | 1667.7613 | 0 | 89.8923
0 | 47.6935 | 0 | 0 | 0 | 0 | 4.8065 | 52.5 | 133.7193 | 3000 | 8.5886 | 3008.5886 | 1835.1773 | 0 | 95.6494
0 | 43.0743 | 0 | 0 | 0 | 0 | 9.4257 | 52.5 | 143.1449 | 3000 | 16.8424 | 3016.8424 | 1940.7648 | 0 | 99.1731
0 | 53.3861 | 0 | 0 | 0 | 0 | -0.88605 | 52.5 | 142.2589 | 3000 | 0 | 3000 | 2069.9229 | 0 | 105.6903
0 | 37.7253 | 0 | 0 | 0 | 0 | 14.7747 | 52.5 | 157.0336 | 3000 | 26.4004 | 3026.4004 | 2366.6945 | 0 | 126.3105
0 | 51.6992 | 0 | 0 | 0 | 0 | 0.80085 | 52.5 | 157.8344 | 3000 | 1.431 | 3001.431 | 2449.8736 | 0 | 141.8967
0 | 42.1235 | 0 | 0 | 0 | 0 | 10.3765 | 52.5 | 168.211 | 3000 | 18.5415 | 3018.5415 | 2569.7252 | 0 | 176.6429
0 | 37.0333 | 0 | 0 | 0 | 0 | -37.0333 | 0 | 131.1776 | 0 | 0 | 0 | 0 | 286.5935 | 0
0 | 50.2722 | 0 | 0 | 0 | 0 | -50.2722 | 0 | 80.9055 | 0 | 0 | 0 | 0 | 178.445 | 0
0 | 35.7492 | 0 | 0 | 0 | 0 | -35.7492 | 0 | 45.1563 | 0 | 0 | 0 | 0 | 21.6297 | 0
0 | 20.3483 | 0 | 0 | 0 | 0 | 32.1517 | 52.5 | 77.308 | 3000 | 57.4508 | 3057.4508 | 3057.4508 | 0 | 208.5181
0 | 36.4541 | 0 | 0 | 0 | 0 | 16.0459 | 52.5 | 93.3538 | 3000 | 28.6719 | 3028.6719 | 3028.6719 | 0 | 187.7777
0 | 29.8523 | 0 | 0 | 0 | 0 | 22.6477 | 52.5 | 116.0016 | 3000 | 40.4685 | 3040.4685 | 3040.4685 | 0 | 158.3476
0 | 27.752 | 0 | 0 | 0 | 0 | 24.748 | 52.5 | 140.7496 | 3000 | 44.2213 | 3044.2213 | 3044.2213 | 0 | 149.5322
0 | 27.8167 | 0 | 0 | 0 | 0 | 24.6833 | 52.5 | 165.4329 | 3000 | 44.1058 | 3044.1058 | 3044.1058 | 0 | 153.1794
0 | 17.5071 | 0 | 0 | 0 | 0 | 34.9929 | 52.5 | 200.4258 | 3000 | 62.5277 | 3062.5277 | 3062.5277 | 0 | 153.3101
0 | 25.5526 | 0 | 0 | 0 | 0 | 26.9474 | 52.5 | 227.3732 | 3000 | 48.1515 | 3048.1515 | 3048.1515 | 0 | 153.5964
0 | 25.7138 | 0 | 0 | 0 | 0 | 26.7862 | 52.5 | 254.1595 | 3000 | 47.8634 | 3047.8634 | 3020.8263 | 0 | 151.0715
0 | 41.9737 | 0 | 0 | 0 | 0 | 10.5263 | 52.5 | 264.6858 | 3000 | 18.8092 | 3018.8092 | 2797.1047 | 0 | 131.5758
0 | 67.5772 | 0 | 0 | 0 | 0 | -15.0772 | 52.5 | 249.6086 | 3000 | 0 | 3000 | 2551.1837 | 0 | 142.7642
0 | 46.8997 | 0 | 0 | 0 | 0 | 5.6003 | 52.5 | 255.209 | 3000 | 10.0071 | 3010.0071 | 2344.8938 | 0 | 157.8114
0 | 57.0739 | 0 | 0 | 0 | 0 | -42.974 | 14.0999 | 212.235 | 805.7064 | 0 | 805.7064 | 0 | 0 | 0
0 | 69.5525 | 0 | 0 | 0 | 0 | -17.0525 | 52.5 | 195.1825 | 3000 | 0 | 3000 | 2232.1456 | 0 | 142.4779
0 | 98.7811 | 0 | 0 | 0 | 0 | -46.2811 | 52.5 | 148.9014 | 3000 | 0 | 3000 | 2816.1475 | 0 | 163.2802
0 | 73.4467 | 0 | 0 | 0 | 0 | -20.9467 | 52.5 | 127.9547 | 3000 | 0 | 3000 | 2253.7753 | 0 | 125.7832
0 | 34.4723 | 0 | 0 | 0 | 0 | 18.0277 | 52.5 | 145.9824 | 3000 | 32.2131 | 3032.2131 | 1853.3944 | 0 | 96.395
0 | 45.1536 | 0 | 0 | 0 | 0 | 7.3464 | 52.5 | 153.3287 | 3000 | 13.127 | 3013.127 | 1563.937 | 0 | 81.2152
0 | 26.8328 | 0 | 0 | 0 | 0 | 25.6672 | 52.5 | 178.996 | 3000 | 45.864 | 3045.864 | 2434.8249 | 0 | 124.8822
0 | 52.721 | 0 | 0 | 0 | 0 | -0.22102 | 52.5 | 178.775 | 3000 | 0 | 3000 | 2405.1832 | 0 | 122.8808
0 | 46.2463 | 0 | 0 | 0 | 0 | 6.2537 | 52.5 | 185.0287 | 3000 | 11.1746 | 3011.1746 | 2140.5791 | 0 | 106.8363
0 | 44.2142 | 0 | 0 | 0 | 0 | 8.2858 | 52.5 | 193.3144 | 3000 | 14.8056 | 3014.8056 | 2593.0264 | 0 | 147.232
0 | 41.2496 | 0 | 0 | 0 | 0 | 11.2504 | 52.5 | 204.5649 | 3000 | 20.103 | 3020.103 | 2955.2139 | 0 | 191.9116
0 | 40.9808 | 0 | 0 | 0 | 0 | 11.5192 | 52.5 | 216.0841 | 3000 | 20.5833 | 3020.5833 | 2993.5462 | 0 | 204.07
0 | 233.8047 | 0 | 0 | 0 | 0 | -181.3047 | 52.5 | 34.7794 | 3000 | 0 | 3000 | 2972.9629 | 0 | 196.4237
0 | 31.0897 | 0 | 0 | 0 | 0 | 21.4103 | 52.5 | 56.1897 | 3000 | 38.2573 | 3038.2573 | 3038.2573 | 0 | 184.2399
0 | 34.4248 | 0 | 0 | 0 | 0 | 18.0752 | 52.5 | 74.2649 | 3000 | 32.298 | 3032.298 | 3032.298 | 0 | 167.019
0 | 30.5092 | 0 | 0 | 0 | 0 | 21.9908 | 52.5 | 96.2557 | 3000 | 39.2946 | 3039.2946 | 3039.2946 | 0 | 151.9343
0 | 30.3457 | 0 | 0 | 0 | 0 | 22.1543 | 52.5 | 118.41 | 3000 | 39.5867 | 3039.5867 | 3039.5867 | 0 | 139.2131
0 | 28.8563 | 0 | 0 | 0 | 0 | 23.6437 | 52.5 | 142.0536 | 3000 | 42.2481 | 3042.2481 | 3042.2481 | 0 | 140.6431
0 | 33.2672 | 0 | 0 | 0 | 0 | 19.2328 | 52.5 | 161.2864 | 3000 | 34.3665 | 3034.3665 | 3034.3665 | 0 | 136.7892
0 | 22.6683 | 0 | 0 | 0 | 0 | 29.8317 | 52.5 | 191.1182 | 3000 | 53.3054 | 3053.3054 | 3053.3054 | 0 | 137.3987
0 | 27.6075 | 0 | 0 | 0 | 0 | 24.8925 | 52.5 | 216.0107 | 3000 | 44.4796 | 3044.4796 | 3028.2573 | 0 | 141.4196
0 | 51.3956 | 0 | 0 | 0 | 0 | 1.1044 | 52.5 | 217.1151 | 3000 | 1.9735 | 3001.9735 | 2964.1215 | 0 | 133.4744
0 | 89.6994 | 0 | 0 | 0 | 0 | -37.1994 | 52.5 | 179.9157 | 3000 | 0 | 3000 | 2837.7772 | 0 | 133.3188
0 | 81.674 | 0 | 0 | 0 | 0 | -29.174 | 52.5 | 150.7418 | 3000 | 0 | 3000 | 2783.703 | 0 | 142.2194
0 | 63.1741 | 0 | 0 | 0 | 0 | -10.6741 | 52.5 | 140.0677 | 3000 | 0 | 3000 | 2583.6283 | 0 | 146.6467
0 | 41.0701 | 0 | 0 | 0 | 0 | 11.4299 | 52.5 | 151.4975 | 3000 | 20.4236 | 3020.4236 | 2436.4217 | 0 | 158.538
0 | 30.452 | 0 | 0 | 0 | 0 | 22.048 | 52.5 | 173.5455 | 3000 | 39.3968 | 3039.3968 | 2163.394 | 0 | 129.5873
0 | 46.7211 | 0 | 0 | 0 | 0 | 5.7789 | 52.5 | 179.3244 | 3000 | 10.3261 | 3010.3261 | 1642.2475 | 0 | 89.1576
0 | 36.2918 | 0 | 0 | 0 | 0 | 16.2082 | 52.5 | 195.5326 | 3000 | 28.9619 | 3028.9619 | 1617.6239 | 0 | 82.6282
0 | 47.2834 | 0 | 0 | 0 | 0 | 5.2166 | 52.5 | 200.7492 | 3000 | 9.3214 | 3009.3214 | 1506.0572 | 0 | 73.9323
0 | 48.167 | 0 | 0 | 0 | 0 | 4.333 | 52.5 | 205.0822 | 3000 | 7.7425 | 3007.7425 | 1720.7753 | 0 | 82.8897
0 | 47.8253 | 0 | 0 | 0 | 0 | 4.6747 | 52.5 | 209.757 | 3000 | 8.3531 | 3008.3531 | 2202.6467 | 0 | 107.7755
0 | 40.1752 | 0 | 0 | 0 | 0 | 12.3248 | 52.5 | 222.0818 | 3000 | 22.0228 | 3022.0228 | 2091.9457 | 0 | 101.543
0 | 31.3156 | 0 | 0 | 0 | 0 | 21.1844 | 52.5 | 243.2662 | 3000 | 37.8538 | 3037.8538 | 2291.6291 | 0 | 118.5001
0 | 42.0318 | 0 | 0 | 0 | 0 | 10.4682 | 52.5 | 253.7344 | 3000 | 18.7052 | 3018.7052 | 2537.4444 | 0 | 138.5952
0 | 36.2664 | 0 | 0 | 0 | 0 | 16.2336 | 52.5 | 269.968 | 3000 | 29.0074 | 3029.0074 | 2823.5252 | 0 | 168.9033
0 | 28.3278 | 0 | 0 | 0 | 0 | 24.1722 | 52.5 | 294.1402 | 3000 | 43.1926 | 3043.1926 | 3021.5629 | 0 | 202.3239
0 | 30.8401 | 0 | 0 | 0 | 0 | 21.6599 | 52.5 | 315.8001 | 3000 | 38.7034 | 3038.7034 | 3038.7034 | 0 | 197.5157
0 | 37.281 | 0 | 0 | 0 | 0 | 15.219 | 52.5 | 331.0191 | 3000 | 27.1943 | 3027.1943 | 3027.1943 | 0 | 186.233
0 | 26.1955 | 0 | 0 | 0 | 0 | 26.3045 | 52.5 | 357.3237 | 3000 | 47.0027 | 3047.0027 | 3047.0027 | 0 | 165.3913
0 | 27.3786 | 0 | 0 | 0 | 0 | 25.1214 | 52.5 | 382.4451 | 3000 | 44.8886 | 3044.8886 | 3044.8886 | 0 | 150.113
0 | 29.4147 | 0 | 0 | 0 | 0 | 23.0853 | 52.5 | 405.5304 | 3000 | 41.2504 | 3041.2504 | 3041.2504 | 0 | 143.03
0 | 29.1685 | 0 | 0 | 0 | 0 | 23.3315 | 52.5 | 428.8619 | 3000 | 41.6902 | 3041.6902 | 3041.6902 | 0 | 141.4994
0 | 29.5078 | 0 | 0 | 0 | 0 | 22.9922 | 52.5 | 451.8541 | 3000 | 41.0841 | 3041.0841 | 3041.0841 | 0 | 142.3531
0 | 30.0764 | 0 | 0 | 0 | 0 | 22.4236 | 52.5 | 474.2777 | 3000 | 40.068 | 3040.068 | 3007.6235 | 0 | 141.4786
0 | 35.5374 | 0 | 0 | 0 | 0 | 16.9626 | 52.5 | 491.2403 | 3000 | 30.3098 | 3030.3098 | 2819.4202 | 0 | 135.8679
0 | 98.7091 | 0 | 0 | 0 | 0 | -46.2091 | 52.5 | 445.0311 | 3000 | 0 | 3000 | 2540.3689 | 0 | 138.4755
0 | 104.0835 | 0 | 0 | 0 | 0 | -51.5835 | 52.5 | 393.4477 | 3000 | 0 | 3000 | 2280.8124 | 0 | 137.7155
0 | 110.5417 | 0 | 0 | 0 | 0 | -58.0417 | 52.5 | 335.406 | 3000 | 0 | 3000 | 2167.2565 | 0 | 134.565
0 | 120.2855 | 0 | 0 | 0 | 0 | -67.7855 | 52.5 | 267.6205 | 3000 | 0 | 3000 | 1923.9224 | 0 | 114.3002
0 | 90.9752 | 0 | 0 | 0 | 0 | -38.4752 | 52.5 | 229.1453 | 3000 | 0 | 3000 | 1680.5882 | 0 | 99.0371
0 | 41.9089 | 0 | 0 | 0 | 0 | 10.5911 | 52.5 | 239.7364 | 3000 | 18.9249 | 3018.9249 | 1861.7359 | 0 | 104.3317
0 | 33.9907 | 0 | 0 | 0 | 0 | 18.5093 | 52.5 | 258.2457 | 3000 | 33.0737 | 3033.0737 | 1621.7357 | 0 | 83.0491
0 | 42.2132 | 0 | 0 | 0 | 0 | 10.2868 | 52.5 | 268.5325 | 3000 | 18.3811 | 3018.3811 | 2120.7485 | 0 | 102.9199
0 | 41.7238 | 0 | 0 | 0 | 0 | 10.7762 | 52.5 | 279.3087 | 3000 | 19.2557 | 3019.2557 | 2278.4384 | 0 | 108.0208
0 | 45.5305 | 0 | 0 | 0 | 0 | 6.9695 | 52.5 | 286.2782 | 3000 | 12.4536 | 3012.4536 | 2287.8586 | 0 | 108.1242
0 | 227.8324 | 0 | 0 | 0 | 0 | -175.3324 | 52.5 | 110.9458 | 3000 | 0 | 3000 | 2205.1085 | 0 | 104.1252
0 | 48.303 | 0 | 0 | 0 | 0 | 4.197 | 52.5 | 115.1428 | 3000 | 7.4996 | 3007.4996 | 2391.0531 | 0 | 119.5048
0 | 48.1462 | 0 | 0 | 0 | 0 | 4.3538 | 52.5 | 119.4967 | 3000 | 7.7797 | 3007.7797 | 2510.2966 | 0 | 140.0494
0 | 31.7489 | 0 | 0 | 0 | 0 | 20.7511 | 52.5 | 140.2478 | 3000 | 37.0795 | 3037.0795 | 2831.5973 | 0 | 168.48
0 | 26.8352 | 0 | 0 | 0 | 0 | 25.6648 | 52.5 | 165.9126 | 3000 | 45.8596 | 3045.8596 | 2986.378 | 0 | 187.664
0 | 31.5466 | 0 | 0 | 0 | 0 | 20.9534 | 52.5 | 186.866 | 3000 | 37.441 | 3037.441 | 3037.441 | 0 | 197.1603
0 | 28.4512 | 0 | 0 | 0 | 0 | 24.0488 | 52.5 | 210.9148 | 3000 | 42.972 | 3042.972 | 3042.972 | 0 | 180.3265
0 | 23.7331 | 0 | 0 | 0 | 0 | 28.7669 | 52.5 | 239.6817 | 3000 | 51.4026 | 3051.4026 | 3051.4026 | 0 | 158.5204
0 | 24.9372 | 0 | 0 | 0 | 0 | 27.5628 | 52.5 | 267.2445 | 3000 | 49.251 | 3049.251 | 3049.251 | 0 | 154.2311
0 | 36.1872 | 0 | 0 | 0 | 0 | 16.3128 | 52.5 | 283.5573 | 3000 | 29.1488 | 3029.1488 | 3029.1488 | 0 | 141.8853
0 | 33.0471 | 0 | 0 | 0 | 0 | 19.4529 | 52.5 | 303.0102 | 3000 | 34.7598 | 3034.7598 | 3034.7598 | 0 | 134.8647
0 | 35.0225 | 0 | 0 | 0 | 0 | 17.4775 | 52.5 | 320.4877 | 3000 | 31.2299 | 3031.2299 | 3031.2299 | 0 | 134.2229
0 | 33.6426 | 0 | 0 | 0 | 0 | 18.8574 | 52.5 | 339.3451 | 3000 | 33.6957 | 3033.6957 | 3001.2511 | 0 | 131.995
0 | 33.1499 | 0 | 0 | 0 | 0 | 19.3501 | 52.5 | 358.6951 | 3000 | 34.576 | 3034.576 | 2861.5384 | 0 | 124.7345
0 | 27.4158 | 0 | 0 | 0 | 0 | 25.0842 | 52.5 | 383.7793 | 3000 | 44.8222 | 3044.8222 | 2752.8212 | 0 | 122.4455
0 | 28.1296 | 0 | 0 | 0 | 0 | 24.3704 | 52.5 | 408.1498 | 3000 | 43.5468 | 3043.5468 | 2508.2117 | 0 | 118.7889
0 | 43.2216 | 0 | 0 | 0 | 0 | 9.2784 | 52.5 | 417.4282 | 3000 | 16.5793 | 3016.5793 | 2508.2814 | 0 | 124.0596
0 | 42.4326 | 0 | 0 | 0 | 0 | 10.0674 | 52.5 | 427.4957 | 3000 | 17.9892 | 3017.9892 | 1882.4299 | 0 | 88.2107
0 | 33.8003 | 0 | 0 | 0 | 0 | 18.6997 | 52.5 | 446.1954 | 3000 | 33.4139 | 3033.4139 | 1643.7056 | 0 | 75.479
0 | 43.9807 | 0 | 0 | 0 | 0 | 8.5193 | 52.5 | 454.7147 | 3000 | 15.2228 | 3015.2228 | 1495.7364 | 0 | 66.994
0 | 36.9747 | 0 | 0 | 0 | 0 | 15.5253 | 52.5 | 470.24 | 3000 | 27.7417 | 3027.7417 | 1524.4775 | 0 | 68.5558
0 | 39.4808 | 0 | 0 | 0 | 0 | 13.0192 | 52.5 | 483.2592 | 3000 | 23.2637 | 3023.2637 | 1292.8876 | 0 | 56.3053
0 | 41.7422 | 0 | 0 | 0 | 0 | 10.7578 | 52.5 | 494.017 | 3000 | 19.2227 | 3019.2227 | 2013.4416 | 0 | 86.9404
0 | 32.0483 | 0 | 0 | 0 | 0 | 20.4517 | 52.5 | 514.4687 | 3000 | 36.5444 | 3036.5444 | 1960.4668 | 0 | 84.7118
0 | 33.1679 | 0 | 0 | 0 | 0 | 19.3321 | 52.5 | 533.8008 | 3000 | 34.5439 | 3034.5439 | 2136.9113 | 0 | 94.9002
0 | 40.7763 | 0 | 0 | 0 | 0 | 11.7237 | 52.5 | 545.5245 | 3000 | 20.9487 | 3020.9487 | 2263.9092 | 0 | 107.2414
0 | 39.4067 | 0 | 0 | 0 | 0 | 13.0933 | 52.5 | 558.6178 | 3000 | 23.396 | 3023.396 | 2509.6906 | 0 | 123.9034
0 | 42.3963 | 0 | 0 | 0 | 0 | 10.1037 | 52.5 | 568.7215 | 3000 | 18.054 | 3018.054 | 2785.5347 | 0 | 147.3826
0 | 30.518 | 0 | 0 | 0 | 0 | 21.982 | 52.5 | 590.7035 | 3000 | 39.2789 | 3039.2789 | 2985.2046 | 0 | 150.3946
0 | 24.3154 | 0 | 0 | 0 | 0 | 28.1846 | 52.5 | 618.8881 | 3000 | 50.3621 | 3050.3621 | 3050.3621 | 0 | 145.2887
0 | 29.7448 | 0 | 0 | 0 | 0 | 22.7552 | 52.5 | 641.6433 | 3000 | 40.6604 | 3040.6604 | 3040.6604 | 0 | 149.0836
0 | 31.0277 | 0 | 0 | 0 | 0 | 21.4723 | 52.5 | 663.1156 | 3000 | 38.3682 | 3038.3682 | 3038.3682 | 0 | 135.4505
0 | 21.5355 | 0 | 0 | 0 | 0 | 30.9645 | 52.5 | 694.0802 | 3000 | 55.3295 | 3055.3295 | 3055.3295 | 0 | 131.6847
0 | 26.3507 | 0 | 0 | 0 | 0 | 26.1493 | 52.5 | 720.2295 | 3000 | 46.7254 | 3046.7254 | 3046.7254 | 0 | 127.7797
0 | 232.2044 | 0 | 0 | 0 | 0 | -179.7044 | 52.5 | 540.5251 | 3000 | 0 | 3000 | 3000 | 0 | 139.86
0 | 22.3246 | 0 | 0 | 0 | 0 | 30.1754 | 52.5 | 570.7005 | 3000 | 53.9194 | 3053.9194 | 3053.9194 | 0 | 156.9409
0 | 29.0848 | 0 | 0 | 0 | 0 | 23.4152 | 52.5 | 594.1156 | 3000 | 41.8398 | 3041.8398 | 3020.2101 | 0 | 158.9235
0 | 20.9887 | 0 | 0 | 0 | 0 | 31.5113 | 52.5 | 625.627 | 3000 | 56.3065 | 3056.3065 | 2899.4912 | 0 | 136.624
0 | 26.2524 | 0 | 0 | 0 | 0 | 26.2476 | 52.5 | 651.8746 | 3000 | 46.9009 | 3046.9009 | 2581.8624 | 0 | 120.1341
0 | 27.4363 | 0 | 0 | 0 | 0 | 25.0637 | 52.5 | 676.9382 | 3000 | 44.7855 | 3044.7855 | 2298.5608 | 0 | 114.4683
0 | 46.052 | 0 | 0 | 0 | 0 | 6.448 | 52.5 | 683.3863 | 3000 | 11.5217 | 3011.5217 | 2146.3337 | 0 | 102.2513
0 | 47.0349 | 0 | 0 | 0 | 0 | 5.4651 | 52.5 | 688.8513 | 3000 | 9.7654 | 3009.7654 | 1933.6878 | 0 | 92.0242
0 | 36.3937 | 0 | 0 | 0 | 0 | 16.1063 | 52.5 | 704.9577 | 3000 | 28.7799 | 3028.7799 | 1584.9974 | 0 | 63.0829
0 | 41.0546 | 0 | 0 | 0 | 0 | 11.4454 | 52.5 | 716.403 | 3000 | 20.4513 | 3020.4513 | 1555.0391 | 0 | 61.8906
0 | 41.8308 | 0 | 0 | 0 | 0 | 10.6692 | 52.5 | 727.0722 | 3000 | 19.0644 | 3019.0644 | 1775.3566 | 0 | 60.3621
0 | 28.3624 | 0 | 0 | 0 | 0 | 24.1376 | 52.5 | 751.2098 | 3000 | 43.1307 | 3043.1307 | 1842.6823 | 0 | 55.0962
0 | 49.934 | 0 | 0 | 0 | 0 | 2.566 | 52.5 | 753.7758 | 3000 | 4.5851 | 3004.5851 | 1998.804 | 0 | 63.6819
0 | 46.0785 | 0 | 0 | 0 | 0 | 6.4215 | 52.5 | 760.1973 | 3000 | 11.4743 | 3011.4743 | 1794.8036 | 0 | 67.3949
0 | 51.0649 | 0 | 0 | 0 | 0 | 1.4351 | 52.5 | 761.6324 | 3000 | 2.5643 | 3002.5643 | 1883.2273 | 0 | 74.557
0 | 41.0357 | 0 | 0 | 0 | 0 | 11.4643 | 52.5 | 773.0967 | 3000 | 20.4852 | 3020.4852 | 2322.9274 | 0 | 109.4796
0 | 41.603 | 0 | 0 | 0 | 0 | 10.897 | 52.5 | 783.9937 | 3000 | 19.4716 | 3019.4716 | 2570.6553 | 0 | 121.9519
0 | 49.0047 | 0 | 0 | 0 | 0 | 3.4953 | 52.5 | 787.4891 | 3000 | 6.2457 | 3006.2457 | 2849.4304 | 0 | 160.081
0 | 29.9235 | 0 | 0 | 0 | 0 | 22.5765 | 52.5 | 810.0656 | 3000 | 40.3412 | 3040.3412 | 3002.4892 | 0 | 188.7665
0 | 22.9598 | 0 | 0 | 0 | 0 | 29.5402 | 52.5 | 839.6057 | 3000 | 52.7844 | 3052.7844 | 3052.7844 | 0 | 146.381
0 | 30.5755 | 0 | 0 | 0 | 0 | 21.9245 | 52.5 | 861.5302 | 3000 | 39.1761 | 3039.1761 | 3039.1761 | 0 | 149.4971
0 | 31.8417 | 0 | 0 | 0 | 0 | 20.6583 | 52.5 | 882.1885 | 3000 | 36.9136 | 3036.9136 | 3036.9136 | 0 | 150.0235
0 | 27.7644 | 0 | 0 | 0 | 0 | 24.7356 | 52.5 | 906.9241 | 3000 | 44.1993 | 3044.1993 | 3044.1993 | 0 | 127.765
0 | 27.6207 | 0 | 0 | 0 | 0 | 24.8793 | 52.5 | 931.8034 | 3000 | 44.4559 | 3044.4559 | 3044.4559 | 0 | 123.8485
0 | 26.2927 | 0 | 0 | 0 | 0 | 26.2073 | 52.5 | 958.0106 | 3000 | 46.8289 | 3046.8289 | 3046.8289 | 0 | 118.8263
0 | 29.1545 | 0 | 0 | 0 | 0 | 23.3455 | 52.5 | 981.3561 | 3000 | 41.7153 | 3041.7153 | 3041.7153 | 0 | 120.7865
0 | 23.7802 | 0 | 0 | 0 | 0 | 28.7198 | 52.5 | 1010.0759 | 3000 | 51.3184 | 3051.3184 | 3018.8739 | 0 | 129.3587
0 | 21.1197 | 0 | 0 | 0 | 0 | 31.3803 | 52.5 | 1041.4562 | 3000 | 56.0723 | 3056.0723 | 2861.405 | 0 | 117.4034
0 | 32.815 | 0 | 0 | 0 | 0 | 19.685 | 52.5 | 1061.1412 | 3000 | 35.1745 | 3035.1745 | 2732.3587 | 0 | 137.3557
0 | 26.96 | 0 | 0 | 0 | 0 | 25.54 | 52.5 | 1086.6812 | 3000 | 45.6366 | 3045.6366 | 2423.7827 | 0 | 153.1346
0 | 38.4534 | 0 | 0 | 0 | 0 | 14.0466 | 52.5 | 1100.7278 | 3000 | 25.0994 | 3025.0994 | 2170.7262 | 0 | 125.4246
0 | 41.0558 | 0 | 0 | 0 | 0 | 11.4442 | 52.5 | 1112.172 | 3000 | 20.4493 | 3020.4493 | 1971.4088 | 0 | 101.015
0 | 48.928 | 0 | 0 | 0 | 0 | 3.572 | 52.5 | 1115.744 | 3000 | 6.3826 | 3006.3826 | 1627.4892 | 0 | 77.5824
0 | 43.5692 | 0 | 0 | 0 | 0 | 8.9308 | 52.5 | 1124.6748 | 3000 | 15.9582 | 3015.9582 | 1626.2499 | 0 | 77.6372
0 | 42.5622 | 0 | 0 | 0 | 0 | 9.9378 | 52.5 | 1134.6126 | 3000 | 17.7576 | 3017.7576 | 1779.4572 | 0 | 88.1899
0 | 44.2317 | 0 | 0 | 0 | 0 | 8.2683 | 52.5 | 1142.8809 | 3000 | 14.7744 | 3014.7744 | 1852.1779 | 0 | 90.9975
0 | 35.6328 | 0 | 0 | 0 | 0 | 16.8672 | 52.5 | 1159.7481 | 3000 | 30.1395 | 3030.1395 | 1862.1356 | 0 | 91.0771
0 | 41.58 | 0 | 0 | 0 | 0 | 10.92 | 52.5 | 1170.6681 | 3000 | 19.5125 | 3019.5125 | 1981.2869 | 0 | 95.6565
0 | 45.6097 | 0 | 0 | 0 | 0 | 6.8903 | 52.5 | 1177.5584 | 3000 | 12.3121 | 3012.3121 | 2195.7909 | 0 | 107.3083
0 | 48.7075 | 0 | 0 | 0 | 0 | 3.7925 | 52.5 | 1181.3509 | 3000 | 6.7766 | 3006.7766 | 2411.9599 | 0 | 122.8894
0 | 34.9009 | 0 | 0 | 0 | 0 | 17.5991 | 52.5 | 1198.95 | 3000 | 31.4472 | 3031.4472 | 2734.0388 | 0 | 172.4905
0 | 46.2036 | 0 | 0 | 0 | 0 | -46.2036 | 0 | 1152.7464 | 0 | 0 | 0 | 0 | 151.4079 | 0
0 | 23.8786 | 0 | 0 | 0 | 0 | -23.8786 | 0 | 1128.8678 | 0 | 0 | 0 | 0 | 27.0371 | 0
0 | 32.6627 | 0 | 0 | 0 | 0 | 19.8373 | 52.5 | 1148.705 | 3000 | 35.4465 | 3035.4465 | 3035.4465 | 0 | 180.518
0 | 28.7602 | 0 | 0 | 0 | 0 | 23.7398 | 52.5 | 1172.4449 | 3000 | 42.4199 | 3042.4199 | 3042.4199 | 0 | 149.9913
0 | 28.0302 | 0 | 0 | 0 | 0 | 24.4698 | 52.5 | 1196.9146 | 3000 | 43.7242 | 3043.7242 | 3043.7242 | 0 | 133.9239
0 | 23.1305 | 0 | 0 | 0 | 0 | 29.3695 | 52.5 | 1226.2841 | 3000 | 52.4794 | 3052.4794 | 3052.4794 | 0 | 139.5288
0 | 29.9756 | 0 | 0 | 0 | 0 | 22.5244 | 52.5 | 1248.8085 | 3000 | 40.2481 | 3040.2481 | 3040.2481 | 0 | 123.4341
0 | 21.7072 | 0 | 0 | 0 | 0 | 30.7928 | 52.5 | 1279.6013 | 3000 | 55.0226 | 3055.0226 | 3055.0226 | 0 | 120.6123
0 | 41.5941 | 0 | 0 | 0 | 0 | 10.9059 | 52.5 | 1290.5072 | 3000 | 19.4873 | 3019.4873 | 3019.4873 | 0 | 122.8629
0 | 64.1515 | 0 | 0 | 0 | 0 | -11.6515 | 52.5 | 1278.8557 | 3000 | 0 | 3000 | 2978.3703 | 0 | 125.0916
0 | 88.1702 | 0 | 0 | 0 | 0 | -35.6702 | 52.5 | 1243.1855 | 3000 | 0 | 3000 | 2891.8515 | 0 | 127.5017
0 | 98.2064 | 0 | 0 | 0 | 0 | -45.7064 | 52.5 | 1197.479 | 3000 | 0 | 3000 | 2675.5545 | 0 | 128.7209
0 | 102.8108 | 0 | 0 | 0 | 0 | -50.3108 | 52.5 | 1147.1683 | 3000 | 0 | 3000 | 2491.702 | 0 | 146.7862
0 | 93.8527 | 0 | 0 | 0 | 0 | -41.3527 | 52.5 | 1105.8155 | 3000 | 0 | 3000 | 2118.5897 | 0 | 135.9711
0 | 62.1941 | 0 | 0 | 0 | 0 | -9.6941 | 52.5 | 1096.1214 | 3000 | 0 | 3000 | 2091.5526 | 0 | 117.0433
0 | 83.4296 | 0 | 0 | 0 | 0 | -30.9296 | 52.5 | 1065.1918 | 3000 | 0 | 3000 | 1626.514 | 0 | 85.8311
0 | 88.2768 | 0 | 0 | 0 | 0 | -35.7768 | 52.5 | 1029.415 | 3000 | 0 | 3000 | 1599.4769 | 0 | 82.2931
0 | 105.0984 | 0 | 0 | 0 | 0 | -52.5984 | 52.5 | 976.8167 | 3000 | 0 | 3000 | 1799.5516 | 0 | 90.1035
0 | 102.5069 | 0 | 0 | 0 | 0 | -50.0069 | 52.5 | 926.8098 | 3000 | 0 | 3000 | 1821.1813 | 0 | 90.9134
0 | 92.3009 | 0 | 0 | 0 | 0 | -39.8009 | 52.5 | 887.0089 | 3000 | 0 | 3000 | 1859.0333 | 0 | 92.9888
0 | 76.5036 | 0 | 0 | 0 | 0 | -24.0036 | 52.5 | 863.0053 | 3000 | 0 | 3000 | 1994.2189 | 0 | 99.5315
0 | 42.8747 | 0 | 0 | 0 | 0 | 9.6253 | 52.5 | 872.6306 | 3000 | 17.1992 | 3017.1992 | 2146.6037 | 0 | 111.4731
0 | 48.7452 | 0 | 0 | 0 | 0 | -37.2949 | 11.4502 | 835.3357 | 654.2985 | 0 | 654.2985 | 0 | 0 | 0
0 | 48.8457 | 0 | 0 | 0 | 0 | -42.127 | 6.7187 | 793.2087 | 383.9272 | 0 | 383.9272 | 0 | 0 | 0
0 | 27.6409 | 0 | 0 | 0 | 0 | -27.6409 | 0 | 765.5679 | 0 | 0 | 0 | 0 | 210.8896 | 0
0 | 30.2064 | 0 | 0 | 0 | 0 | -30.2064 | 0 | 735.3615 | 0 | 0 | 0 | 0 | 37.852 | 0
0 | 216.457 | 0 | 0 | 0 | 0 | -216.457 | 0 | 518.9045 | 0 | 0 | 0 | 0 | 0 | 0
0 | 38.8241 | 0 | 0 | 0 | 0 | 13.6759 | 52.5 | 532.5804 | 3000 | 24.4371 | 3024.4371 | 3024.4371 | 0 | 186.0029
0 | 27.5555 | 0 | 0 | 0 | 0 | 24.9445 | 52.5 | 557.5249 | 3000 | 44.5724 | 3044.5724 | 3044.5724 | 0 | 159.5356
0 | 22.7354 | 0 | 0 | 0 | 0 | 29.7646 | 52.5 | 587.2895 | 3000 | 53.1855 | 3053.1855 | 3053.1855 | 0 | 167.7725
0 | 31.3733 | 0 | 0 | 0 | 0 | 21.1267 | 52.5 | 608.4162 | 3000 | 37.7507 | 3037.7507 | 3037.7507 | 0 | 148.7283
0 | 28.0252 | 0 | 0 | 0 | 0 | 24.4748 | 52.5 | 632.891 | 3000 | 43.7332 | 3043.7332 | 3043.7332 | 0 | 151.5779
0 | 30.1706 | 0 | 0 | 0 | 0 | 22.3294 | 52.5 | 655.2204 | 3000 | 39.8997 | 3039.8997 | 3039.8997 | 0 | 154.4573
0 | 28.4517 | 0 | 0 | 0 | 0 | 24.0483 | 52.5 | 679.2687 | 3000 | 42.9711 | 3042.9711 | 3026.7489 | 0 | 149.4003
0 | 41.7836 | 0 | 0 | 0 | 0 | 10.7164 | 52.5 | 689.9852 | 3000 | 19.1488 | 3019.1488 | 2975.8894 | 0 | 146.7113
0 | 86.1067 | 0 | 0 | 0 | 0 | -33.6067 | 52.5 | 656.3785 | 3000 | 0 | 3000 | 2794.5178 | 0 | 164.5412
0 | 112.9043 | 0 | 0 | 0 | 0 | -100.9809 | 11.9234 | 555.3975 | 681.3356 | 0 | 681.3356 | 0 | 0 | 0
0 | 301.0981 | 0 | 0 | 0 | 0 | -286.2412 | 14.8569 | 269.1564 | 848.9658 | 0 | 848.9658 | 0 | 0 | 0
0 | 97.4351 | 0 | 0 | 0 | 0 | -44.9351 | 52.5 | 224.2213 | 3000 | 0 | 3000 | 1945.5521 | 0 | 130.0212
0 | 93.9789 | 0 | 0 | 0 | 0 | -41.4789 | 52.5 | 182.7424 | 3000 | 0 | 3000 | 1615.6991 | 0 | 86.6823
0 | 102.5337 | 0 | 0 | 0 | 0 | -50.0337 | 52.5 | 132.7087 | 3000 | 0 | 3000 | 1664.366 | 0 | 86.0477
0 | 130.8599 | 0 | 0 | 0 | 0 | -78.3599 | 52.5 | 54.3488 | 3000 | 0 | 3000 | 1972.5892 | 0 | 98.7873
0 | 98.3881 | 0 | 0 | 0 | 0 | -45.8881 | 52.5 | 8.4607 | 3000 | 0 | 3000 | 1869.8481 | 0 | 89.921
0 | 57.767 | 0 | 0 | 0 | 0 | -5.267 | 52.5 | 3.1937 | 3000 | 0 | 3000 | 1864.4407 | 0 | 87.405
0 | 37.2208 | 0 | 0 | 0 | 0 | 15.2792 | 52.5 | 18.4729 | 3000 | 27.3019 | 3027.3019 | 1967.4465 | 0 | 90.2861
0 | 31.8009 | 0 | 0 | 0 | 0 | 20.6991 | 52.5 | 39.172 | 3000 | 36.9865 | 3036.9865 | 2025.798 | 0 | 94.1388
0 | 42.3427 | 0 | 0 | 0 | 0 | 10.1573 | 52.5 | 49.3293 | 3000 | 18.1497 | 3018.1497 | 2196.2211 | 0 | 108.2078
0 | 52.8022 | 0 | 0 | 0 | 0 | -0.30217 | 52.5 | 49.0271 | 3000 | 0 | 3000 | 2470.0723 | 0 | 133.3345
0 | 49.8348 | 0 | 0 | 0 | 0 | 2.6652 | 52.5 | 51.6923 | 3000 | 4.7624 | 3004.7624 | 2745.206 | 0 | 178.2188
0 | 31.7277 | 0 | 0 | 0 | 0 | 20.7723 | 52.5 | 72.4646 | 3000 | 37.1174 | 3037.1174 | 2977.6357 | 0 | 193.8441
0 | 21.938 | 0 | 0 | 0 | 0 | 30.562 | 52.5 | 103.0266 | 3000 | 54.6102 | 3054.6102 | 3054.6102 | 0 | 177.0147
0 | 27.0798 | 0 | 0 | 0 | 0 | 25.4202 | 52.5 | 128.4468 | 3000 | 45.4226 | 3045.4226 | 3045.4226 | 0 | 157.4483
0 | 21.179 | 0 | 0 | 0 | 0 | 31.321 | 52.5 | 159.7678 | 3000 | 55.9664 | 3055.9664 | 3055.9664 | 0 | 138.8937
0 | 29.4693 | 0 | 0 | 0 | 0 | 23.0307 | 52.5 | 182.7985 | 3000 | 41.1527 | 3041.1527 | 3041.1527 | 0 | 130.7696
0 | 27.8638 | 0 | 0 | 0 | 0 | 24.6362 | 52.5 | 207.4347 | 3000 | 44.0216 | 3044.0216 | 3044.0216 | 0 | 127.8489
0 | 30.6409 | 0 | 0 | 0 | 0 | 21.8591 | 52.5 | 229.2937 | 3000 | 39.0593 | 3039.0593 | 3039.0593 | 0 | 128.5826
0 | 28.425 | 0 | 0 | 0 | 0 | 24.075 | 52.5 | 253.3688 | 3000 | 43.0189 | 3043.0189 | 3043.0189 | 0 | 131.5193
0 | 28.6482 | 0 | 0 | 0 | 0 | 23.8518 | 52.5 | 277.2206 | 3000 | 42.62 | 3042.62 | 3026.3978 | 0 | 134.4326
0 | 37.5591 | 0 | 0 | 0 | 0 | 14.9409 | 52.5 | 292.1615 | 3000 | 26.6973 | 3026.6973 | 2929.3637 | 0 | 131.1769
0 | 90.5135 | 0 | 0 | 0 | 0 | -38.0135 | 52.5 | 254.148 | 3000 | 0 | 3000 | 2670.1471 | 0 | 133.6676
0 | 96.8806 | 0 | 0 | 0 | 0 | -44.3806 | 52.5 | 209.7674 | 3000 | 0 | 3000 | 2205.1085 | 0 | 128.5358
0 | 76.6269 | 0 | 0 | 0 | 0 | -24.1269 | 52.5 | 185.6405 | 3000 | 0 | 3000 | 2167.2565 | 0 | 123.7503
0 | 53.8644 | 0 | 0 | 0 | 0 | -1.3644 | 52.5 | 184.2761 | 3000 | 0 | 3000 | 1945.5521 | 0 | 100.1959
0 | 106.0034 | 0 | 0 | 0 | 0 | -53.5034 | 52.5 | 130.7727 | 3000 | 0 | 3000 | 1572.4397 | 0 | 77.9301
0 | 107.8123 | 0 | 0 | 0 | 0 | -55.3123 | 52.5 | 75.4605 | 3000 | 0 | 3000 | 1545.4026 | 0 | 76.4511
0 | 126.8535 | 0 | 0 | 0 | 0 | -74.3535 | 52.5 | 1.107 | 3000 | 0 | 3000 | 1631.9214 | 0 | 76.6513
0 | 53.607 | 0 | 0 | 0 | 0 | -1.107 | 52.5 | 0 | 3000 | 0 | 3000 | 1669.7734 | 0 | 78.3959
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1761.6996 | 0 | 80.8796
0 | 52.2011 | 0 | 0 | 0 | 0 | 0.29893 | 52.5 | 0.29893 | 3000 | 0.53414 | 3000.5341 | 1946.0862 | 0 | 90.1233
0 | 43.9612 | 0 | 0 | 0 | 0 | 8.5388 | 52.5 | 8.8377 | 3000 | 15.2577 | 3015.2577 | 1944.5875 | 0 | 91.2789
0 | 33.1806 | 0 | 0 | 0 | 0 | 19.3194 | 52.5 | 28.1571 | 3000 | 34.5212 | 3034.5212 | 2163.9257 | 0 | 110.3169
0 | 28.6709 | 0 | 0 | 0 | 0 | 23.8291 | 52.5 | 51.9863 | 3000 | 42.5795 | 3042.5795 | 2463.985 | 0 | 140.2007
0 | 45.4737 | 0 | 0 | 0 | 0 | 7.0263 | 52.5 | 59.0126 | 3000 | 12.5551 | 3012.5551 | 2731.369 | 0 | 188.7649
0 | 27.0427 | 0 | 0 | 0 | 0 | 25.4573 | 52.5 | 84.4699 | 3000 | 45.4888 | 3045.4888 | 2986.0072 | 0 | 200.7493
0 | 29.4854 | 0 | 0 | 0 | 0 | 23.0146 | 52.5 | 107.4845 | 3000 | 41.1241 | 3041.1241 | 3041.1241 | 0 | 179.4871
0 | 24.8768 | 0 | 0 | 0 | 0 | 27.6232 | 52.5 | 135.1077 | 3000 | 49.359 | 3049.359 | 3049.359 | 0 | 171.2825
0 | 30.1057 | 0 | 0 | 0 | 0 | 22.3943 | 52.5 | 157.502 | 3000 | 40.0157 | 3040.0157 | 3040.0157 | 0 | 153.764
0 | 23.1979 | 0 | 0 | 0 | 0 | 29.3021 | 52.5 | 186.8041 | 3000 | 52.359 | 3052.359 | 3052.359 | 0 | 141.4158
0 | 29.5139 | 0 | 0 | 0 | 0 | 22.9861 | 52.5 | 209.7903 | 3000 | 41.0732 | 3041.0732 | 3041.0732 | 0 | 141.2883
0 | 28.5794 | 0 | 0 | 0 | 0 | 23.9206 | 52.5 | 233.7109 | 3000 | 42.743 | 3042.743 | 3042.743 | 0 | 145.1693
0 | 30.1312 | 0 | 0 | 0 | 0 | 22.3688 | 52.5 | 256.0797 | 3000 | 39.9701 | 3039.9701 | 3039.9701 | 0 | 147.0738
0 | 31.5074 | 0 | 0 | 0 | 0 | 20.9926 | 52.5 | 277.0723 | 3000 | 37.5109 | 3037.5109 | 3026.6961 | 0 | 143.4049
0 | 28.5228 | 0 | 0 | 0 | 0 | 23.9772 | 52.5 | 301.0495 | 3000 | 42.8441 | 3042.8441 | 2983.3624 | 0 | 141.9484
0 | 64.944 | 0 | 0 | 0 | 0 | -12.444 | 52.5 | 288.6055 | 3000 | 0 | 3000 | 2870.2218 | 0 | 170.4912
0 | 105.1994 | 0 | 0 | 0 | 0 | -105.1994 | 0 | 183.4061 | 0 | 0 | 0 | 0 | 254.149 | 0
0 | 115.2802 | 0 | 0 | 0 | 0 | -107.6152 | 7.665 | 75.7909 | 438.0014 | 0 | 438.0014 | 0 | 0 | 0
0 | 97.6949 | 0 | 0 | 0 | 0 | -45.1949 | 52.5 | 30.5959 | 3000 | 0 | 3000 | 2059.108 | 0 | 131.4123
0 | 83.0959 | 0 | 0 | 0 | 0 | -30.5959 | 52.5 | 0 | 3000 | 0 | 3000 | 1588.662 | 0 | 93.7152
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1539.9952 | 0 | 83.9759
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1680.5882 | 0 | 86.9704
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1680.5882 | 0 | 82.9034
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1750.8848 | 0 | 85.6008
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1896.8853 | 0 | 92.7767
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1934.7372 | 0 | 95.576
0 | 50.8307 | 0 | 0 | 0 | 0 | 1.6693 | 52.5 | 1.6693 | 3000 | 2.9829 | 3002.9829 | 2121.5726 | 0 | 114.6498
0 | 40.7761 | 0 | 0 | 0 | 0 | 11.7239 | 52.5 | 13.3933 | 3000 | 20.9491 | 3020.9491 | 2442.3546 | 0 | 167.6432
0 | 13.3933 | 0 | 0 | 0 | 0 | -13.3933 | 0 | 0 | 0 | 0 | 0 | 0 | 286.5935 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 59.4817 | 0
0 | 26.6921 | 0 | 0 | 0 | 0 | 25.8079 | 52.5 | 25.8079 | 3000 | 46.1152 | 3046.1152 | 3046.1152 | 0 | 210.9435
0 | 22.5659 | 0 | 0 | 0 | 0 | 29.9341 | 52.5 | 55.742 | 3000 | 53.4883 | 3053.4883 | 3053.4883 | 0 | 194.0186
0 | 25.7539 | 0 | 0 | 0 | 0 | 26.7461 | 52.5 | 82.4881 | 3000 | 47.7917 | 3047.7917 | 3047.7917 | 0 | 164.7331
0 | 19.5012 | 0 | 0 | 0 | 0 | 32.9988 | 52.5 | 115.4869 | 3000 | 58.9644 | 3058.9644 | 3058.9644 | 0 | 153.6824
0 | 25.6042 | 0 | 0 | 0 | 0 | 26.8958 | 52.5 | 142.3827 | 3000 | 48.0591 | 3048.0591 | 3048.0591 | 0 | 142.1615
0 | 36.6349 | 0 | 0 | 0 | 0 | 15.8651 | 52.5 | 158.2478 | 3000 | 28.3488 | 3028.3488 | 3028.3488 | 0 | 137.0631
0 | 20.3799 | 0 | 0 | 0 | 0 | 32.1201 | 52.5 | 190.3678 | 3000 | 57.3943 | 3057.3943 | 3057.3943 | 0 | 134.984
0 | 30.9875 | 0 | 0 | 0 | 0 | 21.5125 | 52.5 | 211.8803 | 3000 | 38.4399 | 3038.4399 | 3005.9954 | 0 | 134.0073
0 | 50.4711 | 0 | 0 | 0 | 0 | 2.0289 | 52.5 | 213.9092 | 3000 | 3.6253 | 3003.6253 | 2787.3283 | 0 | 122.0571
0 | 78.302 | 0 | 0 | 0 | 0 | -25.802 | 52.5 | 188.1072 | 3000 | 0 | 3000 | 2507.9243 | 0 | 113.2579
0 | 87.4648 | 0 | 0 | 0 | 0 | -34.9648 | 52.5 | 153.1424 | 3000 | 0 | 3000 | 2210.5159 | 0 | 102.7448
0 | 97.9765 | 0 | 0 | 0 | 0 | -45.4765 | 52.5 | 107.666 | 3000 | 0 | 3000 | 2069.9229 | 0 | 93.3742
0 | 113.4909 | 0 | 0 | 0 | 0 | -60.9909 | 52.5 | 46.6751 | 3000 | 0 | 3000 | 1831.9962 | 0 | 82.7146
0 | 81.9165 | 0 | 0 | 0 | 0 | -29.4165 | 52.5 | 17.2586 | 3000 | 0 | 3000 | 1502.1432 | 0 | 64.6973
0 | 69.7586 | 0 | 0 | 0 | 0 | -17.2586 | 52.5 | 0 | 3000 | 0 | 3000 | 1421.0318 | 0 | 61.1186
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1545.4026 | 0 | 66.4678
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1577.8472 | 0 | 64.4077
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1626.514 | 0 | 65.1582
0 | 44.1775 | 0 | 0 | 0 | 0 | 8.3225 | 52.5 | 8.3225 | 3000 | 14.8711 | 3014.8711 | 1776.5708 | 0 | 71.4004
0 | 46.7474 | 0 | 0 | 0 | 0 | 5.7526 | 52.5 | 14.075 | 3000 | 10.2791 | 3010.2791 | 1907.1643 | 0 | 78.9375
0 | 39.5733 | 0 | 0 | 0 | 0 | 12.9267 | 52.5 | 27.0017 | 3000 | 23.0983 | 3023.0983 | 2114.6509 | 0 | 95.5399
0 | 29.9397 | 0 | 0 | 0 | 0 | 22.5603 | 52.5 | 49.562 | 3000 | 40.3122 | 3040.3122 | 2456.3103 | 0 | 135.0971
0 | 51.7757 | 0 | 0 | 0 | 0 | 0.72435 | 52.5 | 50.2863 | 3000 | 1.2943 | 3001.2943 | 2720.1082 | 0 | 183.4985
0 | 22.0391 | 0 | 0 | 0 | 0 | -22.0391 | 0 | 28.2473 | 0 | 0 | 0 | 0 | 48.6668 | 0
0 | 27.4249 | 0 | 0 | 0 | 0 | 25.0751 | 52.5 | 53.3223 | 3000 | 44.8058 | 3044.8058 | 3044.8058 | 0 | 197.5774
0 | 23.1426 | 0 | 0 | 0 | 0 | 29.3574 | 52.5 | 82.6797 | 3000 | 52.4578 | 3052.4578 | 3052.4578 | 0 | 171.0292
0 | 29.2458 | 0 | 0 | 0 | 0 | 23.2542 | 52.5 | 105.9339 | 3000 | 41.5522 | 3041.5522 | 3041.5522 | 0 | 153.933
0 | 31.2493 | 0 | 0 | 0 | 0 | 21.2507 | 52.5 | 127.1847 | 3000 | 37.9722 | 3037.9722 | 3037.9722 | 0 | 137.9543
0 | 28.0501 | 0 | 0 | 0 | 0 | 24.4499 | 52.5 | 151.6346 | 3000 | 43.6888 | 3043.6888 | 3043.6888 | 0 | 127.5306
0 | 204.1346 | 0 | 0 | 0 | 0 | -151.6346 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 127.17
0 | 30.8697 | 0 | 0 | 0 | 0 | 21.6303 | 52.5 | 21.6303 | 3000 | 38.6504 | 3038.6504 | 3038.6504 | 0 | 120.8775
0 | 26.6693 | 0 | 0 | 0 | 0 | 25.8307 | 52.5 | 47.461 | 3000 | 46.1561 | 3046.1561 | 3019.1189 | 0 | 104.4615
0 | 30.8964 | 0 | 0 | 0 | 0 | 21.6036 | 52.5 | 69.0645 | 3000 | 38.6027 | 3038.6027 | 2849.3428 | 0 | 71.6895
0 | 15.7347 | 0 | 0 | 0 | 0 | 36.7653 | 52.5 | 105.8298 | 3000 | 65.6947 | 3065.6947 | 2627.6932 | 0 | 71.6572
0 | 26.8911 | 0 | 0 | 0 | 0 | 25.6089 | 52.5 | 131.4387 | 3000 | 45.7596 | 3045.7596 | 2348.2018 | 0 | 69.3894
0 | 49.0152 | 0 | 0 | 0 | 0 | 3.4848 | 52.5 | 134.9235 | 3000 | 6.2269 | 3006.2269 | 2135.6315 | 0 | 76.178
0 | 27.1568 | 0 | 0 | 0 | 0 | 25.3432 | 52.5 | 160.2667 | 3000 | 45.2849 | 3045.2849 | 1931.3553 | 0 | 62.2669
0 | 47.7693 | 0 | 0 | 0 | 0 | 4.7307 | 52.5 | 164.9974 | 3000 | 8.4531 | 3008.4531 | 1586.3003 | 0 | 51.3961
0 | 47.5215 | 0 | 0 | 0 | 0 | 4.9785 | 52.5 | 169.9758 | 3000 | 8.8959 | 3008.8959 | 1657.0396 | 0 | 58.1621
0 | 46.1773 | 0 | 0 | 0 | 0 | 6.3227 | 52.5 | 176.2986 | 3000 | 11.2979 | 3011.2979 | 1594.5525 | 0 | 76.6182
0 | 51.0915 | 0 | 0 | 0 | 0 | 1.4085 | 52.5 | 177.707 | 3000 | 2.5167 | 3002.5167 | 1585.7713 | 0 | 62.416
0 | 44.0746 | 0 | 0 | 0 | 0 | 8.4254 | 52.5 | 186.1324 | 3000 | 15.055 | 3015.055 | 1901.1254 | 0 | 69.8093
0 | 41.3908 | 0 | 0 | 0 | 0 | 11.1092 | 52.5 | 197.2416 | 3000 | 19.8506 | 3019.8506 | 2268.2185 | 0 | 92.634
0 | 31.9678 | 0 | 0 | 0 | 0 | 20.5322 | 52.5 | 217.7738 | 3000 | 36.6883 | 3036.6883 | 1949.7959 | 0 | 73.1173
0 | 44.4332 | 0 | 0 | 0 | 0 | 8.0668 | 52.5 | 225.8406 | 3000 | 14.4143 | 3014.4143 | 2197.893 | 0 | 77.0362
0 | 46.576 | 0 | 0 | 0 | 0 | 5.924 | 52.5 | 231.7645 | 3000 | 10.5854 | 3010.5854 | 2442.8057 | 0 | 107.0682
0 | 38.246 | 0 | 0 | 0 | 0 | 14.254 | 52.5 | 246.0186 | 3000 | 25.47 | 3025.47 | 2755.0988 | 0 | 142.2457
0 | 21.8013 | 0 | 0 | 0 | 0 | 30.6987 | 52.5 | 276.7172 | 3000 | 54.8545 | 3054.8545 | 3000.7802 | 0 | 158.8613
0 | 30.534 | 0 | 0 | 0 | 0 | 21.966 | 52.5 | 298.6832 | 3000 | 39.2502 | 3039.2502 | 3039.2502 | 0 | 158.2538
0 | 31.85 | 0 | 0 | 0 | 0 | 20.65 | 52.5 | 319.3332 | 3000 | 36.8988 | 3036.8988 | 3036.8988 | 0 | 176.7171
0 | 28.4316 | 0 | 0 | 0 | 0 | 24.0684 | 52.5 | 343.4016 | 3000 | 43.0071 | 3043.0071 | 3043.0071 | 0 | 157.3843
0 | 33.1516 | 0 | 0 | 0 | 0 | 19.3484 | 52.5 | 362.75 | 3000 | 34.573 | 3034.573 | 3034.573 | 0 | 133.4605
0 | 28.6264 | 0 | 0 | 0 | 0 | 23.8736 | 52.5 | 386.6236 | 3000 | 42.6589 | 3042.6589 | 3042.6589 | 0 | 125.4488
0 | 34.8612 | 0 | 0 | 0 | 0 | 17.6388 | 52.5 | 404.2624 | 3000 | 31.5181 | 3031.5181 | 3031.5181 | 0 | 121.3214
0 | 28.0311 | 0 | 0 | 0 | 0 | 24.4689 | 52.5 | 428.7312 | 3000 | 43.7226 | 3043.7226 | 3043.7226 | 0 | 121.3532
0 | 27.9065 | 0 | 0 | 0 | 0 | 24.5935 | 52.5 | 453.3247 | 3000 | 43.9453 | 3043.9453 | 3022.3156 | 0 | 123.6127
0 | 22.3091 | 0 | 0 | 0 | 0 | 30.1909 | 52.5 | 483.5156 | 3000 | 53.9471 | 3053.9471 | 2870.0947 | 0 | 120.2283
0 | 24.0556 | 0 | 0 | 0 | 0 | 28.4444 | 52.5 | 511.9599 | 3000 | 50.8263 | 3050.8263 | 2612.8248 | 0 | 139.2636
0 | 34.0983 | 0 | 0 | 0 | 0 | 18.4017 | 52.5 | 530.3616 | 3000 | 32.8814 | 3032.8814 | 2340.7309 | 0 | 155.7756
0 | 50.5197 | 0 | 0 | 0 | 0 | 1.9803 | 52.5 | 532.3419 | 3000 | 3.5385 | 3003.5385 | 2132.9431 | 0 | 143.6324
0 | 42.4138 | 0 | 0 | 0 | 0 | 10.0862 | 52.5 | 542.4281 | 3000 | 18.0227 | 3018.0227 | 2039.2787 | 0 | 114.4647
0 | 43.7647 | 0 | 0 | 0 | 0 | 8.7353 | 52.5 | 551.1634 | 3000 | 15.6088 | 3015.6088 | 2393.7549 | 0 | 125.8397
0 | 39.8692 | 0 | 0 | 0 | 0 | 12.6308 | 52.5 | 563.7941 | 3000 | 22.5695 | 3022.5695 | 1665.3058 | 0 | 79.6849
0 | 54.323 | 0 | 0 | 0 | 0 | -1.823 | 52.5 | 561.9712 | 3000 | 0 | 3000 | 1734.6625 | 0 | 77.1231
0 | 48.5759 | 0 | 0 | 0 | 0 | 3.9241 | 52.5 | 565.8953 | 3000 | 7.0118 | 3007.0118 | 1671.3778 | 0 | 70.8831
0 | 37.5717 | 0 | 0 | 0 | 0 | 14.9283 | 52.5 | 580.8236 | 3000 | 26.6749 | 3026.6749 | 1685.6335 | 0 | 71.2686
0 | 52.1897 | 0 | 0 | 0 | 0 | 0.31025 | 52.5 | 581.1338 | 3000 | 0.55438 | 3000.5544 | 1773.0689 | 0 | 74.4689
0 | 40.2814 | 0 | 0 | 0 | 0 | 12.2186 | 52.5 | 593.3524 | 3000 | 21.833 | 3021.833 | 2259.386 | 0 | 96.2498
0 | 32.0941 | 0 | 0 | 0 | 0 | 20.4059 | 52.5 | 613.7583 | 3000 | 36.4626 | 3036.4626 | 2333.4973 | 0 | 101.2971
0 | 51.2519 | 0 | 0 | 0 | 0 | 1.2481 | 52.5 | 615.0064 | 3000 | 2.2302 | 3002.2302 | 2602.0807 | 0 | 119.7738
0 | 50.9375 | 0 | 0 | 0 | 0 | 1.5625 | 52.5 | 616.5689 | 3000 | 2.792 | 3002.792 | 2878.4212 | 0 | 148.2099
0 | 26.1847 | 0 | 0 | 0 | 0 | 26.3153 | 52.5 | 642.8842 | 3000 | 47.0219 | 3047.0219 | 3025.3922 | 0 | 155.2631
0 | 28.8511 | 0 | 0 | 0 | 0 | 23.6489 | 52.5 | 666.533 | 3000 | 42.2574 | 3042.2574 | 3042.2574 | 0 | 151.8999
0 | 34.6715 | 0 | 0 | 0 | 0 | 17.8285 | 52.5 | 684.3616 | 3000 | 31.8572 | 3031.8572 | 3031.8572 | 0 | 163.4171
0 | 32.3852 | 0 | 0 | 0 | 0 | 20.1148 | 52.5 | 704.4763 | 3000 | 35.9424 | 3035.9424 | 3035.9424 | 0 | 142.5982
0 | 30.5701 | 0 | 0 | 0 | 0 | 21.9299 | 52.5 | 726.4063 | 3000 | 39.1859 | 3039.1859 | 3039.1859 | 0 | 133.4203
0 | 27.6681 | 0 | 0 | 0 | 0 | 24.8319 | 52.5 | 751.2382 | 3000 | 44.3713 | 3044.3713 | 3044.3713 | 0 | 127.7723
0 | 24.838 | 0 | 0 | 0 | 0 | 27.662 | 52.5 | 778.9001 | 3000 | 49.4282 | 3049.4282 | 3049.4282 | 0 | 123.4409
0 | 32.5395 | 0 | 0 | 0 | 0 | 19.9605 | 52.5 | 798.8607 | 3000 | 35.6668 | 3035.6668 | 3035.6668 | 0 | 120.6678
0 | 57.5505 | 0 | 0 | 0 | 0 | -5.0505 | 52.5 | 793.8101 | 3000 | 0 | 3000 | 2972.9629 | 0 | 118.6509
0 | 108.3715 | 0 | 0 | 0 | 0 | -55.8715 | 52.5 | 737.9386 | 3000 | 0 | 3000 | 2794.5178 | 0 | 117.3418
0 | 90.0722 | 0 | 0 | 0 | 0 | -37.5722 | 52.5 | 700.3665 | 3000 | 0 | 3000 | 2513.3317 | 0 | 115.6133
0 | 96.6411 | 0 | 0 | 0 | 0 | -44.1411 | 52.5 | 656.2253 | 3000 | 0 | 3000 | 2313.257 | 0 | 118.2537
0 | 88.0368 | 0 | 0 | 0 | 0 | -35.5368 | 52.5 | 620.6885 | 3000 | 0 | 3000 | 1961.7744 | 0 | 100.2467
0 | 60.3506 | 0 | 0 | 0 | 0 | -7.8506 | 52.5 | 612.8379 | 3000 | 0 | 3000 | 1761.6996 | 0 | 96.7878
0 | 44.6309 | 0 | 0 | 0 | 0 | 7.8691 | 52.5 | 620.7071 | 3000 | 14.0611 | 3014.0611 | 1570.2786 | 0 | 88.7207
0 | 77.5277 | 0 | 0 | 0 | 0 | -25.0277 | 52.5 | 595.6794 | 3000 | 0 | 3000 | 1291.2536 | 0 | 72.93
0 | 88.7857 | 0 | 0 | 0 | 0 | -36.2857 | 52.5 | 559.3937 | 3000 | 0 | 3000 | 1794.1442 | 0 | 100.4362
0 | 45.9036 | 0 | 0 | 0 | 0 | 6.5964 | 52.5 | 565.99 | 3000 | 11.7869 | 3011.7869 | 1811.3385 | 0 | 99.8047
0 | 41.8227 | 0 | 0 | 0 | 0 | 10.6773 | 52.5 | 576.6673 | 3000 | 19.0789 | 3019.0789 | 1369.8142 | 0 | 72.9563
0 | 236.842 | 0 | 0 | 0 | 0 | -184.342 | 52.5 | 392.3253 | 3000 | 0 | 3000 | 1648.1437 | 0 | 79.1109
0 | 45.3096 | 0 | 0 | 0 | 0 | 7.1904 | 52.5 | 399.5158 | 3000 | 12.8484 | 3012.8484 | 2012.4747 | 0 | 90.4809
0 | 45.5788 | 0 | 0 | 0 | 0 | 6.9212 | 52.5 | 406.437 | 3000 | 12.3672 | 3012.3672 | 2098.5124 | 0 | 100.8335
0 | 42.8071 | 0 | 0 | 0 | 0 | 9.6929 | 52.5 | 416.1298 | 3000 | 17.3199 | 3017.3199 | 2460.3551 | 0 | 130.448
0 | 49.4468 | 0 | 0 | 0 | 0 | 3.0532 | 52.5 | 419.1831 | 3000 | 5.4557 | 3005.4557 | 2745.8993 | 0 | 162.0081
0 | 73.3867 | 0 | 0 | 0 | 0 | -20.8867 | 52.5 | 398.2964 | 3000 | 0 | 3000 | 2945.9257 | 0 | 198.6143
0 | 98.5209 | 0 | 0 | 0 | 0 | -46.0209 | 52.5 | 352.2755 | 3000 | 0 | 3000 | 3000 | 0 | 187.95
0 | 83.8811 | 0 | 0 | 0 | 0 | -31.3811 | 52.5 | 320.8944 | 3000 | 0 | 3000 | 3000 | 0 | 171.42
0 | 38.8735 | 0 | 0 | 0 | 0 | 13.6265 | 52.5 | 334.5209 | 3000 | 24.3487 | 3024.3487 | 3024.3487 | 0 | 157.4174
0 | 26.217 | 0 | 0 | 0 | 0 | 26.283 | 52.5 | 360.8038 | 3000 | 46.9642 | 3046.9642 | 3046.9642 | 0 | 139.9775
0 | 29.241 | 0 | 0 | 0 | 0 | 23.259 | 52.5 | 384.0629 | 3000 | 41.5608 | 3041.5608 | 3041.5608 | 0 | 131
0 | 30.8636 | 0 | 0 | 0 | 0 | 21.6364 | 52.5 | 405.6992 | 3000 | 38.6614 | 3038.6614 | 3038.6614 | 0 | 129.447
0 | 28.0574 | 0 | 0 | 0 | 0 | 24.4426 | 52.5 | 430.1419 | 3000 | 43.6757 | 3043.6757 | 3043.6757 | 0 | 128.8388
0 | 25.7677 | 0 | 0 | 0 | 0 | 26.7323 | 52.5 | 456.8742 | 3000 | 47.7671 | 3047.7671 | 3026.1374 | 0 | 129.9121
0 | 44.5534 | 0 | 0 | 0 | 0 | 7.9466 | 52.5 | 464.8207 | 3000 | 14.1995 | 3014.1995 | 2911.4584 | 0 | 128.1042
0 | 103.8668 | 0 | 0 | 0 | 0 | -51.3668 | 52.5 | 413.4539 | 3000 | 0 | 3000 | 2626.8877 | 0 | 139.803
0 | 108.0302 | 0 | 0 | 0 | 0 | -55.5302 | 52.5 | 357.9237 | 3000 | 0 | 3000 | 2210.5159 | 0 | 138.3783
0 | 124.7751 | 0 | 0 | 0 | 0 | -72.2751 | 52.5 | 285.6486 | 3000 | 0 | 3000 | 2167.2565 | 0 | 136.5372
0 | 105.0336 | 0 | 0 | 0 | 0 | -52.5336 | 52.5 | 233.115 | 3000 | 0 | 3000 | 2351.109 | 0 | 123.5038
0 | 110.2817 | 0 | 0 | 0 | 0 | -57.7817 | 52.5 | 175.3333 | 3000 | 0 | 3000 | 2415.9981 | 0 | 117.6108
0 | 135.1453 | 0 | 0 | 0 | 0 | -82.6453 | 52.5 | 92.688 | 3000 | 0 | 3000 | 2156.4417 | 0 | 104.3718
0 | 143.6228 | 0 | 0 | 0 | 0 | -91.1228 | 52.5 | 1.5652 | 3000 | 0 | 3000 | 1891.4778 | 0 | 87.3674
0 | 54.0652 | 0 | 0 | 0 | 0 | -1.5652 | 52.5 | 0 | 3000 | 0 | 3000 | 1869.8481 | 0 | 84.4049
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1853.6259 | 0 | 83.5985
0 | 46.5159 | 0 | 0 | 0 | 0 | 5.9841 | 52.5 | 5.9841 | 3000 | 10.6928 | 3010.6928 | 1831.8741 | 0 | 82.3977
0 | 45.2818 | 0 | 0 | 0 | 0 | 7.2182 | 52.5 | 13.2023 | 3000 | 12.898 | 3012.898 | 2358.5995 | 0 | 106.3257
0 | 41.5143 | 0 | 0 | 0 | 0 | 10.9857 | 52.5 | 24.188 | 3000 | 19.6299 | 3019.6299 | 2192.2938 | 0 | 105.2301
0 | 38.3715 | 0 | 0 | 0 | 0 | 14.1285 | 52.5 | 38.3164 | 3000 | 25.2457 | 3025.2457 | 2533.17 | 0 | 130.4329
0 | 54.5705 | 0 | 0 | 0 | 0 | -2.0705 | 52.5 | 36.2459 | 3000 | 0 | 3000 | 2745.851 | 0 | 159.4516
0 | 29.8185 | 0 | 0 | 0 | 0 | 22.6815 | 52.5 | 58.9275 | 3000 | 40.5289 | 3040.5289 | 2991.8621 | 0 | 196.5354
0 | 33.8698 | 0 | 0 | 0 | 0 | 18.6302 | 52.5 | 77.5577 | 3000 | 33.2898 | 3033.2898 | 3033.2898 | 0 | 171.0775
0 | 74.5345 | 0 | 0 | 0 | 0 | -22.0345 | 52.5 | 55.5232 | 3000 | 0 | 3000 | 3000 | 0 | 157.71
0 | 59.8328 | 0 | 0 | 0 | 0 | -7.3328 | 52.5 | 48.1904 | 3000 | 0 | 3000 | 3000 | 0 | 145.23
0 | 49.3157 | 0 | 0 | 0 | 0 | 3.1843 | 52.5 | 51.3747 | 3000 | 5.6899 | 3005.6899 | 3005.6899 | 0 | 135.0456
0 | 77.8758 | 0 | 0 | 0 | 0 | -25.3758 | 52.5 | 25.9989 | 3000 | 0 | 3000 | 3000 | 0 | 131.49
0 | 43.9011 | 0 | 0 | 0 | 0 | 8.5989 | 52.5 | 34.5977 | 3000 | 15.365 | 3015.365 | 3015.365 | 0 | 129.6004
0 | 30.9695 | 0 | 0 | 0 | 0 | 21.5305 | 52.5 | 56.1282 | 3000 | 38.4721 | 3038.4721 | 3038.4721 | 0 | 133.3585
0 | 24.9729 | 0 | 0 | 0 | 0 | 27.5271 | 52.5 | 83.6553 | 3000 | 49.1873 | 3049.1873 | 3022.1502 | 0 | 134.2439
0 | 39.0053 | 0 | 0 | 0 | 0 | 13.4947 | 52.5 | 97.15 | 3000 | 24.1133 | 3024.1133 | 2867.2979 | 0 | 131.0642
0 | 149.65 | 0 | 0 | 0 | 0 | -97.15 | 52.5 | 0 | 3000 | 0 | 3000 | 2578.2208 | 0 | 133.294
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2248.3679 | 0 | 133.3507
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1956.3669 | 0 | 107.0524
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1718.4402 | 0 | 85.5268
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1512.9581 | 0 | 70.9275
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1453.4764 | 0 | 66.7
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1507.5506 | 0 | 67.7946
0 | 49.413 | 0 | 0 | 0 | 0 | 3.087 | 52.5 | 3.087 | 3000 | 5.516 | 3005.516 | 1729.3637 | 0 | 77.2161
0 | 28.2711 | 0 | 0 | 0 | 0 | 24.2289 | 52.5 | 27.3159 | 3000 | 43.2938 | 3043.2938 | 1572.4742 | 0 | 70.0223
0 | 36.0911 | 0 | 0 | 0 | 0 | 16.4089 | 52.5 | 43.7247 | 3000 | 29.3204 | 3029.3204 | 1704.5013 | 0 | 76.4469
0 | 42.724 | 0 | 0 | 0 | 0 | 9.776 | 52.5 | 53.5007 | 3000 | 17.4683 | 3017.4683 | 1963.0204 | 0 | 87.9433
0 | 43.7434 | 0 | 0 | 0 | 0 | 8.7566 | 52.5 | 62.2573 | 3000 | 15.647 | 3015.647 | 2334.3114 | 0 | 112.0003
0 | 40.1342 | 0 | 0 | 0 | 0 | 12.3658 | 52.5 | 74.6231 | 3000 | 22.096 | 3022.096 | 2638.1688 | 0 | 136.9737
0 | 49.6744 | 0 | 0 | 0 | 0 | 2.8256 | 52.5 | 77.4487 | 3000 | 5.049 | 3005.049 | 2837.4189 | 0 | 166.216
0 | 41.7873 | 0 | 0 | 0 | 0 | 10.7127 | 52.5 | 88.1614 | 3000 | 19.1421 | 3019.1421 | 2992.105 | 0 | 179.4665
0 | 98.528 | 0 | 0 | 0 | 0 | -46.028 | 52.5 | 42.1334 | 3000 | 0 | 3000 | 3000 | 0 | 164.7
0 | 61.1438 | 0 | 0 | 0 | 0 | -8.6438 | 52.5 | 33.4895 | 3000 | 0 | 3000 | 3000 | 0 | 162.18
0 | 57.0993 | 0 | 0 | 0 | 0 | -4.5993 | 52.5 | 28.8903 | 3000 | 0 | 3000 | 3000 | 0 | 149.7
0 | 40.2474 | 0 | 0 | 0 | 0 | 12.2526 | 52.5 | 41.1429 | 3000 | 21.8938 | 3021.8938 | 3021.8938 | 0 | 135.3808
0 | 37.9765 | 0 | 0 | 0 | 0 | 14.5235 | 52.5 | 55.6664 | 3000 | 25.9516 | 3025.9516 | 3025.9516 | 0 | 133.1419
0 | 46.8086 | 0 | 0 | 0 | 0 | 5.6914 | 52.5 | 61.3578 | 3000 | 10.1698 | 3010.1698 | 3010.1698 | 0 | 128.8353
0 | 27.8158 | 0 | 0 | 0 | 0 | 24.6842 | 52.5 | 86.0419 | 3000 | 44.1073 | 3044.1073 | 3044.1073 | 0 | 129.8007
0 | 39.7767 | 0 | 0 | 0 | 0 | 12.7233 | 52.5 | 98.7652 | 3000 | 22.7348 | 3022.7348 | 3011.9199 | 0 | 129.2114
0 | 82.7714 | 0 | 0 | 0 | 0 | -30.2714 | 52.5 | 68.4938 | 3000 | 0 | 3000 | 2913.4812 | 0 | 128.4263
0 | 89.0924 | 0 | 0 | 0 | 0 | -36.5924 | 52.5 | 31.9014 | 3000 | 0 | 3000 | 2729.6287 | 0 | 135.4442
0 | 71.4238 | 0 | 0 | 0 | 0 | -18.9238 | 52.5 | 12.9776 | 3000 | 0 | 3000 | 2448.4426 | 0 | 141.7403
0 | 65.4776 | 0 | 0 | 0 | 0 | -12.9776 | 52.5 | 0 | 3000 | 0 | 3000 | 2421.4055 | 0 | 147.512
0 | 35.4934 | 0 | 0 | 0 | 0 | 17.0066 | 52.5 | 17.0066 | 3000 | 30.3886 | 3030.3886 | 2035.4224 | 0 | 118.8687
0 | 50.6901 | 0 | 0 | 0 | 0 | 1.8099 | 52.5 | 18.8165 | 3000 | 3.2341 | 3003.2341 | 1797.3782 | 0 | 95.261
0 | 71.3165 | 0 | 0 | 0 | 0 | -18.8165 | 52.5 | 0 | 3000 | 0 | 3000 | 1399.4021 | 0 | 72.2092
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1448.069 | 0 | 69.5363
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1707.6254 | 0 | 78.6361
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1491.3284 | 0 | 66.6326
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1621.1066 | 0 | 71.7015
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1880.663 | 0 | 85.3821
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2178.0714 | 0 | 104.4821
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2497.1095 | 0 | 125.7295
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2799.9253 | 0 | 154.4159
0 | 25.6601 | 0 | 0 | 0 | 0 | 26.8399 | 52.5 | 26.8399 | 3000 | 47.9593 | 3047.9593 | 2999.2925 | 0 | 182.5369
0 | 33.5241 | 0 | 0 | 0 | 0 | 18.9759 | 52.5 | 45.8158 | 3000 | 33.9075 | 3033.9075 | 3033.9075 | 0 | 184.3099
0 | 64.1792 | 0 | 0 | 0 | 0 | -11.6792 | 52.5 | 34.1366 | 3000 | 0 | 3000 | 3000 | 0 | 171.21
0 | 83.7831 | 0 | 0 | 0 | 0 | -31.2831 | 52.5 | 2.8535 | 3000 | 0 | 3000 | 3000 | 0 | 159.27
0 | 30.0563 | 0 | 0 | 0 | 0 | 22.4437 | 52.5 | 25.2972 | 3000 | 40.1039 | 3040.1039 | 3040.1039 | 0 | 161.0343
0 | 22.2761 | 0 | 0 | 0 | 0 | 30.2239 | 52.5 | 55.5211 | 3000 | 54.006 | 3054.006 | 3054.006 | 0 | 149.9517
0 | 22.5288 | 0 | 0 | 0 | 0 | 29.9712 | 52.5 | 85.4922 | 3000 | 53.5545 | 3053.5545 | 3053.5545 | 0 | 140.433
0 | 29.0898 | 0 | 0 | 0 | 0 | 23.4102 | 52.5 | 108.9025 | 3000 | 41.831 | 3041.831 | 3041.831 | 0 | 138.4641
0 | 24.9835 | 0 | 0 | 0 | 0 | 27.5165 | 52.5 | 136.4189 | 3000 | 49.1683 | 3049.1683 | 3038.3535 | 0 | 136.7259
0 | 39.8615 | 0 | 0 | 0 | 0 | 12.6385 | 52.5 | 149.0575 | 3000 | 22.5834 | 3022.5834 | 2914.4349 | 0 | 128.9055
0 | 66.4162 | 0 | 0 | 0 | 0 | -13.9162 | 52.5 | 135.1413 | 3000 | 0 | 3000 | 2816.1475 | 0 | 124.5019
0 | 34.7791 | 0 | 0 | 0 | 0 | 17.7209 | 52.5 | 152.8622 | 3000 | 31.665 | 3031.665 | 2366.5517 | 0 | 105.8795
0 | 35.9553 | 0 | 0 | 0 | 0 | 16.5447 | 52.5 | 169.407 | 3000 | 29.5632 | 3029.5632 | 2391.487 | 0 | 110.128
0 | 72.5666 | 0 | 0 | 0 | 0 | -20.0666 | 52.5 | 149.3403 | 3000 | 0 | 3000 | 2188.8862 | 0 | 101.236
0 | 85.6924 | 0 | 0 | 0 | 0 | -33.1924 | 52.5 | 116.148 | 3000 | 0 | 3000 | 2232.1456 | 0 | 101.9644
0 | 34.5027 | 0 | 0 | 0 | 0 | 17.9973 | 52.5 | 134.1453 | 3000 | 32.1589 | 3032.1589 | 2226.4525 | 0 | 99.0103
0 | 38.4116 | 0 | 0 | 0 | 0 | 14.0884 | 52.5 | 148.2337 | 3000 | 25.174 | 3025.174 | 2441.1721 | 0 | 106.0201
0 | 44.8008 | 0 | 0 | 0 | 0 | 7.6992 | 52.5 | 155.9328 | 3000 | 13.7574 | 3013.7574 | 2554.1263 | 0 | 110.0062
0 | 38.3931 | 0 | 0 | 0 | 0 | 14.1069 | 52.5 | 170.0397 | 3000 | 25.2071 | 3025.2071 | 2846.7621 | 0 | 121.5567
0 | 49.2401 | 0 | 0 | 0 | 0 | 3.2599 | 52.5 | 173.2996 | 3000 | 5.8251 | 3005.8251 | 2773.3058 | 0 | 116.9226
0 | 41.2268 | 0 | 0 | 0 | 0 | 11.2732 | 52.5 | 184.5729 | 3000 | 20.1437 | 3020.1437 | 2749.7725 | 0 | 117.4153
0 | 40.8075 | 0 | 0 | 0 | 0 | 11.6925 | 52.5 | 196.2654 | 3000 | 20.893 | 3020.893 | 2858.6703 | 0 | 128.4972
0 | 47.4584 | 0 | 0 | 0 | 0 | 5.0416 | 52.5 | 201.307 | 3000 | 9.0087 | 3009.0087 | 2922.4899 | 0 | 133.6455
0 | 36.5032 | 0 | 0 | 0 | 0 | 15.9968 | 52.5 | 217.3038 | 3000 | 28.5842 | 3028.5842 | 2969.1025 | 0 | 148.1582
0 | 26.8087 | 0 | 0 | 0 | 0 | 25.6913 | 52.5 | 242.9952 | 3000 | 45.907 | 3045.907 | 3013.4624 | 0 | 165.4391
0 | 23.5494 | 0 | 0 | 0 | 0 | 28.9506 | 52.5 | 271.9458 | 3000 | 51.7309 | 3051.7309 | 3051.7309 | 0 | 159.9107
0 | 25.1584 | 0 | 0 | 0 | 0 | 27.3416 | 52.5 | 299.2874 | 3000 | 48.8558 | 3048.8558 | 3048.8558 | 0 | 196.6817
0 | 26.485 | 0 | 0 | 0 | 0 | 26.015 | 52.5 | 325.3023 | 3000 | 46.4853 | 3046.4853 | 3046.4853 | 0 | 167.5567
0 | 21.456 | 0 | 0 | 0 | 0 | 31.044 | 52.5 | 356.3463 | 3000 | 55.4714 | 3055.4714 | 3055.4714 | 0 | 190.4781
0 | 27.3453 | 0 | 0 | 0 | 0 | 25.1547 | 52.5 | 381.501 | 3000 | 44.9481 | 3044.9481 | 3044.9481 | 0 | 159.6162
0 | 27.3063 | 0 | 0 | 0 | 0 | 25.1937 | 52.5 | 406.6947 | 3000 | 45.0178 | 3045.0178 | 3045.0178 | 0 | 133.9808
0 | 34.8906 | 0 | 0 | 0 | 0 | 17.6094 | 52.5 | 424.3041 | 3000 | 31.4656 | 3031.4656 | 3031.4656 | 0 | 119.0457
0 | 29.0103 | 0 | 0 | 0 | 0 | 23.4897 | 52.5 | 447.7938 | 3000 | 41.973 | 3041.973 | 3036.5656 | 0 | 118.7297
0 | 24.0802 | 0 | 0 | 0 | 0 | 28.4198 | 52.5 | 476.2136 | 3000 | 50.7825 | 3050.7825 | 2985.8934 | 0 | 120.0628
0 | 23.4372 | 0 | 0 | 0 | 0 | 29.0628 | 52.5 | 505.2765 | 3000 | 51.9314 | 3051.9314 | 2711.2636 | 0 | 112.409
0 | 26.2293 | 0 | 0 | 0 | 0 | 26.2707 | 52.5 | 531.5472 | 3000 | 46.9423 | 3046.9423 | 2700.8671 | 0 | 112.6262
0 | 35.7518 | 0 | 0 | 0 | 0 | 16.7482 | 52.5 | 548.2954 | 3000 | 29.9268 | 3029.9268 | 2656.8145 | 0 | 113.6585
0 | 41.0064 | 0 | 0 | 0 | 0 | 11.4936 | 52.5 | 559.789 | 3000 | 20.5376 | 3020.5376 | 2339.202 | 0 | 102.7611
0 | 42.9723 | 0 | 0 | 0 | 0 | 9.5277 | 52.5 | 569.3167 | 3000 | 17.0248 | 3017.0248 | 2119.3922 | 0 | 94.3765
0 | 50.2401 | 0 | 0 | 0 | 0 | 2.2599 | 52.5 | 571.5766 | 3000 | 4.0381 | 3004.0381 | 1911.7382 | 0 | 84.1165
0 | 27.7456 | 0 | 0 | 0 | 0 | 24.7544 | 52.5 | 596.331 | 3000 | 44.2328 | 3044.2328 | 2006.0071 | 0 | 84.3727
0 | 40.5512 | 0 | 0 | 0 | 0 | 11.9488 | 52.5 | 608.2798 | 3000 | 21.3509 | 3021.3509 | 1961.4956 | 0 | 82.0886
0 | 47.5775 | 0 | 0 | 0 | 0 | 4.9225 | 52.5 | 613.2024 | 3000 | 8.7959 | 3008.7959 | 2046.2742 | 0 | 81.851
0 | 47.2713 | 0 | 0 | 0 | 0 | 5.2287 | 52.5 | 618.431 | 3000 | 9.343 | 3009.343 | 2706.5271 | 0 | 111.2924
0 | 37.9473 | 0 | 0 | 0 | 0 | 14.5527 | 52.5 | 632.9837 | 3000 | 26.0037 | 3026.0037 | 2409.5572 | 0 | 100.2376
0 | 20.0599 | 0 | 0 | 0 | 0 | 32.4401 | 52.5 | 665.4239 | 3000 | 57.9662 | 3057.9662 | 2711.891 | 0 | 119.5944
0 | 41.4465 | 0 | 0 | 0 | 0 | 11.0535 | 52.5 | 676.4774 | 3000 | 19.7512 | 3019.7512 | 2765.6022 | 0 | 122.2396
0 | 50.1116 | 0 | 0 | 0 | 0 | 2.3884 | 52.5 | 678.8658 | 3000 | 4.2677 | 3004.2677 | 2912.3415 | 0 | 135.3365
0 | 23.3173 | 0 | 0 | 0 | 0 | 29.1827 | 52.5 | 708.0485 | 3000 | 52.1456 | 3052.1456 | 3019.701 | 0 | 142.6809
0 | 27.2687 | 0 | 0 | 0 | 0 | 25.2313 | 52.5 | 733.2798 | 3000 | 45.085 | 3045.085 | 3045.085 | 0 | 146.3468
0 | 27.8964 | 0 | 0 | 0 | 0 | 24.6036 | 52.5 | 757.8834 | 3000 | 43.9634 | 3043.9634 | 3043.9634 | 0 | 158.347
0 | 24.101 | 0 | 0 | 0 | 0 | 28.399 | 52.5 | 786.2824 | 3000 | 50.7453 | 3050.7453 | 3050.7453 | 0 | 146.4968
0 | 20.3061 | 0 | 0 | 0 | 0 | 32.1939 | 52.5 | 818.4763 | 3000 | 57.5261 | 3057.5261 | 3057.5261 | 0 | 152.6623
0 | 27.6087 | 0 | 0 | 0 | 0 | 24.8913 | 52.5 | 843.3676 | 3000 | 44.4774 | 3044.4774 | 3044.4774 | 0 | 137.3364
0 | 35.117 | 0 | 0 | 0 | 0 | 17.383 | 52.5 | 860.7505 | 3000 | 31.0611 | 3031.0611 | 3031.0611 | 0 | 135.0338
0 | 31.8897 | 0 | 0 | 0 | 0 | 20.6103 | 52.5 | 881.3609 | 3000 | 36.8279 | 3036.8279 | 3036.8279 | 0 | 137.5076
0 | 26.2423 | 0 | 0 | 0 | 0 | 26.2577 | 52.5 | 907.6186 | 3000 | 46.919 | 3046.919 | 3036.1042 | 0 | 136.7461
0 | 27.5277 | 0 | 0 | 0 | 0 | 24.9723 | 52.5 | 932.5909 | 3000 | 44.6221 | 3044.6221 | 2974.3256 | 0 | 133.9041
0 | 29.0599 | 0 | 0 | 0 | 0 | 23.4401 | 52.5 | 956.031 | 3000 | 41.8844 | 3041.8844 | 2787.7354 | 0 | 138.7177
0 | 224.2116 | 0 | 0 | 0 | 0 | -171.7116 | 52.5 | 784.3194 | 3000 | 0 | 3000 | 2578.2208 | 0 | 139.3786
0 | 38.9238 | 0 | 0 | 0 | 0 | 13.5762 | 52.5 | 797.8956 | 3000 | 24.2588 | 3024.2588 | 2299.6639 | 0 | 126.4585
0 | 33.115 | 0 | 0 | 0 | 0 | 19.385 | 52.5 | 817.2806 | 3000 | 34.6385 | 3034.6385 | 2207.3024 | 0 | 118.2893
0 | 39.6534 | 0 | 0 | 0 | 0 | 12.8466 | 52.5 | 830.1273 | 3000 | 22.9552 | 3022.9552 | 1946.8776 | 0 | 101.8022
0 | 49.1257 | 0 | 0 | 0 | 0 | 3.3743 | 52.5 | 833.5016 | 3000 | 6.0295 | 3006.0295 | 1810.9885 | 0 | 99.4957
0 | 244.6237 | 0 | 0 | 0 | 0 | -192.1237 | 52.5 | 641.3779 | 3000 | 0 | 3000 | 1842.811 | 0 | 98.9221
0 | 30.6465 | 0 | 0 | 0 | 0 | 21.8535 | 52.5 | 663.2314 | 3000 | 39.0493 | 3039.0493 | 2763.2706 | 0 | 138.4122
0 | 39.1922 | 0 | 0 | 0 | 0 | 13.3078 | 52.5 | 676.5392 | 3000 | 23.7793 | 3023.7793 | 2812.8897 | 0 | 136.3689
0 | 52.2204 | 0 | 0 | 0 | 0 | 0.2796 | 52.5 | 676.8188 | 3000 | 0.4996 | 3000.4996 | 2503.0165 | 0 | 122.0471
0 | 41.6226 | 0 | 0 | 0 | 0 | 10.8774 | 52.5 | 687.6963 | 3000 | 19.4365 | 3019.4365 | 2543.5831 | 0 | 125.8311
0 | 28.2898 | 0 | 0 | 0 | 0 | 24.2102 | 52.5 | 711.9065 | 3000 | 43.2604 | 3043.2604 | 2637.7035 | 0 | 131.6742
0 | 28.7414 | 0 | 0 | 0 | 0 | 23.7586 | 52.5 | 735.6651 | 3000 | 42.4535 | 3042.4535 | 2847.7862 | 0 | 150.9327
0 | 41.2451 | 0 | 0 | 0 | 0 | 11.2549 | 52.5 | 746.92 | 3000 | 20.111 | 3020.111 | 2911.9624 | 0 | 168.6026
0 | 19.4321 | 0 | 0 | 0 | 0 | 33.0679 | 52.5 | 779.9878 | 3000 | 59.0879 | 3059.0879 | 3032.0508 | 0 | 161.7599
0 | 30.7558 | 0 | 0 | 0 | 0 | 21.7442 | 52.5 | 801.732 | 3000 | 38.854 | 3038.854 | 3038.854 | 0 | 160.8465
0 | 29.9711 | 0 | 0 | 0 | 0 | 22.5289 | 52.5 | 824.2609 | 3000 | 40.2561 | 3040.2561 | 3040.2561 | 0 | 165.4811
0 | 27.6325 | 0 | 0 | 0 | 0 | 24.8675 | 52.5 | 849.1285 | 3000 | 44.435 | 3044.435 | 3044.435 | 0 | 151.0953
0 | 17.7274 | 0 | 0 | 0 | 0 | 34.7726 | 52.5 | 883.9011 | 3000 | 62.134 | 3062.134 | 3062.134 | 0 | 142.573
0 | 30.1682 | 0 | 0 | 0 | 0 | 22.3318 | 52.5 | 906.2329 | 3000 | 39.904 | 3039.904 | 3039.904 | 0 | 137.3733
0 | 29.7873 | 0 | 0 | 0 | 0 | 22.7127 | 52.5 | 928.9456 | 3000 | 40.5845 | 3040.5845 | 3040.5845 | 0 | 136.2486
0 | 32.9086 | 0 | 0 | 0 | 0 | 19.5914 | 52.5 | 948.5369 | 3000 | 35.0072 | 3035.0072 | 3035.0072 | 0 | 134.9971
0 | 39.3664 | 0 | 0 | 0 | 0 | 13.1336 | 52.5 | 961.6705 | 3000 | 23.468 | 3023.468 | 3012.6532 | 0 | 136.1418
0 | 72.0686 | 0 | 0 | 0 | 0 | -19.5686 | 52.5 | 942.102 | 3000 | 0 | 3000 | 2805.3327 | 0 | 127.7829
0 | 107.4766 | 0 | 0 | 0 | 0 | -54.9766 | 52.5 | 887.1254 | 3000 | 0 | 3000 | 2578.2208 | 0 | 131.9018
0 | 109.3008 | 0 | 0 | 0 | 0 | -56.8008 | 52.5 | 830.3246 | 3000 | 0 | 3000 | 2259.1827 | 0 | 133.1788
0 | 97.6076 | 0 | 0 | 0 | 0 | -45.1076 | 52.5 | 785.217 | 3000 | 0 | 3000 | 1923.9224 | 0 | 113.6269
0 | 107.5758 | 0 | 0 | 0 | 0 | -55.0758 | 52.5 | 730.1413 | 3000 | 0 | 3000 | 1886.0704 | 0 | 105.7897
0 | 52.4713 | 0 | 0 | 0 | 0 | 0.028666 | 52.5 | 730.17 | 3000 | 0.051223 | 3000.0512 | 1826.6399 | 0 | 97.1224
0 | 53.9239 | 0 | 0 | 0 | 0 | -1.4239 | 52.5 | 728.746 | 3000 | 0 | 3000 | 1810.3664 | 0 | 96.0218
0 | 68.7576 | 0 | 0 | 0 | 0 | -16.2576 | 52.5 | 712.4884 | 3000 | 0 | 3000 | 1783.3293 | 0 | 92.8401
0 | 134.9745 | 0 | 0 | 0 | 0 | -82.4745 | 52.5 | 630.0139 | 3000 | 0 | 3000 | 1675.1808 | 0 | 84.0103
0 | 108.2673 | 0 | 0 | 0 | 0 | -55.7673 | 52.5 | 574.2466 | 3000 | 0 | 3000 | 1788.7367 | 0 | 88.9897
0 | 69.3164 | 0 | 0 | 0 | 0 | -16.8164 | 52.5 | 557.4302 | 3000 | 0 | 3000 | 2226.7382 | 0 | 109.6446
0 | 45.4016 | 0 | 0 | 0 | 0 | 7.0984 | 52.5 | 564.5286 | 3000 | 12.6839 | 3012.6839 | 2185.3478 | 0 | 108.6992
0 | 33.5779 | 0 | 0 | 0 | 0 | 18.9221 | 52.5 | 583.4507 | 3000 | 33.8113 | 3033.8113 | 2325.4385 | 0 | 120.2484
0 | 37.5818 | 0 | 0 | 0 | 0 | 14.9182 | 52.5 | 598.3689 | 3000 | 26.6568 | 3026.6568 | 2507.544 | 0 | 138.7675
0 | 38.5128 | 0 | 0 | 0 | 0 | 13.9872 | 52.5 | 612.3561 | 3000 | 24.9932 | 3024.9932 | 2776.2517 | 0 | 172.1276
0 | 25.3026 | 0 | 0 | 0 | 0 | 27.1974 | 52.5 | 639.5534 | 3000 | 48.5981 | 3048.5981 | 2999.9313 | 0 | 188.6957
0 | 34.1072 | 0 | 0 | 0 | 0 | 18.3928 | 52.5 | 657.9462 | 3000 | 32.8654 | 3032.8654 | 3032.8654 | 0 | 184.9745
0 | 30.0028 | 0 | 0 | 0 | 0 | 22.4972 | 52.5 | 680.4434 | 3000 | 40.1995 | 3040.1995 | 3040.1995 | 0 | 179.0069
0 | 29.3333 | 0 | 0 | 0 | 0 | 23.1667 | 52.5 | 703.6101 | 3000 | 41.3958 | 3041.3958 | 3041.3958 | 0 | 157.1185
0 | 31.6635 | 0 | 0 | 0 | 0 | 20.8365 | 52.5 | 724.4466 | 3000 | 37.2321 | 3037.2321 | 3037.2321 | 0 | 154.6255
0 | 32.1413 | 0 | 0 | 0 | 0 | 20.3587 | 52.5 | 744.8053 | 3000 | 36.3784 | 3036.3784 | 3036.3784 | 0 | 147.3858
0 | 26.1927 | 0 | 0 | 0 | 0 | 26.3073 | 52.5 | 771.1127 | 3000 | 47.0077 | 3047.0077 | 3047.0077 | 0 | 146.1954
0 | 27.1904 | 0 | 0 | 0 | 0 | 25.3096 | 52.5 | 796.4223 | 3000 | 45.225 | 3045.225 | 3045.225 | 0 | 145.9272
0 | 34.5111 | 0 | 0 | 0 | 0 | 17.9889 | 52.5 | 814.4112 | 3000 | 32.1438 | 3032.1438 | 3021.3289 | 0 | 145.9302
0 | 20.2027 | 0 | 0 | 0 | 0 | 32.2973 | 52.5 | 846.7086 | 3000 | 57.711 | 3057.711 | 2976.5996 | 0 | 144.0079
0 | 35.7824 | 0 | 0 | 0 | 0 | 16.7176 | 52.5 | 863.4262 | 3000 | 29.8722 | 3029.8722 | 2748.6861 | 0 | 156.1254
0 | 88.9258 | 0 | 0 | 0 | 0 | -36.4258 | 52.5 | 827.0004 | 3000 | 0 | 3000 | 2410.5907 | 0 | 155.3626
0 | 137.6358 | 0 | 0 | 0 | 0 | -85.1358 | 52.5 | 741.8646 | 3000 | 0 | 3000 | 2129.4045 | 0 | 135.856
0 | 112.7913 | 0 | 0 | 0 | 0 | -60.2913 | 52.5 | 681.5732 | 3000 | 0 | 3000 | 1875.2556 | 0 | 110.6213
0 | 117.0384 | 0 | 0 | 0 | 0 | -64.5384 | 52.5 | 617.0349 | 3000 | 0 | 3000 | 1777.9219 | 0 | 100.1681
0 | 81.3988 | 0 | 0 | 0 | 0 | -28.8988 | 52.5 | 588.1361 | 3000 | 0 | 3000 | 2486.2946 | 0 | 142.042
0 | 29.9563 | 0 | 0 | 0 | 0 | 22.5437 | 52.5 | 610.6798 | 3000 | 40.2826 | 3040.2826 | 2640.1332 | 0 | 142.9896
0 | 53.6394 | 0 | 0 | 0 | 0 | -1.1394 | 52.5 | 609.5404 | 3000 | 0 | 3000 | 2567.406 | 0 | 134.3267
0 | 101.8857 | 0 | 0 | 0 | 0 | -49.3857 | 52.5 | 560.1547 | 3000 | 0 | 3000 | 2616.0728 | 0 | 136.0096
0 | 88.8038 | 0 | 0 | 0 | 0 | -36.3038 | 52.5 | 523.8509 | 3000 | 0 | 3000 | 2675.5545 | 0 | 139.2626
0 | 127.9213 | 0 | 0 | 0 | 0 | -75.4213 | 52.5 | 448.4296 | 3000 | 0 | 3000 | 2729.6287 | 0 | 146.9632
0 | 124.0835 | 0 | 0 | 0 | 0 | -71.5835 | 52.5 | 376.8461 | 3000 | 0 | 3000 | 2691.7768 | 0 | 159.0302
0 | 99.4743 | 0 | 0 | 0 | 0 | -46.9743 | 52.5 | 329.8718 | 3000 | 0 | 3000 | 2870.2218 | 0 | 183.5507
0 | 59.4546 | 0 | 0 | 0 | 0 | -6.9546 | 52.5 | 322.9172 | 3000 | 0 | 3000 | 2945.9257 | 0 | 200.8827
0 | 68.0961 | 0 | 0 | 0 | 0 | -15.5961 | 52.5 | 307.3212 | 3000 | 0 | 3000 | 2983.7777 | 0 | 198.3317
0 | 45.1754 | 0 | 0 | 0 | 0 | 7.3246 | 52.5 | 314.6458 | 3000 | 13.0881 | 3013.0881 | 3013.0881 | 0 | 190.0053
0 | 23.0285 | 0 | 0 | 0 | 0 | 29.4715 | 52.5 | 344.1172 | 3000 | 52.6616 | 3052.6616 | 3052.6616 | 0 | 191.4935
0 | 32.5432 | 0 | 0 | 0 | 0 | 19.9568 | 52.5 | 364.0741 | 3000 | 35.6602 | 3035.6602 | 3035.6602 | 0 | 175.0058
0 | 28.8415 | 0 | 0 | 0 | 0 | 23.6585 | 52.5 | 387.7326 | 3000 | 42.2747 | 3042.2747 | 3042.2747 | 0 | 156.738
0 | 27.5319 | 0 | 0 | 0 | 0 | 24.9681 | 52.5 | 412.7007 | 3000 | 44.6147 | 3044.6147 | 3044.6147 | 0 | 155.2449
0 | 56.3379 | 0 | 0 | 0 | 0 | -3.8379 | 52.5 | 408.8628 | 3000 | 0 | 3000 | 3000 | 0 | 150.36
0 | 98.7068 | 0 | 0 | 0 | 0 | -46.2068 | 52.5 | 362.656 | 3000 | 0 | 3000 | 3000 | 0 | 149.64
0 | 65.7266 | 0 | 0 | 0 | 0 | -13.2266 | 52.5 | 349.4293 | 3000 | 0 | 3000 | 3000 | 0 | 149.58
0 | 75.9412 | 0 | 0 | 0 | 0 | -23.4412 | 52.5 | 325.9882 | 3000 | 0 | 3000 | 2967.5554 | 0 | 151.0486
0 | 298.384 | 0 | 0 | 0 | 0 | -245.884 | 52.5 | 80.1041 | 3000 | 0 | 3000 | 2751.2584 | 0 | 157.7572
0 | 95.9756 | 0 | 0 | 0 | 0 | -43.4756 | 52.5 | 36.6286 | 3000 | 0 | 3000 | 2664.7396 | 0 | 175.2599
0 | 89.1286 | 0 | 0 | 0 | 0 | -36.6286 | 52.5 | 0 | 3000 | 0 | 3000 | 2843.1847 | 0 | 189.7257
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2751.2584 | 0 | 186.6454
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2545.7763 | 0 | 170.0069
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2161.8491 | 0 | 149.146
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2367.3312 | 0 | 157.2381
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2686.3693 | 0 | 174.614
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2518.7392 | 0 | 155.2803
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2399.7758 | 0 | 145.2104
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2248.3679 | 0 | 137.1504
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2648.5174 | 0 | 171.412
0 | 35.2434 | 0 | 0 | 0 | 0 | 17.2566 | 52.5 | 17.2566 | 3000 | 30.8353 | 3030.8353 | 2592.8339 | 0 | 174.4459
0 | 45.6301 | 0 | 0 | 0 | 0 | 6.8699 | 52.5 | 24.1265 | 3000 | 12.2756 | 3012.2756 | 2850.0528 | 0 | 194.7726
0 | 36.3913 | 0 | 0 | 0 | 0 | 16.1087 | 52.5 | 40.2352 | 3000 | 28.7841 | 3028.7841 | 3001.747 | 0 | 200.2465
0 | 25.0119 | 0 | 0 | 0 | 0 | 27.4881 | 52.5 | 67.7234 | 3000 | 49.1177 | 3049.1177 | 3049.1177 | 0 | 194.8386
0 | 43.5779 | 0 | 0 | 0 | 0 | 8.9221 | 52.5 | 76.6455 | 3000 | 15.9426 | 3015.9426 | 3015.9426 | 0 | 189.2806
0 | 88.8531 | 0 | 0 | 0 | 0 | -36.3531 | 52.5 | 40.2923 | 3000 | 0 | 3000 | 3000 | 0 | 165.51
0 | 92.7923 | 0 | 0 | 0 | 0 | -40.2923 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 161.82
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 158.67
0 | 29.7836 | 0 | 0 | 0 | 0 | 22.7164 | 52.5 | 22.7164 | 3000 | 40.5911 | 3040.5911 | 3040.5911 | 0 | 159.2662
0 | 26.3371 | 0 | 0 | 0 | 0 | 26.1629 | 52.5 | 48.8793 | 3000 | 46.7496 | 3046.7496 | 3046.7496 | 0 | 159.0403
0 | 26.8626 | 0 | 0 | 0 | 0 | 25.6374 | 52.5 | 74.5166 | 3000 | 45.8106 | 3045.8106 | 3034.9957 | 0 | 159.1855
0 | 24.9825 | 0 | 0 | 0 | 0 | 27.5175 | 52.5 | 102.0341 | 3000 | 49.1701 | 3049.1701 | 2973.4661 | 0 | 156.7314
0 | 31.9997 | 0 | 0 | 0 | 0 | 20.5003 | 52.5 | 122.5344 | 3000 | 36.6314 | 3036.6314 | 2809.5195 | 0 | 162.8678
0 | 40.5214 | 0 | 0 | 0 | 0 | 11.9786 | 52.5 | 134.513 | 3000 | 21.4042 | 3021.4042 | 2723.9958 | 0 | 187.2202
0 | 97.9661 | 0 | 0 | 0 | 0 | -88.2192 | 9.7469 | 46.2938 | 556.9648 | 0 | 556.9648 | 0 | 0 | 0
0 | 60.0152 | 0 | 0 | 0 | 0 | -46.2938 | 13.7213 | 0 | 784.0767 | 0 | 784.0767 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2167.2565 | 0 | 146.0731
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2480.8872 | 0 | 163.6641
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2951.3332 | 0 | 175.7224
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2551.1837 | 0 | 144.7287
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2637.7025 | 0 | 146.9992
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2632.2951 | 0 | 139.5116
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2659.3322 | 0 | 142.6466
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2670.1471 | 0 | 151.9047
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2751.2584 | 0 | 181.0603
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2837.7772 | 0 | 195.3526
0 | 25.5788 | 0 | 0 | 0 | 0 | 26.9212 | 52.5 | 26.9212 | 3000 | 48.1047 | 3048.1047 | 3031.8824 | 0 | 208.6238
0 | 17.7226 | 0 | 0 | 0 | 0 | 34.7774 | 52.5 | 61.6987 | 3000 | 62.1427 | 3062.1427 | 3062.1427 | 0 | 193.558
0 | 51.7735 | 0 | 0 | 0 | 0 | 0.72647 | 52.5 | 62.4251 | 3000 | 1.2981 | 3001.2981 | 3001.2981 | 0 | 176.7164
0 | 75.4528 | 0 | 0 | 0 | 0 | -22.9528 | 52.5 | 39.4723 | 3000 | 0 | 3000 | 3000 | 0 | 169.26
0 | 44.1592 | 0 | 0 | 0 | 0 | 8.3408 | 52.5 | 47.8131 | 3000 | 14.9039 | 3014.9039 | 3014.9039 | 0 | 168.9854
0 | 34.3692 | 0 | 0 | 0 | 0 | 18.1308 | 52.5 | 65.9439 | 3000 | 32.3973 | 3032.3973 | 3032.3973 | 0 | 161.8694
0 | 36.1708 | 0 | 0 | 0 | 0 | 16.3292 | 52.5 | 82.2731 | 3000 | 29.1781 | 3029.1781 | 3029.1781 | 0 | 157.1235
0 | 27.7854 | 0 | 0 | 0 | 0 | 24.7146 | 52.5 | 106.9877 | 3000 | 44.1617 | 3044.1617 | 3044.1617 | 0 | 155.6784
0 | 28.2 | 0 | 0 | 0 | 0 | 24.3 | 52.5 | 131.2877 | 3000 | 43.4209 | 3043.4209 | 3038.0135 | 0 | 158.2197
0 | 18.8793 | 0 | 0 | 0 | 0 | 33.6207 | 52.5 | 164.9084 | 3000 | 60.0757 | 3060.0757 | 3016.8163 | 0 | 151.9872
0 | 24.5264 | 0 | 0 | 0 | 0 | 27.9736 | 52.5 | 192.882 | 3000 | 49.9851 | 3049.9851 | 2968.8737 | 0 | 151.7094
0 | 24.0674 | 0 | 0 | 0 | 0 | 28.4326 | 52.5 | 221.3146 | 3000 | 50.8053 | 3050.8053 | 2888.5825 | 0 | 152.4883
0 | 44.1882 | 0 | 0 | 0 | 0 | 8.3118 | 52.5 | 229.6264 | 3000 | 14.8522 | 3014.8522 | 2684.9992 | 0 | 143.5401
0 | 32.5513 | 0 | 0 | 0 | 0 | 19.9487 | 52.5 | 249.5751 | 3000 | 35.6456 | 3035.6456 | 2516.5328 | 0 | 137.9815
0 | 50.7906 | 0 | 0 | 0 | 0 | 1.7094 | 52.5 | 251.2845 | 3000 | 3.0545 | 3003.0545 | 2527.2011 | 0 | 138.5412
0 | 91.0388 | 0 | 0 | 0 | 0 | -38.5388 | 52.5 | 212.7457 | 3000 | 0 | 3000 | 1977.9966 | 0 | 106.8118
0 | 94.652 | 0 | 0 | 0 | 0 | -42.152 | 52.5 | 170.5937 | 3000 | 0 | 3000 | 2010.4412 | 0 | 106.292
0 | 30.0209 | 0 | 0 | 0 | 0 | 22.4791 | 52.5 | 193.0728 | 3000 | 40.1672 | 3040.1672 | 1872.1634 | 0 | 93.0465
0 | 46.7304 | 0 | 0 | 0 | 0 | 5.7696 | 52.5 | 198.8424 | 3000 | 10.3095 | 3010.3095 | 1988.3062 | 0 | 97.3077
0 | 38.4104 | 0 | 0 | 0 | 0 | 14.0896 | 52.5 | 212.932 | 3000 | 25.1763 | 3025.1763 | 1813.913 | 0 | 87.9929
0 | 29.7366 | 0 | 0 | 0 | 0 | 22.7634 | 52.5 | 235.6955 | 3000 | 40.6753 | 3040.6753 | 2126.8204 | 0 | 103.2784
0 | 48.1429 | 0 | 0 | 0 | 0 | 4.3571 | 52.5 | 240.0526 | 3000 | 7.7855 | 3007.7855 | 2537.3395 | 0 | 126.1311
0 | 39.0719 | 0 | 0 | 0 | 0 | 13.4281 | 52.5 | 253.4806 | 3000 | 23.9942 | 3023.9942 | 2942.8828 | 0 | 152.765
0 | 35.9584 | 0 | 0 | 0 | 0 | 16.5416 | 52.5 | 270.0222 | 3000 | 29.5576 | 3029.5576 | 2980.8907 | 0 | 157.9276
0 | 33.727 | 0 | 0 | 0 | 0 | 18.773 | 52.5 | 288.7952 | 3000 | 33.5449 | 3033.5449 | 3017.3226 | 0 | 159.2845
0 | 57.141 | 0 | 0 | 0 | 0 | -4.641 | 52.5 | 284.1542 | 3000 | 0 | 3000 | 3000 | 0 | 158.16
0 | 101.663 | 0 | 0 | 0 | 0 | -49.163 | 52.5 | 234.9911 | 3000 | 0 | 3000 | 3000 | 0 | 168.6
0 | 62.033 | 0 | 0 | 0 | 0 | -9.533 | 52.5 | 225.4582 | 3000 | 0 | 3000 | 3000 | 0 | 159.51
0 | 26.1913 | 0 | 0 | 0 | 0 | 26.3087 | 52.5 | 251.7669 | 3000 | 47.0102 | 3047.0102 | 3047.0102 | 0 | 154.9405
0 | 28.524 | 0 | 0 | 0 | 0 | 23.976 | 52.5 | 275.7429 | 3000 | 42.8419 | 3042.8419 | 3042.8419 | 0 | 152.2638
0 | 18.9235 | 0 | 0 | 0 | 0 | 33.5765 | 52.5 | 309.3194 | 3000 | 59.9967 | 3059.9967 | 3059.9967 | 0 | 149.236
0 | 228.5838 | 0 | 0 | 0 | 0 | -176.0838 | 52.5 | 133.2355 | 3000 | 0 | 3000 | 3000 | 0 | 143.07
0 | 28.1392 | 0 | 0 | 0 | 0 | 24.3608 | 52.5 | 157.5963 | 3000 | 43.5295 | 3043.5295 | 3038.122 | 0 | 143.2475
0 | 34.4218 | 0 | 0 | 0 | 0 | 18.0782 | 52.5 | 175.6745 | 3000 | 32.3033 | 3032.3033 | 2983.6365 | 0 | 140.6486
0 | 70.7324 | 0 | 0 | 0 | 0 | -18.2324 | 52.5 | 157.442 | 3000 | 0 | 3000 | 2881.0366 | 0 | 136.3018
0 | 76.4194 | 0 | 0 | 0 | 0 | -23.9194 | 52.5 | 133.5226 | 3000 | 0 | 3000 | 2702.5916 | 0 | 138.9402
0 | 56.0542 | 0 | 0 | 0 | 0 | -3.5542 | 52.5 | 129.9684 | 3000 | 0 | 3000 | 2653.9248 | 0 | 138.641
0 | 37.7691 | 0 | 0 | 0 | 0 | 14.7309 | 52.5 | 144.6993 | 3000 | 26.3221 | 3026.3221 | 2604.5429 | 0 | 138.0408
0 | 46.6953 | 0 | 0 | 0 | 0 | 5.8047 | 52.5 | 150.504 | 3000 | 10.3723 | 3010.3723 | 2188.4436 | 0 | 117.4757
0 | 42.1937 | 0 | 0 | 0 | 0 | 10.3063 | 52.5 | 160.8104 | 3000 | 18.4161 | 3018.4161 | 2131.5983 | 0 | 117.2379
0 | 48.6637 | 0 | 0 | 0 | 0 | 3.8363 | 52.5 | 164.6466 | 3000 | 6.8549 | 3006.8549 | 2314.7045 | 0 | 119.0453
0 | 43.5085 | 0 | 0 | 0 | 0 | 8.9915 | 52.5 | 173.6381 | 3000 | 16.0666 | 3016.0666 | 2377.9904 | 0 | 116.6167
0 | 45.4013 | 0 | 0 | 0 | 0 | 7.0987 | 52.5 | 180.7369 | 3000 | 12.6845 | 3012.6845 | 2374.6083 | 0 | 115.6672
0 | 45.274 | 0 | 0 | 0 | 0 | 7.226 | 52.5 | 187.9628 | 3000 | 12.9118 | 3012.9118 | 2272.0946 | 0 | 106.8793
0 | 37.6363 | 0 | 0 | 0 | 0 | 14.8637 | 52.5 | 202.8265 | 3000 | 26.5595 | 3026.5595 | 2485.8169 | 0 | 121.8299
0 | 35.8243 | 0 | 0 | 0 | 0 | 16.6757 | 52.5 | 219.5022 | 3000 | 29.7972 | 3029.7972 | 2662.0923 | 0 | 141.011
0 | 42.4339 | 0 | 0 | 0 | 0 | 10.0661 | 52.5 | 229.5683 | 3000 | 17.9869 | 3017.9869 | 2877.3938 | 0 | 156.4439
0 | 42.8421 | 0 | 0 | 0 | 0 | 9.6579 | 52.5 | 239.2263 | 3000 | 17.2575 | 3017.2575 | 2968.5906 | 0 | 166.1223
0 | 23.8915 | 0 | 0 | 0 | 0 | 28.6085 | 52.5 | 267.8348 | 3000 | 51.1196 | 3051.1196 | 3040.3048 | 0 | 169.801
0 | 25.3396 | 0 | 0 | 0 | 0 | 27.1604 | 52.5 | 294.9951 | 3000 | 48.5319 | 3048.5319 | 3048.5319 | 0 | 166.8157
0 | 14.1065 | 0 | 0 | 0 | 0 | 38.3935 | 52.5 | 333.3886 | 3000 | 68.604 | 3068.604 | 3068.604 | 0 | 180.1884
0 | 22.1088 | 0 | 0 | 0 | 0 | 30.3912 | 52.5 | 363.7798 | 3000 | 54.3051 | 3054.3051 | 3054.3051 | 0 | 165.2684
0 | 25.1893 | 0 | 0 | 0 | 0 | 27.3107 | 52.5 | 391.0905 | 3000 | 48.8006 | 3048.8006 | 3048.8006 | 0 | 160.9767
0 | 22.3337 | 0 | 0 | 0 | 0 | 30.1663 | 52.5 | 421.2568 | 3000 | 53.9031 | 3053.9031 | 3053.9031 | 0 | 157.1844
0 | 29.5244 | 0 | 0 | 0 | 0 | 22.9756 | 52.5 | 444.2323 | 3000 | 41.0543 | 3041.0543 | 3041.0543 | 0 | 156.1885
0 | 27.1882 | 0 | 0 | 0 | 0 | 25.3118 | 52.5 | 469.5441 | 3000 | 45.2288 | 3045.2288 | 3045.2288 | 0 | 151.9874
0 | 29.2559 | 0 | 0 | 0 | 0 | 23.2441 | 52.5 | 492.7882 | 3000 | 41.5341 | 3041.5341 | 3036.1267 | 0 | 150.9866
0 | 23.0164 | 0 | 0 | 0 | 0 | 29.4836 | 52.5 | 522.2718 | 3000 | 52.6833 | 3052.6833 | 3031.0536 | 0 | 156.857
0 | 30.5812 | 0 | 0 | 0 | 0 | 21.9188 | 52.5 | 544.1906 | 3000 | 39.166 | 3039.166 | 2985.0917 | 0 | 177.3144
0 | 29.0708 | 0 | 0 | 0 | 0 | 23.4292 | 52.5 | 567.6198 | 3000 | 41.8648 | 3041.8648 | 2863.4198 | 0 | 185.4923
0 | 44.6428 | 0 | 0 | 0 | 0 | 7.8572 | 52.5 | 575.477 | 3000 | 14.0398 | 3014.0398 | 2651.7424 | 0 | 172.5224
0 | 37.1644 | 0 | 0 | 0 | 0 | 15.3356 | 52.5 | 590.8126 | 3000 | 27.4026 | 3027.4026 | 2535.3269 | 0 | 159.5735
0 | 36.9607 | 0 | 0 | 0 | 0 | 15.5393 | 52.5 | 606.3519 | 3000 | 27.7666 | 3027.7666 | 2411.3202 | 0 | 147.5728
0 | 37.7968 | 0 | 0 | 0 | 0 | 14.7032 | 52.5 | 621.0551 | 3000 | 26.2727 | 3026.2727 | 2420.641 | 0 | 145.9647
0 | 39.9941 | 0 | 0 | 0 | 0 | 12.5059 | 52.5 | 633.5609 | 3000 | 22.3463 | 3022.3463 | 2049.0098 | 0 | 120.8916
0 | 42.9975 | 0 | 0 | 0 | 0 | 9.5025 | 52.5 | 643.0635 | 3000 | 16.9798 | 3016.9798 | 2076.0878 | 0 | 116.2609
0 | 77.8782 | 0 | 0 | 0 | 0 | -25.3782 | 52.5 | 617.6852 | 3000 | 0 | 3000 | 2415.9981 | 0 | 130.9229
0 | 108.7024 | 0 | 0 | 0 | 0 | -56.2024 | 52.5 | 561.4828 | 3000 | 0 | 3000 | 2199.7011 | 0 | 118.8498
0 | 78.5453 | 0 | 0 | 0 | 0 | -26.0453 | 52.5 | 535.4375 | 3000 | 0 | 3000 | 2205.1085 | 0 | 117.9513
0 | 53.5231 | 0 | 0 | 0 | 0 | -1.0231 | 52.5 | 534.4145 | 3000 | 0 | 3000 | 2626.8877 | 0 | 141.9045
0 | 34.5548 | 0 | 0 | 0 | 0 | 17.9452 | 52.5 | 552.3597 | 3000 | 32.0657 | 3032.0657 | 2680.5831 | 0 | 154.2944
0 | 55.8292 | 0 | 0 | 0 | 0 | -3.3292 | 52.5 | 549.0305 | 3000 | 0 | 3000 | 2924.296 | 0 | 178.2066
0 | 28.8598 | 0 | 0 | 0 | 0 | 23.6402 | 52.5 | 572.6707 | 3000 | 42.2418 | 3042.2418 | 3031.427 | 0 | 179.0967
0 | 26.8624 | 0 | 0 | 0 | 0 | 25.6376 | 52.5 | 598.3082 | 3000 | 45.8109 | 3045.8109 | 3045.8109 | 0 | 177.9972
0 | 30.7093 | 0 | 0 | 0 | 0 | 21.7907 | 52.5 | 620.0989 | 3000 | 38.937 | 3038.937 | 3038.937 | 0 | 181.1206
0 | 26.0919 | 0 | 0 | 0 | 0 | 26.4081 | 52.5 | 646.507 | 3000 | 47.1877 | 3047.1877 | 3047.1877 | 0 | 162.9331
0 | 15.6266 | 0 | 0 | 0 | 0 | 36.8734 | 52.5 | 683.3804 | 3000 | 65.8879 | 3065.8879 | 3065.8879 | 0 | 162.6147
0 | 22.8844 | 0 | 0 | 0 | 0 | 29.6156 | 52.5 | 712.996 | 3000 | 52.9191 | 3052.9191 | 3052.9191 | 0 | 156.5232
0 | 23.4858 | 0 | 0 | 0 | 0 | 29.0142 | 52.5 | 742.0103 | 3000 | 51.8446 | 3051.8446 | 3051.8446 | 0 | 152.3786
0 | 29.9283 | 0 | 0 | 0 | 0 | 22.5717 | 52.5 | 764.5819 | 3000 | 40.3326 | 3040.3326 | 3040.3326 | 0 | 148.6419
0 | 35.362 | 0 | 0 | 0 | 0 | 17.138 | 52.5 | 781.72 | 3000 | 30.6234 | 3030.6234 | 3025.2159 | 0 | 145.6036
0 | 44.7792 | 0 | 0 | 0 | 0 | 7.7208 | 52.5 | 789.4408 | 3000 | 13.7961 | 3013.7961 | 2981.3515 | 0 | 149.3955
0 | 101.2738 | 0 | 0 | 0 | 0 | -48.7738 | 52.5 | 740.667 | 3000 | 0 | 3000 | 2918.8886 | 0 | 158.233
0 | 110.9519 | 0 | 0 | 0 | 0 | -58.4519 | 52.5 | 682.2151 | 3000 | 0 | 3000 | 2853.9995 | 0 | 176.8053
0 | 106.3658 | 0 | 0 | 0 | 0 | -53.8658 | 52.5 | 628.3493 | 3000 | 0 | 3000 | 2789.1104 | 0 | 178.8935
0 | 88.3456 | 0 | 0 | 0 | 0 | -35.8456 | 52.5 | 592.5036 | 3000 | 0 | 3000 | 2756.6659 | 0 | 173.5321
0 | 71.8736 | 0 | 0 | 0 | 0 | -19.3736 | 52.5 | 573.1301 | 3000 | 0 | 3000 | 2707.999 | 0 | 168.248
0 | 118.4989 | 0 | 0 | 0 | 0 | -65.9989 | 52.5 | 507.1312 | 3000 | 0 | 3000 | 2626.8877 | 0 | 162.6569
0 | 117.4387 | 0 | 0 | 0 | 0 | -64.9387 | 52.5 | 442.1924 | 3000 | 0 | 3000 | 2534.9614 | 0 | 144.6702
0 | 68.7479 | 0 | 0 | 0 | 0 | -16.2479 | 52.5 | 425.9446 | 3000 | 0 | 3000 | 2589.0357 | 0 | 142.1381
0 | 47.6313 | 0 | 0 | 0 | 0 | 4.8687 | 52.5 | 430.8133 | 3000 | 8.6998 | 3008.6998 | 2576.1058 | 0 | 140.2947
0 | 53.2358 | 0 | 0 | 0 | 0 | -0.73585 | 52.5 | 430.0775 | 3000 | 0 | 3000 | 2659.3322 | 0 | 143.7103
0 | 43.3847 | 0 | 0 | 0 | 0 | 9.1153 | 52.5 | 439.1928 | 3000 | 16.2878 | 3016.2878 | 2756.7314 | 0 | 149.6905
0 | 33.5209 | 0 | 0 | 0 | 0 | 18.9791 | 52.5 | 458.1718 | 3000 | 33.9131 | 3033.9131 | 2850.0606 | 0 | 172.0867
0 | 49.4846 | 0 | 0 | 0 | 0 | 3.0154 | 52.5 | 461.1872 | 3000 | 5.3881 | 3005.3881 | 2826.943 | 0 | 180.3872
0 | 35.7671 | 0 | 0 | 0 | 0 | 16.7329 | 52.5 | 477.9201 | 3000 | 29.8994 | 3029.8994 | 2883.8989 | 0 | 195.0669
0 | 30.4011 | 0 | 0 | 0 | 0 | 22.0989 | 52.5 | 500.019 | 3000 | 39.4878 | 3039.4878 | 3007.0432 | 0 | 201.3516
0 | 29.6932 | 0 | 0 | 0 | 0 | 22.8068 | 52.5 | 522.8258 | 3000 | 40.7527 | 3040.7527 | 3040.7527 | 0 | 195.1859
0 | 18.8458 | 0 | 0 | 0 | 0 | 33.6542 | 52.5 | 556.48 | 3000 | 60.1356 | 3060.1356 | 3060.1356 | 0 | 195.8487
0 | 34.9186 | 0 | 0 | 0 | 0 | 17.5814 | 52.5 | 574.0614 | 3000 | 31.4157 | 3031.4157 | 3031.4157 | 0 | 182.4609
0 | 428.9361 | 0 | 0 | 0 | 0 | -376.4361 | 52.5 | 197.6253 | 3000 | 0 | 3000 | 3000 | 0 | 165.06
0 | 27.0097 | 0 | 0 | 0 | 0 | 25.4903 | 52.5 | 223.1156 | 3000 | 45.5478 | 3045.5478 | 3045.5478 | 0 | 164.0637
0 | 22.648 | 0 | 0 | 0 | 0 | 29.852 | 52.5 | 252.9676 | 3000 | 53.3416 | 3053.3416 | 3053.3416 | 0 | 162.1935
0 | 28.6753 | 0 | 0 | 0 | 0 | 23.8247 | 52.5 | 276.7923 | 3000 | 42.5716 | 3042.5716 | 3042.5716 | 0 | 159.0656
0 | 33.1305 | 0 | 0 | 0 | 0 | 19.3695 | 52.5 | 296.1619 | 3000 | 34.6108 | 3034.6108 | 3023.796 | 0 | 159.9588
0 | 39.8033 | 0 | 0 | 0 | 0 | 12.6967 | 52.5 | 308.8585 | 3000 | 22.6872 | 3022.6872 | 2957.7981 | 0 | 160.0169
0 | 86.2308 | 0 | 0 | 0 | 0 | -33.7308 | 52.5 | 275.1277 | 3000 | 0 | 3000 | 2864.8144 | 0 | 169.11
0 | 78.7351 | 0 | 0 | 0 | 0 | -26.2351 | 52.5 | 248.8926 | 3000 | 0 | 3000 | 2626.8877 | 0 | 180.6773
0 | 67.134 | 0 | 0 | 0 | 0 | -14.634 | 52.5 | 234.2587 | 3000 | 0 | 3000 | 2491.702 | 0 | 173.6218
0 | 61.7501 | 0 | 0 | 0 | 0 | -9.2501 | 52.5 | 225.0085 | 3000 | 0 | 3000 | 2253.7753 | 0 | 147.0138
0 | 72.7892 | 0 | 0 | 0 | 0 | -20.2892 | 52.5 | 204.7193 | 3000 | 0 | 3000 | 1745.4773 | 0 | 111.3265
0 | 108.5776 | 0 | 0 | 0 | 0 | -56.0776 | 52.5 | 148.6417 | 3000 | 0 | 3000 | 1480.5135 | 0 | 92.8282
0 | 117.4841 | 0 | 0 | 0 | 0 | -64.9841 | 52.5 | 83.6576 | 3000 | 0 | 3000 | 1285.8462 | 0 | 77.1508
0 | 100.5406 | 0 | 0 | 0 | 0 | -48.0406 | 52.5 | 35.617 | 3000 | 0 | 3000 | 1345.3279 | 0 | 78.2174
0 | 28.0363 | 0 | 0 | 0 | 0 | 24.4637 | 52.5 | 60.0807 | 3000 | 43.7134 | 3043.7134 | 1891.9319 | 0 | 105.0401
0 | 49.7693 | 0 | 0 | 0 | 0 | 2.7307 | 52.5 | 62.8114 | 3000 | 4.8794 | 3004.8794 | 2280.2844 | 0 | 126.6698
0 | 45.1252 | 0 | 0 | 0 | 0 | 7.3748 | 52.5 | 70.1862 | 3000 | 13.1777 | 3013.1777 | 2018.2115 | 0 | 114.2308
0 | 30.9808 | 0 | 0 | 0 | 0 | 21.5192 | 52.5 | 91.7053 | 3000 | 38.4519 | 3038.4519 | 2308.4495 | 0 | 145.4323
0 | 44.7207 | 0 | 0 | 0 | 0 | 7.7793 | 52.5 | 99.4846 | 3000 | 13.9005 | 3013.9005 | 2608.3436 | 0 | 174.759
0 | 37.3323 | 0 | 0 | 0 | 0 | 15.1677 | 52.5 | 114.6523 | 3000 | 27.1027 | 3027.1027 | 2799.9909 | 0 | 193.2274
0 | 25.6313 | 0 | 0 | 0 | 0 | 26.8687 | 52.5 | 141.521 | 3000 | 48.0108 | 3048.0108 | 3020.9737 | 0 | 210.9244
0 | 30.8721 | 0 | 0 | 0 | 0 | 21.6279 | 52.5 | 163.149 | 3000 | 38.6462 | 3038.6462 | 3038.6462 | 0 | 209.302
0 | 27.3589 | 0 | 0 | 0 | 0 | 25.1411 | 52.5 | 188.2901 | 3000 | 44.9238 | 3044.9238 | 3044.9238 | 0 | 199.8688
0 | 30.8983 | 0 | 0 | 0 | 0 | 21.6017 | 52.5 | 209.8918 | 3000 | 38.5994 | 3038.5994 | 3038.5994 | 0 | 185.0507
0 | 22.3561 | 0 | 0 | 0 | 0 | 30.1439 | 52.5 | 240.0357 | 3000 | 53.8632 | 3053.8632 | 3053.8632 | 0 | 169.3978
0 | 29.8457 | 0 | 0 | 0 | 0 | 22.6543 | 52.5 | 262.69 | 3000 | 40.4802 | 3040.4802 | 3040.4802 | 0 | 164.1859
0 | 30.9315 | 0 | 0 | 0 | 0 | 21.5685 | 52.5 | 284.2585 | 3000 | 38.54 | 3038.54 | 3038.54 | 0 | 154.9959
0 | 30.8045 | 0 | 0 | 0 | 0 | 21.6955 | 52.5 | 305.954 | 3000 | 38.767 | 3038.767 | 3038.767 | 0 | 149.9024
0 | 31.144 | 0 | 0 | 0 | 0 | 21.356 | 52.5 | 327.31 | 3000 | 38.1604 | 3038.1604 | 3032.753 | 0 | 144.2681
0 | 85.1475 | 0 | 0 | 0 | 0 | -32.6475 | 52.5 | 294.6625 | 3000 | 0 | 3000 | 2902.6663 | 0 | 140.8374
0 | 101.9821 | 0 | 0 | 0 | 0 | -49.4821 | 52.5 | 245.1804 | 3000 | 0 | 3000 | 2789.1104 | 0 | 156.7201
0 | 85.4481 | 0 | 0 | 0 | 0 | -32.9481 | 52.5 | 212.2323 | 3000 | 0 | 3000 | 2497.1095 | 0 | 160.9886
0 | 79.2032 | 0 | 0 | 0 | 0 | -26.7032 | 52.5 | 185.529 | 3000 | 0 | 3000 | 2134.812 | 0 | 136.5426
0 | 96.8037 | 0 | 0 | 0 | 0 | -44.3037 | 52.5 | 141.2254 | 3000 | 0 | 3000 | 1886.0704 | 0 | 117.8794
0 | 73.3503 | 0 | 0 | 0 | 0 | -20.8503 | 52.5 | 120.3751 | 3000 | 0 | 3000 | 1740.0699 | 0 | 104.2476
0 | 104.3608 | 0 | 0 | 0 | 0 | -51.8608 | 52.5 | 68.5143 | 3000 | 0 | 3000 | 1685.9957 | 0 | 98.6139
0 | 102.8932 | 0 | 0 | 0 | 0 | -50.3932 | 52.5 | 18.1211 | 3000 | 0 | 3000 | 1761.6996 | 0 | 97.6158
0 | 70.6211 | 0 | 0 | 0 | 0 | -18.1211 | 52.5 | 0 | 3000 | 0 | 3000 | 2059.108 | 0 | 111.7066
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2145.6268 | 0 | 115.8424
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2156.4417 | 0 | 118.0005
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2415.9981 | 0 | 130.9713
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2513.3317 | 0 | 157.6362
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2729.6287 | 0 | 176.9891
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2918.8886 | 0 | 202.8628
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2989.1851 | 0 | 205.1179
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 192.48
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 189.03
0 | 27.3002 | 0 | 0 | 0 | 0 | 25.1998 | 52.5 | 25.1998 | 3000 | 45.0288 | 3045.0288 | 3045.0288 | 0 | 178.8345
0 | 31.5567 | 0 | 0 | 0 | 0 | 20.9433 | 52.5 | 46.1431 | 3000 | 37.4228 | 3037.4228 | 3037.4228 | 0 | 160.5582
0 | 25.0786 | 0 | 0 | 0 | 0 | 27.4214 | 52.5 | 73.5644 | 3000 | 48.9983 | 3048.9983 | 3048.9983 | 0 | 155.1025
0 | 32.2415 | 0 | 0 | 0 | 0 | 20.2585 | 52.5 | 93.8229 | 3000 | 36.1992 | 3036.1992 | 3036.1992 | 0 | 152.8726
0 | 31.8238 | 0 | 0 | 0 | 0 | 20.6762 | 52.5 | 114.4991 | 3000 | 36.9456 | 3036.9456 | 3036.9456 | 0 | 145.986
0 | 41.7071 | 0 | 0 | 0 | 0 | 10.7929 | 52.5 | 125.2921 | 3000 | 19.2855 | 3019.2855 | 3013.8781 | 0 | 145.9018
0 | 67.3668 | 0 | 0 | 0 | 0 | -14.8668 | 52.5 | 110.4253 | 3000 | 0 | 3000 | 2918.8886 | 0 | 145.9444
0 | 68.4197 | 0 | 0 | 0 | 0 | -15.9197 | 52.5 | 94.5056 | 3000 | 0 | 3000 | 2783.703 | 0 | 160.8145
0 | 74.0152 | 0 | 0 | 0 | 0 | -21.5152 | 52.5 | 72.9904 | 3000 | 0 | 3000 | 2502.5169 | 0 | 167.2682
0 | 110.708 | 0 | 0 | 0 | 0 | -58.208 | 52.5 | 14.7824 | 3000 | 0 | 3000 | 2226.7382 | 0 | 149.9263
0 | 67.2824 | 0 | 0 | 0 | 0 | -14.7824 | 52.5 | 0 | 3000 | 0 | 3000 | 1848.2184 | 0 | 119.0807
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1588.662 | 0 | 99.8633
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1458.8838 | 0 | 90.4946
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1707.6254 | 0 | 100.767
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2156.4417 | 0 | 117.7202
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1723.8476 | 0 | 93.7773
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2464.6649 | 0 | 133.5848
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2264.5902 | 0 | 123.1031
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2464.6649 | 0 | 150.8621
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2745.851 | 0 | 181.638
0 | 25.3646 | 0 | 0 | 0 | 0 | 27.1354 | 52.5 | 27.1354 | 3000 | 48.4873 | 3048.4873 | 2978.1908 | 0 | 198.2284
0 | 35.8571 | 0 | 0 | 0 | 0 | 16.6429 | 52.5 | 43.7782 | 3000 | 29.7386 | 3029.7386 | 3024.3312 | 0 | 201.4507
0 | 96.2782 | 0 | 0 | 0 | 0 | -43.7782 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 192.48
0 | 19.4153 | 0 | 0 | 0 | 0 | 33.0847 | 52.5 | 33.0847 | 3000 | 59.1179 | 3059.1179 | 3059.1179 | 0 | 200.6781
0 | 19.3406 | 0 | 0 | 0 | 0 | 33.1594 | 52.5 | 66.2441 | 3000 | 59.2515 | 3059.2515 | 3059.2515 | 0 | 183.3104
0 | 31.01 | 0 | 0 | 0 | 0 | 21.49 | 52.5 | 87.7341 | 3000 | 38.3997 | 3038.3997 | 3038.3997 | 0 | 170.7884
0 | 26.294 | 0 | 0 | 0 | 0 | 26.206 | 52.5 | 113.94 | 3000 | 46.8266 | 3046.8266 | 3046.8266 | 0 | 161.7256
0 | 37.2776 | 0 | 0 | 0 | 0 | 15.2224 | 52.5 | 129.1624 | 3000 | 27.2003 | 3027.2003 | 3027.2003 | 0 | 156.8392
0 | 57.3606 | 0 | 0 | 0 | 0 | -4.8606 | 52.5 | 124.3018 | 3000 | 0 | 3000 | 3000 | 0 | 151.62
0 | 89.2159 | 0 | 0 | 0 | 0 | -36.7159 | 52.5 | 87.5859 | 3000 | 0 | 3000 | 2994.5926 | 0 | 147.6933
0 | 100.1762 | 0 | 0 | 0 | 0 | -47.6762 | 52.5 | 39.9097 | 3000 | 0 | 3000 | 2935.1109 | 0 | 143.7617
0 | 76.3464 | 0 | 0 | 0 | 0 | -23.8464 | 52.5 | 16.0633 | 3000 | 0 | 3000 | 2778.2956 | 0 | 138.6647
0 | 68.5633 | 0 | 0 | 0 | 0 | -16.0633 | 52.5 | 0 | 3000 | 0 | 3000 | 2529.554 | 0 | 128.476
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2648.5174 | 0 | 136.8224
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2183.4788 | 0 | 113.1042
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2697.1842 | 0 | 134.9671
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2870.2218 | 0 | 137.5123
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2951.3332 | 0 | 137.6207
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2297.0347 | 0 | 98.2901
0 | 50.6079 | 0 | 0 | 0 | 0 | 1.8921 | 52.5 | 1.8921 | 3000 | 3.3809 | 3003.3809 | 1921.8959 | 0 | 82.6031
0 | 53.5929 | 0 | 0 | 0 | 0 | -1.0929 | 52.5 | 0.79922 | 3000 | 0 | 3000 | 2053.7006 | 0 | 89.9726
0 | 43.1865 | 0 | 0 | 0 | 0 | 9.3135 | 52.5 | 10.1127 | 3000 | 16.6419 | 3016.6419 | 2070.3425 | 0 | 96.9541
0 | 35.9751 | 0 | 0 | 0 | 0 | 16.5249 | 52.5 | 26.6376 | 3000 | 29.5278 | 3029.5278 | 2867.305 | 0 | 144.9136
0 | 42.507 | 0 | 0 | 0 | 0 | 9.993 | 52.5 | 36.6306 | 3000 | 17.8562 | 3017.8562 | 2936.7448 | 0 | 152.3877
0 | 39.8861 | 0 | 0 | 0 | 0 | 12.6139 | 52.5 | 49.2445 | 3000 | 22.5394 | 3022.5394 | 2833.2796 | 0 | 151.2405
0 | 28.4333 | 0 | 0 | 0 | 0 | 24.0667 | 52.5 | 73.3112 | 3000 | 43.004 | 3043.004 | 3015.9669 | 0 | 158.4287
0 | 26.8766 | 0 | 0 | 0 | 0 | 25.6234 | 52.5 | 98.9347 | 3000 | 45.7857 | 3045.7857 | 3045.7857 | 0 | 160.5738
0 | 16.9483 | 0 | 0 | 0 | 0 | 35.5517 | 52.5 | 134.4864 | 3000 | 63.5262 | 3063.5262 | 3063.5262 | 0 | 166.0431
0 | 23.1711 | 0 | 0 | 0 | 0 | 29.3289 | 52.5 | 163.8153 | 3000 | 52.4068 | 3052.4068 | 3052.4068 | 0 | 159.6104
0 | 28.9867 | 0 | 0 | 0 | 0 | 23.5133 | 52.5 | 187.3286 | 3000 | 42.0151 | 3042.0151 | 3042.0151 | 0 | 150.5797
0 | 31.8408 | 0 | 0 | 0 | 0 | 20.6592 | 52.5 | 207.9878 | 3000 | 36.9153 | 3036.9153 | 3036.9153 | 0 | 143.9498
0 | 25.8257 | 0 | 0 | 0 | 0 | 26.6743 | 52.5 | 234.6622 | 3000 | 47.6635 | 3047.6635 | 3047.6635 | 0 | 143.1792
0 | 229.3561 | 0 | 0 | 0 | 0 | -176.8561 | 52.5 | 57.806 | 3000 | 0 | 3000 | 3000 | 0 | 135.81
0 | 62.3281 | 0 | 0 | 0 | 0 | -9.8281 | 52.5 | 47.9779 | 3000 | 0 | 3000 | 2994.5926 | 0 | 134.7567
0 | 82.0357 | 0 | 0 | 0 | 0 | -29.5357 | 52.5 | 18.4423 | 3000 | 0 | 3000 | 2918.8886 | 0 | 131.4376
0 | 70.9423 | 0 | 0 | 0 | 0 | -18.4423 | 52.5 | 0 | 3000 | 0 | 3000 | 2702.5916 | 0 | 121.2923
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2351.109 | 0 | 107.3751
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2107.7748 | 0 | 96.9998
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1783.3293 | 0 | 82.051
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1621.1066 | 0 | 72.4473
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1648.1437 | 0 | 74.3807
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1783.3293 | 0 | 78.9837
0 | 47.2822 | 0 | 0 | 0 | 0 | 5.2178 | 52.5 | 5.2178 | 3000 | 9.3234 | 3009.3234 | 1711.5414 | 0 | 68.4617
0 | 31.3977 | 0 | 0 | 0 | 0 | 21.1023 | 52.5 | 26.3201 | 3000 | 37.707 | 3037.707 | 1739.925 | 0 | 71.6849
0 | 48.8165 | 0 | 0 | 0 | 0 | 3.6835 | 52.5 | 30.0036 | 3000 | 6.582 | 3006.582 | 1979.1712 | 0 | 70.9731
0 | 44.9683 | 0 | 0 | 0 | 0 | 7.5317 | 52.5 | 37.5353 | 3000 | 13.4581 | 3013.4581 | 2202.3443 | 0 | 94.7889
0 | 40.6488 | 0 | 0 | 0 | 0 | 11.8512 | 52.5 | 49.3864 | 3000 | 21.1764 | 3021.1764 | 2318.2112 | 0 | 109.0023
0 | 41.1596 | 0 | 0 | 0 | 0 | 11.3404 | 52.5 | 60.7268 | 3000 | 20.2638 | 3020.2638 | 2614.7069 | 0 | 133.0886
0 | 49.9598 | 0 | 0 | 0 | 0 | 2.5402 | 52.5 | 63.267 | 3000 | 4.539 | 3004.539 | 2842.3162 | 0 | 163.2058
0 | 23.7777 | 0 | 0 | 0 | 0 | 28.7223 | 52.5 | 91.9893 | 3000 | 51.3229 | 3051.3229 | 3040.508 | 0 | 178.1738
0 | 33.9495 | 0 | 0 | 0 | 0 | 18.5505 | 52.5 | 110.5398 | 3000 | 33.1474 | 3033.1474 | 3033.1474 | 0 | 181.7462
0 | 27.8331 | 0 | 0 | 0 | 0 | 24.6669 | 52.5 | 135.2068 | 3000 | 44.0766 | 3044.0766 | 3044.0766 | 0 | 187.576
0 | 32.5373 | 0 | 0 | 0 | 0 | 19.9627 | 52.5 | 155.1695 | 3000 | 35.6707 | 3035.6707 | 3035.6707 | 0 | 166.9619
0 | 23.3942 | 0 | 0 | 0 | 0 | 29.1058 | 52.5 | 184.2753 | 3000 | 52.0081 | 3052.0081 | 3052.0081 | 0 | 160.1389
0 | 27.294 | 0 | 0 | 0 | 0 | 25.206 | 52.5 | 209.4813 | 3000 | 45.0398 | 3045.0398 | 3045.0398 | 0 | 152.5869
0 | 28.8432 | 0 | 0 | 0 | 0 | 23.6568 | 52.5 | 233.1381 | 3000 | 42.2716 | 3042.2716 | 3042.2716 | 0 | 146.455
0 | 19.4964 | 0 | 0 | 0 | 0 | 33.0036 | 52.5 | 266.1416 | 3000 | 58.973 | 3058.973 | 3058.973 | 0 | 137.8679
0 | 28.9616 | 0 | 0 | 0 | 0 | 23.5384 | 52.5 | 289.68 | 3000 | 42.06 | 3042.06 | 3036.6525 | 0 | 131.0316
0 | 35.5941 | 0 | 0 | 0 | 0 | 16.9059 | 52.5 | 306.5859 | 3000 | 30.2085 | 3030.2085 | 2965.3194 | 0 | 136.3454
0 | 79.4122 | 0 | 0 | 0 | 0 | -26.9122 | 52.5 | 279.6737 | 3000 | 0 | 3000 | 2864.8144 | 0 | 151.5773
0 | 83.1468 | 0 | 0 | 0 | 0 | -30.6468 | 52.5 | 249.0269 | 3000 | 0 | 3000 | 2675.5545 | 0 | 165.7506
0 | 99.5065 | 0 | 0 | 0 | 0 | -47.0065 | 52.5 | 202.0204 | 3000 | 0 | 3000 | 2513.3317 | 0 | 158.3399
0 | 99.4791 | 0 | 0 | 0 | 0 | -46.9791 | 52.5 | 155.0414 | 3000 | 0 | 3000 | 2351.109 | 0 | 138.6449
0 | 60.8565 | 0 | 0 | 0 | 0 | -8.3565 | 52.5 | 146.6848 | 3000 | 0 | 3000 | 2242.9605 | 0 | 130.8992
0 | 45.8911 | 0 | 0 | 0 | 0 | 6.6089 | 52.5 | 153.2937 | 3000 | 11.8092 | 3011.8092 | 1908.6944 | 0 | 106.467
0 | 37.9622 | 0 | 0 | 0 | 0 | 14.5378 | 52.5 | 167.8314 | 3000 | 25.9771 | 3025.9771 | 2074.2702 | 0 | 104.2736
0 | 58.0062 | 0 | 0 | 0 | 0 | -5.5062 | 52.5 | 162.3252 | 3000 | 0 | 3000 | 1426.4393 | 0 | 72.6343
0 | 34.0994 | 0 | 0 | 0 | 0 | 18.4006 | 52.5 | 180.7258 | 3000 | 32.8794 | 3032.8794 | 1681.0231 | 0 | 85.5641
0 | 46.7104 | 0 | 0 | 0 | 0 | 5.7896 | 52.5 | 186.5155 | 3000 | 10.3453 | 3010.3453 | 2112.7127 | 0 | 108.847
0 | 53.15 | 0 | 0 | 0 | 0 | -0.64999 | 52.5 | 185.8655 | 3000 | 0 | 3000 | 2237.553 | 0 | 120.6265
0 | 238.3655 | 0 | 0 | 0 | 0 | -185.8655 | 52.5 | 0 | 3000 | 0 | 3000 | 2378.1461 | 0 | 142.6412
0 | 41.8712 | 0 | 0 | 0 | 0 | 10.6288 | 52.5 | 10.6288 | 3000 | 18.9922 | 3018.9922 | 2575.5833 | 0 | 164.7858
0 | 45.7077 | 0 | 0 | 0 | 0 | 6.7923 | 52.5 | 17.4211 | 3000 | 12.137 | 3012.137 | 2817.4697 | 0 | 194.2364
0 | 22.6042 | 0 | 0 | 0 | 0 | 29.8958 | 52.5 | 47.3169 | 3000 | 53.4198 | 3053.4198 | 3026.3827 | 0 | 206.823
0 | 24.1959 | 0 | 0 | 0 | 0 | 28.3041 | 52.5 | 75.621 | 3000 | 50.5757 | 3050.5757 | 3050.5757 | 0 | 200.0873
0 | 21.6397 | 0 | 0 | 0 | 0 | 30.8603 | 52.5 | 106.4813 | 3000 | 55.1433 | 3055.1433 | 3055.1433 | 0 | 204.2974
0 | 25.5077 | 0 | 0 | 0 | 0 | 26.9923 | 52.5 | 133.4736 | 3000 | 48.2317 | 3048.2317 | 3048.2317 | 0 | 177.8948
0 | 30.4587 | 0 | 0 | 0 | 0 | 22.0413 | 52.5 | 155.5149 | 3000 | 39.3849 | 3039.3849 | 3039.3849 | 0 | 162.9414
0 | 24.815 | 0 | 0 | 0 | 0 | 27.685 | 52.5 | 183.1999 | 3000 | 49.4694 | 3049.4694 | 3049.4694 | 0 | 160.3411
0 | 29.8956 | 0 | 0 | 0 | 0 | 22.6044 | 52.5 | 205.8043 | 3000 | 40.3911 | 3040.3911 | 3040.3911 | 0 | 158.0395
0 | 32.7859 | 0 | 0 | 0 | 0 | 19.7141 | 52.5 | 225.5184 | 3000 | 35.2265 | 3035.2265 | 3035.2265 | 0 | 156.3749
0 | 27.2061 | 0 | 0 | 0 | 0 | 25.2939 | 52.5 | 250.8124 | 3000 | 45.1969 | 3045.1969 | 3039.7895 | 0 | 150.7432
0 | 54.781 | 0 | 0 | 0 | 0 | -2.281 | 52.5 | 248.5314 | 3000 | 0 | 3000 | 2853.9995 | 0 | 150.4058
0 | 102.6676 | 0 | 0 | 0 | 0 | -50.1676 | 52.5 | 198.3638 | 3000 | 0 | 3000 | 2643.1099 | 0 | 158.9831
0 | 62.7749 | 0 | 0 | 0 | 0 | -10.2749 | 52.5 | 188.0889 | 3000 | 0 | 3000 | 2340.2941 | 0 | 147.5321
0 | 114.3933 | 0 | 0 | 0 | 0 | -61.8933 | 52.5 | 126.1956 | 3000 | 0 | 3000 | 2069.9229 | 0 | 136.5735
0 | 88.9271 | 0 | 0 | 0 | 0 | -36.4271 | 52.5 | 89.7685 | 3000 | 0 | 3000 | 1788.7367 | 0 | 115.6418
0 | 91.0109 | 0 | 0 | 0 | 0 | -38.5109 | 52.5 | 51.2576 | 3000 | 0 | 3000 | 1567.0323 | 0 | 96.2158
0 | 85.5736 | 0 | 0 | 0 | 0 | -33.0736 | 52.5 | 18.184 | 3000 | 0 | 3000 | 1421.0318 | 0 | 82.6756
0 | 70.684 | 0 | 0 | 0 | 0 | -18.184 | 52.5 | 0 | 3000 | 0 | 3000 | 1361.5502 | 0 | 75.389
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1388.5873 | 0 | 76.6917
0 | 42.696 | 0 | 0 | 0 | 0 | 9.804 | 52.5 | 9.804 | 3000 | 17.5184 | 3017.5184 | 1519.6616 | 0 | 82.9887
0 | 42.3825 | 0 | 0 | 0 | 0 | 10.1175 | 52.5 | 19.9215 | 3000 | 18.0787 | 3018.0787 | 1714.8892 | 0 | 94.9877
0 | 47.7306 | 0 | 0 | 0 | 0 | 4.7694 | 52.5 | 24.6909 | 3000 | 8.5223 | 3008.5223 | 1970.2967 | 0 | 117.9026
0 | 54.6051 | 0 | 0 | 0 | 0 | -2.1051 | 52.5 | 22.5858 | 3000 | 0 | 3000 | 2253.7753 | 0 | 153.1891
0 | 30.3455 | 0 | 0 | 0 | 0 | -22.5858 | 7.7597 | 0 | 443.4089 | 0 | 443.4089 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173.0376 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.2223 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 26.3795 | 0 | 0 | 0 | 0 | 26.1205 | 52.5 | 26.1205 | 3000 | 46.6739 | 3046.6739 | 3046.6739 | 0 | 184.3238
0 | 26.5829 | 0 | 0 | 0 | 0 | 25.9171 | 52.5 | 52.0376 | 3000 | 46.3104 | 3046.3104 | 3046.3104 | 0 | 174.4013
0 | 23.013 | 0 | 0 | 0 | 0 | 29.487 | 52.5 | 81.5246 | 3000 | 52.6893 | 3052.6893 | 3052.6893 | 0 | 166.8295
0 | 17.1591 | 0 | 0 | 0 | 0 | 35.3409 | 52.5 | 116.8655 | 3000 | 63.1495 | 3063.1495 | 3063.1495 | 0 | 163.8172
0 | 22.9771 | 0 | 0 | 0 | 0 | 29.5229 | 52.5 | 146.3884 | 3000 | 52.7535 | 3052.7535 | 3052.7535 | 0 | 158.499
0 | 31.4537 | 0 | 0 | 0 | 0 | 21.0463 | 52.5 | 167.4347 | 3000 | 37.6069 | 3037.6069 | 3032.1995 | 0 | 156.4615
0 | 51.1985 | 0 | 0 | 0 | 0 | 1.3015 | 52.5 | 168.7362 | 3000 | 2.3256 | 3002.3256 | 2904.9919 | 0 | 154.6618
0 | 89.6666 | 0 | 0 | 0 | 0 | -37.1666 | 52.5 | 131.5696 | 3000 | 0 | 3000 | 2675.5545 | 0 | 162.0048
0 | 82.858 | 0 | 0 | 0 | 0 | -30.358 | 52.5 | 101.2116 | 3000 | 0 | 3000 | 2372.7387 | 0 | 160.8717
0 | 85.1761 | 0 | 0 | 0 | 0 | -68.1427 | 17.0334 | 33.0689 | 973.3365 | 0 | 973.3365 | 0 | 0 | 0
0 | 54.0768 | 0 | 0 | 0 | 0 | -33.0689 | 21.0078 | 0 | 1200.4484 | 0 | 1200.4484 | 0 | 0 | 0
0 | 42.0432 | 0 | 0 | 0 | 0 | 10.4568 | 52.5 | 10.4568 | 3000 | 18.685 | 3018.685 | 1607.347 | 0 | 104.5097
0 | 39.8097 | 0 | 0 | 0 | 0 | 12.6903 | 52.5 | 23.1472 | 3000 | 22.6759 | 3022.6759 | 1465.3375 | 0 | 84.1104
0 | 75.6472 | 0 | 0 | 0 | 0 | -23.1472 | 52.5 | 0 | 3000 | 0 | 3000 | 1404.8096 | 0 | 76.6324
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1453.4764 | 0 | 80.6825
0 | 48.0181 | 0 | 0 | 0 | 0 | 4.4819 | 52.5 | 4.4819 | 3000 | 8.0086 | 3008.0086 | 1575.0409 | 0 | 86.4855
0 | 46.7452 | 0 | 0 | 0 | 0 | 5.7548 | 52.5 | 10.2366 | 3000 | 10.283 | 3010.283 | 1771.9826 | 0 | 102.6864
0 | 38.6987 | 0 | 0 | 0 | 0 | 13.8013 | 52.5 | 24.0379 | 3000 | 24.661 | 3024.661 | 2083.769 | 0 | 132.111
0 | 34.8257 | 0 | 0 | 0 | 0 | -24.0379 | 10.7878 | 0 | 616.4465 | 0 | 616.4465 | 0 | 0 | 0
0 | 6.6241 | 0 | 0 | 0 | 0 | 0 | 6.6241 | 0 | 378.5198 | 0 | 378.5198 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151.4079 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.0371 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 24.1539 | 0 | 0 | 0 | 0 | 28.3461 | 52.5 | 28.3461 | 3000 | 50.6506 | 3050.6506 | 3050.6506 | 0 | 197.6822
0 | 30.1692 | 0 | 0 | 0 | 0 | 22.3308 | 52.5 | 50.6768 | 3000 | 39.9021 | 3039.9021 | 3039.9021 | 0 | 184.2789
0 | 27.2978 | 0 | 0 | 0 | 0 | 25.2022 | 52.5 | 75.879 | 3000 | 45.0329 | 3045.0329 | 3045.0329 | 0 | 173.7191
0 | 30.4625 | 0 | 0 | 0 | 0 | 22.0375 | 52.5 | 97.9165 | 3000 | 39.3781 | 3039.3781 | 3039.3781 | 0 | 165.8893
0 | 25.9078 | 0 | 0 | 0 | 0 | 26.5922 | 52.5 | 124.5087 | 3000 | 47.5168 | 3047.5168 | 3047.5168 | 0 | 164.8402
0 | 42.0967 | 0 | 0 | 0 | 0 | 10.4033 | 52.5 | 134.9121 | 3000 | 18.5894 | 3018.5894 | 3013.182 | 0 | 162.4105
0 | 65.5835 | 0 | 0 | 0 | 0 | -13.0835 | 52.5 | 121.8286 | 3000 | 0 | 3000 | 2908.0738 | 0 | 161.8925
0 | 96.8887 | 0 | 0 | 0 | 0 | -44.3887 | 52.5 | 77.4399 | 3000 | 0 | 3000 | 2691.7768 | 0 | 166.6479
0 | 86.7136 | 0 | 0 | 0 | 0 | -77.4399 | 9.2737 | 0 | 529.9277 | 0 | 529.9277 | 0 | 0 | 0
0 | 14.3838 | 0 | 0 | 0 | 0 | 0 | 14.3838 | 0 | 821.9286 | 0 | 821.9286 | 0 | 0 | 0
0 | 18.5475 | 0 | 0 | 0 | 0 | 0 | 18.5475 | 0 | 1059.8553 | 0 | 1059.8553 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1658.9585 | 0 | 112.4442
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1491.3284 | 0 | 96.8916
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1480.5135 | 0 | 92.0287
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1594.0694 | 0 | 98.3541
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1599.4769 | 0 | 93.4574
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1788.7367 | 0 | 112.2969
0 | 47.9091 | 0 | 0 | 0 | 0 | 4.5909 | 52.5 | 4.5909 | 3000 | 8.2033 | 3008.2033 | 1997.0148 | 0 | 130.1055
0 | 16.8928 | 0 | 0 | 0 | 0 | -4.5909 | 12.3019 | 0 | 702.9653 | 0 | 702.9653 | 0 | 0 | 0
0 | 5.9617 | 0 | 0 | 0 | 0 | 0 | 5.9617 | 0 | 340.6678 | 0 | 340.6678 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 118.9634 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8149 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 50.4559 | 0 | 0 | 0 | 0 | 2.0441 | 52.5 | 2.0441 | 3000 | 3.6525 | 3003.6525 | 3003.6525 | 0 | 197.4601
0 | 54.5441 | 0 | 0 | 0 | 0 | -2.0441 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 170.64
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 160.83
0 | 24.5452 | 0 | 0 | 0 | 0 | 27.9548 | 52.5 | 27.9548 | 3000 | 49.9515 | 3049.9515 | 3049.9515 | 0 | 160.8239
0 | 27.3269 | 0 | 0 | 0 | 0 | 25.1731 | 52.5 | 53.1279 | 3000 | 44.981 | 3044.981 | 3044.981 | 0 | 158.9176
0 | 25.7497 | 0 | 0 | 0 | 0 | 26.7503 | 52.5 | 79.8782 | 3000 | 47.7992 | 3047.7992 | 3047.7992 | 0 | 157.175
0 | 32.5963 | 0 | 0 | 0 | 0 | 19.9037 | 52.5 | 99.7819 | 3000 | 35.5652 | 3035.5652 | 3030.1578 | 0 | 155.6592
0 | 70.889 | 0 | 0 | 0 | 0 | -18.389 | 52.5 | 81.3929 | 3000 | 0 | 3000 | 2891.8515 | 0 | 154.6851
0 | 83.4514 | 0 | 0 | 0 | 0 | -30.9514 | 52.5 | 50.4414 | 3000 | 0 | 3000 | 2691.7768 | 0 | 156.3384
0 | 82.7846 | 0 | 0 | 0 | 0 | -30.2846 | 52.5 | 20.1568 | 3000 | 0 | 3000 | 2405.1832 | 0 | 155.5191
0 | 72.6568 | 0 | 0 | 0 | 0 | -20.1568 | 52.5 | 0 | 3000 | 0 | 3000 | 2123.9971 | 0 | 146.9381
0 | 20.3454 | 0 | 0 | 0 | 0 | 0 | 20.3454 | 0 | 1162.5964 | 0 | 1162.5964 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1637.3288 | 0 | 112.3371
0 | 52.1418 | 0 | 0 | 0 | 0 | 0.35816 | 52.5 | 0.35816 | 3000 | 0.63998 | 3000.64 | 1475.7461 | 0 | 93.4295
0 | 52.8582 | 0 | 0 | 0 | 0 | -0.35816 | 52.5 | 0 | 3000 | 0 | 3000 | 1388.5873 | 0 | 79.7049
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1426.4393 | 0 | 82.3769
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1545.4026 | 0 | 86.898
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1745.4773 | 0 | 96.2282
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2005.0338 | 0 | 116.1917
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2297.0347 | 0 | 147.3548
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2599.8505 | 0 | 174.372
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2908.0738 | 0 | 199.552
0 | 48.6977 | 0 | 0 | 0 | 0 | 3.8023 | 52.5 | 3.8023 | 3000 | 6.7942 | 3006.7942 | 2995.9793 | 0 | 200.9104
0 | 56.3023 | 0 | 0 | 0 | 0 | -3.8023 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 191.91
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 195.15
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 164.85
0 | 20.1563 | 0 | 0 | 0 | 0 | 32.3437 | 52.5 | 32.3437 | 3000 | 57.794 | 3057.794 | 3057.794 | 0 | 165.1515
0 | 25.9077 | 0 | 0 | 0 | 0 | 26.5923 | 52.5 | 58.936 | 3000 | 47.5169 | 3047.5169 | 3047.5169 | 0 | 160.2689
0 | 28.3661 | 0 | 0 | 0 | 0 | 24.1339 | 52.5 | 83.07 | 3000 | 43.1241 | 3043.1241 | 3043.1241 | 0 | 158.2729
0 | 26.8544 | 0 | 0 | 0 | 0 | 25.6456 | 52.5 | 108.7155 | 3000 | 45.8253 | 3045.8253 | 3045.8253 | 0 | 155.4589
0 | 25.4327 | 0 | 0 | 0 | 0 | 27.0673 | 52.5 | 135.7828 | 3000 | 48.3657 | 3048.3657 | 3048.3657 | 0 | 152.7231
0 | 19.4628 | 0 | 0 | 0 | 0 | 33.0372 | 52.5 | 168.82 | 3000 | 59.033 | 3059.033 | 2967.1068 | 0 | 149.1861
0 | 28.8052 | 0 | 0 | 0 | 0 | 23.6948 | 52.5 | 192.5148 | 3000 | 42.3394 | 3042.3394 | 2712.4865 | 0 | 133.4543
0 | 27.2613 | 0 | 0 | 0 | 0 | 25.2387 | 52.5 | 217.7535 | 3000 | 45.0981 | 3045.0981 | 2553.0224 | 0 | 127.4724
0 | 49.8782 | 0 | 0 | 0 | 0 | 2.6218 | 52.5 | 220.3752 | 3000 | 4.6848 | 3004.6848 | 2096.2373 | 0 | 109.8848
0 | 39.0802 | 0 | 0 | 0 | 0 | 13.4198 | 52.5 | 233.7951 | 3000 | 23.9795 | 3023.9795 | 1812.7162 | 0 | 98.6661
0 | 40.5015 | 0 | 0 | 0 | 0 | 11.9985 | 52.5 | 245.7936 | 3000 | 21.4398 | 3021.4398 | 1577.6573 | 0 | 83.8683
0 | 48.2081 | 0 | 0 | 0 | 0 | 4.2919 | 52.5 | 250.0855 | 3000 | 7.669 | 3007.669 | 1547.6642 | 0 | 80.3083
0 | 43.9809 | 0 | 0 | 0 | 0 | 8.5191 | 52.5 | 258.6046 | 3000 | 15.2226 | 3015.2226 | 1425.4396 | 0 | 71.1294
0 | 43.5318 | 0 | 0 | 0 | 0 | 8.9682 | 52.5 | 267.5729 | 3000 | 16.025 | 3016.025 | 1442.4643 | 0 | 70.2624
0 | 48.5174 | 0 | 0 | 0 | 0 | 3.9826 | 52.5 | 271.5555 | 3000 | 7.1164 | 3007.1164 | 1471.4076 | 0 | 71.1278
0 | 38.1632 | 0 | 0 | 0 | 0 | 14.3368 | 52.5 | 285.8923 | 3000 | 25.618 | 3025.618 | 1771.0953 | 0 | 84.5521
0 | 36.5032 | 0 | 0 | 0 | 0 | 15.9968 | 52.5 | 301.8891 | 3000 | 28.5842 | 3028.5842 | 2249.9149 | 0 | 109.9083
0 | 37.2292 | 0 | 0 | 0 | 0 | 15.2708 | 52.5 | 317.1599 | 3000 | 27.2869 | 3027.2869 | 2427.0627 | 0 | 122.8579
0 | 38.6898 | 0 | 0 | 0 | 0 | 13.8102 | 52.5 | 330.9701 | 3000 | 24.6769 | 3024.6769 | 2754.3057 | 0 | 148.1541
0 | 33.4989 | 0 | 0 | 0 | 0 | 19.0011 | 52.5 | 349.9711 | 3000 | 33.9524 | 3033.9524 | 2904.1742 | 0 | 156.6512
0 | 26.9608 | 0 | 0 | 0 | 0 | 25.5392 | 52.5 | 375.5103 | 3000 | 45.6351 | 3045.6351 | 3029.4128 | 0 | 160.2862
0 | 33.1057 | 0 | 0 | 0 | 0 | 19.3943 | 52.5 | 394.9046 | 3000 | 34.655 | 3034.655 | 3034.655 | 0 | 155.344
0 | 22.1474 | 0 | 0 | 0 | 0 | 30.3526 | 52.5 | 425.2572 | 3000 | 54.2361 | 3054.2361 | 3054.2361 | 0 | 156.3463
0 | 23.9476 | 0 | 0 | 0 | 0 | 28.5524 | 52.5 | 453.8096 | 3000 | 51.0194 | 3051.0194 | 3051.0194 | 0 | 149.5
0 | 25.1323 | 0 | 0 | 0 | 0 | 27.3677 | 52.5 | 481.1773 | 3000 | 48.9025 | 3048.9025 | 3048.9025 | 0 | 140.1885
0 | 27.2638 | 0 | 0 | 0 | 0 | 25.2362 | 52.5 | 506.4135 | 3000 | 45.0937 | 3045.0937 | 3045.0937 | 0 | 137.0901
0 | 26.19 | 0 | 0 | 0 | 0 | 26.31 | 52.5 | 532.7235 | 3000 | 47.0124 | 3047.0124 | 3047.0124 | 0 | 131.6309
0 | 28.653 | 0 | 0 | 0 | 0 | 23.847 | 52.5 | 556.5705 | 3000 | 42.6115 | 3042.6115 | 3042.6115 | 0 | 125.5686
0 | 25.8555 | 0 | 0 | 0 | 0 | 26.6445 | 52.5 | 583.2151 | 3000 | 47.6102 | 3047.6102 | 3047.6102 | 0 | 128.3044
0 | 25.7644 | 0 | 0 | 0 | 0 | 26.7356 | 52.5 | 609.9507 | 3000 | 47.773 | 3047.773 | 2982.8839 | 0 | 124.6845
0 | 27.7528 | 0 | 0 | 0 | 0 | 24.7472 | 52.5 | 634.6979 | 3000 | 44.22 | 3044.22 | 2757.6264 | 0 | 111.9596
0 | 19.2743 | 0 | 0 | 0 | 0 | 33.2257 | 52.5 | 667.9236 | 3000 | 59.3699 | 3059.3699 | 2496.9976 | 0 | 107.6206
0 | 45.6649 | 0 | 0 | 0 | 0 | 6.8351 | 52.5 | 674.7587 | 3000 | 12.2134 | 3012.2134 | 2222.7293 | 0 | 100.134
0 | 35.6053 | 0 | 0 | 0 | 0 | 16.8947 | 52.5 | 691.6533 | 3000 | 30.1885 | 3030.1885 | 1991.9629 | 0 | 90.1961
0 | 236.2795 | 0 | 0 | 0 | 0 | -183.7795 | 52.5 | 507.8738 | 3000 | 0 | 3000 | 1637.3288 | 0 | 77.0527
0 | 54.5323 | 0 | 0 | 0 | 0 | -2.0323 | 52.5 | 505.8415 | 3000 | 0 | 3000 | 1480.5135 | 0 | 70.4872
0 | 38.0388 | 0 | 0 | 0 | 0 | 14.4612 | 52.5 | 520.3027 | 3000 | 25.8402 | 3025.8402 | 1387.3903 | 0 | 64.7634
0 | 39.3015 | 0 | 0 | 0 | 0 | 13.1985 | 52.5 | 533.5011 | 3000 | 23.5839 | 3023.5839 | 1747.4316 | 0 | 77.4462
0 | 32.2624 | 0 | 0 | 0 | 0 | 20.2376 | 52.5 | 553.7388 | 3000 | 36.162 | 3036.162 | 2673.8645 | 0 | 116.1794
0 | 42.8425 | 0 | 0 | 0 | 0 | 9.6575 | 52.5 | 563.3963 | 3000 | 17.2566 | 3017.2566 | 2757.7002 | 0 | 119.8221
0 | 54.5239 | 0 | 0 | 0 | 0 | -2.0239 | 52.5 | 561.3723 | 3000 | 0 | 3000 | 2626.8877 | 0 | 126.3008
0 | 42.8976 | 0 | 0 | 0 | 0 | 9.6024 | 52.5 | 570.9747 | 3000 | 17.1582 | 3017.1582 | 2557.527 | 0 | 142.4287
0 | 36.7592 | 0 | 0 | 0 | 0 | 15.7408 | 52.5 | 586.7155 | 3000 | 28.1268 | 3028.1268 | 2860.4966 | 0 | 156.1259
0 | 36.7414 | 0 | 0 | 0 | 0 | 15.7586 | 52.5 | 602.4742 | 3000 | 28.1586 | 3028.1586 | 2979.4918 | 0 | 163.9614
0 | 25.3542 | 0 | 0 | 0 | 0 | 27.1458 | 52.5 | 629.62 | 3000 | 48.506 | 3048.506 | 3043.0986 | 0 | 168.2834
0 | 28.909 | 0 | 0 | 0 | 0 | 23.591 | 52.5 | 653.211 | 3000 | 42.1539 | 3042.1539 | 3042.1539 | 0 | 169.9651
0 | 19.7809 | 0 | 0 | 0 | 0 | 32.7191 | 52.5 | 685.9301 | 3000 | 58.4646 | 3058.4646 | 3058.4646 | 0 | 172.6809
0 | 30.477 | 0 | 0 | 0 | 0 | 22.023 | 52.5 | 707.9531 | 3000 | 39.3521 | 3039.3521 | 3039.3521 | 0 | 164.1554
0 | 25.0535 | 0 | 0 | 0 | 0 | 27.4465 | 52.5 | 735.3995 | 3000 | 49.0432 | 3049.0432 | 3049.0432 | 0 | 154.7999
0 | 30.3669 | 0 | 0 | 0 | 0 | 22.1331 | 52.5 | 757.5326 | 3000 | 39.5488 | 3039.5488 | 3039.5488 | 0 | 149.0899
0 | 27.9131 | 0 | 0 | 0 | 0 | 24.5869 | 52.5 | 782.1195 | 3000 | 43.9335 | 3043.9335 | 3043.9335 | 0 | 145.0434
0 | 22.1079 | 0 | 0 | 0 | 0 | 30.3921 | 52.5 | 812.5115 | 3000 | 54.3066 | 3054.3066 | 3054.3066 | 0 | 147.4314
0 | 28.1709 | 0 | 0 | 0 | 0 | 24.3291 | 52.5 | 836.8406 | 3000 | 43.4729 | 3043.4729 | 3043.4729 | 0 | 148.1867
0 | 24.4444 | 0 | 0 | 0 | 0 | 28.0556 | 52.5 | 864.8962 | 3000 | 50.1316 | 3050.1316 | 3017.6871 | 0 | 151.1559
0 | 24.7995 | 0 | 0 | 0 | 0 | 27.7005 | 52.5 | 892.5968 | 3000 | 49.4972 | 3049.4972 | 2854.8299 | 0 | 158.2147
0 | 20.6238 | 0 | 0 | 0 | 0 | 31.8762 | 52.5 | 924.473 | 3000 | 56.9585 | 3056.9585 | 2478.364 | 0 | 152.0972
0 | 38.1814 | 0 | 0 | 0 | 0 | 14.3186 | 52.5 | 938.7916 | 3000 | 25.5855 | 3025.5855 | 2138.7677 | 0 | 134.6782
0 | 39.2757 | 0 | 0 | 0 | 0 | 13.2243 | 52.5 | 952.0159 | 3000 | 23.63 | 3023.63 | 1855.6261 | 0 | 120.4301
0 | 29.616 | 0 | 0 | 0 | 0 | 22.884 | 52.5 | 974.8998 | 3000 | 40.8906 | 3040.8906 | 1640.3675 | 0 | 100.7186
0 | 46.6746 | 0 | 0 | 0 | 0 | 5.8254 | 52.5 | 980.7252 | 3000 | 10.4091 | 3010.4091 | 1550.4043 | 0 | 93.5514
0 | 46.0573 | 0 | 0 | 0 | 0 | 6.4427 | 52.5 | 987.1679 | 3000 | 11.5123 | 3011.5123 | 1232.4694 | 0 | 73.3073
0 | 56.7193 | 0 | 0 | 0 | 0 | -4.2193 | 52.5 | 982.9485 | 3000 | 0 | 3000 | 2080.7377 | 0 | 117.5617
0 | 42.3266 | 0 | 0 | 0 | 0 | 10.1734 | 52.5 | 993.1219 | 3000 | 18.1785 | 3018.1785 | 1904.2489 | 0 | 103.096
0 | 239.7204 | 0 | 0 | 0 | 0 | -187.2204 | 52.5 | 805.9015 | 3000 | 0 | 3000 | 1875.2556 | 0 | 100.1386
0 | 41.3193 | 0 | 0 | 0 | 0 | 11.1807 | 52.5 | 817.0822 | 3000 | 19.9784 | 3019.9784 | 1976.3454 | 0 | 109.8848
0 | 42.3041 | 0 | 0 | 0 | 0 | 10.1959 | 52.5 | 827.2781 | 3000 | 18.2187 | 3018.2187 | 2634.2915 | 0 | 158.6107
0 | 44.824 | 0 | 0 | 0 | 0 | 7.676 | 52.5 | 834.9541 | 3000 | 13.7159 | 3013.7159 | 2710.9001 | 0 | 174.5006
0 | 41.195 | 0 | 0 | 0 | 0 | -41.195 | 0 | 793.7591 | 0 | 0 | 0 | 0 | 97.3337 | 0
0 | 29.3316 | 0 | 0 | 0 | 0 | -29.3316 | 0 | 764.4275 | 0 | 0 | 0 | 0 | 10.8149 | 0
0 | 25.6329 | 0 | 0 | 0 | 0 | 26.8671 | 52.5 | 791.2946 | 3000 | 48.008 | 3048.008 | 3048.008 | 0 | 206.8683
0 | 29.5576 | 0 | 0 | 0 | 0 | 22.9424 | 52.5 | 814.237 | 3000 | 40.995 | 3040.995 | 3040.995 | 0 | 195.7793
0 | 24.4122 | 0 | 0 | 0 | 0 | 28.0878 | 52.5 | 842.3248 | 3000 | 50.1891 | 3050.1891 | 3050.1891 | 0 | 177.6735
0 | 26.2687 | 0 | 0 | 0 | 0 | 26.2313 | 52.5 | 868.5561 | 3000 | 46.8719 | 3046.8719 | 3046.8719 | 0 | 152.3436
0 | 28.5064 | 0 | 0 | 0 | 0 | 23.9936 | 52.5 | 892.5497 | 3000 | 42.8733 | 3042.8733 | 3042.8733 | 0 | 158.5946
0 | 27.763 | 0 | 0 | 0 | 0 | 24.737 | 52.5 | 917.2866 | 3000 | 44.2017 | 3044.2017 | 3044.2017 | 0 | 152.0579
0 | 27.7184 | 0 | 0 | 0 | 0 | 24.7816 | 52.5 | 942.0682 | 3000 | 44.2815 | 3044.2815 | 3044.2815 | 0 | 148.6218
0 | 26.9217 | 0 | 0 | 0 | 0 | 25.5783 | 52.5 | 967.6465 | 3000 | 45.705 | 3045.705 | 3045.705 | 0 | 143.6659
0 | 31.0599 | 0 | 0 | 0 | 0 | 21.4401 | 52.5 | 989.0866 | 3000 | 38.3106 | 3038.3106 | 2951.7918 | 0 | 137.9372
0 | 30.7109 | 0 | 0 | 0 | 0 | 21.7891 | 52.5 | 1010.8757 | 3000 | 38.9342 | 3038.9342 | 2714.4887 | 0 | 168.054
0 | 24.3122 | 0 | 0 | 0 | 0 | 28.1878 | 52.5 | 1039.0635 | 3000 | 50.3679 | 3050.3679 | 2439.3288 | 0 | 166.533
0 | 38.2802 | 0 | 0 | 0 | 0 | 14.2198 | 52.5 | 1053.2834 | 3000 | 25.4089 | 3025.4089 | 2116.9615 | 0 | 147.9544
0 | 46.2765 | 0 | 0 | 0 | 0 | 6.2235 | 52.5 | 1059.5069 | 3000 | 11.1206 | 3011.1206 | 1837.7093 | 0 | 125.8096
0 | 38.8107 | 0 | 0 | 0 | 0 | 13.6893 | 52.5 | 1073.1961 | 3000 | 24.4609 | 3024.4609 | 1634.7526 | 0 | 106.4551
0 | 47.0418 | 0 | 0 | 0 | 0 | 5.4582 | 52.5 | 1078.6543 | 3000 | 9.753 | 3009.753 | 1484.8591 | 0 | 91.2297
0 | 48.8106 | 0 | 0 | 0 | 0 | 3.6894 | 52.5 | 1082.3437 | 3000 | 6.5925 | 3006.5925 | 1460.0689 | 0 | 83.3699
0 | 36.1987 | 0 | 0 | 0 | 0 | 16.3013 | 52.5 | 1098.645 | 3000 | 29.1283 | 3029.1283 | 1569.1235 | 0 | 88.2475
0 | 37.9538 | 0 | 0 | 0 | 0 | 14.5462 | 52.5 | 1113.1912 | 3000 | 25.9921 | 3025.9921 | 1593.0244 | 0 | 88.2695
0 | 44.3541 | 0 | 0 | 0 | 0 | 8.1459 | 52.5 | 1121.3371 | 3000 | 14.5557 | 3014.5557 | 2149.3676 | 0 | 118.817
0 | 46.29 | 0 | 0 | 0 | 0 | 6.21 | 52.5 | 1127.5471 | 3000 | 11.0964 | 3011.0964 | 2729.9103 | 0 | 149.9813
0 | 38.969 | 0 | 0 | 0 | 0 | 13.531 | 52.5 | 1141.0781 | 3000 | 24.1782 | 3024.1782 | 2753.8069 | 0 | 157.0771
0 | 46.0209 | 0 | 0 | 0 | 0 | 6.4791 | 52.5 | 1147.5573 | 3000 | 11.5774 | 3011.5774 | 2806.0952 | 0 | 173.7254
0 | 31.4483 | 0 | 0 | 0 | 0 | 21.0517 | 52.5 | 1168.609 | 3000 | 37.6166 | 3037.6166 | 2924.0607 | 0 | 197.1109
0 | 30.0142 | 0 | 0 | 0 | 0 | 22.4858 | 52.5 | 1191.0947 | 3000 | 40.1791 | 3040.1791 | 3034.7716 | 0 | 201.9337
0 | 33.3783 | 0 | 0 | 0 | 0 | 19.1217 | 52.5 | 1210.2164 | 3000 | 34.1679 | 3034.1679 | 3034.1679 | 0 | 187.906
0 | 21.014 | 0 | 0 | 0 | 0 | 31.486 | 52.5 | 1241.7024 | 3000 | 56.2613 | 3056.2613 | 3056.2613 | 0 | 179.2803
0 | 30.9178 | 0 | 0 | 0 | 0 | 21.5822 | 52.5 | 1263.2846 | 3000 | 38.5645 | 3038.5645 | 3038.5645 | 0 | 163.0494
0 | 26.4101 | 0 | 0 | 0 | 0 | 26.0899 | 52.5 | 1289.3745 | 3000 | 46.6191 | 3046.6191 | 3046.6191 | 0 | 157.693
0 | 34.269 | 0 | 0 | 0 | 0 | 18.231 | 52.5 | 1307.6055 | 3000 | 32.5764 | 3032.5764 | 3032.5764 | 0 | 145.0785
0 | 27.289 | 0 | 0 | 0 | 0 | 25.211 | 52.5 | 1332.8165 | 3000 | 45.0488 | 3045.0488 | 3045.0488 | 0 | 136.205
0 | 30.1052 | 0 | 0 | 0 | 0 | 22.3948 | 52.5 | 1355.2113 | 3000 | 40.0165 | 3040.0165 | 3040.0165 | 0 | 128.2583
0 | 26.6414 | 0 | 0 | 0 | 0 | 25.8586 | 52.5 | 1381.0699 | 3000 | 46.2058 | 3046.2058 | 3046.2058 | 0 | 125.1077
0 | 31.2288 | 0 | 0 | 0 | 0 | 21.2712 | 52.5 | 1402.3411 | 3000 | 38.0088 | 3038.0088 | 2962.3048 | 0 | 135.2588
0 | 26.7389 | 0 | 0 | 0 | 0 | 25.7611 | 52.5 | 1428.1021 | 3000 | 46.0316 | 3046.0316 | 2737.8084 | 0 | 136.863
0 | 19.2402 | 0 | 0 | 0 | 0 | 33.2598 | 52.5 | 1461.3619 | 3000 | 59.4308 | 3059.4308 | 2572.7625 | 0 | 153.2337
0 | 38.0779 | 0 | 0 | 0 | 0 | 14.4221 | 52.5 | 1475.784 | 3000 | 25.7704 | 3025.7704 | 2225.4714 | 0 | 133.5283
0 | 48.7011 | 0 | 0 | 0 | 0 | 3.7989 | 52.5 | 1479.5829 | 3000 | 6.7881 | 3006.7881 | 2044.2664 | 0 | 121.6134
0 | 233.0545 | 0 | 0 | 0 | 0 | -180.5545 | 52.5 | 1299.0284 | 3000 | 0 | 3000 | 2069.9229 | 0 | 116.4125
0 | 36.4041 | 0 | 0 | 0 | 0 | 16.0959 | 52.5 | 1315.1243 | 3000 | 28.7613 | 3028.7613 | 2093.2767 | 0 | 118.1445
0 | 42.3909 | 0 | 0 | 0 | 0 | 10.1091 | 52.5 | 1325.2334 | 3000 | 18.0636 | 3018.0636 | 1931.1711 | 0 | 108.5704
0 | 36.5327 | 0 | 0 | 0 | 0 | 15.9673 | 52.5 | 1341.2007 | 3000 | 28.5315 | 3028.5315 | 2460.7518 | 0 | 134.111
0 | 38.7085 | 0 | 0 | 0 | 0 | 13.7915 | 52.5 | 1354.9922 | 3000 | 24.6436 | 3024.6436 | 2743.4574 | 0 | 145.5953
0 | 46.336 | 0 | 0 | 0 | 0 | 6.164 | 52.5 | 1361.1562 | 3000 | 11.0142 | 3011.0142 | 2637.9019 | 0 | 139.8352
0 | 35.6809 | 0 | 0 | 0 | 0 | 16.8191 | 52.5 | 1377.9753 | 3000 | 30.0534 | 3030.0534 | 2592.052 | 0 | 136.8344
0 | 29.7587 | 0 | 0 | 0 | 0 | 22.7413 | 52.5 | 1400.7166 | 3000 | 40.6357 | 3040.6357 | 2781.0793 | 0 | 152.9594
0 | 42.9473 | 0 | 0 | 0 | 0 | 9.5527 | 52.5 | 1410.2693 | 3000 | 17.0694 | 3017.0694 | 2827.8095 | 0 | 189.5198
0 | 33.9993 | 0 | 0 | 0 | 0 | 18.5007 | 52.5 | 1428.77 | 3000 | 33.0583 | 3033.0583 | 2978.9841 | 0 | 207.5756
0 | 25.5542 | 0 | 0 | 0 | 0 | -25.5542 | 0 | 1403.2158 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 21.8275 | 0 | 0 | 0 | 0 | 30.6725 | 52.5 | 1433.8883 | 3000 | 54.8076 | 3054.8076 | 3054.8076 | 0 | 213.7754
0 | 26.2348 | 0 | 0 | 0 | 0 | 26.2652 | 52.5 | 1460.1536 | 3000 | 46.9325 | 3046.9325 | 3046.9325 | 0 | 195.4607
0 | 22.8663 | 0 | 0 | 0 | 0 | 29.6337 | 52.5 | 1489.7873 | 3000 | 52.9515 | 3052.9515 | 3052.9515 | 0 | 174.6288
0 | 27.4933 | 0 | 0 | 0 | 0 | 10.2127 | 37.706 | 1500 | 2154.6283 | 18.2488 | 2172.8771 | 2172.8771 | 0 | 117.3354
0 | 3.309 | 0 | 0 | 0 | 0 | 9.2815e-14 | 3.309 | 1500 | 189.086 | 1.6585e-13 | 189.086 | 189.086 | 0 | 9.8457
0 | 4.407 | 0 | 0 | 0 | 0 | -2.8422e-14 | 4.407 | 1500 | 251.8314 | 0 | 251.8314 | 251.8314 | 0 | 12.9064
0 | 4.1469 | 0 | 0 | 0 | 0 | -6.1284e-14 | 4.1469 | 1500 | 236.9673 | 0 | 236.9673 | 236.9673 | 0 | 11.8223
0 | 4.5681 | 0 | 0 | 0 | 0 | 4.3521e-14 | 4.5681 | 1500 | 261.0317 | 7.7766e-14 | 261.0317 | 261.0317 | 0 | 12.754
0 | 3.5466 | 0 | 0 | 0 | 0 | -9.1926e-14 | 3.5466 | 1500 | 202.6627 | 0 | 202.6627 | 170.2181 | 0 | 8.7935
0 | 4.9782 | 0 | 0 | 0 | 0 | 0 | 4.9782 | 1500 | 284.4709 | 4.7612e-15 | 284.4709 | 165.5076 | 0 | 9.2353
0 | 4.17 | 0 | 0 | 0 | 0 | 8.0824e-14 | 4.17 | 1500 | 238.2857 | 1.4442e-13 | 238.2857 | 11.1739 | 0 | 0.66429
0 | 14.3434 | 0 | 0 | 0 | 0 | -5.5067e-14 | 14.3434 | 1500 | 819.6224 | 0 | 819.6224 | 359.9912 | 0 | 21.2719
0 | 16.5934 | 0 | 0 | 0 | 0 | -3.1974e-14 | 16.5934 | 1500 | 948.1948 | 0 | 948.1948 | 310.1186 | 0 | 17.8101
0 | 18.7351 | 0 | 0 | 0 | 0 | -9.4147e-14 | 18.7351 | 1500 | 1070.5768 | 0 | 1070.5768 | 243.2407 | 0 | 13.5631
0 | 25.329 | 0 | 0 | 0 | 0 | -1.0481e-13 | 25.329 | 1500 | 1447.374 | 0 | 1447.374 | 620.0379 | 0 | 33.6619
0 | 24.9714 | 0 | 0 | 0 | 0 | -7.816e-14 | 24.9714 | 1500 | 1426.9391 | 0 | 1426.9391 | 951.0857 | 0 | 50.8641
0 | 19.8983 | 0 | 0 | 0 | 0 | 8.3489e-14 | 19.8983 | 1500 | 1137.0459 | 1.4918e-13 | 1137.0459 | 742.3038 | 0 | 39.9211
0 | 20.0535 | 0 | 0 | 0 | 0 | -6.5725e-14 | 20.0535 | 1500 | 1145.9138 | 0 | 1145.9138 | 286.1332 | 0 | 15.3797
0 | 18.3256 | 0 | 0 | 0 | 0 | 1.0836e-13 | 18.3256 | 1500 | 1047.1756 | 1.9362e-13 | 1047.1756 | 203.6172 | 0 | 11.1542
0 | 19.8183 | 0 | 0 | 0 | 0 | -5.5067e-14 | 19.8183 | 1500 | 1132.4725 | 0 | 1132.4725 | 591.73 | 0 | 32.6221
0 | 21.6721 | 0 | 0 | 0 | 0 | -9.77e-14 | 21.6721 | 1500 | 1238.4048 | 0 | 1238.4048 | 773.3662 | 0 | 46.6572
0 | 10.7999 | 0 | 0 | 0 | 0 | -5.406 | 5.3939 | 1494.594 | 308.2232 | 0 | 308.2232 | 0 | 0 | 0
0 | 25.9775 | 0 | 0 | 0 | 0 | -25.9775 | 0 | 1468.6165 | 0 | 0 | 0 | 0 | 118.9634 | 0
0 | 4.0538 | 0 | 0 | 0 | 0 | -4.0538 | 0 | 1464.5627 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 3.3646 | 0 | 0 | 0 | 0 | -3.3646 | 0 | 1461.1981 | 0 | 0 | 0 | 0 | 0 | 0
0 | 4.5363 | 0 | 0 | 0 | 0 | 38.8019 | 43.3382 | 1500 | 2476.4685 | 69.3339 | 2545.8024 | 2545.8024 | 0 | 169.3722
0 | 4.7637 | 0 | 0 | 0 | 0 | 2.3981e-14 | 4.7637 | 1500 | 272.2108 | 4.2851e-14 | 272.2108 | 272.2108 | 0 | 16.2074
0 | 4.3999 | 0 | 0 | 0 | 0 | -2.3981e-14 | 4.3999 | 1500 | 251.4252 | 0 | 251.4252 | 251.4252 | 0 | 13.8284
0 | 5.4957 | 0 | 0 | 0 | 0 | 2.5757e-14 | 5.4957 | 1500 | 314.0397 | 4.6025e-14 | 314.0397 | 314.0397 | 0 | 16.9236
0 | 3.4441 | 0 | 0 | 0 | 0 | 9.5479e-14 | 3.4441 | 1500 | 196.8082 | 1.7061e-13 | 196.8082 | 196.8082 | 0 | 10.3088
0 | 5.6476 | 0 | 0 | 0 | 0 | 0 | 5.6476 | 1500 | 322.7223 | 0 | 322.7223 | 322.7223 | 0 | 15.8715
0 | 4.7705 | 0 | 0 | 0 | 0 | 6.4837e-14 | 4.7705 | 1500 | 272.6001 | 1.1586e-13 | 272.6001 | 272.6001 | 0 | 13.3656
0 | 4.3992 | 0 | 0 | 0 | 0 | -8.5265e-14 | 4.3992 | 1500 | 251.3831 | 0 | 251.3831 | 202.7163 | 0 | 10.3993
0 | 3.9498 | 0 | 0 | 0 | 0 | 4.5297e-14 | 3.9498 | 1500 | 225.7017 | 8.094e-14 | 225.7017 | 0 | 23.0399 | 0
0 | 5.4832 | 0 | 0 | 0 | 0 | 0 | 5.4832 | 1500 | 313.3242 | 0 | 313.3242 | 0 | 286.9 | 0
0 | 27.4499 | 0 | 0 | 0 | 0 | 0 | 27.4499 | 1500 | 1568.566 | 2.5393e-14 | 1568.566 | 1022.4161 | 0 | 64.9848
0 | 18.9688 | 0 | 0 | 0 | 0 | 6.7502e-14 | 18.9688 | 1500 | 1083.9332 | 1.2062e-13 | 1083.9332 | 575.6352 | 0 | 37.6868
0 | 12.9742 | 0 | 0 | 0 | 0 | -6.0396e-14 | 12.9742 | 1500 | 741.3824 | 0 | 741.3824 | 243.8992 | 0 | 15.3535
0 | 19.8009 | 0 | 0 | 0 | 0 | -7.9936e-14 | 19.8009 | 1500 | 1131.4819 | 0 | 1131.4819 | 455.5537 | 0 | 27.315
0 | 13.9426 | 0 | 0 | 0 | 0 | -7.9936e-14 | 13.9426 | 1500 | 796.7186 | 0 | 796.7186 | 450.6434 | 0 | 25.8264
0 | 15.0152 | 0 | 0 | 0 | 0 | -8.5265e-14 | 15.0152 | 1500 | 858.0089 | 0 | 858.0089 | 695.7862 | 0 | 39.1588
0 | 13.3333 | 0 | 0 | 0 | 0 | 0 | 13.3333 | 1500 | 761.9014 | 0 | 761.9014 | 621.3083 | 0 | 34.2217
0 | 14.8251 | 0 | 0 | 0 | 0 | 1.1191e-13 | 14.8251 | 1500 | 847.1484 | 1.9997e-13 | 847.1484 | 230.7019 | 0 | 12.7394
0 | 17.4553 | 0 | 0 | 0 | 0 | 3.5527e-15 | 17.4553 | 1500 | 997.4458 | 0 | 997.4458 | 0 | 35.3724 | 0
0 | 25.0804 | 0 | 0 | 0 | 0 | 8.8818e-14 | 25.0804 | 1500 | 1433.1642 | 1.5871e-13 | 1433.1642 | 908.644 | 0 | 52.5105
0 | 17.4461 | 0 | 0 | 0 | 0 | 1.0303e-13 | 17.4461 | 1500 | 996.9174 | 1.841e-13 | 996.9174 | 748.1758 | 0 | 45.6013
0 | 16.2086 | 0 | 0 | 0 | 0 | -3.908e-14 | 16.2086 | 1500 | 926.2043 | 0 | 926.2043 | 758.5741 | 0 | 48.9356
0 | 4.016 | 0 | 0 | 0 | 0 | -3.8192e-14 | 4.016 | 1500 | 229.4853 | 0 | 229.4853 | 218.6705 | 0 | 14.1524
0 | 204.0217 | 0 | 0 | 0 | 0 | -151.5217 | 52.5 | 1348.4783 | 3000 | 0 | 3000 | 3000 | 0 | 186.51
0 | 3.7537 | 0 | 0 | 0 | 0 | 48.7463 | 52.5 | 1397.2246 | 3000 | 87.1031 | 3087.1031 | 3087.1031 | 0 | 182.0156
0 | 5.3119 | 0 | 0 | 0 | 0 | 47.1881 | 52.5 | 1444.4127 | 3000 | 84.3189 | 3084.3189 | 3084.3189 | 0 | 173.092
0 | 4.7562 | 0 | 0 | 0 | 0 | 47.7438 | 52.5 | 1492.1565 | 3000 | 85.3118 | 3085.3118 | 3085.3118 | 0 | 166.4834
0 | 3.2435 | 0 | 0 | 0 | 0 | 7.8435 | 11.087 | 1500 | 633.5407 | 14.0153 | 647.556 | 647.556 | 0 | 33.6341
0 | 3.3771 | 0 | 0 | 0 | 0 | -3.5971e-14 | 3.3771 | 1500 | 192.9798 | 0 | 192.9798 | 192.9798 | 0 | 10.0041
0 | 4.7375 | 0 | 0 | 0 | 0 | -9.5923e-14 | 4.7375 | 1500 | 270.7139 | 0 | 270.7139 | 270.7139 | 0 | 13.9499
0 | 3.4439 | 0 | 0 | 0 | 0 | 8.5709e-14 | 3.4439 | 1500 | 196.7933 | 1.5315e-13 | 196.7933 | 196.7933 | 0 | 9.1312
0 | 3.806 | 0 | 0 | 0 | 0 | 4.13e-14 | 3.806 | 1500 | 217.4852 | 7.3798e-14 | 217.4852 | 179.6332 | 0 | 9.2799
0 | 4.4213 | 0 | 0 | 0 | 0 | -7.3719e-14 | 4.4213 | 1500 | 252.645 | 0 | 252.645 | 182.3485 | 0 | 9.2287
0 | 4.4448 | 0 | 0 | 0 | 0 | 7.6383e-14 | 4.4448 | 1500 | 253.9898 | 1.3649e-13 | 253.9898 | 124.2116 | 0 | 6.5708
0 | 218.0889 | 0 | 0 | 0 | 0 | -165.5889 | 52.5 | 1334.4111 | 3000 | 0 | 3000 | 2772.8881 | 0 | 146.1867
0 | 14.5309 | 0 | 0 | 0 | 0 | 37.9691 | 52.5 | 1372.3802 | 3000 | 67.8458 | 3067.8458 | 2629.8443 | 0 | 140.723
0 | 14.5786 | 0 | 0 | 0 | 0 | 37.9214 | 52.5 | 1410.3016 | 3000 | 67.7605 | 3067.7605 | 2364.7952 | 0 | 123.0639
0 | 6.0064 | 0 | 0 | 0 | 0 | 46.4936 | 52.5 | 1456.7952 | 3000 | 84.4762 | 3084.4762 | 2695.1416 | 0 | 136.455
0 | 12.7786 | 0 | 0 | 0 | 0 | 39.7214 | 52.5 | 1496.5167 | 3000 | 76.5456 | 3076.5456 | 2162.6908 | 0 | 108.221
0 | 21.191 | 0 | 0 | 0 | 0 | 3.4833 | 24.6743 | 1500 | 1409.9612 | 6.2242 | 1416.1854 | 599.6642 | 0 | 28.4421
0 | 17.2857 | 0 | 0 | 0 | 0 | -8.7041e-14 | 17.2857 | 1500 | 987.7545 | 0 | 987.7545 | 279.3817 | 0 | 12.6001
0 | 8.6019 | 0 | 0 | 0 | 0 | 1.7764e-15 | 8.6019 | 1500 | 491.5361 | 0 | 491.5361 | 0 | 97.8732 | 0
0 | 20.3152 | 0 | 0 | 0 | 0 | -5.3291e-14 | 20.3152 | 1500 | 1160.8669 | 0 | 1160.8669 | 966.1996 | 0 | 43.9814
0 | 15.9747 | 0 | 0 | 0 | 0 | 6.0396e-14 | 15.9747 | 1500 | 912.8374 | 1.0792e-13 | 912.8374 | 610.0216 | 0 | 29.946
0 | 29.3797 | 0 | 0 | 0 | 0 | -1.0303e-13 | 29.3797 | 1500 | 1678.8402 | 0 | 1678.8402 | 1370.617 | 0 | 73.9448
0 | 33.1624 | 0 | 0 | 0 | 0 | 0 | 33.1624 | 1500 | 1894.9924 | 0 | 1894.9924 | 1830.1033 | 0 | 102.6322
0 | 4.442 | 0 | 0 | 0 | 0 | -7.6383e-14 | 4.442 | 1500 | 253.8266 | 0 | 253.8266 | 248.4192 | 0 | 13.9164
0 | 4.0183 | 0 | 0 | 0 | 0 | -4.0856e-14 | 4.0183 | 1500 | 229.6163 | 0 | 229.6163 | 229.6163 | 0 | 12.9917
0 | 3.9473 | 0 | 0 | 0 | 0 | -7.5939e-14 | 3.9473 | 1500 | 225.559 | 0 | 225.559 | 225.559 | 0 | 12.8478
0 | 3.8725 | 0 | 0 | 0 | 0 | 1.0658e-14 | 3.8725 | 1500 | 221.2877 | 1.9045e-14 | 221.2877 | 221.2877 | 0 | 12.0535
0 | 4.5483 | 0 | 0 | 0 | 0 | -3.3751e-14 | 4.5483 | 1500 | 259.9048 | 0 | 259.9048 | 259.9048 | 0 | 13.6944
0 | 3.2168 | 0 | 0 | 0 | 0 | 5.6843e-14 | 3.2168 | 1500 | 183.8152 | 1.0157e-13 | 183.8152 | 183.8152 | 0 | 9.1908
0 | 4.9938 | 0 | 0 | 0 | 0 | 2.4869e-14 | 4.9938 | 1500 | 285.3615 | 4.4438e-14 | 285.3615 | 285.3615 | 0 | 14.3851
0 | 4.2061 | 0 | 0 | 0 | 0 | 5.3291e-14 | 4.2061 | 1500 | 240.3492 | 9.5223e-14 | 240.3492 | 240.3492 | 0 | 12.2554
0 | 5.3555 | 0 | 0 | 0 | 0 | 5.2403e-14 | 5.3555 | 1500 | 306.0275 | 9.3636e-14 | 306.0275 | 306.0275 | 0 | 15.5676
0 | 4.5025 | 0 | 0 | 0 | 0 | -2.7534e-14 | 4.5025 | 1500 | 257.2831 | 0 | 257.2831 | 214.0237 | 0 | 10.4551
0 | 4.4113 | 0 | 0 | 0 | 0 | 5.5067e-14 | 4.4113 | 1500 | 252.0746 | 9.8398e-14 | 252.0746 | 111.4815 | 0 | 5.7079
0 | 4.2903 | 0 | 0 | 0 | 0 | 6.6613e-14 | 4.2903 | 1500 | 245.1608 | 1.1903e-13 | 245.1608 | 23.4563 | 0 | 1.1564
0 | 22.1918 | 0 | 0 | 0 | 0 | -5.1514e-14 | 22.1918 | 1500 | 1268.1006 | 0 | 1268.1006 | 781.4324 | 0 | 37.6338
0 | 19.9445 | 0 | 0 | 0 | 0 | 6.0396e-14 | 19.9445 | 1500 | 1139.6883 | 1.0792e-13 | 1139.6883 | 328.5746 | 0 | 15.1473
0 | 18.6125 | 0 | 0 | 0 | 0 | 0 | 18.6125 | 1500 | 1063.5704 | 0 | 1063.5704 | 0 | 126.0631 | 0
0 | 22.4594 | 0 | 0 | 0 | 0 | 3.5527e-15 | 22.4594 | 1500 | 1283.3969 | 0 | 1283.3969 | 0 | 19.7926 | 0
0 | 11.3081 | 0 | 0 | 0 | 0 | 1.7764e-15 | 11.3081 | 1500 | 646.1744 | 0 | 646.1744 | 0 | 440.718 | 0
0 | 16.1174 | 0 | 0 | 0 | 0 | 3.5527e-15 | 16.1174 | 1500 | 920.9915 | 0 | 920.9915 | 0 | 355.1609 | 0
0 | 11.6679 | 0 | 0 | 0 | 0 | 1.7764e-15 | 11.6679 | 1500 | 666.7392 | 0 | 666.7392 | 0 | 625.6354 | 0
0 | 28.4367 | 0 | 0 | 0 | 0 | 6.3949e-14 | 28.4367 | 1500 | 1624.955 | 1.1427e-13 | 1624.955 | 581.322 | 0 | 25.1654
0 | 13.9482 | 0 | 0 | 0 | 0 | 1.7764e-15 | 13.9482 | 1500 | 797.0384 | 0 | 797.0384 | 0 | 170.8907 | 0
0 | 25.0397 | 0 | 0 | 0 | 0 | 6.7502e-14 | 25.0397 | 1500 | 1430.8412 | 1.2062e-13 | 1430.8412 | 792.7651 | 0 | 39.0278
0 | 19.6351 | 0 | 0 | 0 | 0 | 9.2371e-14 | 19.6351 | 1500 | 1122.0049 | 1.6505e-13 | 1122.0049 | 911.1153 | 0 | 49.2184
0 | 22.1254 | 0 | 0 | 0 | 0 | -6.0396e-14 | 22.1254 | 1500 | 1264.3083 | 0 | 1264.3083 | 1177.7895 | 0 | 67.134
0 | 4.6044 | 0 | 0 | 0 | 0 | -8.8818e-15 | 4.6044 | 1500 | 263.1082 | 0 | 263.1082 | 257.7008 | 0 | 15.2018
0 | 4.6401 | 0 | 0 | 0 | 0 | 9.6811e-14 | 4.6401 | 1500 | 265.1474 | 1.7299e-13 | 265.1474 | 265.1474 | 0 | 16.4391
0 | 3.1952 | 0 | 0 | 0 | 0 | 0 | 3.1952 | 1500 | 182.5852 | 4.7612e-15 | 182.5852 | 182.5852 | 0 | 11.2765
0 | 4.9198 | 0 | 0 | 0 | 0 | -4.3521e-14 | 4.9198 | 1500 | 281.1305 | 0 | 281.1305 | 281.1305 | 0 | 16.0919
0 | 3.9217 | 0 | 0 | 0 | 0 | -1.0525e-13 | 3.9217 | 1500 | 224.0988 | 0 | 224.0988 | 224.0988 | 0 | 11.9803
0 | 4.0493 | 0 | 0 | 0 | 0 | 3.8192e-14 | 4.0493 | 1500 | 231.3863 | 6.8243e-14 | 231.3863 | 231.3863 | 0 | 11.1667
0 | 3.7332 | 0 | 0 | 0 | 0 | -7.6383e-14 | 3.7332 | 1500 | 213.3267 | 0 | 213.3267 | 213.3267 | 0 | 9.956
0 | 4.5513 | 0 | 0 | 0 | 0 | 2.5757e-14 | 4.5513 | 1500 | 260.0751 | 4.6025e-14 | 260.0751 | 260.0751 | 0 | 11.5577
0 | 3.8037 | 0 | 0 | 0 | 0 | -2.4425e-14 | 3.8037 | 1500 | 217.3538 | 0 | 217.3538 | 217.3538 | 0 | 9.8679
0 | 3.8794 | 0 | 0 | 0 | 0 | -9.2815e-14 | 3.8794 | 1500 | 221.678 | 0 | 221.678 | 210.8631 | 0 | 10.0793
0 | 4.5495 | 0 | 0 | 0 | 0 | -2.931e-14 | 4.5495 | 1500 | 259.9723 | 0 | 259.9723 | 162.6386 | 0 | 9.0248
0 | 4.8702 | 0 | 0 | 0 | 0 | -9.1482e-14 | 4.8702 | 1500 | 278.2987 | 0 | 278.2987 | 105.2611 | 0 | 6.7157
0 | 19.0176 | 0 | 0 | 0 | 0 | 0 | 19.0176 | 1500 | 1086.7189 | 0 | 1086.7189 | 821.7551 | 0 | 51.7377
0 | 21.4822 | 0 | 0 | 0 | 0 | 3.1974e-14 | 21.4822 | 1500 | 1227.5523 | 5.7134e-14 | 1227.5523 | 1011.2553 | 0 | 67.299
0 | 21.2653 | 0 | 0 | 0 | 0 | 3.5527e-14 | 21.2653 | 1500 | 1215.159 | 6.3482e-14 | 1215.159 | 247.2299 | 0 | 16.5422
0 | 25.7169 | 0 | 0 | 0 | 0 | 1.0658e-14 | 25.7169 | 1500 | 1469.5361 | 1.9045e-14 | 1469.5361 | 371.8287 | 0 | 23.9086
0 | 15.1652 | 0 | 0 | 0 | 0 | 1.7764e-15 | 15.1652 | 1500 | 866.5802 | 0 | 866.5802 | 0 | 263.5717 | 0
0 | 16.4461 | 0 | 0 | 0 | 0 | 3.5527e-15 | 16.4461 | 1500 | 939.7799 | 0 | 939.7799 | 0 | 260.6685 | 0
0 | 19.0024 | 0 | 0 | 0 | 0 | 3.5527e-15 | 19.0024 | 1500 | 1085.8509 | 0 | 1085.8509 | 0 | 22.6713 | 0
0 | 16.1924 | 0 | 0 | 0 | 0 | -8.5265e-14 | 16.1924 | 1500 | 925.2815 | 0 | 925.2815 | 108.7603 | 0 | 5.7882
0 | 16.8477 | 0 | 0 | 0 | 0 | -9.0594e-14 | 16.8477 | 1500 | 962.728 | 0 | 962.728 | 281.3924 | 0 | 14.9729
0 | 13.0481 | 0 | 0 | 0 | 0 | -1.0036e-13 | 13.0481 | 1500 | 745.6064 | 0 | 745.6064 | 388.7164 | 0 | 21.2628
0 | 22.4012 | 0 | 0 | 0 | 0 | -4.9738e-14 | 22.4012 | 1500 | 1280.0714 | 0 | 1280.0714 | 1101.6263 | 0 | 63.2334
0 | 15.5015 | 0 | 0 | 0 | 0 | -2.4869e-14 | 15.5015 | 1500 | 885.7993 | 0 | 885.7993 | 826.3177 | 0 | 53.9833
0 | 3.504 | 0 | 0 | 0 | 0 | 7.3275e-14 | 3.504 | 1500 | 200.2282 | 1.3093e-13 | 200.2282 | 200.2282 | 0 | 13.6956
0 | 4.7134 | 0 | 0 | 0 | 0 | -4.6185e-14 | 4.7134 | 1500 | 269.336 | 0 | 269.336 | 269.336 | 0 | 17.4799
0 | 4.6366 | 0 | 0 | 0 | 0 | 6.3061e-14 | 4.6366 | 1500 | 264.9485 | 1.1268e-13 | 264.9485 | 264.9485 | 0 | 15.8969
0 | 3.9079 | 0 | 0 | 0 | 0 | -3.5527e-15 | 3.9079 | 1500 | 223.3063 | 0 | 223.3063 | 223.3063 | 0 | 12.2528
0 | 3.2093 | 0 | 0 | 0 | 0 | -6.6613e-15 | 3.2093 | 1500 | 183.3885 | 0 | 183.3885 | 183.3885 | 0 | 9.8076
0 | 3.9984 | 0 | 0 | 0 | 0 | 9.3703e-14 | 3.9984 | 1500 | 228.4828 | 1.6743e-13 | 228.4828 | 228.4828 | 0 | 11.8628
0 | 4.3218 | 0 | 0 | 0 | 0 | 6.7502e-14 | 4.3218 | 1500 | 246.9623 | 1.2062e-13 | 246.9623 | 246.9623 | 0 | 12.2543
0 | 4.2901 | 0 | 0 | 0 | 0 | -6.3061e-14 | 4.2901 | 1500 | 245.1509 | 0 | 245.1509 | 245.1509 | 0 | 11.9364
0 | 3.964 | 0 | 0 | 0 | 0 | -9.9032e-14 | 3.964 | 1500 | 226.5157 | 0 | 226.5157 | 226.5157 | 0 | 10.986
0 | 3.7351 | 0 | 0 | 0 | 0 | 1.199e-14 | 3.7351 | 1500 | 213.4362 | 2.1425e-14 | 213.4362 | 170.1768 | 0 | 8.7947
0 | 4.3585 | 0 | 0 | 0 | 0 | -6.3061e-14 | 4.3585 | 1500 | 249.0554 | 0 | 249.0554 | 0 | 32.1307 | 0
0 | 203.7435 | 0 | 0 | 0 | 0 | -151.2435 | 52.5 | 1348.7565 | 3000 | 0 | 3000 | 2507.9243 | 0 | 146.9142
0 | 24.9281 | 0 | 0 | 0 | 0 | 27.5719 | 52.5 | 1376.3284 | 3000 | 49.2673 | 3049.2673 | 2205.7089 | 0 | 132.3425
0 | 15.514 | 0 | 0 | 0 | 0 | 36.986 | 52.5 | 1413.3144 | 3000 | 66.7542 | 3066.7542 | 2158.3067 | 0 | 127.3401
0 | 32.5893 | 0 | 0 | 0 | 0 | 19.9107 | 52.5 | 1433.2251 | 3000 | 35.5778 | 3035.5778 | 1883.7963 | 0 | 107.301
0 | 23.7978 | 0 | 0 | 0 | 0 | 28.7022 | 52.5 | 1461.9273 | 3000 | 51.287 | 3051.287 | 1834.6163 | 0 | 103.4173
0 | 17.8377 | 0 | 0 | 0 | 0 | 34.6623 | 52.5 | 1496.5896 | 3000 | 64.9704 | 3064.9704 | 1945.6334 | 0 | 107.0487
0 | 31.6828 | 0 | 0 | 0 | 0 | 3.4104 | 35.0932 | 1500 | 2005.3236 | 6.0939 | 2011.4175 | 994.8216 | 0 | 53.591
0 | 44.0079 | 0 | 0 | 0 | 0 | 1.1013e-13 | 44.0079 | 1500 | 2514.7357 | 1.968e-13 | 2514.7357 | 1438.6581 | 0 | 77.6444
0 | 84.4255 | 0 | 0 | 0 | 0 | -31.9255 | 52.5 | 1468.0745 | 3000 | 0 | 3000 | 2048.2932 | 0 | 110.5873
0 | 74.0348 | 0 | 0 | 0 | 0 | -21.5348 | 52.5 | 1446.5397 | 3000 | 0 | 3000 | 2313.257 | 0 | 127.3217
0 | 51.9969 | 0 | 0 | 0 | 0 | 0.5031 | 52.5 | 1447.0428 | 3000 | 0.89898 | 3000.899 | 2557.4901 | 0 | 150.4827
0 | 16.7024 | 0 | 0 | 0 | 0 | 35.7976 | 52.5 | 1482.8404 | 3000 | 63.9656 | 3063.9656 | 2842.2612 | 0 | 181.7058
0 | 17.2881 | 0 | 0 | 0 | 0 | 17.1596 | 34.4477 | 1500 | 1968.4377 | 30.6619 | 1999.0996 | 1885.5436 | 0 | 130.819
0 | 5.2194 | 0 | 0 | 0 | 0 | -4.7962e-14 | 5.2194 | 1500 | 298.2495 | 0 | 298.2495 | 292.842 | 0 | 20.0655
0 | 3.8651 | 0 | 0 | 0 | 0 | -7.3275e-14 | 3.8651 | 1500 | 220.8616 | 0 | 220.8616 | 220.8616 | 0 | 14.9501
0 | 4.3625 | 0 | 0 | 0 | 0 | 3.1086e-14 | 4.3625 | 1500 | 249.2872 | 5.5547e-14 | 249.2872 | 249.2872 | 0 | 15.9843
0 | 4.4168 | 0 | 0 | 0 | 0 | 1.6875e-14 | 4.4168 | 1500 | 252.39 | 3.0154e-14 | 252.39 | 252.39 | 0 | 14.1263
0 | 3.8606 | 0 | 0 | 0 | 0 | -3.2419e-14 | 3.8606 | 1500 | 220.6081 | 0 | 220.6081 | 220.6081 | 0 | 11.4782
0 | 4.6657 | 0 | 0 | 0 | 0 | 4.6185e-14 | 4.6657 | 1500 | 266.6098 | 8.2527e-14 | 266.6098 | 266.6098 | 0 | 12.8426
0 | 205.3897 | 0 | 0 | 0 | 0 | -152.8897 | 52.5 | 1347.1103 | 3000 | 0 | 3000 | 3000 | 0 | 139.59
0 | 4.6973 | 0 | 0 | 0 | 0 | 47.8027 | 52.5 | 1394.9129 | 3000 | 85.417 | 3085.417 | 3085.417 | 0 | 141.6823
0 | 5.4994 | 0 | 0 | 0 | 0 | 47.0006 | 52.5 | 1441.9135 | 3000 | 83.9839 | 3083.9839 | 3083.9839 | 0 | 141.0614
0 | 25.4455 | 0 | 0 | 0 | 0 | 27.0545 | 52.5 | 1468.968 | 3000 | 48.3428 | 3048.3428 | 3021.3057 | 0 | 144.6299
0 | 82.1044 | 0 | 0 | 0 | 0 | -29.6044 | 52.5 | 1439.3636 | 3000 | 0 | 3000 | 2826.9624 | 0 | 146.0974
0 | 46.0302 | 0 | 0 | 0 | 0 | 6.4698 | 52.5 | 1445.8334 | 3000 | 11.5607 | 3011.5607 | 2514.0776 | 0 | 145.2383
0 | 42.772 | 0 | 0 | 0 | 0 | 9.728 | 52.5 | 1455.5614 | 3000 | 17.3826 | 3017.3826 | 2141.3797 | 0 | 127.8618
0 | 44.3397 | 0 | 0 | 0 | 0 | 8.1603 | 52.5 | 1463.7216 | 3000 | 14.5813 | 3014.5813 | 2138.5784 | 0 | 128.2719
0 | 61.2105 | 0 | 0 | 0 | 0 | -8.7105 | 52.5 | 1455.0111 | 3000 | 0 | 3000 | 1902.2927 | 0 | 112.1021
0 | 72.8803 | 0 | 0 | 0 | 0 | -20.3803 | 52.5 | 1434.6308 | 3000 | 0 | 3000 | 2221.3308 | 0 | 131.7471
0 | 69.1216 | 0 | 0 | 0 | 0 | -16.6216 | 52.5 | 1418.0093 | 3000 | 0 | 3000 | 1837.4036 | 0 | 105.026
0 | 73.9265 | 0 | 0 | 0 | 0 | -21.4265 | 52.5 | 1396.5827 | 3000 | 0 | 3000 | 2583.6283 | 0 | 142.3321
0 | 83.5278 | 0 | 0 | 0 | 0 | -31.0278 | 52.5 | 1365.5549 | 3000 | 0 | 3000 | 1837.4036 | 0 | 97.2538
0 | 86.0017 | 0 | 0 | 0 | 0 | -33.5017 | 52.5 | 1332.0532 | 3000 | 0 | 3000 | 1961.7744 | 0 | 99.717
0 | 95.8563 | 0 | 0 | 0 | 0 | -43.3563 | 52.5 | 1288.6969 | 3000 | 0 | 3000 | 2096.96 | 0 | 106.4207
0 | 97.7452 | 0 | 0 | 0 | 0 | -45.2452 | 52.5 | 1243.4517 | 3000 | 0 | 3000 | 2340.2941 | 0 | 127.546
0 | 77.5624 | 0 | 0 | 0 | 0 | -25.0624 | 52.5 | 1218.3893 | 3000 | 0 | 3000 | 2637.7025 | 0 | 152.1954
0 | 80.4379 | 0 | 0 | 0 | 0 | -27.9379 | 52.5 | 1190.4514 | 3000 | 0 | 3000 | 2891.8515 | 0 | 168.1612
0 | 53.7259 | 0 | 0 | 0 | 0 | -1.2259 | 52.5 | 1189.2256 | 3000 | 0 | 3000 | 3000 | 0 | 172.86
0 | 39.0273 | 0 | 0 | 0 | 0 | 13.4727 | 52.5 | 1202.6983 | 3000 | 24.074 | 3024.074 | 3024.074 | 0 | 172.1908
0 | 44.6835 | 0 | 0 | 0 | 0 | 7.8165 | 52.5 | 1210.5147 | 3000 | 13.967 | 3013.967 | 3013.967 | 0 | 167.4259
0 | 36.9546 | 0 | 0 | 0 | 0 | 15.5454 | 52.5 | 1226.0601 | 3000 | 27.7775 | 3027.7775 | 3027.7775 | 0 | 159.3822
0 | 3.785 | 0 | 0 | 0 | 0 | 48.715 | 52.5 | 1274.7751 | 3000 | 87.0472 | 3087.0472 | 3087.0472 | 0 | 147.3756
0 | 3.1618 | 0 | 0 | 0 | 0 | 49.3382 | 52.5 | 1324.1132 | 3000 | 88.1607 | 3088.1607 | 3088.1607 | 0 | 143.1054
0 | 11.6979 | 0 | 0 | 0 | 0 | 40.8021 | 52.5 | 1364.9153 | 3000 | 72.9079 | 3072.9079 | 3072.9079 | 0 | 130.66
0 | 30.5781 | 0 | 0 | 0 | 0 | 21.9219 | 52.5 | 1386.8372 | 3000 | 39.1716 | 3039.1716 | 3039.1716 | 0 | 127.1893
0 | 23.7552 | 0 | 0 | 0 | 0 | 28.7448 | 52.5 | 1415.582 | 3000 | 51.3631 | 3051.3631 | 3051.3631 | 0 | 129.7134
0 | 21.9329 | 0 | 0 | 0 | 0 | 30.5671 | 52.5 | 1446.1491 | 3000 | 54.6193 | 3054.6193 | 3022.1748 | 0 | 136.3303
0 | 55.9639 | 0 | 0 | 0 | 0 | -3.4639 | 52.5 | 1442.6852 | 3000 | 0 | 3000 | 2805.3327 | 0 | 139.0603
0 | 48.4496 | 0 | 0 | 0 | 0 | 4.0504 | 52.5 | 1446.7355 | 3000 | 7.2374 | 3007.2374 | 2671.9771 | 0 | 146.7984
0 | 57.6704 | 0 | 0 | 0 | 0 | -5.1704 | 52.5 | 1441.5652 | 3000 | 0 | 3000 | 2437.6278 | 0 | 134.0208
0 | 61.0342 | 0 | 0 | 0 | 0 | -8.5342 | 52.5 | 1433.0309 | 3000 | 0 | 3000 | 2383.5535 | 0 | 125.0651
0 | 65.789 | 0 | 0 | 0 | 0 | -13.289 | 52.5 | 1419.7419 | 3000 | 0 | 3000 | 2394.3684 | 0 | 113.8762
0 | 38.6326 | 0 | 0 | 0 | 0 | 13.8674 | 52.5 | 1433.6094 | 3000 | 24.7792 | 3024.7792 | 2056.8501 | 0 | 93.5044
0 | 18.8248 | 0 | 0 | 0 | 0 | 33.6752 | 52.5 | 1467.2845 | 3000 | 70.1862 | 3070.1862 | 1664.2556 | 0 | 72.4783
0 | 16.5133 | 0 | 0 | 0 | 0 | 32.7155 | 49.2287 | 1500 | 2813.0708 | 59.8513 | 2872.9221 | 1883.3633 | 0 | 81.9263
0 | 20.1378 | 0 | 0 | 0 | 0 | 3.5527e-15 | 20.1378 | 1500 | 1150.73 | 0 | 1150.73 | 0 | 298.46 | 0
0 | 19.7297 | 0 | 0 | 0 | 0 | 3.5527e-15 | 19.7297 | 1500 | 1127.4109 | 0 | 1127.4109 | 0 | 29.7781 | 0
0 | 12.0523 | 0 | 0 | 0 | 0 | 1.7764e-15 | 12.0523 | 1500 | 688.7004 | 0 | 688.7004 | 0 | 268.4138 | 0
0 | 22.5758 | 0 | 0 | 0 | 0 | -5.6843e-14 | 22.5758 | 1500 | 1290.0438 | 0 | 1290.0438 | 630.3379 | 0 | 32.1409
0 | 20.5507 | 0 | 0 | 0 | 0 | 0 | 20.5507 | 1500 | 1174.3235 | 1.5871e-14 | 1174.3235 | 855.2854 | 0 | 46.2196
0 | 26.5221 | 0 | 0 | 0 | 0 | -6.3949e-14 | 26.5221 | 1500 | 1515.5497 | 0 | 1515.5497 | 1407.4012 | 0 | 81.6996
0 | 2.8824 | 0 | 0 | 0 | 0 | -7.5051e-14 | 2.8824 | 1500 | 164.707 | 0 | 164.707 | 164.707 | 0 | 9.6139
0 | 3.5458 | 0 | 0 | 0 | 0 | -2.176e-14 | 3.5458 | 1500 | 202.6188 | 0 | 202.6188 | 202.6188 | 0 | 11.8795
0 | 5.1589 | 0 | 0 | 0 | 0 | -8.2601e-14 | 5.1589 | 1500 | 294.7959 | 0 | 294.7959 | 294.7959 | 0 | 16.8328
0 | 3.3998 | 0 | 0 | 0 | 0 | 4.5297e-14 | 3.3998 | 1500 | 194.2719 | 8.094e-14 | 194.2719 | 194.2719 | 0 | 10.3197
0 | 3.9845 | 0 | 0 | 0 | 0 | 7.6827e-14 | 3.9845 | 1500 | 227.6843 | 1.3728e-13 | 227.6843 | 227.6843 | 0 | 11.366
0 | 5.3986 | 0 | 0 | 0 | 0 | 4.3521e-14 | 5.3986 | 1500 | 308.4933 | 7.7766e-14 | 308.4933 | 308.4933 | 0 | 15.0792
0 | 4.7574 | 0 | 0 | 0 | 0 | 4.4409e-14 | 4.7574 | 1500 | 271.8539 | 7.9353e-14 | 271.8539 | 271.8539 | 0 | 12.0866
0 | 4.3014 | 0 | 0 | 0 | 0 | 1.1102e-13 | 4.3014 | 1500 | 245.7968 | 1.9838e-13 | 245.7968 | 245.7968 | 0 | 10.4513
0 | 3.432 | 0 | 0 | 0 | 0 | -1.0214e-13 | 3.432 | 1500 | 196.1158 | 0 | 196.1158 | 196.1158 | 0 | 8.0251
0 | 4.3552 | 0 | 0 | 0 | 0 | -7.1054e-14 | 4.3552 | 1500 | 248.8674 | 0 | 248.8674 | 189.3857 | 0 | 8.1625
0 | 204.0823 | 0 | 0 | 0 | 0 | -151.5823 | 52.5 | 1348.4177 | 3000 | 0 | 3000 | 2881.0366 | 0 | 163.3548
0 | 3.8266 | 0 | 0 | 0 | 0 | 48.6734 | 52.5 | 1397.0911 | 3000 | 86.9729 | 3086.9729 | 2989.6392 | 0 | 193.34
0 | 20.2658 | 0 | 0 | 0 | 0 | 32.2342 | 52.5 | 1429.3254 | 3000 | 57.5983 | 3057.5983 | 2911.5978 | 0 | 183.9256
0 | 15.0616 | 0 | 0 | 0 | 0 | 37.4384 | 52.5 | 1466.7638 | 3000 | 66.8974 | 3066.8974 | 2769.4891 | 0 | 160.2703
0 | 31.4052 | 0 | 0 | 0 | 0 | 21.0948 | 52.5 | 1487.8585 | 3000 | 37.6935 | 3037.6935 | 2718.6555 | 0 | 150.2601
0 | 23.2553 | 0 | 0 | 0 | 0 | 12.1415 | 35.3967 | 1500 | 2022.6712 | 21.6952 | 2044.3663 | 1865.9213 | 0 | 103.372
0 | 18.9189 | 0 | 0 | 0 | 0 | -1.0658e-13 | 18.9189 | 1500 | 1081.0812 | 0 | 1081.0812 | 870.1916 | 0 | 47.1644
0 | 26.017 | 0 | 0 | 0 | 0 | -7.816e-14 | 26.017 | 1500 | 1486.6884 | 0 | 1486.6884 | 1340.6879 | 0 | 72.7055
0 | 12.5113 | 0 | 0 | 0 | 0 | -1.5987e-14 | 12.5113 | 1500 | 714.9303 | 0 | 714.9303 | 331.0031 | 0 | 18.0992
0 | 19.3659 | 0 | 0 | 0 | 0 | -9.2371e-14 | 19.3659 | 1500 | 1106.6201 | 0 | 1106.6201 | 555.0628 | 0 | 29.8124
0 | 19.9207 | 0 | 0 | 0 | 0 | 9.77e-14 | 19.9207 | 1500 | 1138.3278 | 1.7458e-13 | 1138.3278 | 754.4006 | 0 | 38.9044
0 | 12.4364 | 0 | 0 | 0 | 0 | 7.2831e-14 | 12.4364 | 1500 | 710.6516 | 1.3014e-13 | 710.6516 | 499.762 | 0 | 27.237
0 | 16.4857 | 0 | 0 | 0 | 0 | -2.8422e-14 | 16.4857 | 1500 | 942.0382 | 0 | 942.0382 | 833.8897 | 0 | 48.0654
0 | 14.9378 | 0 | 0 | 0 | 0 | -8.8818e-14 | 14.9378 | 1500 | 853.5877 | 0 | 853.5877 | 810.3283 | 0 | 49.1869
0 | 3.8404 | 0 | 0 | 0 | 0 | 8.3045e-14 | 3.8404 | 1500 | 219.4526 | 1.4839e-13 | 219.4526 | 219.4526 | 0 | 11.8899
0 | 4.0587 | 0 | 0 | 0 | 0 | -8.4377e-14 | 4.0587 | 1500 | 231.9248 | 0 | 231.9248 | 231.9248 | 0 | 12.0462
0 | 4.8724 | 0 | 0 | 0 | 0 | -4.6185e-14 | 4.8724 | 1500 | 278.4234 | 0 | 278.4234 | 278.4234 | 0 | 13.7151
0 | 3.1686 | 0 | 0 | 0 | 0 | 4.4409e-15 | 3.1686 | 1500 | 181.0627 | 7.9353e-15 | 181.0627 | 181.0627 | 0 | 8.376
0 | 3.6423 | 0 | 0 | 0 | 0 | -1.0747e-13 | 3.6423 | 1500 | 208.1327 | 0 | 208.1327 | 208.1327 | 0 | 10.1465
0 | 4.821 | 0 | 0 | 0 | 0 | -2.6645e-14 | 4.821 | 1500 | 275.4858 | 0 | 275.4858 | 275.4858 | 0 | 13.3803
0 | 2.8492 | 0 | 0 | 0 | 0 | 9.8588e-14 | 2.8492 | 1500 | 162.8137 | 1.7616e-13 | 162.8137 | 162.8137 | 0 | 6.9798
0 | 4.2589 | 0 | 0 | 0 | 0 | -7.0166e-14 | 4.2589 | 1500 | 243.3682 | 0 | 243.3682 | 243.3682 | 0 | 9.3453
0 | 3.5316 | 0 | 0 | 0 | 0 | -6.2617e-14 | 3.5316 | 1500 | 201.8045 | 0 | 201.8045 | 201.8045 | 0 | 6.4154
0 | 4.2727 | 0 | 0 | 0 | 0 | -3.7303e-14 | 4.2727 | 1500 | 244.1556 | 0 | 244.1556 | 206.3037 | 0 | 6.5316
0 | 4.6593 | 0 | 0 | 0 | 0 | 4.3521e-14 | 4.6593 | 1500 | 266.2437 | 7.7766e-14 | 266.2437 | 22.9096 | 0 | 0.77893
0 | 3.3748 | 0 | 0 | 0 | 0 | 4.4409e-16 | 3.3748 | 1500 | 192.8463 | 0 | 192.8463 | 0 | 315.4517 | 0
0 | 11.6792 | 0 | 0 | 0 | 0 | 7.816e-14 | 11.6792 | 1500 | 667.3805 | 1.3966e-13 | 667.3805 | 115.8231 | 0 | 5.6881
0 | 32.2322 | 0 | 0 | 0 | 0 | 0 | 32.2322 | 1500 | 1841.8373 | 0 | 1841.8373 | 1479.5398 | 0 | 73.829
0 | 74.2144 | 0 | 0 | 0 | 0 | -21.7144 | 52.5 | 1478.2856 | 3000 | 0 | 3000 | 2605.258 | 0 | 113.3287
0 | 57.7523 | 0 | 0 | 0 | 0 | -5.2523 | 52.5 | 1473.0334 | 3000 | 0 | 3000 | 1896.8853 | 0 | 80.997
0 | 90.8093 | 0 | 0 | 0 | 0 | -38.3093 | 52.5 | 1434.724 | 3000 | 0 | 3000 | 1604.8843 | 0 | 64.3559
0 | 95.2641 | 0 | 0 | 0 | 0 | -42.7641 | 52.5 | 1391.96 | 3000 | 0 | 3000 | 2237.553 | 0 | 89.0546
0 | 79.8396 | 0 | 0 | 0 | 0 | -27.3396 | 52.5 | 1364.6204 | 3000 | 0 | 3000 | 2005.0338 | 0 | 68.1711
0 | 85.3797 | 0 | 0 | 0 | 0 | -32.8797 | 52.5 | 1331.7407 | 3000 | 0 | 3000 | 2123.9971 | 0 | 63.7199
0 | 73.9935 | 0 | 0 | 0 | 0 | -21.4935 | 52.5 | 1310.2472 | 3000 | 0 | 3000 | 2264.5902 | 0 | 89.8589
0 | 7.3509 | 0 | 0 | 0 | 0 | 45.1491 | 52.5 | 1355.3963 | 3000 | 85.8109 | 3085.8109 | 2496.4015 | 0 | 110.965
0 | 22.697 | 0 | 0 | 0 | 0 | 29.803 | 52.5 | 1385.1993 | 3000 | 53.254 | 3053.254 | 2755.8456 | 0 | 119.8793
0 | 10.3136 | 0 | 0 | 0 | 0 | 42.1864 | 52.5 | 1427.3857 | 3000 | 75.3815 | 3075.3815 | 2983.4553 | 0 | 142.9672
0 | 2.8268 | 0 | 0 | 0 | 0 | 49.6732 | 52.5 | 1477.0589 | 3000 | 88.7594 | 3088.7594 | 3088.7594 | 0 | 154.8086
0 | 4.8085 | 0 | 0 | 0 | 0 | 22.9411 | 27.7496 | 1500 | 1585.689 | 40.9926 | 1626.6817 | 1626.6817 | 0 | 75.4618
0 | 3.1215 | 0 | 0 | 0 | 0 | -5.1958e-14 | 3.1215 | 1500 | 178.3688 | 0 | 178.3688 | 178.3688 | 0 | 8.353
0 | 2.5487 | 0 | 0 | 0 | 0 | 4.9738e-14 | 2.5487 | 1500 | 145.6389 | 8.8875e-14 | 145.6389 | 145.6389 | 0 | 7.0009
0 | 4.4086 | 0 | 0 | 0 | 0 | 6.9278e-14 | 4.4086 | 1500 | 251.9227 | 1.2379e-13 | 251.9227 | 251.9227 | 0 | 10.5833
0 | 3.6217 | 0 | 0 | 0 | 0 | -3.153e-14 | 3.6217 | 1500 | 206.9552 | 0 | 206.9552 | 206.9552 | 0 | 7.6304
0 | 4.7704 | 0 | 0 | 0 | 0 | -2.5757e-14 | 4.7704 | 1500 | 272.5935 | 0 | 272.5935 | 272.5935 | 0 | 8.614
0 | 2.4673 | 0 | 0 | 0 | 0 | 1.5099e-14 | 2.4673 | 1500 | 140.9886 | 2.698e-14 | 140.9886 | 140.9886 | 0 | 3.9054
0 | 2.8548 | 0 | 0 | 0 | 0 | -8.7486e-14 | 2.8548 | 1500 | 163.1295 | 0 | 163.1295 | 163.1295 | 0 | 4.5888
0 | 4.932 | 0 | 0 | 0 | 0 | -1.128e-13 | 4.932 | 1500 | 281.8268 | 0 | 281.8268 | 249.3823 | 0 | 7.1373
0 | 204.3664 | 0 | 0 | 0 | 0 | -151.8664 | 52.5 | 1348.1336 | 3000 | 0 | 3000 | 2794.5178 | 0 | 82.2706
0 | 3.0525 | 0 | 0 | 0 | 0 | 49.4475 | 52.5 | 1397.5811 | 3000 | 99.2996 | 3099.2996 | 2563.9645 | 0 | 91.0464
0 | 18.4973 | 0 | 0 | 0 | 0 | 34.0027 | 52.5 | 1431.5838 | 3000 | 60.7583 | 3060.7583 | 2195.5702 | 0 | 94.7828
0 | 18.6457 | 0 | 0 | 0 | 0 | 33.8543 | 52.5 | 1465.4381 | 3000 | 62.6185 | 3062.6185 | 1927.0592 | 0 | 88.5676
0 | 14.1551 | 0 | 0 | 0 | 0 | 34.5619 | 48.7171 | 1500 | 2783.8323 | 64.4491 | 2848.2815 | 1950.6489 | 0 | 85.8286
0 | 12.8293 | 0 | 0 | 0 | 0 | 1.7764e-15 | 12.8293 | 1500 | 733.1011 | 0 | 733.1011 | 0 | 153.7167 | 0
0 | 19.9466 | 0 | 0 | 0 | 0 | 0 | 19.9466 | 1500 | 1139.8035 | 0 | 1139.8035 | 0 | 103.9043 | 0
0 | 8.1928 | 0 | 0 | 0 | 0 | 0 | 8.1928 | 1500 | 468.1616 | 0 | 468.1616 | 0 | 369.9893 | 0
0 | 23.5734 | 0 | 0 | 0 | 0 | -1.0303e-13 | 23.5734 | 1500 | 1347.0541 | 0 | 1347.0541 | 303.4211 | 0 | 13.839
0 | 17.5124 | 0 | 0 | 0 | 0 | -8.5265e-14 | 17.5124 | 1500 | 1000.7089 | 0 | 1000.7089 | 59.8169 | 0 | 2.7773
0 | 11.3672 | 0 | 0 | 0 | 0 | 2.6645e-14 | 11.3672 | 1500 | 649.5533 | 4.7612e-14 | 649.5533 | 130.4405 | 0 | 6.0003
0 | 14.7971 | 0 | 0 | 0 | 0 | -5.6843e-14 | 14.7971 | 1500 | 845.5513 | 0 | 845.5513 | 483.2538 | 0 | 23.1575
0 | 13.8462 | 0 | 0 | 0 | 0 | -3.1974e-14 | 13.8462 | 1500 | 791.2118 | 0 | 791.2118 | 699.2856 | 0 | 34.3769
0 | 26.2369 | 0 | 0 | 0 | 0 | 0 | 26.2369 | 1500 | 1499.2527 | 0 | 1499.2527 | 1483.0304 | 0 | 80.6324
0 | 3.7456 | 0 | 0 | 0 | 0 | -2.1316e-14 | 3.7456 | 1500 | 214.0364 | 0 | 214.0364 | 214.0364 | 0 | 12.0952
0 | 4.2206 | 0 | 0 | 0 | 0 | -1.5987e-14 | 4.2206 | 1500 | 241.1783 | 0 | 241.1783 | 241.1783 | 0 | 13.7375
0 | 4.4342 | 0 | 0 | 0 | 0 | 3.8192e-14 | 4.4342 | 1500 | 253.3833 | 6.8243e-14 | 253.3833 | 253.3833 | 0 | 13.9361
0 | 4.4328 | 0 | 0 | 0 | 0 | 1.954e-14 | 4.4328 | 1500 | 253.3031 | 3.4915e-14 | 253.3031 | 253.3031 | 0 | 13.2452
0 | 4.0356 | 0 | 0 | 0 | 0 | -2.3093e-14 | 4.0356 | 1500 | 230.6058 | 0 | 230.6058 | 230.6058 | 0 | 10.0982
0 | 3.9051 | 0 | 0 | 0 | 0 | 8.4377e-14 | 3.9051 | 1500 | 223.1511 | 1.5077e-13 | 223.1511 | 223.1511 | 0 | 9.8343
0 | 4.9918 | 0 | 0 | 0 | 0 | 0 | 4.9918 | 1500 | 285.2438 | 9.5223e-15 | 285.2438 | 285.2438 | 0 | 12.1172
0 | 3.3135 | 0 | 0 | 0 | 0 | -1.0081e-13 | 3.3135 | 1500 | 189.3443 | 0 | 189.3443 | 189.3443 | 0 | 7.7821
0 | 4.0884 | 0 | 0 | 0 | 0 | 9.5923e-14 | 4.0884 | 1500 | 233.6216 | 1.714e-13 | 233.6216 | 233.6216 | 0 | 9.4617
0 | 203.8123 | 0 | 0 | 0 | 0 | -151.3123 | 52.5 | 1348.6877 | 3000 | 0 | 3000 | 2962.148 | 0 | 124.7657
0 | 3.7652 | 0 | 0 | 0 | 0 | 48.7348 | 52.5 | 1397.4225 | 3000 | 87.0826 | 3087.0826 | 2876.193 | 0 | 141.3936
0 | 4.4041 | 0 | 0 | 0 | 0 | 48.0959 | 52.5 | 1445.5184 | 3000 | 94.0506 | 3094.0506 | 2574.9377 | 0 | 139.0981
0 | 23.6758 | 0 | 0 | 0 | 0 | 28.8242 | 52.5 | 1474.3427 | 3000 | 51.5051 | 3051.5051 | 2283.6507 | 0 | 123.477
0 | 13.7865 | 0 | 0 | 0 | 0 | 25.6573 | 39.4438 | 1500 | 2253.9319 | 49.8325 | 2303.7645 | 1384.5022 | 0 | 73.6417
0 | 16.4693 | 0 | 0 | 0 | 0 | 3.5527e-15 | 16.4693 | 1500 | 941.1026 | 0 | 941.1026 | 0 | 248.5309 | 0
0 | 22.5969 | 0 | 0 | 0 | 0 | 3.5527e-15 | 22.5969 | 1500 | 1291.2495 | 0 | 1291.2495 | 0 | 82.2365 | 0
0 | 17.0106 | 0 | 0 | 0 | 0 | 3.5527e-15 | 17.0106 | 1500 | 972.0328 | 0 | 972.0328 | 0 | 158.1191 | 0
0 | 26.6865 | 0 | 0 | 0 | 0 | -4.6185e-14 | 26.6865 | 1500 | 1524.9404 | 0 | 1524.9404 | 335.3069 | 0 | 17.0302
0 | 11.5909 | 0 | 0 | 0 | 0 | 1.7764e-15 | 11.5909 | 1500 | 662.3352 | 0 | 662.3352 | 0 | 375.8905 | 0
0 | 22.0297 | 0 | 0 | 0 | 0 | 6.5725e-14 | 22.0297 | 1500 | 1258.8396 | 1.1744e-13 | 1258.8396 | 550.4669 | 0 | 27.9472
0 | 15.8273 | 0 | 0 | 0 | 0 | 0 | 15.8273 | 1500 | 904.4197 | 0 | 904.4197 | 834.1232 | 0 | 41.6061
0 | 18.5062 | 0 | 0 | 0 | 0 | 1.0303e-13 | 18.5062 | 1500 | 1057.4976 | 1.841e-13 | 1057.4976 | 992.6085 | 0 | 58.6235
0 | 28.1648 | 0 | 0 | 0 | 0 | -28.1648 | 0 | 1471.8352 | 0 | 0 | 0 | 0 | 54.0743 | 0
0 | 29.1751 | 0 | 0 | 0 | 0 | -29.1751 | 0 | 1442.6601 | 0 | 0 | 0 | 0 | 37.852 | 0
0 | 50.3719 | 0 | 0 | 0 | 0 | -50.3719 | 0 | 1392.2881 | 0 | 0 | 0 | 0 | 0 | 0
0 | 10.0968 | 0 | 0 | 0 | 0 | -10.0968 | 0 | 1382.1913 | 0 | 0 | 0 | 0 | 0 | 0
0 | 18.7363 | 0 | 0 | 0 | 0 | 33.7637 | 52.5 | 1415.955 | 3000 | 60.3312 | 3060.3312 | 3060.3312 | 0 | 182.4876
0 | 4.3027 | 0 | 0 | 0 | 0 | 48.1973 | 52.5 | 1464.1523 | 3000 | 86.1221 | 3086.1221 | 3086.1221 | 0 | 159.3365
0 | 4.3039 | 0 | 0 | 0 | 0 | 35.8477 | 40.1516 | 1500 | 2294.379 | 64.0551 | 2358.4341 | 2358.4341 | 0 | 117.45
0 | 4.0016 | 0 | 0 | 0 | 0 | -1.3323e-14 | 4.0016 | 1500 | 228.6646 | 0 | 228.6646 | 228.6646 | 0 | 11.136
0 | 4.5238 | 0 | 0 | 0 | 0 | -9.77e-15 | 4.5238 | 1500 | 258.502 | 0 | 258.502 | 258.502 | 0 | 12.253
0 | 5.9065 | 0 | 0 | 0 | 0 | -3.9968e-14 | 5.9065 | 1500 | 337.5154 | 0 | 337.5154 | 337.5154 | 0 | 16.0084
0 | 5.1007 | 0 | 0 | 0 | 0 | 3.1086e-14 | 5.1007 | 1500 | 291.4712 | 5.5547e-14 | 291.4712 | 291.4712 | 0 | 13.7691
0 | 12.6731 | 0 | 0 | 0 | 0 | -7.1054e-14 | 12.6731 | 1500 | 724.1743 | 0 | 724.1743 | 718.7669 | 0 | 34.3211
0 | 24.3111 | 0 | 0 | 0 | 0 | 6.7502e-14 | 24.3111 | 1500 | 1389.2054 | 1.2062e-13 | 1389.2054 | 1281.0569 | 0 | 73.2252
0 | 5.551 | 0 | 0 | 0 | 0 | 8.8818e-16 | 5.551 | 1500 | 317.2016 | 0 | 317.2016 | 0 | 223.541 | 0
0 | 25.3198 | 0 | 0 | 0 | 0 | -3.3751e-14 | 25.3198 | 1500 | 1446.8444 | 0 | 1446.8444 | 770.9162 | 0 | 49.3001
0 | 13.9737 | 0 | 0 | 0 | 0 | 1.7764e-15 | 13.9737 | 1500 | 798.4973 | 0 | 798.4973 | 0 | 109.9502 | 0
0 | 18.0246 | 0 | 0 | 0 | 0 | 3.5527e-15 | 18.0246 | 1500 | 1029.9746 | 0 | 1029.9746 | 0 | 240.7704 | 0
0 | 2.0164 | 0 | 0 | 0 | 0 | 4.4409e-16 | 2.0164 | 1500 | 115.2224 | 0 | 115.2224 | 0 | 641.8171 | 0
0 | 15.5037 | 0 | 0 | 0 | 0 | 0 | 15.5037 | 1500 | 885.9229 | 0 | 885.9229 | 0 | 487.5631 | 0
0 | 17.3045 | 0 | 0 | 0 | 0 | -2.8422e-14 | 17.3045 | 1500 | 988.8294 | 0 | 988.8294 | 540.0131 | 0 | 24.8082
0 | 18.4424 | 0 | 0 | 0 | 0 | 6.0396e-14 | 18.4424 | 1500 | 1053.8506 | 1.0792e-13 | 1053.8506 | 561.7749 | 0 | 24.9091
0 | 16.2211 | 0 | 0 | 0 | 0 | -1.0658e-14 | 16.2211 | 1500 | 926.9172 | 0 | 926.9172 | 2.2475 | 0 | 0.10064
0 | 21.8364 | 0 | 0 | 0 | 0 | 7.2831e-14 | 21.8364 | 1500 | 1247.7937 | 1.3014e-13 | 1247.7937 | 863.8665 | 0 | 43.1069
0 | 15.9306 | 0 | 0 | 0 | 0 | -6.5725e-14 | 15.9306 | 1500 | 910.3185 | 0 | 910.3185 | 391.2057 | 0 | 20.6048
0 | 25.274 | 0 | 0 | 0 | 0 | 9.5923e-14 | 25.274 | 1500 | 1444.2305 | 1.714e-13 | 1444.2305 | 1179.2666 | 0 | 62.7016
0 | 23.0517 | 0 | 0 | 0 | 0 | -8.8818e-14 | 23.0517 | 1500 | 1317.2389 | 0 | 1317.2389 | 1257.7572 | 0 | 77.1508
0 | 4.7385 | 0 | 0 | 0 | 0 | 7.9048e-14 | 4.7385 | 1500 | 270.7711 | 1.4125e-13 | 270.7711 | 270.7711 | 0 | 17.3023
0 | 4.2462 | 0 | 0 | 0 | 0 | 2.3093e-14 | 4.2462 | 1500 | 242.6425 | 4.1263e-14 | 242.6425 | 242.6425 | 0 | 15.1894
0 | 4.2044 | 0 | 0 | 0 | 0 | 3.2863e-14 | 4.2044 | 1500 | 240.2542 | 5.8721e-14 | 240.2542 | 240.2542 | 0 | 13.6512
0 | 4.916 | 0 | 0 | 0 | 0 | -3.4639e-14 | 4.916 | 1500 | 280.9155 | 0 | 280.9155 | 280.9155 | 0 | 14.411
0 | 3.6328 | 0 | 0 | 0 | 0 | -3.5527e-15 | 3.6328 | 1500 | 207.5909 | 0 | 207.5909 | 207.5909 | 0 | 9.8377
0 | 5.0846 | 0 | 0 | 0 | 0 | -7.816e-14 | 5.0846 | 1500 | 290.5465 | 0 | 290.5465 | 290.5465 | 0 | 13.1763
0 | 3.8708 | 0 | 0 | 0 | 0 | 4.4853e-14 | 3.8708 | 1500 | 221.1886 | 8.0146e-14 | 221.1886 | 221.1886 | 0 | 9.5664
0 | 3.6867 | 0 | 0 | 0 | 0 | 3.3751e-14 | 3.6867 | 1500 | 210.666 | 6.0308e-14 | 210.666 | 210.666 | 0 | 9.0966
0 | 3.2501 | 0 | 0 | 0 | 0 | 7.9048e-14 | 3.2501 | 1500 | 185.7212 | 1.4125e-13 | 185.7212 | 185.7212 | 0 | 8.2312
0 | 4.1474 | 0 | 0 | 0 | 0 | -1.1013e-13 | 4.1474 | 1500 | 236.9933 | 0 | 236.9933 | 204.5488 | 0 | 9.2661
0 | 4.4283 | 0 | 0 | 0 | 0 | 0 | 4.4283 | 1500 | 253.046 | 1.1109e-14 | 253.046 | 36.749 | 0 | 1.9451
0 | 3.5461 | 0 | 0 | 0 | 0 | 4.4409e-16 | 3.5461 | 1500 | 202.6368 | 0 | 202.6368 | 0 | 300.2537 | 0
0 | 18.6215 | 0 | 0 | 0 | 0 | -9.4147e-14 | 18.6215 | 1500 | 1064.0874 | 0 | 1064.0874 | 236.7513 | 0 | 14.2572
0 | 14.828 | 0 | 0 | 0 | 0 | 1.7764e-15 | 14.828 | 1500 | 847.3118 | 0 | 847.3118 | 0 | 244.9881 | 0
0 | 10.1384 | 0 | 0 | 0 | 0 | 1.7764e-15 | 10.1384 | 1500 | 579.3389 | 0 | 579.3389 | 0 | 745.4803 | 0
0 | 18.1283 | 0 | 0 | 0 | 0 | 3.5527e-15 | 18.1283 | 1500 | 1035.9001 | 0 | 1035.9001 | 0 | 359.2156 | 0
0 | 22.093 | 0 | 0 | 0 | 0 | 3.5527e-15 | 22.093 | 1500 | 1262.4571 | 0 | 1262.4571 | 0 | 78.5843 | 0
0 | 17.2992 | 0 | 0 | 0 | 0 | 3.5527e-15 | 17.2992 | 1500 | 988.5277 | 0 | 988.5277 | 0 | 238.9578 | 0
0 | 19.5041 | 0 | 0 | 0 | 0 | 1.0658e-14 | 19.5041 | 1500 | 1114.5216 | 1.9045e-14 | 1114.5216 | 43.8514 | 0 | 2.0176
0 | 10.1335 | 0 | 0 | 0 | 0 | 0 | 10.1335 | 1500 | 579.0545 | 0 | 579.0545 | 0 | 383.4672 | 0
0 | 32.239 | 0 | 0 | 0 | 0 | -8.5265e-14 | 32.239 | 1500 | 1842.2263 | 0 | 1842.2263 | 1106.8164 | 0 | 54.0569
0 | 11.5543 | 0 | 0 | 0 | 0 | -9.1482e-14 | 11.5543 | 1500 | 660.2472 | 0 | 660.2472 | 270.9126 | 0 | 14.3123
0 | 11.8964 | 0 | 0 | 0 | 0 | 0 | 11.8964 | 1500 | 679.7915 | 3.1741e-15 | 679.7915 | 593.2727 | 0 | 37.2991
0 | 21.7053 | 0 | 0 | 0 | 0 | -21.7053 | 0 | 1478.2947 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 3.5441 | 0 | 0 | 0 | 0 | 21.7053 | 25.2493 | 1500 | 1442.8183 | 38.7844 | 1481.6027 | 1481.6027 | 0 | 99.7859
0 | 3.5682 | 0 | 0 | 0 | 0 | -4.6185e-14 | 3.5682 | 1500 | 203.8997 | 0 | 203.8997 | 203.8997 | 0 | 13.4574
0 | 2.9512 | 0 | 0 | 0 | 0 | -6.2172e-15 | 2.9512 | 1500 | 168.6428 | 0 | 168.6428 | 168.6428 | 0 | 9.245
0 | 3.9332 | 0 | 0 | 0 | 0 | 9.5479e-14 | 3.9332 | 1500 | 224.7537 | 1.7061e-13 | 224.7537 | 224.7537 | 0 | 11.4512
0 | 4.2025 | 0 | 0 | 0 | 0 | 1.4211e-14 | 4.2025 | 1500 | 240.1433 | 2.5393e-14 | 240.1433 | 240.1433 | 0 | 10.6023
0 | 3.7886 | 0 | 0 | 0 | 0 | -9.015e-14 | 3.7886 | 1500 | 216.4906 | 0 | 216.4906 | 216.4906 | 0 | 9.2528
0 | 4.6619 | 0 | 0 | 0 | 0 | -6.0396e-14 | 4.6619 | 1500 | 266.3924 | 0 | 266.3924 | 266.3924 | 0 | 11.5614
0 | 4.3457 | 0 | 0 | 0 | 0 | -8.9706e-14 | 4.3457 | 1500 | 248.3279 | 0 | 248.3279 | 248.3279 | 0 | 10.3826
0 | 12.8552 | 0 | 0 | 0 | 0 | 5.862e-14 | 12.8552 | 1500 | 734.5823 | 1.0475e-13 | 734.5823 | 734.5823 | 0 | 29.4568
0 | 241.4439 | 0 | 0 | 0 | 0 | -188.9439 | 52.5 | 1311.0561 | 3000 | 0 | 3000 | 2994.5926 | 0 | 109.093
0 | 51.4125 | 0 | 0 | 0 | 0 | 1.0875 | 52.5 | 1312.1436 | 3000 | 1.9433 | 3001.9433 | 2937.0542 | 0 | 123.0626
0 | 27.0007 | 0 | 0 | 0 | 0 | 25.4993 | 52.5 | 1337.6429 | 3000 | 45.5638 | 3045.5638 | 2904.9707 | 0 | 136.5046
0 | 18.0074 | 0 | 0 | 0 | 0 | 34.4926 | 52.5 | 1372.1355 | 3000 | 61.6337 | 3061.6337 | 2866.9664 | 0 | 143.893
0 | 25.4292 | 0 | 0 | 0 | 0 | 27.0708 | 52.5 | 1399.2063 | 3000 | 48.372 | 3048.372 | 2767.1859 | 0 | 161.7974
0 | 30.9509 | 0 | 0 | 0 | 0 | 21.5491 | 52.5 | 1420.7554 | 3000 | 38.5054 | 3038.5054 | 2638.356 | 0 | 150.4391
0 | 28.4526 | 0 | 0 | 0 | 0 | 24.0474 | 52.5 | 1444.8029 | 3000 | 42.9696 | 3042.9696 | 2431.9305 | 0 | 122.2775
0 | 225.1175 | 0 | 0 | 0 | 0 | -172.6175 | 52.5 | 1272.1853 | 3000 | 0 | 3000 | 2134.812 | 0 | 105.2035
0 | 16.7186 | 0 | 0 | 0 | 0 | 35.7814 | 52.5 | 1307.9668 | 3000 | 63.9367 | 3063.9367 | 2393.4159 | 0 | 110.1689
0 | 22.6048 | 0 | 0 | 0 | 0 | 29.8952 | 52.5 | 1337.862 | 3000 | 53.4187 | 3053.4187 | 2236.8975 | 0 | 95.9629
0 | 14.0231 | 0 | 0 | 0 | 0 | 38.4769 | 52.5 | 1376.3389 | 3000 | 68.7532 | 3068.7532 | 2517.1958 | 0 | 108.9946
0 | 8.9474 | 0 | 0 | 0 | 0 | 43.5526 | 52.5 | 1419.8915 | 3000 | 79.8639 | 3079.8639 | 2501.2694 | 0 | 117.3596
0 | 28.3566 | 0 | 0 | 0 | 0 | 24.1434 | 52.5 | 1444.0349 | 3000 | 43.1411 | 3043.1411 | 2832.2515 | 0 | 142.6605
0 | 8.7228 | 0 | 0 | 0 | 0 | 43.7772 | 52.5 | 1487.8121 | 3000 | 78.224 | 3078.224 | 2943.0383 | 0 | 149.3886
0 | 3.749 | 0 | 0 | 0 | 0 | 12.1879 | 15.9369 | 1500 | 910.6804 | 21.7782 | 932.4586 | 894.6066 | 0 | 47.9599
0 | 3.8408 | 0 | 0 | 0 | 0 | -9.77e-14 | 3.8408 | 1500 | 219.4755 | 0 | 219.4755 | 219.4755 | 0 | 12.2204
0 | 4.1874 | 0 | 0 | 0 | 0 | 7.1054e-14 | 4.1874 | 1500 | 239.2774 | 1.2696e-13 | 239.2774 | 239.2774 | 0 | 12.239
0 | 4.1317 | 0 | 0 | 0 | 0 | -1.128e-13 | 4.1317 | 1500 | 236.1 | 0 | 236.1 | 236.1 | 0 | 11.8215
0 | 3.2851 | 0 | 0 | 0 | 0 | -1.0347e-13 | 3.2851 | 1500 | 187.7227 | 0 | 187.7227 | 187.7227 | 0 | 9.0726
0 | 3.41 | 0 | 0 | 0 | 0 | 5.3291e-14 | 3.41 | 1500 | 194.8581 | 9.5223e-14 | 194.8581 | 194.8581 | 0 | 8.7355
0 | 4.048 | 0 | 0 | 0 | 0 | 1.0658e-14 | 4.048 | 1500 | 231.3115 | 1.9045e-14 | 231.3115 | 231.3115 | 0 | 9.7845
0 | 4.0055 | 0 | 0 | 0 | 0 | 9.9476e-14 | 4.0055 | 1500 | 228.8836 | 1.7775e-13 | 228.8836 | 228.8836 | 0 | 9.4712
0 | 3.4407 | 0 | 0 | 0 | 0 | 3.7303e-14 | 3.4407 | 1500 | 196.6103 | 6.6656e-14 | 196.6103 | 196.6103 | 0 | 8.002
0 | 11.5756 | 0 | 0 | 0 | 0 | -5.3291e-14 | 11.5756 | 1500 | 661.4652 | 0 | 661.4652 | 661.4652 | 0 | 26.8886
0 | 29.7704 | 0 | 0 | 0 | 0 | -1.0303e-13 | 29.7704 | 1500 | 1701.1655 | 0 | 1701.1655 | 1657.9061 | 0 | 72.1852
0 | 34.1518 | 0 | 0 | 0 | 0 | 0 | 34.1518 | 1500 | 1951.5291 | 7.6179e-14 | 1951.5291 | 1708.195 | 0 | 84.8631
0 | 17.4905 | 0 | 0 | 0 | 0 | -5.1514e-14 | 17.4905 | 1500 | 999.4596 | 0 | 999.4596 | 512.7913 | 0 | 28.4702
0 | 8.9663 | 0 | 0 | 0 | 0 | 1.7764e-15 | 8.9663 | 1500 | 512.3616 | 0 | 512.3616 | 0 | 179.7889 | 0
0 | 15.2891 | 0 | 0 | 0 | 0 | 1.7764e-15 | 15.2891 | 1500 | 873.6606 | 0 | 873.6606 | 0 | 142.9353 | 0
0 | 31.4641 | 0 | 0 | 0 | 0 | 9.2371e-14 | 31.4641 | 1500 | 1797.9488 | 1.6505e-13 | 1797.9488 | 770.538 | 0 | 39.8599
0 | 11.2429 | 0 | 0 | 0 | 0 | 1.7764e-15 | 11.2429 | 1500 | 642.452 | 0 | 642.452 | 0 | 260.588 | 0
0 | 8.6055 | 0 | 0 | 0 | 0 | 1.7764e-15 | 8.6055 | 1500 | 491.7401 | 0 | 491.7401 | 0 | 492.4113 | 0
0 | 18.6528 | 0 | 0 | 0 | 0 | 3.5527e-15 | 18.6528 | 1500 | 1065.8733 | 0 | 1065.8733 | 0 | 75.0935 | 0
0 | 18.7441 | 0 | 0 | 0 | 0 | 3.5527e-15 | 18.7441 | 1500 | 1071.0937 | 0 | 1071.0937 | 0 | 15.7987 | 0
0 | 8.5921 | 0 | 0 | 0 | 0 | 1.7764e-15 | 8.5921 | 1500 | 490.9756 | 0 | 490.9756 | 0 | 309.3234 | 0
0 | 16.6611 | 0 | 0 | 0 | 0 | 0 | 16.6611 | 1500 | 952.0629 | 0 | 952.0629 | 286.9496 | 0 | 13.2026
0 | 18.0879 | 0 | 0 | 0 | 0 | 9.9476e-14 | 18.0879 | 1500 | 1033.5948 | 1.7775e-13 | 1033.5948 | 665.8899 | 0 | 34.8926
0 | 21.1043 | 0 | 0 | 0 | 0 | 9.2371e-14 | 21.1043 | 1500 | 1205.9612 | 1.6505e-13 | 1205.9612 | 1097.8127 | 0 | 66.7909
0 | 20.3939 | 0 | 0 | 0 | 0 | -20.3939 | 0 | 1479.6061 | 0 | 0 | 0 | 0 | 16.2223 | 0
0 | 3.9894 | 0 | 0 | 0 | 0 | 20.3939 | 24.3833 | 1500 | 1393.3328 | 36.4412 | 1429.774 | 1429.774 | 0 | 94.0219
0 | 3.907 | 0 | 0 | 0 | 0 | -3.4195e-14 | 3.907 | 1500 | 223.2552 | 0 | 223.2552 | 223.2552 | 0 | 13.2658
0 | 3.0934 | 0 | 0 | 0 | 0 | 2.4425e-14 | 3.0934 | 1500 | 176.7634 | 4.3644e-14 | 176.7634 | 176.7634 | 0 | 9.1493
0 | 4.4748 | 0 | 0 | 0 | 0 | 1.1013e-13 | 4.4748 | 1500 | 255.7035 | 1.968e-13 | 255.7035 | 255.7035 | 0 | 11.8109
0 | 3.8519 | 0 | 0 | 0 | 0 | 6.2172e-15 | 3.8519 | 1500 | 220.1075 | 1.1109e-14 | 220.1075 | 220.1075 | 0 | 9.7728
0 | 3.8562 | 0 | 0 | 0 | 0 | -3.0642e-14 | 3.8562 | 1500 | 220.3571 | 0 | 220.3571 | 220.3571 | 0 | 8.2832
0 | 5.0559 | 0 | 0 | 0 | 0 | -7.3719e-14 | 5.0559 | 1500 | 288.9062 | 0 | 288.9062 | 288.9062 | 0 | 9.5715
0 | 5.4341 | 0 | 0 | 0 | 0 | -3.3751e-14 | 5.4341 | 1500 | 310.5218 | 0 | 310.5218 | 310.5218 | 0 | 9.8466
0 | 4.1842 | 0 | 0 | 0 | 0 | 0 | 4.1842 | 1500 | 239.0979 | 0 | 239.0979 | 239.0979 | 0 | 6.6947
0 | 4.1254 | 0 | 0 | 0 | 0 | 1.3323e-14 | 4.1254 | 1500 | 235.7391 | 2.3806e-14 | 235.7391 | 230.3317 | 0 | 6.3364
0 | 4.0026 | 0 | 0 | 0 | 0 | 3.5527e-14 | 4.0026 | 1500 | 228.7213 | 6.3482e-14 | 228.7213 | 153.0173 | 0 | 4.8308
0 | 3.9947 | 0 | 0 | 0 | 0 | 2.6645e-14 | 3.9947 | 1500 | 228.2676 | 4.7612e-14 | 228.2676 | 114.7116 | 0 | 3.7362
0 | 13.7371 | 0 | 0 | 0 | 0 | 2.6645e-14 | 13.7371 | 1500 | 784.9778 | 4.7612e-14 | 784.9778 | 666.0145 | 0 | 26.7272
0 | 22.1627 | 0 | 0 | 0 | 0 | 0 | 22.1627 | 1500 | 1266.4428 | 0 | 1266.4428 | 1077.1829 | 0 | 53.0082
0 | 14.2985 | 0 | 0 | 0 | 0 | 9.5923e-14 | 14.2985 | 1500 | 817.0574 | 1.714e-13 | 817.0574 | 595.353 | 0 | 28.1364
0 | 25.8827 | 0 | 0 | 0 | 0 | 0 | 25.8827 | 1500 | 1479.009 | 0 | 1479.009 | 1084.267 | 0 | 50.8955
0 | 14.0827 | 0 | 0 | 0 | 0 | 1.6875e-14 | 14.0827 | 1500 | 804.7262 | 3.0154e-14 | 804.7262 | 372.1322 | 0 | 15.5551
0 | 25.5762 | 0 | 0 | 0 | 0 | 9.2371e-14 | 25.5762 | 1500 | 1461.4998 | 1.6505e-13 | 1461.4998 | 991.0538 | 0 | 40.7026
0 | 30.9227 | 0 | 0 | 0 | 0 | 4.2633e-14 | 30.9227 | 1500 | 1767.009 | 7.6179e-14 | 1767.009 | 1383.0818 | 0 | 54.037
0 | 27.1833 | 0 | 0 | 0 | 0 | 9.9476e-14 | 27.1833 | 1500 | 1553.3333 | 1.7775e-13 | 1553.3333 | 1320.814 | 0 | 51.5646
0 | 11.7454 | 0 | 0 | 0 | 0 | 2.6645e-14 | 11.7454 | 1500 | 671.1649 | 4.7612e-14 | 671.1649 | 541.3867 | 0 | 21.7096
0 | 7.0257 | 0 | 0 | 0 | 0 | 0 | 7.0257 | 1500 | 401.4714 | 0 | 401.4714 | 309.5452 | 0 | 14.4465
0 | 18.9468 | 0 | 0 | 0 | 0 | 0 | 18.9468 | 1500 | 1082.6721 | 2.5393e-14 | 1082.6721 | 979.931 | 0 | 48.4576
0 | 16.0184 | 0 | 0 | 0 | 0 | 6.7502e-14 | 16.0184 | 1500 | 915.3395 | 1.2062e-13 | 915.3395 | 877.4875 | 0 | 44.5413
0 | 4.1681 | 0 | 0 | 0 | 0 | 3.2863e-14 | 4.1681 | 1500 | 238.1782 | 5.8721e-14 | 238.1782 | 238.1782 | 0 | 12.6115
0 | 5.0408 | 0 | 0 | 0 | 0 | -9.0594e-14 | 5.0408 | 1500 | 288.0436 | 0 | 288.0436 | 288.0436 | 0 | 15.8424
0 | 4.9699 | 0 | 0 | 0 | 0 | 9.5923e-14 | 4.9699 | 1500 | 283.9954 | 1.714e-13 | 283.9954 | 283.9954 | 0 | 16.3354
0 | 3.1474 | 0 | 0 | 0 | 0 | -4.3521e-14 | 3.1474 | 1500 | 179.8521 | 0 | 179.8521 | 179.8521 | 0 | 8.8829
0 | 4.4642 | 0 | 0 | 0 | 0 | 0 | 4.4642 | 1500 | 255.0945 | 0 | 255.0945 | 255.0945 | 0 | 12.0634
0 | 3.2772 | 0 | 0 | 0 | 0 | 1.3323e-14 | 3.2772 | 1500 | 187.2659 | 2.3806e-14 | 187.2659 | 187.2659 | 0 | 8.6386
0 | 3.4809 | 0 | 0 | 0 | 0 | -1.0525e-13 | 3.4809 | 1500 | 198.9105 | 0 | 198.9105 | 198.9105 | 0 | 9.1698
0 | 3.8764 | 0 | 0 | 0 | 0 | -1.1147e-13 | 3.8764 | 1500 | 221.5061 | 0 | 221.5061 | 221.5061 | 0 | 11.0354
0 | 204.4257 | 0 | 0 | 0 | 0 | -151.9257 | 52.5 | 1348.0743 | 3000 | 0 | 3000 | 3000 | 0 | 134.7
0 | 3.0976 | 0 | 0 | 0 | 0 | 49.4024 | 52.5 | 1397.4767 | 3000 | 88.2755 | 3088.2755 | 3082.8681 | 0 | 136.941
0 | 2.9315 | 0 | 0 | 0 | 0 | 49.5685 | 52.5 | 1447.0453 | 3000 | 88.5724 | 3088.5724 | 3029.0907 | 0 | 143.6092
0 | 3.9784 | 0 | 0 | 0 | 0 | 48.5216 | 52.5 | 1495.5668 | 3000 | 86.7016 | 3086.7016 | 2962.3308 | 0 | 147.4648
0 | 18.9681 | 0 | 0 | 0 | 0 | 4.4332 | 23.4012 | 1500 | 1337.214 | 7.9215 | 1345.1354 | 1085.579 | 0 | 53.5299
0 | 22.5137 | 0 | 0 | 0 | 0 | -1.1369e-13 | 22.5137 | 1500 | 1286.496 | 0 | 1286.496 | 978.2727 | 0 | 47.1234
0 | 15.5397 | 0 | 0 | 0 | 0 | 1.5987e-14 | 15.5397 | 1500 | 887.9801 | 2.8567e-14 | 887.9801 | 482.4232 | 0 | 23.5423
0 | 17.3896 | 0 | 0 | 0 | 0 | 4.4409e-14 | 17.3896 | 1500 | 993.6921 | 7.9353e-14 | 993.6921 | 577.3204 | 0 | 28.1444
0 | 21.3542 | 0 | 0 | 0 | 0 | -6.7502e-14 | 21.3542 | 1500 | 1220.2381 | 0 | 1220.2381 | 636.2362 | 0 | 28.7833
0 | 10.8829 | 0 | 0 | 0 | 0 | 9.9476e-14 | 10.8829 | 1500 | 621.8795 | 1.7775e-13 | 621.8795 | 5.433 | 0 | 0.22982
0 | 12.0771 | 0 | 0 | 0 | 0 | 8.8818e-15 | 12.0771 | 1500 | 690.1203 | 1.5871e-14 | 690.1203 | 230.4892 | 0 | 8.5604
0 | 23.9516 | 0 | 0 | 0 | 0 | -1.0125e-13 | 23.9516 | 1500 | 1368.6649 | 0 | 1368.6649 | 849.5521 | 0 | 24.5266
0 | 15.5913 | 0 | 0 | 0 | 0 | -1.954e-14 | 15.5913 | 1500 | 890.9314 | 0 | 890.9314 | 333.9666 | 0 | 11.1044
0 | 15.2265 | 0 | 0 | 0 | 0 | 8.5265e-14 | 15.2265 | 1500 | 870.0837 | 1.5236e-13 | 870.0837 | 459.1194 | 0 | 22.1433
0 | 24.1894 | 0 | 0 | 0 | 0 | -9.9476e-14 | 24.1894 | 1500 | 1382.2542 | 0 | 1382.2542 | 1122.6978 | 0 | 57.0555
0 | 7.4355 | 0 | 0 | 0 | 0 | -2.2204e-14 | 7.4355 | 1500 | 424.8843 | 0 | 424.8843 | 392.4397 | 0 | 20.7169
0 | 3.7767 | 0 | 0 | 0 | 0 | 3.0642e-14 | 3.7767 | 1500 | 215.8126 | 5.4753e-14 | 215.8126 | 215.8126 | 0 | 11.9064
0 | 2.9982 | 0 | 0 | 0 | 0 | -1.1102e-13 | 2.9982 | 1500 | 171.3273 | 0 | 171.3273 | 171.3273 | 0 | 9.1968
0 | 3.9276 | 0 | 0 | 0 | 0 | 5.107e-14 | 3.9276 | 1500 | 224.4328 | 9.1256e-14 | 224.4328 | 224.4328 | 0 | 11.6638
0 | 3.7609 | 0 | 0 | 0 | 0 | 6.5281e-14 | 3.7609 | 1500 | 214.91 | 1.1665e-13 | 214.91 | 214.91 | 0 | 10.4898
0 | 3.9346 | 0 | 0 | 0 | 0 | 6.4837e-14 | 3.9346 | 1500 | 224.8321 | 1.1586e-13 | 224.8321 | 224.8321 | 0 | 9.8117
0 | 4.2358 | 0 | 0 | 0 | 0 | -1.128e-13 | 4.2358 | 1500 | 242.047 | 0 | 242.047 | 242.047 | 0 | 10.2749
0 | 4.1914 | 0 | 0 | 0 | 0 | 0 | 4.1914 | 1500 | 239.5108 | 1.1109e-14 | 239.5108 | 239.5108 | 0 | 9.8199
0 | 4.2477 | 0 | 0 | 0 | 0 | 2.8422e-14 | 4.2477 | 1500 | 242.7281 | 5.0786e-14 | 242.7281 | 242.7281 | 0 | 9.9009
0 | 3.4398 | 0 | 0 | 0 | 0 | -1.5543e-14 | 3.4398 | 1500 | 196.5615 | 0 | 196.5615 | 196.5615 | 0 | 8.2674
0 | 5.1438 | 0 | 0 | 0 | 0 | -3.4639e-14 | 5.1438 | 1500 | 293.9294 | 0 | 293.9294 | 272.2997 | 0 | 11.7361
0 | 4.1831 | 0 | 0 | 0 | 0 | -9.3259e-14 | 4.1831 | 1500 | 239.0318 | 0 | 239.0318 | 44.3645 | 0 | 2.1007
0 | 4.3158 | 0 | 0 | 0 | 0 | 0 | 4.3158 | 1500 | 246.6153 | 0 | 246.6153 | 0 | 229.2381 | 0
0 | 9.9836 | 0 | 0 | 0 | 0 | 1.7764e-15 | 9.9836 | 1500 | 570.4933 | 0 | 570.4933 | 0 | 213.5834 | 0
0 | 19.1538 | 0 | 0 | 0 | 0 | -1.0658e-13 | 19.1538 | 1500 | 1094.5049 | 0 | 1094.5049 | 94.1312 | 0 | 4.8929
0 | 15.017 | 0 | 0 | 0 | 0 | 1.7764e-15 | 15.017 | 1500 | 858.1127 | 0 | 858.1127 | 0 | 61.1496 | 0
0 | 25.2072 | 0 | 0 | 0 | 0 | -3.5527e-14 | 25.2072 | 1500 | 1440.4093 | 0 | 1440.4093 | 169.6644 | 0 | 7.9844
0 | 16.9886 | 0 | 0 | 0 | 0 | 3.5527e-14 | 16.9886 | 1500 | 970.775 | 6.3482e-14 | 970.775 | 240.7726 | 0 | 10.8107
0 | 23.5468 | 0 | 0 | 0 | 0 | 1.0125e-13 | 23.5468 | 1500 | 1345.5325 | 1.8092e-13 | 1345.5325 | 664.197 | 0 | 28.494
0 | 22.1101 | 0 | 0 | 0 | 0 | -1.4211e-14 | 22.1101 | 1500 | 1263.4354 | 0 | 1263.4354 | 371.2102 | 0 | 15.8878
0 | 19.5768 | 0 | 0 | 0 | 0 | -6.0396e-14 | 19.5768 | 1500 | 1118.6723 | 0 | 1118.6723 | 37.1873 | 0 | 1.589
0 | 10.1273 | 0 | 0 | 0 | 0 | 0 | 10.1273 | 1500 | 578.7013 | 0 | 578.7013 | 0 | 53.9674 | 0
0 | 8.082 | 0 | 0 | 0 | 0 | 1.7764e-15 | 8.082 | 1500 | 461.8298 | 0 | 461.8298 | 0 | 41.0608 | 0
0 | 18.3391 | 0 | 0 | 0 | 0 | -6.0396e-14 | 18.3391 | 1500 | 1047.9511 | 0 | 1047.9511 | 945.21 | 0 | 50.0961
0 | 207.9549 | 0 | 0 | 0 | 0 | -155.4549 | 52.5 | 1344.5451 | 3000 | 0 | 3000 | 2951.3332 | 0 | 174.0106
0 | 5.2842 | 0 | 0 | 0 | 0 | 47.2158 | 52.5 | 1391.7609 | 3000 | 84.3684 | 3084.3684 | 3084.3684 | 0 | 202.643
0 | 3.7637 | 0 | 0 | 0 | 0 | 48.7363 | 52.5 | 1440.4973 | 3000 | 87.0853 | 3087.0853 | 3087.0853 | 0 | 190.8127
0 | 4.712 | 0 | 0 | 0 | 0 | 47.788 | 52.5 | 1488.2853 | 3000 | 85.3908 | 3085.3908 | 3085.3908 | 0 | 171.2392
0 | 4.6349 | 0 | 0 | 0 | 0 | 11.7147 | 16.3496 | 1500 | 934.2646 | 20.9327 | 955.1973 | 955.1973 | 0 | 47.6834
0 | 4.1212 | 0 | 0 | 0 | 0 | -2.4869e-14 | 4.1212 | 1500 | 235.4976 | 0 | 235.4976 | 235.4976 | 0 | 10.9224
0 | 3.3583 | 0 | 0 | 0 | 0 | -3.0198e-14 | 3.3583 | 1500 | 191.9056 | 0 | 191.9056 | 191.9056 | 0 | 8.5859
0 | 4.1581 | 0 | 0 | 0 | 0 | 5.1514e-14 | 4.1581 | 1500 | 237.6063 | 9.2049e-14 | 237.6063 | 237.6063 | 0 | 10.5497
0 | 4.5925 | 0 | 0 | 0 | 0 | -4.3521e-14 | 4.5925 | 1500 | 262.4297 | 0 | 262.4297 | 262.4297 | 0 | 11.3658
0 | 4.0695 | 0 | 0 | 0 | 0 | -7.4607e-14 | 4.0695 | 1500 | 232.5451 | 0 | 232.5451 | 232.5451 | 0 | 10.3483
0 | 3.9075 | 0 | 0 | 0 | 0 | 1.0214e-13 | 3.9075 | 1500 | 223.2879 | 1.8251e-13 | 223.2879 | 207.0656 | 0 | 9.6803
0 | 3.1963 | 0 | 0 | 0 | 0 | -6.2172e-15 | 3.1963 | 1500 | 182.6456 | 0 | 182.6456 | 0 | 1.2068 | 0
0 | 4.9293 | 0 | 0 | 0 | 0 | 8.8818e-16 | 4.9293 | 1500 | 281.6756 | 0 | 281.6756 | 0 | 177.9555 | 0
0 | 29.7173 | 0 | 0 | 0 | 0 | 0 | 29.7173 | 1500 | 1698.1287 | 0 | 1698.1287 | 995.1635 | 0 | 62.2276
0 | 19.3037 | 0 | 0 | 0 | 0 | -3.1974e-14 | 19.3037 | 1500 | 1103.0689 | 0 | 1103.0689 | 172.9918 | 0 | 10.3328
0 | 16.6762 | 0 | 0 | 0 | 0 | 0 | 16.6762 | 1500 | 952.9282 | 0 | 952.9282 | 0 | 193.4459 | 0
0 | 28.2417 | 0 | 0 | 0 | 0 | -5.3291e-14 | 28.2417 | 1500 | 1613.8097 | 0 | 1613.8097 | 305.2128 | 0 | 16.454
0 | 19.1156 | 0 | 0 | 0 | 0 | 4.4409e-14 | 19.1156 | 1500 | 1092.3207 | 7.9353e-14 | 1092.3207 | 416.3925 | 0 | 22.0397
0 | 9.6099 | 0 | 0 | 0 | 0 | 1.7764e-15 | 9.6099 | 1500 | 549.1366 | 0 | 549.1366 | 0 | 94.347 | 0
0 | 15.0847 | 0 | 0 | 0 | 0 | 1.7764e-15 | 15.0847 | 1500 | 861.9847 | 0 | 861.9847 | 0 | 316.834 | 0
0 | 16.3715 | 0 | 0 | 0 | 0 | 6.7502e-14 | 16.3715 | 1500 | 935.5151 | 1.2062e-13 | 935.5151 | 16.2528 | 0 | 0.86107
0 | 20.0907 | 0 | 0 | 0 | 0 | -1.1013e-13 | 20.0907 | 1500 | 1148.0394 | 0 | 1148.0394 | 720.8528 | 0 | 37.8592
0 | 14.0349 | 0 | 0 | 0 | 0 | 8.8818e-14 | 14.0349 | 1500 | 801.9956 | 1.5871e-13 | 801.9956 | 472.1426 | 0 | 27.9084
0 | 13.3501 | 0 | 0 | 0 | 0 | -1.0658e-13 | 13.3501 | 1500 | 762.8607 | 0 | 762.8607 | 595.2305 | 0 | 38.2971
0 | 6.61 | 0 | 0 | 0 | 0 | -7.0166e-14 | 6.61 | 1500 | 377.7168 | 0 | 377.7168 | 334.4574 | 0 | 22.7431
0 | 4.009 | 0 | 0 | 0 | 0 | 9.1482e-14 | 4.009 | 1500 | 229.0859 | 1.6347e-13 | 229.0859 | 229.0859 | 0 | 15.6443
0 | 4.1591 | 0 | 0 | 0 | 0 | -1.0392e-13 | 4.1591 | 1500 | 237.6628 | 0 | 237.6628 | 237.6628 | 0 | 15.0559
0 | 4.3408 | 0 | 0 | 0 | 0 | 1.0747e-13 | 4.3408 | 1500 | 248.0449 | 1.9203e-13 | 248.0449 | 248.0449 | 0 | 13.7938
0 | 2.8921 | 0 | 0 | 0 | 0 | 1.0658e-13 | 2.8921 | 1500 | 165.2635 | 1.9045e-13 | 165.2635 | 165.2635 | 0 | 8.4037
0 | 4.8388 | 0 | 0 | 0 | 0 | -8.6153e-14 | 4.8388 | 1500 | 276.5004 | 0 | 276.5004 | 276.5004 | 0 | 13.2914
0 | 120.2373 | 0 | 0 | 0 | 0 | -67.7373 | 52.5 | 1432.2627 | 3000 | 0 | 3000 | 3000 | 0 | 143.88
0 | 118.2414 | 0 | 0 | 0 | 0 | -65.7414 | 52.5 | 1366.5212 | 3000 | 0 | 3000 | 3000 | 0 | 140.52
0 | 100.8689 | 0 | 0 | 0 | 0 | -48.3689 | 52.5 | 1318.1524 | 3000 | 0 | 3000 | 3000 | 0 | 137.4
0 | 273.803 | 0 | 0 | 0 | 0 | -221.303 | 52.5 | 1096.8493 | 3000 | 0 | 3000 | 3000 | 0 | 139.59
0 | 141.5506 | 0 | 0 | 0 | 0 | -89.0506 | 52.5 | 1007.7987 | 3000 | 0 | 3000 | 2983.7777 | 0 | 136.1498
0 | 178.0654 | 0 | 0 | 0 | 0 | -125.5654 | 52.5 | 882.2333 | 3000 | 0 | 3000 | 2821.555 | 0 | 159.1921
0 | 123.8866 | 0 | 0 | 0 | 0 | -115.9377 | 7.9489 | 766.2956 | 454.2237 | 0 | 454.2237 | 0 | 0 | 0
0 | 119.2142 | 0 | 0 | 0 | 0 | -105.966 | 13.2482 | 660.3296 | 757.0395 | 0 | 757.0395 | 0 | 0 | 0
0 | 144.3667 | 0 | 0 | 0 | 0 | -91.8667 | 52.5 | 568.4628 | 3000 | 0 | 3000 | 2010.4412 | 0 | 114.4946
0 | 152.4359 | 0 | 0 | 0 | 0 | -99.9359 | 52.5 | 468.5269 | 3000 | 0 | 3000 | 1794.1442 | 0 | 95.0896
0 | 207.7419 | 0 | 0 | 0 | 0 | -155.2419 | 52.5 | 313.285 | 3000 | 0 | 3000 | 1539.9952 | 0 | 80.0335
0 | 176.3972 | 0 | 0 | 0 | 0 | -123.8972 | 52.5 | 189.3878 | 3000 | 0 | 3000 | 1615.6991 | 0 | 81.9483
0 | 127.9979 | 0 | 0 | 0 | 0 | -75.4979 | 52.5 | 113.8899 | 3000 | 0 | 3000 | 1810.3664 | 0 | 88.7985
0 | 123.1464 | 0 | 0 | 0 | 0 | -70.6464 | 52.5 | 43.2435 | 3000 | 0 | 3000 | 1783.3293 | 0 | 85.903
0 | 95.7435 | 0 | 0 | 0 | 0 | -43.2435 | 52.5 | 0 | 3000 | 0 | 3000 | 2448.4426 | 0 | 117.5008
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2610.6654 | 0 | 131.682
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2561.9986 | 0 | 141.2686
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2816.1475 | 0 | 180.9656
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 43.2594 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 201.63
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 178.74
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 158.82
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 144.78
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 140.61
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 135.12
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 134.37
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 128.73
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2978.3703 | 0 | 130.7802
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2789.1104 | 0 | 142.0773
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2545.7763 | 0 | 142.869
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2242.9605 | 0 | 124.7983
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2010.4412 | 0 | 106.3523
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1831.9962 | 0 | 91.4349
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1669.7734 | 0 | 80.1658
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1567.0323 | 0 | 73.6662
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1615.6991 | 0 | 73.5628
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1756.2922 | 0 | 81.1583
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1950.9595 | 0 | 90.0173
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2194.2936 | 0 | 103.0001
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2529.554 | 0 | 131.5115
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2789.1104 | 0 | 160.2902
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2972.9629 | 0 | 206.9182
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 198.21
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 181.2
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 160.44
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 146.85
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 135.84
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 135.24
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 134.37
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 133.86
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 135
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2978.3703 | 0 | 139.9834
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2837.7772 | 0 | 154.5737
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2529.554 | 0 | 147.726
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2264.5902 | 0 | 126.2509
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2053.7006 | 0 | 106.1352
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1902.2927 | 0 | 94.7342
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1680.5882 | 0 | 82.5673
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1669.7734 | 0 | 78.3959
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1734.6625 | 0 | 80.1934
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1896.8853 | 0 | 86.8963
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1945.5521 | 0 | 90.6044
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2264.5902 | 0 | 107.0698
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2545.7763 | 0 | 139.4322
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2783.703 | 0 | 173.7031
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.4446 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 179.49
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 155.91
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 149.04
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 147.21
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 140.58
0 | 26.7862 | 0 | 0 | 0 | 0 | 25.7138 | 52.5 | 25.7138 | 3000 | 45.9471 | 3045.9471 | 3045.9471 | 0 | 139.6871
0 | 28.083 | 0 | 0 | 0 | 0 | 24.417 | 52.5 | 50.1308 | 3000 | 43.63 | 3043.63 | 3043.63 | 0 | 139.4591
0 | 36.9304 | 0 | 0 | 0 | 0 | 15.5696 | 52.5 | 65.7004 | 3000 | 27.8208 | 3027.8208 | 3027.8208 | 0 | 136.3428
0 | 38.5015 | 0 | 0 | 0 | 0 | 13.9985 | 52.5 | 79.6989 | 3000 | 25.0135 | 3025.0135 | 3014.1986 | 0 | 136.3925
0 | 69.4247 | 0 | 0 | 0 | 0 | -16.9247 | 52.5 | 62.7742 | 3000 | 0 | 3000 | 2843.1847 | 0 | 135.8758
0 | 77.8533 | 0 | 0 | 0 | 0 | -25.3533 | 52.5 | 37.4209 | 3000 | 0 | 3000 | 2556.5911 | 0 | 125.1707
0 | 89.9209 | 0 | 0 | 0 | 0 | -37.4209 | 52.5 | 0 | 3000 | 0 | 3000 | 2253.7753 | 0 | 114.8299
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2010.4412 | 0 | 101.0247
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1799.5516 | 0 | 80.098
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1615.6991 | 0 | 68.6672
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1539.9952 | 0 | 64.418
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1599.4769 | 0 | 66.9221
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1745.4773 | 0 | 73.3275
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1950.9595 | 0 | 83.9498
0 | 50.7053 | 0 | 0 | 0 | 0 | 1.7947 | 52.5 | 1.7947 | 3000 | 3.2069 | 3003.2069 | 2202.9079 | 0 | 94.7911
0 | 44.6871 | 0 | 0 | 0 | 0 | 7.8129 | 52.5 | 9.6076 | 3000 | 13.9606 | 3013.9606 | 2505.6626 | 0 | 120.9984
0 | 37.9704 | 0 | 0 | 0 | 0 | 14.5296 | 52.5 | 24.1372 | 3000 | 25.9625 | 3025.9625 | 2815.073 | 0 | 146.1867
0 | 49.1774 | 0 | 0 | 0 | 0 | 3.3226 | 52.5 | 27.4599 | 3000 | 5.9371 | 3005.9371 | 2984.3074 | 0 | 171.2694
0 | 30.9011 | 0 | 0 | 0 | 0 | 21.5989 | 52.5 | 49.0587 | 3000 | 38.5943 | 3038.5943 | 3038.5943 | 0 | 163.3244
0 | 25.2941 | 0 | 0 | 0 | 0 | 27.2059 | 52.5 | 76.2647 | 3000 | 48.6134 | 3048.6134 | 3048.6134 | 0 | 156.3634
0 | 25.7738 | 0 | 0 | 0 | 0 | 26.7262 | 52.5 | 102.9909 | 3000 | 47.7562 | 3047.7562 | 3047.7562 | 0 | 152.2354
0 | 33.1687 | 0 | 0 | 0 | 0 | 19.3313 | 52.5 | 122.3221 | 3000 | 34.5424 | 3034.5424 | 3034.5424 | 0 | 141.6221
0 | 21.0229 | 0 | 0 | 0 | 0 | 31.4771 | 52.5 | 153.7993 | 3000 | 56.2455 | 3056.2455 | 3056.2455 | 0 | 134.7193
0 | 38.6784 | 0 | 0 | 0 | 0 | 13.8216 | 52.5 | 167.6209 | 3000 | 24.6974 | 3024.6974 | 3024.6974 | 0 | 132.028
0 | 31.8176 | 0 | 0 | 0 | 0 | 20.6824 | 52.5 | 188.3033 | 3000 | 36.9568 | 3036.9568 | 3036.9568 | 0 | 132.715
0 | 23.0724 | 0 | 0 | 0 | 0 | 29.4276 | 52.5 | 217.731 | 3000 | 52.5832 | 3052.5832 | 3052.5832 | 0 | 132.7568
0 | 33.267 | 0 | 0 | 0 | 0 | 19.233 | 52.5 | 236.964 | 3000 | 34.3669 | 3034.3669 | 3034.3669 | 0 | 132.6018
0 | 33.2362 | 0 | 0 | 0 | 0 | 19.2638 | 52.5 | 256.2278 | 3000 | 34.4218 | 3034.4218 | 3023.607 | 0 | 130.1058
0 | 29.5515 | 0 | 0 | 0 | 0 | 22.9485 | 52.5 | 279.1763 | 3000 | 41.0059 | 3041.0059 | 2889.598 | 0 | 125.0618
0 | 29.6809 | 0 | 0 | 0 | 0 | 22.8191 | 52.5 | 301.9953 | 3000 | 40.7747 | 3040.7747 | 2597.3658 | 0 | 121.1411
0 | 40.9017 | 0 | 0 | 0 | 0 | 11.5983 | 52.5 | 313.5937 | 3000 | 20.7246 | 3020.7246 | 2279.9074 | 0 | 105.1265
0 | 50.6598 | 0 | 0 | 0 | 0 | 1.8402 | 52.5 | 315.4338 | 3000 | 3.2882 | 3003.2882 | 2035.359 | 0 | 94.6035
0 | 50.2528 | 0 | 0 | 0 | 0 | 2.2472 | 52.5 | 317.681 | 3000 | 4.0154 | 3004.0154 | 1846.8264 | 0 | 75.5167
0 | 41.1979 | 0 | 0 | 0 | 0 | 11.3021 | 52.5 | 328.9831 | 3000 | 20.1953 | 3020.1953 | 1684.5613 | 0 | 68.8649
0 | 48.6069 | 0 | 0 | 0 | 0 | 3.8931 | 52.5 | 332.8762 | 3000 | 6.9565 | 3006.9565 | 1579.3963 | 0 | 64.4867
0 | 58.1659 | 0 | 0 | 0 | 0 | -5.6659 | 52.5 | 327.2103 | 3000 | 0 | 3000 | 1621.1066 | 0 | 64.8929
0 | 49.2101 | 0 | 0 | 0 | 0 | 3.2899 | 52.5 | 330.5002 | 3000 | 5.8785 | 3005.8785 | 1772.9856 | 0 | 70.9372
0 | 40.2125 | 0 | 0 | 0 | 0 | 12.2875 | 52.5 | 342.7877 | 3000 | 21.9561 | 3021.9561 | 1978.3231 | 0 | 79.9045
0 | 38.5794 | 0 | 0 | 0 | 0 | 13.9206 | 52.5 | 356.7083 | 3000 | 24.8743 | 3024.8743 | 2262.4273 | 0 | 93.6645
0 | 41.1354 | 0 | 0 | 0 | 0 | 11.3646 | 52.5 | 368.0729 | 3000 | 20.307 | 3020.307 | 2544.4535 | 0 | 119.5384
0 | 23.7685 | 0 | 0 | 0 | 0 | 28.7315 | 52.5 | 396.8043 | 3000 | 51.3393 | 3051.3393 | 2851.2646 | 0 | 159.2431
0 | 35.7989 | 0 | 0 | 0 | 0 | 16.7011 | 52.5 | 413.5054 | 3000 | 29.8426 | 3029.8426 | 3008.2129 | 0 | 184.4335
0 | 22.7759 | 0 | 0 | 0 | 0 | 29.7241 | 52.5 | 443.2295 | 3000 | 53.113 | 3053.113 | 3053.113 | 0 | 187.5833
0 | 23.9717 | 0 | 0 | 0 | 0 | 28.5283 | 52.5 | 471.7578 | 3000 | 50.9763 | 3050.9763 | 3050.9763 | 0 | 177.1092
0 | 27.3339 | 0 | 0 | 0 | 0 | 25.1661 | 52.5 | 496.924 | 3000 | 44.9685 | 3044.9685 | 3044.9685 | 0 | 159.8304
0 | 29.5632 | 0 | 0 | 0 | 0 | 22.9368 | 52.5 | 519.8608 | 3000 | 40.9851 | 3040.9851 | 3040.9851 | 0 | 150.5896
0 | 28.3918 | 0 | 0 | 0 | 0 | 24.1082 | 52.5 | 543.969 | 3000 | 43.0781 | 3043.0781 | 3043.0781 | 0 | 148.1066
0 | 31.8252 | 0 | 0 | 0 | 0 | 20.6748 | 52.5 | 564.6438 | 3000 | 36.9431 | 3036.9431 | 3036.9431 | 0 | 145.6214
0 | 21.0581 | 0 | 0 | 0 | 0 | 31.4419 | 52.5 | 596.0857 | 3000 | 56.1824 | 3056.1824 | 3056.1824 | 0 | 143.8239
0 | 22.2769 | 0 | 0 | 0 | 0 | 30.2231 | 52.5 | 626.3087 | 3000 | 54.0046 | 3054.0046 | 3054.0046 | 0 | 143.1107
0 | 27.24 | 0 | 0 | 0 | 0 | 25.26 | 52.5 | 651.5687 | 3000 | 45.1363 | 3045.1363 | 3045.1363 | 0 | 143.4259
0 | 32.8566 | 0 | 0 | 0 | 0 | 19.6434 | 52.5 | 671.2121 | 3000 | 35.1001 | 3035.1001 | 3024.2853 | 0 | 144.1072
0 | 29.557 | 0 | 0 | 0 | 0 | 22.943 | 52.5 | 694.1551 | 3000 | 40.9961 | 3040.9961 | 2922.0327 | 0 | 186.7471
0 | 32.0684 | 0 | 0 | 0 | 0 | -25.6335 | 6.4348 | 668.5216 | 367.7049 | 0 | 367.7049 | 0 | 0 | 0
0 | 43.1828 | 0 | 0 | 0 | 0 | -31.7326 | 11.4502 | 636.789 | 654.2985 | 0 | 654.2985 | 0 | 0 | 0
0 | 39.3849 | 0 | 0 | 0 | 0 | 13.1151 | 52.5 | 649.9041 | 3000 | 23.4349 | 3023.4349 | 2142.0246 | 0 | 136.9611
0 | 54.4761 | 0 | 0 | 0 | 0 | -1.9761 | 52.5 | 647.928 | 3000 | 0 | 3000 | 1913.1075 | 0 | 116.1256
0 | 31.1111 | 0 | 0 | 0 | 0 | 21.3889 | 52.5 | 669.3168 | 3000 | 38.2191 | 3038.2191 | 1778.289 | 0 | 104.4567
0 | 54.4369 | 0 | 0 | 0 | 0 | -1.9369 | 52.5 | 667.38 | 3000 | 0 | 3000 | 1675.1808 | 0 | 93.6594
0 | 49.8491 | 0 | 0 | 0 | 0 | 2.6509 | 52.5 | 670.0308 | 3000 | 4.7367 | 3004.7367 | 1717.7695 | 0 | 92.6908
0 | 43.3915 | 0 | 0 | 0 | 0 | 9.1085 | 52.5 | 679.1393 | 3000 | 16.2757 | 3016.2757 | 1875.309 | 0 | 99.8602
0 | 39.9871 | 0 | 0 | 0 | 0 | 12.5129 | 52.5 | 691.6523 | 3000 | 22.3589 | 3022.3589 | 2065.2447 | 0 | 110.2634
0 | 43.7169 | 0 | 0 | 0 | 0 | 8.7831 | 52.5 | 700.4354 | 3000 | 15.6942 | 3015.6942 | 2318.1364 | 0 | 135.5183
0 | 38.7969 | 0 | 0 | 0 | 0 | 13.7031 | 52.5 | 714.1385 | 3000 | 24.4856 | 3024.4856 | 2613.5213 | 0 | 176.0991
0 | 34.8099 | 0 | 0 | 0 | 0 | -34.8099 | 0 | 679.3285 | 0 | 0 | 0 | 0 | 167.6302 | 0
0 | 45.8633 | 0 | 0 | 0 | 0 | -45.8633 | 0 | 633.4653 | 0 | 0 | 0 | 0 | 16.2223 | 0
0 | 25.5981 | 0 | 0 | 0 | 0 | -25.5981 | 0 | 607.8672 | 0 | 0 | 0 | 0 | 0 | 0
0 | 31.6064 | 0 | 0 | 0 | 0 | -31.6064 | 0 | 576.2608 | 0 | 0 | 0 | 0 | 0 | 0
0 | 30.4714 | 0 | 0 | 0 | 0 | 22.0286 | 52.5 | 598.2894 | 3000 | 39.3622 | 3039.3622 | 3039.3622 | 0 | 191.0847
0 | 27.6507 | 0 | 0 | 0 | 0 | 24.8493 | 52.5 | 623.1387 | 3000 | 44.4024 | 3044.4024 | 3044.4024 | 0 | 165.7373
0 | 229.4414 | 0 | 0 | 0 | 0 | -176.9414 | 52.5 | 446.1973 | 3000 | 0 | 3000 | 3000 | 0 | 159.99
0 | 31.124 | 0 | 0 | 0 | 0 | 21.376 | 52.5 | 467.5733 | 3000 | 38.1962 | 3038.1962 | 3038.1962 | 0 | 152.6997
0 | 28.1178 | 0 | 0 | 0 | 0 | 24.3822 | 52.5 | 491.9555 | 3000 | 43.5677 | 3043.5677 | 3043.5677 | 0 | 151.5392
0 | 66.2924 | 0 | 0 | 0 | 0 | -13.7924 | 52.5 | 478.1631 | 3000 | 0 | 3000 | 3000 | 0 | 148.5
0 | 146.3412 | 0 | 0 | 0 | 0 | -93.8412 | 52.5 | 384.3219 | 3000 | 0 | 3000 | 3000 | 0 | 149.13
0 | 126.5709 | 0 | 0 | 0 | 0 | -74.0709 | 52.5 | 310.251 | 3000 | 0 | 3000 | 2989.1851 | 0 | 151.6713
0 | 88.1216 | 0 | 0 | 0 | 0 | -35.6216 | 52.5 | 274.6294 | 3000 | 0 | 3000 | 2875.6292 | 0 | 171.8188
0 | 97.0856 | 0 | 0 | 0 | 0 | -90.1777 | 6.908 | 184.4518 | 394.742 | 0 | 394.742 | 0 | 0 | 0
0 | 77.819 | 0 | 0 | 0 | 0 | -25.319 | 52.5 | 159.1327 | 3000 | 0 | 3000 | 2313.257 | 0 | 158.8976
0 | 93.8614 | 0 | 0 | 0 | 0 | -41.3614 | 52.5 | 117.7713 | 3000 | 0 | 3000 | 2069.9229 | 0 | 141.8518
0 | 98.3364 | 0 | 0 | 0 | 0 | -45.8364 | 52.5 | 71.9349 | 3000 | 0 | 3000 | 1875.2556 | 0 | 123.6731
0 | 124.4349 | 0 | 0 | 0 | 0 | -71.9349 | 52.5 | 0 | 3000 | 0 | 3000 | 1707.6254 | 0 | 108.9807
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1653.5511 | 0 | 99.4611
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1729.2551 | 0 | 103.6343
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1810.3664 | 0 | 108.7306
0 | 42.1872 | 0 | 0 | 0 | 0 | 10.3128 | 52.5 | 10.3128 | 3000 | 18.4275 | 3018.4275 | 2126.2024 | 0 | 127.806
0 | 32.2698 | 0 | 0 | 0 | 0 | 20.2302 | 52.5 | 30.543 | 3000 | 36.1487 | 3036.1487 | 2316.9612 | 0 | 146.1539
0 | 45.2748 | 0 | 0 | 0 | 0 | 7.2252 | 52.5 | 37.7682 | 3000 | 12.9104 | 3012.9104 | 2601.9461 | 0 | 172.3009
0 | 36.6454 | 0 | 0 | 0 | 0 | -36.6454 | 0 | 1.1227 | 0 | 0 | 0 | 0 | 81.1114 | 0
0 | 1.1227 | 0 | 0 | 0 | 0 | -1.1227 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8149 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 47.2518 | 0 | 0 | 0 | 0 | 5.2482 | 52.5 | 5.2482 | 3000 | 9.3779 | 3009.3779 | 3009.3779 | 0 | 199.2208
0 | 57.7482 | 0 | 0 | 0 | 0 | -5.2482 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 183.54
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 157.47
0 | 46.8058 | 0 | 0 | 0 | 0 | 5.6942 | 52.5 | 5.6942 | 3000 | 10.1748 | 3010.1748 | 3010.1748 | 0 | 159.7801
0 | 58.1942 | 0 | 0 | 0 | 0 | -5.6942 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 151.65
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 149.76
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 148.98
0 | 48.8643 | 0 | 0 | 0 | 0 | 3.6357 | 52.5 | 3.6357 | 3000 | 6.4965 | 3006.4965 | 3006.4965 | 0 | 147.5588
0 | 42.0469 | 0 | 0 | 0 | 0 | 10.4531 | 52.5 | 14.0888 | 3000 | 18.6784 | 3018.6784 | 3013.271 | 0 | 151.6579
0 | 66.5888 | 0 | 0 | 0 | 0 | -14.0888 | 52.5 | 0 | 3000 | 0 | 3000 | 2924.296 | 0 | 183.5288
0 | 6.4348 | 0 | 0 | 0 | 0 | 0 | 6.4348 | 0 | 367.7049 | 0 | 367.7049 | 0 | 0 | 0
0 | 11.7341 | 0 | 0 | 0 | 0 | 0 | 11.7341 | 0 | 670.5207 | 0 | 670.5207 | 0 | 0 | 0
0 | 15.8978 | 0 | 0 | 0 | 0 | 0 | 15.8978 | 0 | 908.4474 | 0 | 908.4474 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1902.2927 | 0 | 128.9564
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1767.107 | 0 | 117.866
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1702.2179 | 0 | 104.7715
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1929.3298 | 0 | 115.2389
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2178.0714 | 0 | 130.6843
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2064.5154 | 0 | 125.1096
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2437.6278 | 0 | 155.5938
0 | 7.0026 | 0 | 0 | 0 | 0 | 0 | 7.0026 | 0 | 400.1495 | 0 | 400.1495 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151.4079 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 197.37
0 | 49.6206 | 0 | 0 | 0 | 0 | 2.8794 | 52.5 | 2.8794 | 3000 | 5.145 | 3005.145 | 3005.145 | 0 | 177.0631
0 | 51.9387 | 0 | 0 | 0 | 0 | 0.56133 | 52.5 | 3.4407 | 3000 | 1.003 | 3001.003 | 3001.003 | 0 | 163.6747
0 | 55.9407 | 0 | 0 | 0 | 0 | -3.4407 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 151.92
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 147.45
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 141.75
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 141.66
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 143.19
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2935.1109 | 0 | 169.7668
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2751.2584 | 0 | 184.6094
0 | 7.1919 | 0 | 0 | 0 | 0 | 0 | 7.1919 | 0 | 410.9643 | 0 | 410.9643 | 0 | 0 | 0
0 | 9.9361 | 0 | 0 | 0 | 0 | 0 | 9.9361 | 0 | 567.7796 | 0 | 567.7796 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2113.1823 | 0 | 141.3719
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1842.811 | 0 | 119.8011
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2324.0718 | 0 | 132.751
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2307.8496 | 0 | 126.0547
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1945.5521 | 0 | 102.6668
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1983.4041 | 0 | 102.899
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2394.3684 | 0 | 125.5128
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2556.5911 | 0 | 150.8389
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2864.8144 | 0 | 188.648
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 197.88
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 179.85
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 157.2
0 | 33.0963 | 0 | 0 | 0 | 0 | 19.4037 | 52.5 | 19.4037 | 3000 | 34.6719 | 3034.6719 | 3034.6719 | 0 | 149.7004
0 | 35.3193 | 0 | 0 | 0 | 0 | 17.1807 | 52.5 | 36.5844 | 3000 | 30.6997 | 3030.6997 | 3030.6997 | 0 | 140.9275
0 | 59.1105 | 0 | 0 | 0 | 0 | -6.6105 | 52.5 | 29.974 | 3000 | 0 | 3000 | 3000 | 0 | 133.23
0 | 71.2272 | 0 | 0 | 0 | 0 | -18.7272 | 52.5 | 11.2468 | 3000 | 0 | 3000 | 3000 | 0 | 131.52
0 | 37.7921 | 0 | 0 | 0 | 0 | 14.7079 | 52.5 | 25.9548 | 3000 | 26.2811 | 3026.2811 | 3026.2811 | 0 | 132.3998
0 | 75.7361 | 0 | 0 | 0 | 0 | -23.2361 | 52.5 | 2.7186 | 3000 | 0 | 3000 | 2994.5926 | 0 | 135.0561
0 | 55.2186 | 0 | 0 | 0 | 0 | -2.7186 | 52.5 | 0 | 3000 | 0 | 3000 | 2870.2218 | 0 | 161.5074
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2556.5911 | 0 | 168.914
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2329.4793 | 0 | 153.1866
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2129.4045 | 0 | 129.9789
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1788.7367 | 0 | 100.8132
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1626.514 | 0 | 86.5143
0 | 37.3537 | 0 | 0 | 0 | 0 | 15.1463 | 52.5 | 15.1463 | 3000 | 27.0644 | 3027.0644 | 1610.319 | 0 | 80.4193
0 | 44.906 | 0 | 0 | 0 | 0 | 7.594 | 52.5 | 22.7403 | 3000 | 13.5695 | 3013.5695 | 1650.8983 | 0 | 81.4388
0 | 53.0758 | 0 | 0 | 0 | 0 | -0.57581 | 52.5 | 22.1645 | 3000 | 0 | 3000 | 1821.1813 | 0 | 89.2925
0 | 49.1376 | 0 | 0 | 0 | 0 | 3.3624 | 52.5 | 25.5268 | 3000 | 6.0081 | 3006.0081 | 2075.9309 | 0 | 104.357
0 | 40.1064 | 0 | 0 | 0 | 0 | 12.3936 | 52.5 | 37.9204 | 3000 | 22.1457 | 3022.1457 | 2362.4398 | 0 | 121.0042
0 | 38.2267 | 0 | 0 | 0 | 0 | 14.2733 | 52.5 | 52.1937 | 3000 | 25.5044 | 3025.5044 | 2592.9104 | 0 | 151.426
0 | 31.0185 | 0 | 0 | 0 | 0 | 21.4815 | 52.5 | 73.6752 | 3000 | 38.3847 | 3038.3847 | 2827.4951 | 0 | 185.1727
0 | 38.8201 | 0 | 0 | 0 | 0 | 13.6799 | 52.5 | 87.3551 | 3000 | 24.4442 | 3024.4442 | 3013.6293 | 0 | 202.9378
0 | 33.7256 | 0 | 0 | 0 | 0 | 18.7744 | 52.5 | 106.1295 | 3000 | 33.5473 | 3033.5473 | 3033.5473 | 0 | 204.7341
0 | 29.0581 | 0 | 0 | 0 | 0 | 23.4419 | 52.5 | 129.5715 | 3000 | 41.8876 | 3041.8876 | 3041.8876 | 0 | 202.3159
0 | 27.2414 | 0 | 0 | 0 | 0 | 25.2586 | 52.5 | 154.8301 | 3000 | 45.1338 | 3045.1338 | 3045.1338 | 0 | 192.2697
0 | 39.1998 | 0 | 0 | 0 | 0 | 13.3002 | 52.5 | 168.1302 | 3000 | 23.7656 | 3023.7656 | 3023.7656 | 0 | 162.4367
0 | 29.1381 | 0 | 0 | 0 | 0 | 23.3619 | 52.5 | 191.4921 | 3000 | 41.7445 | 3041.7445 | 3041.7445 | 0 | 159.357
0 | 28.2341 | 0 | 0 | 0 | 0 | 24.2659 | 52.5 | 215.758 | 3000 | 43.36 | 3043.36 | 3043.36 | 0 | 145.0465
0 | 27.9364 | 0 | 0 | 0 | 0 | 24.5636 | 52.5 | 240.3216 | 3000 | 43.8919 | 3043.8919 | 3043.8919 | 0 | 138.9232
0 | 26.0601 | 0 | 0 | 0 | 0 | 26.4399 | 52.5 | 266.7615 | 3000 | 47.2446 | 3047.2446 | 3047.2446 | 0 | 131.3972
0 | 38.1069 | 0 | 0 | 0 | 0 | 14.3931 | 52.5 | 281.1546 | 3000 | 25.7186 | 3025.7186 | 3025.7186 | 0 | 129.3797
0 | 62.809 | 0 | 0 | 0 | 0 | -10.309 | 52.5 | 270.8457 | 3000 | 0 | 3000 | 2994.5926 | 0 | 126.1622
0 | 99.3796 | 0 | 0 | 0 | 0 | -46.8796 | 52.5 | 223.966 | 3000 | 0 | 3000 | 2891.8515 | 0 | 124.6677
0 | 80.3134 | 0 | 0 | 0 | 0 | -27.8134 | 52.5 | 196.1526 | 3000 | 0 | 3000 | 2632.2951 | 0 | 112.6622
0 | 116.0804 | 0 | 0 | 0 | 0 | -63.5804 | 52.5 | 132.5723 | 3000 | 0 | 3000 | 2302.4421 | 0 | 108.3529
0 | 91.4806 | 0 | 0 | 0 | 0 | -38.9806 | 52.5 | 93.5917 | 3000 | 0 | 3000 | 2010.4412 | 0 | 97.9487
0 | 86.076 | 0 | 0 | 0 | 0 | -33.576 | 52.5 | 60.0156 | 3000 | 0 | 3000 | 1788.7367 | 0 | 82.8006
0 | 48.5222 | 0 | 0 | 0 | 0 | 3.9778 | 52.5 | 63.9934 | 3000 | 7.1078 | 3007.1078 | 1714.7332 | 0 | 77.9175
0 | 33.9966 | 0 | 0 | 0 | 0 | 18.5034 | 52.5 | 82.4969 | 3000 | 33.0631 | 3033.0631 | 1632.54 | 0 | 71.1787
0 | 38.1275 | 0 | 0 | 0 | 0 | 14.3725 | 52.5 | 96.8694 | 3000 | 25.6818 | 3025.6818 | 1711.6774 | 0 | 74.458
0 | 45.997 | 0 | 0 | 0 | 0 | 6.503 | 52.5 | 103.3723 | 3000 | 11.62 | 3011.62 | 1811.1716 | 0 | 77.9347
0 | 37.5203 | 0 | 0 | 0 | 0 | 14.9797 | 52.5 | 118.352 | 3000 | 26.7667 | 3026.7667 | 2064.245 | 0 | 89.0309
0 | 39.5206 | 0 | 0 | 0 | 0 | 12.9794 | 52.5 | 131.3314 | 3000 | 23.1925 | 3023.1925 | 2341.8569 | 0 | 105.0791
0 | 43.6064 | 0 | 0 | 0 | 0 | 8.8936 | 52.5 | 140.2251 | 3000 | 15.8917 | 3015.8917 | 2723.8908 | 0 | 129.63
0 | 34.2676 | 0 | 0 | 0 | 0 | 18.2324 | 52.5 | 158.4574 | 3000 | 32.5788 | 3032.5788 | 2967.6897 | 0 | 165.241
0 | 35.9268 | 0 | 0 | 0 | 0 | 16.5732 | 52.5 | 175.0306 | 3000 | 29.6141 | 3029.6141 | 3029.6141 | 0 | 191.8958
0 | 26.7169 | 0 | 0 | 0 | 0 | 25.7831 | 52.5 | 200.8137 | 3000 | 46.0709 | 3046.0709 | 3046.0709 | 0 | 190.2271
0 | 29.2197 | 0 | 0 | 0 | 0 | 23.2803 | 52.5 | 224.094 | 3000 | 41.5988 | 3041.5988 | 3041.5988 | 0 | 171.607
0 | 23.5334 | 0 | 0 | 0 | 0 | 28.9666 | 52.5 | 253.0605 | 3000 | 51.7594 | 3051.7594 | 3051.7594 | 0 | 158.9051
0 | 32.2444 | 0 | 0 | 0 | 0 | 20.2556 | 52.5 | 273.3162 | 3000 | 36.1941 | 3036.1941 | 3036.1941 | 0 | 145.798
0 | 27.2669 | 0 | 0 | 0 | 0 | 25.2331 | 52.5 | 298.5493 | 3000 | 45.0882 | 3045.0882 | 3045.0882 | 0 | 128.5027
0 | 35.6877 | 0 | 0 | 0 | 0 | 16.8123 | 52.5 | 315.3616 | 3000 | 30.0413 | 3030.0413 | 3030.0413 | 0 | 126.3527
0 | 37.3207 | 0 | 0 | 0 | 0 | 15.1793 | 52.5 | 330.5409 | 3000 | 27.1234 | 3027.1234 | 3027.1234 | 0 | 125.5348
0 | 233.2894 | 0 | 0 | 0 | 0 | -180.7894 | 52.5 | 149.7515 | 3000 | 0 | 3000 | 3000 | 0 | 122.79
0 | 23.7272 | 0 | 0 | 0 | 0 | 28.7728 | 52.5 | 178.5244 | 3000 | 51.4133 | 3051.4133 | 3051.4133 | 0 | 123.094
0 | 31.1954 | 0 | 0 | 0 | 0 | 21.3046 | 52.5 | 199.8289 | 3000 | 38.0684 | 3038.0684 | 3038.0684 | 0 | 124.5304
0 | 34.4809 | 0 | 0 | 0 | 0 | 18.0191 | 52.5 | 217.848 | 3000 | 32.1977 | 3032.1977 | 2983.5309 | 0 | 123.7867
0 | 35.5468 | 0 | 0 | 0 | 0 | 16.9532 | 52.5 | 234.8013 | 3000 | 30.2932 | 3030.2932 | 2884.2927 | 0 | 119.6693
0 | 53.8848 | 0 | 0 | 0 | 0 | -1.3848 | 52.5 | 233.4164 | 3000 | 0 | 3000 | 2561.9986 | 0 | 107.194
0 | 43.6508 | 0 | 0 | 0 | 0 | 8.8492 | 52.5 | 242.2657 | 3000 | 15.8124 | 3015.8124 | 2545.3664 | 0 | 114.796
0 | 47.3409 | 0 | 0 | 0 | 0 | 5.1591 | 52.5 | 247.4247 | 3000 | 9.2186 | 3009.2186 | 2241.3642 | 0 | 100.189
0 | 44.5395 | 0 | 0 | 0 | 0 | 7.9605 | 52.5 | 255.3853 | 3000 | 14.2244 | 3014.2244 | 2181.4809 | 0 | 98.5375
0 | 42.3667 | 0 | 0 | 0 | 0 | 10.1333 | 52.5 | 265.5186 | 3000 | 18.1069 | 3018.1069 | 2347.5862 | 0 | 108.0124
0 | 45.6326 | 0 | 0 | 0 | 0 | 6.8674 | 52.5 | 272.386 | 3000 | 12.2711 | 3012.2711 | 2374.1949 | 0 | 107.3848
0 | 45.414 | 0 | 0 | 0 | 0 | 7.086 | 52.5 | 279.472 | 3000 | 12.6618 | 3012.6618 | 2115.0292 | 0 | 91.7711
0 | 37.505 | 0 | 0 | 0 | 0 | 14.995 | 52.5 | 294.4671 | 3000 | 26.7941 | 3026.7941 | 2377.9031 | 0 | 101.6316
0 | 53.2934 | 0 | 0 | 0 | 0 | -0.7934 | 52.5 | 293.6736 | 3000 | 0 | 3000 | 2334.8867 | 0 | 98.5322
0 | 48.9326 | 0 | 0 | 0 | 0 | 3.5674 | 52.5 | 297.241 | 3000 | 6.3744 | 3006.3744 | 2606.225 | 0 | 117.1237
0 | 54.8373 | 0 | 0 | 0 | 0 | -2.3373 | 52.5 | 294.9037 | 3000 | 0 | 3000 | 2853.9995 | 0 | 140.0458
0 | 248.2936 | 0 | 0 | 0 | 0 | -195.7936 | 52.5 | 99.1101 | 3000 | 0 | 3000 | 2994.5926 | 0 | 154.2814
0 | 27.4699 | 0 | 0 | 0 | 0 | 25.0301 | 52.5 | 124.1402 | 3000 | 44.7255 | 3044.7255 | 3044.7255 | 0 | 166.4551
0 | 28.1355 | 0 | 0 | 0 | 0 | 24.3645 | 52.5 | 148.5047 | 3000 | 43.5361 | 3043.5361 | 3043.5361 | 0 | 163.6205
0 | 30.9459 | 0 | 0 | 0 | 0 | 21.5541 | 52.5 | 170.0588 | 3000 | 38.5143 | 3038.5143 | 3038.5143 | 0 | 159.0055
0 | 32.237 | 0 | 0 | 0 | 0 | 20.263 | 52.5 | 190.3218 | 3000 | 36.2074 | 3036.2074 | 3036.2074 | 0 | 149.8368
0 | 23.0765 | 0 | 0 | 0 | 0 | 29.4235 | 52.5 | 219.7453 | 3000 | 52.5758 | 3052.5758 | 3052.5758 | 0 | 135.1681
0 | 29.5448 | 0 | 0 | 0 | 0 | 22.9552 | 52.5 | 242.7005 | 3000 | 41.0179 | 3041.0179 | 3041.0179 | 0 | 127.6315
0 | 32.7035 | 0 | 0 | 0 | 0 | 19.7965 | 52.5 | 262.497 | 3000 | 35.3737 | 3035.3737 | 3035.3737 | 0 | 124.3289
0 | 36.4747 | 0 | 0 | 0 | 0 | 16.0253 | 52.5 | 278.5223 | 3000 | 28.6352 | 3028.6352 | 3028.6352 | 0 | 121.1454
0 | 28.0253 | 0 | 0 | 0 | 0 | 24.4747 | 52.5 | 302.997 | 3000 | 43.7331 | 3043.7331 | 3043.7331 | 0 | 123.6669
0 | 29.4191 | 0 | 0 | 0 | 0 | 23.0809 | 52.5 | 326.0779 | 3000 | 41.2425 | 3041.2425 | 3035.8351 | 0 | 129.7212
0 | 23.5911 | 0 | 0 | 0 | 0 | 28.9089 | 52.5 | 354.9868 | 3000 | 51.6563 | 3051.6563 | 2959.73 | 0 | 156.5105
0 | 33.2374 | 0 | 0 | 0 | 0 | 19.2626 | 52.5 | 374.2494 | 3000 | 34.4196 | 3034.4196 | 2709.9741 | 0 | 165.5523
0 | 47.0433 | 0 | 0 | 0 | 0 | 5.4567 | 52.5 | 379.706 | 3000 | 9.7503 | 3009.7503 | 2339.2296 | 0 | 150.9973
0 | 38.4221 | 0 | 0 | 0 | 0 | 14.0779 | 52.5 | 393.7839 | 3000 | 25.1554 | 3025.1554 | 2116.7079 | 0 | 133.9664
0 | 54.1857 | 0 | 0 | 0 | 0 | -1.6857 | 52.5 | 392.0983 | 3000 | 0 | 3000 | 1745.4773 | 0 | 103.1053
0 | 38.9454 | 0 | 0 | 0 | 0 | 13.5546 | 52.5 | 405.6529 | 3000 | 24.2202 | 3024.2202 | 2332.0698 | 0 | 132.4849
0 | 39.8047 | 0 | 0 | 0 | 0 | 12.6953 | 52.5 | 418.3482 | 3000 | 22.6848 | 3022.6848 | 2011.4963 | 0 | 108.2788
0 | 41.0136 | 0 | 0 | 0 | 0 | 11.4864 | 52.5 | 429.8345 | 3000 | 20.5246 | 3020.5246 | 2074.2252 | 0 | 110.2451
0 | 48.2162 | 0 | 0 | 0 | 0 | 4.2838 | 52.5 | 434.1183 | 3000 | 7.6546 | 3007.6546 | 1985.6513 | 0 | 102.6582
0 | 35.8829 | 0 | 0 | 0 | 0 | 16.6171 | 52.5 | 450.7355 | 3000 | 29.6926 | 3029.6926 | 2337.5422 | 0 | 119.1913
0 | 32.8006 | 0 | 0 | 0 | 0 | 19.6994 | 52.5 | 470.4349 | 3000 | 35.2003 | 3035.2003 | 2386.3093 | 0 | 125.4483
0 | 46.2222 | 0 | 0 | 0 | 0 | 6.2778 | 52.5 | 476.7127 | 3000 | 11.2177 | 3011.2177 | 2627.2905 | 0 | 146.7079
0 | 51.9321 | 0 | 0 | 0 | 0 | 0.56789 | 52.5 | 477.2806 | 3000 | 1.0147 | 3001.0147 | 2860.4217 | 0 | 172.7981
0 | 42.918 | 0 | 0 | 0 | 0 | 9.582 | 52.5 | 486.8626 | 3000 | 17.1218 | 3017.1218 | 3017.1218 | 0 | 203.0221
0 | 23.9279 | 0 | 0 | 0 | 0 | 28.5721 | 52.5 | 515.4347 | 3000 | 51.0545 | 3051.0545 | 3051.0545 | 0 | 206.0377
0 | 27.0376 | 0 | 0 | 0 | 0 | 25.4624 | 52.5 | 540.8971 | 3000 | 45.4979 | 3045.4979 | 3045.4979 | 0 | 188.5772
0 | 34.3735 | 0 | 0 | 0 | 0 | 18.1265 | 52.5 | 559.0236 | 3000 | 32.3896 | 3032.3896 | 3032.3896 | 0 | 169.086
0 | 27.5506 | 0 | 0 | 0 | 0 | 24.9494 | 52.5 | 583.9729 | 3000 | 44.5812 | 3044.5812 | 3044.5812 | 0 | 152.8989
0 | 28.7229 | 0 | 0 | 0 | 0 | 23.7771 | 52.5 | 607.75 | 3000 | 42.4864 | 3042.4864 | 3042.4864 | 0 | 142.4188
0 | 30.4055 | 0 | 0 | 0 | 0 | 22.0945 | 52.5 | 629.8445 | 3000 | 39.4799 | 3039.4799 | 3039.4799 | 0 | 131.0624
0 | 31.2793 | 0 | 0 | 0 | 0 | 21.2207 | 52.5 | 651.0652 | 3000 | 37.9187 | 3037.9187 | 3037.9187 | 0 | 127.4407
0 | 28.1927 | 0 | 0 | 0 | 0 | 24.3073 | 52.5 | 675.3725 | 3000 | 43.4339 | 3043.4339 | 3043.4339 | 0 | 119.607
0 | 37.6331 | 0 | 0 | 0 | 0 | 14.8669 | 52.5 | 690.2393 | 3000 | 26.5651 | 3026.5651 | 3026.5651 | 0 | 118.3387
0 | 63.2604 | 0 | 0 | 0 | 0 | -10.7604 | 52.5 | 679.4789 | 3000 | 0 | 3000 | 3000 | 0 | 129.69
0 | 100.6489 | 0 | 0 | 0 | 0 | -48.1489 | 52.5 | 631.33 | 3000 | 0 | 3000 | 2978.3703 | 0 | 141.2939
0 | 105.6292 | 0 | 0 | 0 | 0 | -53.1292 | 52.5 | 578.2008 | 3000 | 0 | 3000 | 2821.555 | 0 | 157.2735
0 | 133.5865 | 0 | 0 | 0 | 0 | -81.0865 | 52.5 | 497.1143 | 3000 | 0 | 3000 | 2502.5169 | 0 | 139.8406
0 | 119.6572 | 0 | 0 | 0 | 0 | -67.1572 | 52.5 | 429.9571 | 3000 | 0 | 3000 | 2572.8134 | 0 | 136.2562
0 | 54.2 | 0 | 0 | 0 | 0 | -1.7 | 52.5 | 428.257 | 3000 | 0 | 3000 | 2605.258 | 0 | 124.9221
0 | 62.0577 | 0 | 0 | 0 | 0 | -9.5577 | 52.5 | 418.6994 | 3000 | 0 | 3000 | 2794.5178 | 0 | 131.5659
0 | 65.3304 | 0 | 0 | 0 | 0 | -12.8304 | 52.5 | 405.869 | 3000 | 0 | 3000 | 2675.5545 | 0 | 120.1324
0 | 92.0306 | 0 | 0 | 0 | 0 | -39.5306 | 52.5 | 366.3384 | 3000 | 0 | 3000 | 2448.4426 | 0 | 112.9956
0 | 43.5286 | 0 | 0 | 0 | 0 | 8.9714 | 52.5 | 375.3098 | 3000 | 16.0307 | 3016.0307 | 2610.4738 | 0 | 121.9352
0 | 52.8398 | 0 | 0 | 0 | 0 | -0.33979 | 52.5 | 374.97 | 3000 | 0 | 3000 | 2859.4069 | 0 | 134.4207
0 | 25.4761 | 0 | 0 | 0 | 0 | 27.0239 | 52.5 | 401.9939 | 3000 | 48.2881 | 3048.2881 | 2929.3247 | 0 | 141.4571
0 | 38.9545 | 0 | 0 | 0 | 0 | 13.5455 | 52.5 | 415.5394 | 3000 | 24.2041 | 3024.2041 | 2932.2779 | 0 | 160.5715
0 | 40.9264 | 0 | 0 | 0 | 0 | 11.5736 | 52.5 | 427.1131 | 3000 | 20.6806 | 3020.6806 | 2988.236 | 0 | 179.1746
0 | 28.4771 | 0 | 0 | 0 | 0 | 24.0229 | 52.5 | 451.136 | 3000 | 42.9257 | 3042.9257 | 3042.9257 | 0 | 200.3158
0 | 37.1704 | 0 | 0 | 0 | 0 | 15.3296 | 52.5 | 466.4656 | 3000 | 27.3919 | 3027.3919 | 3027.3919 | 0 | 206.1654
0 | 29.4107 | 0 | 0 | 0 | 0 | 23.0893 | 52.5 | 489.5549 | 3000 | 41.2575 | 3041.2575 | 3041.2575 | 0 | 185.8817
0 | 26.295 | 0 | 0 | 0 | 0 | 26.205 | 52.5 | 515.7598 | 3000 | 46.8248 | 3046.8248 | 3046.8248 | 0 | 170.3175
0 | 33.9137 | 0 | 0 | 0 | 0 | 18.5863 | 52.5 | 534.3461 | 3000 | 33.2112 | 3033.2112 | 3033.2112 | 0 | 154.9364
0 | 21.8439 | 0 | 0 | 0 | 0 | 30.6561 | 52.5 | 565.0022 | 3000 | 54.7783 | 3054.7783 | 3054.7783 | 0 | 141.4668
0 | 32.2349 | 0 | 0 | 0 | 0 | 20.2651 | 52.5 | 585.2672 | 3000 | 36.211 | 3036.211 | 3036.211 | 0 | 133.5933
0 | 35.0647 | 0 | 0 | 0 | 0 | 17.4353 | 52.5 | 602.7026 | 3000 | 31.1546 | 3031.1546 | 3031.1546 | 0 | 133.3708
0 | 32.8435 | 0 | 0 | 0 | 0 | 19.6565 | 52.5 | 622.3591 | 3000 | 35.1235 | 3035.1235 | 3035.1235 | 0 | 129.7515
0 | 41.5665 | 0 | 0 | 0 | 0 | 10.9335 | 52.5 | 633.2926 | 3000 | 19.5367 | 3019.5367 | 3019.5367 | 0 | 130.0514
0 | 31.0333 | 0 | 0 | 0 | 0 | 21.4667 | 52.5 | 654.7593 | 3000 | 38.3582 | 3038.3582 | 3038.3582 | 0 | 118.9517
0 | 43.1887 | 0 | 0 | 0 | 0 | 9.3113 | 52.5 | 664.0706 | 3000 | 16.6381 | 3016.6381 | 2967.9713 | 0 | 161.8138
0 | 50.707 | 0 | 0 | 0 | 0 | 1.793 | 52.5 | 665.8636 | 3000 | 3.2038 | 3003.2038 | 2813.9439 | 0 | 162.6741
0 | 33.32 | 0 | 0 | 0 | 0 | 19.18 | 52.5 | 685.0436 | 3000 | 34.2721 | 3034.2721 | 2434.0479 | 0 | 146.7487
0 | 41.6878 | 0 | 0 | 0 | 0 | 10.8122 | 52.5 | 695.8558 | 3000 | 19.32 | 3019.32 | 2370.429 | 0 | 137.3901
0 | 56.2701 | 0 | 0 | 0 | 0 | -3.7701 | 52.5 | 692.0857 | 3000 | 0 | 3000 | 2297.0347 | 0 | 121.1226
0 | 113.3049 | 0 | 0 | 0 | 0 | -60.8049 | 52.5 | 631.2808 | 3000 | 0 | 3000 | 2567.406 | 0 | 122.1315
0 | 309.1763 | 0 | 0 | 0 | 0 | -256.6763 | 52.5 | 374.6045 | 3000 | 0 | 3000 | 2702.5916 | 0 | 122.9139
0 | 102.0795 | 0 | 0 | 0 | 0 | -49.5795 | 52.5 | 325.025 | 3000 | 0 | 3000 | 2745.851 | 0 | 121.8334
0 | 52.5302 | 0 | 0 | 0 | 0 | -0.030218 | 52.5 | 324.9947 | 3000 | 0 | 3000 | 2859.4069 | 0 | 127.0149
0 | 36.2103 | 0 | 0 | 0 | 0 | 16.2897 | 52.5 | 341.2845 | 3000 | 29.1076 | 3029.1076 | 2866.8848 | 0 | 125.8562
0 | 50.8361 | 0 | 0 | 0 | 0 | 1.6639 | 52.5 | 342.9484 | 3000 | 2.9732 | 3002.9732 | 2943.4915 | 0 | 129.1015
0 | 43.5439 | 0 | 0 | 0 | 0 | 8.9561 | 52.5 | 351.9044 | 3000 | 16.0033 | 3016.0033 | 2815.9285 | 0 | 131.4475
0 | 37.6651 | 0 | 0 | 0 | 0 | 14.8349 | 52.5 | 366.7393 | 3000 | 26.508 | 3026.508 | 2988.656 | 0 | 158.5482
0 | 46.7173 | 0 | 0 | 0 | 0 | 5.7827 | 52.5 | 372.522 | 3000 | 10.3329 | 3010.3329 | 3004.9255 | 0 | 166.1724
0 | 30.9866 | 0 | 0 | 0 | 0 | 21.5134 | 52.5 | 394.0354 | 3000 | 38.4416 | 3038.4416 | 3038.4416 | 0 | 169.15
0 | 33.2608 | 0 | 0 | 0 | 0 | 19.2392 | 52.5 | 413.2746 | 3000 | 34.3779 | 3034.3779 | 3034.3779 | 0 | 161.5806
0 | 32.7342 | 0 | 0 | 0 | 0 | 19.7658 | 52.5 | 433.0404 | 3000 | 35.3188 | 3035.3188 | 3035.3188 | 0 | 152.6765
0 | 22.8008 | 0 | 0 | 0 | 0 | 29.6992 | 52.5 | 462.7396 | 3000 | 53.0686 | 3053.0686 | 3053.0686 | 0 | 135.9837
0 | 31.5561 | 0 | 0 | 0 | 0 | 20.9439 | 52.5 | 483.6835 | 3000 | 37.4239 | 3037.4239 | 3037.4239 | 0 | 130.6092
0 | 24.1971 | 0 | 0 | 0 | 0 | 28.3029 | 52.5 | 511.9864 | 3000 | 50.5735 | 3050.5735 | 3050.5735 | 0 | 124.9515
0 | 31.6068 | 0 | 0 | 0 | 0 | 20.8932 | 52.5 | 532.8795 | 3000 | 37.3333 | 3037.3333 | 3037.3333 | 0 | 121.6452
0 | 35.0568 | 0 | 0 | 0 | 0 | 17.4432 | 52.5 | 550.3227 | 3000 | 31.1686 | 3031.1686 | 3031.1686 | 0 | 116.1544
0 | 35.3842 | 0 | 0 | 0 | 0 | 17.1158 | 52.5 | 567.4385 | 3000 | 30.5837 | 3030.5837 | 3030.5837 | 0 | 114.9803
0 | 27.9686 | 0 | 0 | 0 | 0 | 24.5314 | 52.5 | 591.9699 | 3000 | 43.8343 | 3043.8343 | 3043.8343 | 0 | 125.8321
0 | 51.4621 | 0 | 0 | 0 | 0 | 1.0379 | 52.5 | 593.0078 | 3000 | 1.8546 | 3001.8546 | 2953.1878 | 0 | 143.7612
0 | 96.0731 | 0 | 0 | 0 | 0 | -43.5731 | 52.5 | 549.4348 | 3000 | 0 | 3000 | 2789.1104 | 0 | 152.3412
0 | 91.2204 | 0 | 0 | 0 | 0 | -38.7204 | 52.5 | 510.7144 | 3000 | 0 | 3000 | 2464.6649 | 0 | 136.7396
0 | 313.6136 | 0 | 0 | 0 | 0 | -261.1136 | 52.5 | 249.6008 | 3000 | 0 | 3000 | 2513.3317 | 0 | 129.4115
0 | 109.7762 | 0 | 0 | 0 | 0 | -57.2762 | 52.5 | 192.3246 | 3000 | 0 | 3000 | 2123.9971 | 0 | 99.7004
0 | 121.684 | 0 | 0 | 0 | 0 | -69.184 | 52.5 | 123.1406 | 3000 | 0 | 3000 | 2188.8862 | 0 | 95.5668
0 | 63.1486 | 0 | 0 | 0 | 0 | -10.6486 | 52.5 | 112.492 | 3000 | 0 | 3000 | 2259.1827 | 0 | 92.0843
0 | 50.7432 | 0 | 0 | 0 | 0 | 1.7568 | 52.5 | 114.2488 | 3000 | 3.1391 | 3003.1391 | 2386.6927 | 0 | 96.1837
0 | 41.0433 | 0 | 0 | 0 | 0 | 11.4567 | 52.5 | 125.7055 | 3000 | 20.4716 | 3020.4716 | 2149.8762 | 0 | 87.8009
0 | 45.3116 | 0 | 0 | 0 | 0 | 7.1884 | 52.5 | 132.8939 | 3000 | 12.8447 | 3012.8447 | 2509.9542 | 0 | 105.9201
0 | 41.7798 | 0 | 0 | 0 | 0 | 10.7202 | 52.5 | 143.6141 | 3000 | 19.1555 | 3019.1555 | 2521.6724 | 0 | 111.3571
0 | 47.9255 | 0 | 0 | 0 | 0 | 4.5745 | 52.5 | 148.1885 | 3000 | 8.174 | 3008.174 | 2689.1359 | 0 | 127.0886
0 | 81.3208 | 0 | 0 | 0 | 0 | -28.8208 | 52.5 | 119.3677 | 3000 | 0 | 3000 | 2918.8886 | 0 | 149.126
0 | 113.9353 | 0 | 0 | 0 | 0 | -61.4353 | 52.5 | 57.9324 | 3000 | 0 | 3000 | 3000 | 0 | 164.85
0 | 100.618 | 0 | 0 | 0 | 0 | -48.118 | 52.5 | 9.8144 | 3000 | 0 | 3000 | 3000 | 0 | 167.76
0 | 62.3144 | 0 | 0 | 0 | 0 | -9.8144 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 161.85
0 | 27.9641 | 0 | 0 | 0 | 0 | 24.5359 | 52.5 | 24.5359 | 3000 | 43.8423 | 3043.8423 | 3043.8423 | 0 | 155.8752
0 | 33.3732 | 0 | 0 | 0 | 0 | 19.1268 | 52.5 | 43.6627 | 3000 | 34.177 | 3034.177 | 3034.177 | 0 | 139.4204
0 | 36.6569 | 0 | 0 | 0 | 0 | 15.8431 | 52.5 | 59.5057 | 3000 | 28.3095 | 3028.3095 | 3028.3095 | 0 | 125.0086
0 | 27.1019 | 0 | 0 | 0 | 0 | 25.3981 | 52.5 | 84.9038 | 3000 | 45.383 | 3045.383 | 3045.383 | 0 | 123.7644
0 | 27.0179 | 0 | 0 | 0 | 0 | 25.4821 | 52.5 | 110.3859 | 3000 | 45.5331 | 3045.5331 | 3045.5331 | 0 | 119.8722
0 | 33.8573 | 0 | 0 | 0 | 0 | 18.6427 | 52.5 | 129.0286 | 3000 | 33.312 | 3033.312 | 3033.312 | 0 | 119.2395
0 | 29.2999 | 0 | 0 | 0 | 0 | 23.2001 | 52.5 | 152.2287 | 3000 | 41.4556 | 3041.4556 | 3041.4556 | 0 | 123.0573
0 | 37.0069 | 0 | 0 | 0 | 0 | 15.4931 | 52.5 | 167.7218 | 3000 | 27.6841 | 3027.6841 | 3027.6841 | 0 | 124.68
0 | 52.7991 | 0 | 0 | 0 | 0 | -0.29913 | 52.5 | 167.4226 | 3000 | 0 | 3000 | 2956.7406 | 0 | 143.2245
0 | 92.0128 | 0 | 0 | 0 | 0 | -39.5128 | 52.5 | 127.9099 | 3000 | 0 | 3000 | 2799.9253 | 0 | 149.04
0 | 114.6468 | 0 | 0 | 0 | 0 | -62.1468 | 52.5 | 65.7631 | 3000 | 0 | 3000 | 2605.258 | 0 | 140.8663
0 | 94.2352 | 0 | 0 | 0 | 0 | -41.7352 | 52.5 | 24.0279 | 3000 | 0 | 3000 | 2453.8501 | 0 | 132.4097
0 | 76.5279 | 0 | 0 | 0 | 0 | -24.0279 | 52.5 | 0 | 3000 | 0 | 3000 | 2302.4421 | 0 | 120.4868
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2102.3674 | 0 | 97.9913
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2156.4417 | 0 | 90.5705
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2075.3303 | 0 | 86.1262
0 | 47.794 | 0 | 0 | 0 | 0 | 4.706 | 52.5 | 4.706 | 3000 | 8.4089 | 3008.4089 | 2397.3699 | 0 | 103.926
0 | 46.4839 | 0 | 0 | 0 | 0 | 6.0161 | 52.5 | 10.7221 | 3000 | 10.75 | 3010.75 | 2724.1565 | 0 | 118.3374
0 | 62.1399 | 0 | 0 | 0 | 0 | -9.6399 | 52.5 | 1.0822 | 3000 | 0 | 3000 | 2772.8881 | 0 | 122.3121
0 | 44.6428 | 0 | 0 | 0 | 0 | 7.8572 | 52.5 | 8.9394 | 3000 | 14.0397 | 3014.0397 | 2949.1506 | 0 | 143.0043
0 | 46.4111 | 0 | 0 | 0 | 0 | 6.0889 | 52.5 | 15.0283 | 3000 | 10.88 | 3010.88 | 2989.2503 | 0 | 159.2075
0 | 48.6903 | 0 | 0 | 0 | 0 | 3.8097 | 52.5 | 18.838 | 3000 | 6.8074 | 3006.8074 | 3006.8074 | 0 | 163.2997
0 | 51.8391 | 0 | 0 | 0 | 0 | 0.6609 | 52.5 | 19.4989 | 3000 | 1.1809 | 3001.1809 | 3001.1809 | 0 | 165.275
0 | 71.9989 | 0 | 0 | 0 | 0 | -19.4989 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 160.2
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 158.67
0 | 45.0251 | 0 | 0 | 0 | 0 | 7.4749 | 52.5 | 7.4749 | 3000 | 13.3567 | 3013.3567 | 3013.3567 | 0 | 147.8654
0 | 45.671 | 0 | 0 | 0 | 0 | 6.829 | 52.5 | 14.3039 | 3000 | 12.2024 | 3012.2024 | 3012.2024 | 0 | 141.6036
0 | 66.8039 | 0 | 0 | 0 | 0 | -14.3039 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 135
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 133.32
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 131.07
0 | 36.8978 | 0 | 0 | 0 | 0 | 15.6022 | 52.5 | 15.6022 | 3000 | 27.8791 | 3027.8791 | 3027.8791 | 0 | 134.1956
0 | 68.1022 | 0 | 0 | 0 | 0 | -15.6022 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 134.52
0 | 18.1048 | 0 | 0 | 0 | 0 | 34.3952 | 52.5 | 34.3952 | 3000 | 61.4597 | 3061.4597 | 3007.3854 | 0 | 143.0613
0 | 29.6176 | 0 | 0 | 0 | 0 | 22.8824 | 52.5 | 57.2776 | 3000 | 40.8878 | 3040.8878 | 2829.9982 | 0 | 141.7546
0 | 33.9757 | 0 | 0 | 0 | 0 | 18.5243 | 52.5 | 75.8018 | 3000 | 33.1004 | 3033.1004 | 2470.7282 | 0 | 126.6742
0 | 46.743 | 0 | 0 | 0 | 0 | 5.757 | 52.5 | 81.5589 | 3000 | 10.287 | 3010.287 | 2166.7287 | 0 | 118.8017
0 | 54.5548 | 0 | 0 | 0 | 0 | -2.0548 | 52.5 | 79.5041 | 3000 | 0 | 3000 | 2188.8862 | 0 | 119.7321
0 | 109.1256 | 0 | 0 | 0 | 0 | -56.6256 | 52.5 | 22.8785 | 3000 | 0 | 3000 | 2567.406 | 0 | 133.4794
0 | 75.3785 | 0 | 0 | 0 | 0 | -22.8785 | 52.5 | 0 | 3000 | 0 | 3000 | 2075.3303 | 0 | 105.8418
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2275.405 | 0 | 113.884
0 | 45.9525 | 0 | 0 | 0 | 0 | 6.5475 | 52.5 | 6.5475 | 3000 | 11.6995 | 3011.6995 | 2076.215 | 0 | 101.6515
0 | 37.2679 | 0 | 0 | 0 | 0 | 15.2321 | 52.5 | 21.7797 | 3000 | 27.2178 | 3027.2178 | 2518.9199 | 0 | 118.8174
0 | 44.8079 | 0 | 0 | 0 | 0 | 7.6921 | 52.5 | 29.4718 | 3000 | 13.7448 | 3013.7448 | 2586.5582 | 0 | 125.1636
0 | 57.3802 | 0 | 0 | 0 | 0 | -4.8802 | 52.5 | 24.5916 | 3000 | 0 | 3000 | 2891.8515 | 0 | 151.533
0 | 43.5143 | 0 | 0 | 0 | 0 | 8.9857 | 52.5 | 33.5773 | 3000 | 16.0562 | 3016.0562 | 2967.3894 | 0 | 175.076
0 | 35.6359 | 0 | 0 | 0 | 0 | 16.8641 | 52.5 | 50.4413 | 3000 | 30.1339 | 3030.1339 | 3030.1339 | 0 | 186.9896
0 | 30.3391 | 0 | 0 | 0 | 0 | 22.1609 | 52.5 | 72.6022 | 3000 | 39.5985 | 3039.5985 | 3039.5985 | 0 | 196.7532
0 | 36.9735 | 0 | 0 | 0 | 0 | 15.5265 | 52.5 | 88.1287 | 3000 | 27.7437 | 3027.7437 | 3027.7437 | 0 | 163.4982
0 | 31.836 | 0 | 0 | 0 | 0 | 20.664 | 52.5 | 108.7926 | 3000 | 36.9238 | 3036.9238 | 3036.9238 | 0 | 160.8962
0 | 30.1338 | 0 | 0 | 0 | 0 | 22.3662 | 52.5 | 131.1589 | 3000 | 39.9655 | 3039.9655 | 3039.9655 | 0 | 151.3295
0 | 29.4535 | 0 | 0 | 0 | 0 | 23.0465 | 52.5 | 154.2054 | 3000 | 41.1811 | 3041.1811 | 3041.1811 | 0 | 150.4168
0 | 33.0276 | 0 | 0 | 0 | 0 | 19.4724 | 52.5 | 173.6778 | 3000 | 34.7946 | 3034.7946 | 3034.7946 | 0 | 144.4866
0 | 34.7718 | 0 | 0 | 0 | 0 | 17.7282 | 52.5 | 191.406 | 3000 | 31.6779 | 3031.6779 | 3031.6779 | 0 | 143.5803
0 | 33.9844 | 0 | 0 | 0 | 0 | 18.5156 | 52.5 | 209.9216 | 3000 | 33.085 | 3033.085 | 3033.085 | 0 | 142.5853
0 | 41.4933 | 0 | 0 | 0 | 0 | 11.0067 | 52.5 | 220.9284 | 3000 | 19.6675 | 3019.6675 | 3019.6675 | 0 | 141.6828
0 | 76.9443 | 0 | 0 | 0 | 0 | -24.4443 | 52.5 | 196.4841 | 3000 | 0 | 3000 | 3000 | 0 | 138
0 | 79.0901 | 0 | 0 | 0 | 0 | -26.5901 | 52.5 | 169.894 | 3000 | 0 | 3000 | 2956.7406 | 0 | 140.1199
0 | 26.6278 | 0 | 0 | 0 | 0 | 25.8722 | 52.5 | 195.7662 | 3000 | 46.2301 | 3046.2301 | 2856.9703 | 0 | 137.706
0 | 53.1683 | 0 | 0 | 0 | 0 | -0.66827 | 52.5 | 195.0979 | 3000 | 0 | 3000 | 2643.1099 | 0 | 132.1555
0 | 42.3263 | 0 | 0 | 0 | 0 | 10.1737 | 52.5 | 205.2716 | 3000 | 18.179 | 3018.179 | 2369.288 | 0 | 123.8427
0 | 41.6441 | 0 | 0 | 0 | 0 | 10.8559 | 52.5 | 216.1275 | 3000 | 19.398 | 3019.398 | 2219.0991 | 0 | 113.862
0 | 40.5054 | 0 | 0 | 0 | 0 | 11.9946 | 52.5 | 228.1221 | 3000 | 21.4328 | 3021.4328 | 2286.023 | 0 | 117.0215
0 | 43.9187 | 0 | 0 | 0 | 0 | 8.5813 | 52.5 | 236.7034 | 3000 | 15.3336 | 3015.3336 | 2177.1827 | 0 | 109.8606
0 | 35.161 | 0 | 0 | 0 | 0 | 17.339 | 52.5 | 254.0424 | 3000 | 30.9825 | 3030.9825 | 1917.0529 | 0 | 90.4849
0 | 32.8276 | 0 | 0 | 0 | 0 | 19.6724 | 52.5 | 273.7148 | 3000 | 35.152 | 3035.152 | 2337.5941 | 0 | 110.5682
0 | 43.0364 | 0 | 0 | 0 | 0 | 9.4636 | 52.5 | 283.1784 | 3000 | 16.9101 | 3016.9101 | 2627.5755 | 0 | 124.4683
0 | 45.0315 | 0 | 0 | 0 | 0 | 7.4685 | 52.5 | 290.6469 | 3000 | 13.3453 | 3013.3453 | 2667.2701 | 0 | 131.3897
0 | 39.7472 | 0 | 0 | 0 | 0 | 12.7528 | 52.5 | 303.3997 | 3000 | 22.7876 | 3022.7876 | 2736.1941 | 0 | 148.5753
0 | 48.7014 | 0 | 0 | 0 | 0 | 3.7986 | 52.5 | 307.1983 | 3000 | 6.7876 | 3006.7876 | 2882.4168 | 0 | 173.2333
0 | 40.6332 | 0 | 0 | 0 | 0 | 11.8668 | 52.5 | 319.0651 | 3000 | 21.2043 | 3021.2043 | 3021.2043 | 0 | 202.0581
0 | 25.4853 | 0 | 0 | 0 | 0 | -25.4853 | 0 | 293.5798 | 0 | 0 | 0 | 0 | 0 | 0
0 | 29.7855 | 0 | 0 | 0 | 0 | 22.7145 | 52.5 | 316.2942 | 3000 | 40.5877 | 3040.5877 | 3040.5877 | 0 | 183.9252
0 | 28.2073 | 0 | 0 | 0 | 0 | 24.2927 | 52.5 | 340.5869 | 3000 | 43.4078 | 3043.4078 | 3043.4078 | 0 | 174.996
0 | 28.3608 | 0 | 0 | 0 | 0 | 24.1392 | 52.5 | 364.7261 | 3000 | 43.1335 | 3043.1335 | 3043.1335 | 0 | 162.1077
0 | 22.2734 | 0 | 0 | 0 | 0 | 30.2266 | 52.5 | 394.9528 | 3000 | 54.011 | 3054.011 | 3054.011 | 0 | 162.8704
0 | 24.4389 | 0 | 0 | 0 | 0 | 28.0611 | 52.5 | 423.0138 | 3000 | 50.1414 | 3050.1414 | 3050.1414 | 0 | 149.7314
0 | 31.4192 | 0 | 0 | 0 | 0 | 21.0808 | 52.5 | 444.0946 | 3000 | 37.6685 | 3037.6685 | 3037.6685 | 0 | 145.8992
0 | 27.9679 | 0 | 0 | 0 | 0 | 24.5321 | 52.5 | 468.6267 | 3000 | 43.8356 | 3043.8356 | 3043.8356 | 0 | 143.3342
0 | 25.9253 | 0 | 0 | 0 | 0 | 26.5747 | 52.5 | 495.2014 | 3000 | 47.4854 | 3047.4854 | 3047.4854 | 0 | 144.5727
0 | 27.5069 | 0 | 0 | 0 | 0 | 24.9931 | 52.5 | 520.1945 | 3000 | 44.6593 | 3044.6593 | 3044.6593 | 0 | 149.6146
0 | 27.4751 | 0 | 0 | 0 | 0 | 25.0249 | 52.5 | 545.2193 | 3000 | 44.7161 | 3044.7161 | 2963.6047 | 0 | 186.6478
0 | 25.0736 | 0 | 0 | 0 | 0 | -19.2065 | 5.8671 | 526.0128 | 335.2604 | 0 | 335.2604 | 0 | 0 | 0
0 | 43.0825 | 0 | 0 | 0 | 0 | -32.1054 | 10.9771 | 493.9074 | 627.2613 | 0 | 627.2613 | 0 | 0 | 0
0 | 38.8319 | 0 | 0 | 0 | 0 | -23.0287 | 15.8032 | 470.8787 | 903.04 | 0 | 903.04 | 0 | 0 | 0
0 | 48.1507 | 0 | 0 | 0 | 0 | 4.3493 | 52.5 | 475.228 | 3000 | 7.7717 | 3007.7717 | 1926.2866 | 0 | 122.6467
0 | 44.5767 | 0 | 0 | 0 | 0 | 7.9233 | 52.5 | 483.1513 | 3000 | 14.1578 | 3014.1578 | 2273.3406 | 0 | 141.8792
0 | 43.3509 | 0 | 0 | 0 | 0 | 9.1491 | 52.5 | 492.3004 | 3000 | 16.3482 | 3016.3482 | 1913.2334 | 0 | 116.7072
0 | 40.3698 | 0 | 0 | 0 | 0 | 12.1302 | 52.5 | 504.4306 | 3000 | 21.6751 | 3021.6751 | 2259.2281 | 0 | 136.0733
0 | 36.8052 | 0 | 0 | 0 | 0 | 15.6948 | 52.5 | 520.1254 | 3000 | 28.0444 | 3028.0444 | 2709.0064 | 0 | 156.1471
0 | 247.8707 | 0 | 0 | 0 | 0 | -195.3707 | 52.5 | 324.7546 | 3000 | 0 | 3000 | 2545.7763 | 0 | 145.6948
0 | 50.7449 | 0 | 0 | 0 | 0 | 1.7551 | 52.5 | 326.5097 | 3000 | 3.1361 | 3003.1361 | 2440.7639 | 0 | 138.1472
0 | 50.5474 | 0 | 0 | 0 | 0 | 1.9526 | 52.5 | 328.4623 | 3000 | 3.489 | 3003.489 | 2825.0439 | 0 | 169.8981
0 | 41.5539 | 0 | 0 | 0 | 0 | 10.9461 | 52.5 | 339.4084 | 3000 | 19.5592 | 3019.5592 | 2976.2998 | 0 | 193.4297
0 | 47.2942 | 0 | 0 | 0 | 0 | -47.2942 | 0 | 292.1142 | 0 | 0 | 0 | 0 | 0 | 0
0 | 33.8017 | 0 | 0 | 0 | 0 | -33.8017 | 0 | 258.3125 | 0 | 0 | 0 | 0 | 0 | 0
0 | 35.1031 | 0 | 0 | 0 | 0 | 17.3969 | 52.5 | 275.7094 | 3000 | 31.0859 | 3031.0859 | 3031.0859 | 0 | 184.7144
0 | 18.801 | 0 | 0 | 0 | 0 | 33.699 | 52.5 | 309.4083 | 3000 | 60.2155 | 3060.2155 | 3060.2155 | 0 | 169.4747
0 | 230.0904 | 0 | 0 | 0 | 0 | -177.5904 | 52.5 | 131.818 | 3000 | 0 | 3000 | 3000 | 0 | 148.05
0 | 40.3639 | 0 | 0 | 0 | 0 | 12.1361 | 52.5 | 143.954 | 3000 | 21.6856 | 3021.6856 | 3021.6856 | 0 | 145.0711
0 | 27.0531 | 0 | 0 | 0 | 0 | 25.4469 | 52.5 | 169.401 | 3000 | 45.4703 | 3045.4703 | 3045.4703 | 0 | 144.5076
0 | 28.1879 | 0 | 0 | 0 | 0 | 24.3121 | 52.5 | 193.713 | 3000 | 43.4424 | 3043.4424 | 3043.4424 | 0 | 139.9984
0 | 57.2495 | 0 | 0 | 0 | 0 | -4.7495 | 52.5 | 188.9635 | 3000 | 0 | 3000 | 3000 | 0 | 133.89
0 | 107.9366 | 0 | 0 | 0 | 0 | -55.4366 | 52.5 | 133.5269 | 3000 | 0 | 3000 | 3000 | 0 | 132.03
0 | 104.5831 | 0 | 0 | 0 | 0 | -52.0831 | 52.5 | 81.4438 | 3000 | 0 | 3000 | 3000 | 0 | 140.4
0 | 125.4005 | 0 | 0 | 0 | 0 | -72.9005 | 52.5 | 8.5432 | 3000 | 0 | 3000 | 2956.7406 | 0 | 163.2121
0 | 61.0432 | 0 | 0 | 0 | 0 | -8.5432 | 52.5 | 0 | 3000 | 0 | 3000 | 2843.1847 | 0 | 170.4489
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2518.7392 | 0 | 153.4668
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2145.6268 | 0 | 120.1551
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2421.4055 | 0 | 123.4917
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2345.7015 | 0 | 111.6554
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1707.6254 | 0 | 78.6191
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1729.2551 | 0 | 79.027
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2064.5154 | 0 | 95.5871
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2329.4793 | 0 | 109.5088
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2572.8134 | 0 | 126.3251
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2783.703 | 0 | 150.821
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2935.1109 | 0 | 174.7272
0 | 36.5845 | 0 | 0 | 0 | 0 | 15.9155 | 52.5 | 15.9155 | 3000 | 28.4389 | 3028.4389 | 3028.4389 | 0 | 189.0957
0 | 26.0848 | 0 | 0 | 0 | 0 | 26.4152 | 52.5 | 42.3307 | 3000 | 47.2005 | 3047.2005 | 3047.2005 | 0 | 200.1097
0 | 39.6017 | 0 | 0 | 0 | 0 | 12.8983 | 52.5 | 55.2291 | 3000 | 23.0476 | 3023.0476 | 3023.0476 | 0 | 174.581
0 | 32.5522 | 0 | 0 | 0 | 0 | 19.9478 | 52.5 | 75.1768 | 3000 | 35.644 | 3035.644 | 3035.644 | 0 | 154.4839
0 | 38.093 | 0 | 0 | 0 | 0 | 14.407 | 52.5 | 89.5838 | 3000 | 25.7434 | 3025.7434 | 3025.7434 | 0 | 141.3022
0 | 28.4697 | 0 | 0 | 0 | 0 | 24.0303 | 52.5 | 113.6141 | 3000 | 42.939 | 3042.939 | 3042.939 | 0 | 140.7359
0 | 27.7328 | 0 | 0 | 0 | 0 | 24.7672 | 52.5 | 138.3813 | 3000 | 44.2556 | 3044.2556 | 3044.2556 | 0 | 137.6917
0 | 25.3581 | 0 | 0 | 0 | 0 | 27.1419 | 52.5 | 165.5232 | 3000 | 48.4989 | 3048.4989 | 3048.4989 | 0 | 132.6097
0 | 31.2932 | 0 | 0 | 0 | 0 | 21.2068 | 52.5 | 186.73 | 3000 | 37.8938 | 3037.8938 | 3037.8938 | 0 | 127.8953
0 | 37.851 | 0 | 0 | 0 | 0 | 14.649 | 52.5 | 201.379 | 3000 | 26.1759 | 3026.1759 | 3026.1759 | 0 | 120.9563
0 | 47.0305 | 0 | 0 | 0 | 0 | 5.4695 | 52.5 | 206.8485 | 3000 | 9.7732 | 3009.7732 | 3009.7732 | 0 | 128.2464
0 | 80.6661 | 0 | 0 | 0 | 0 | -28.1661 | 52.5 | 178.6824 | 3000 | 0 | 3000 | 2929.7035 | 0 | 153.1942
0 | 112.4346 | 0 | 0 | 0 | 0 | -59.9346 | 52.5 | 118.7478 | 3000 | 0 | 3000 | 2643.1099 | 0 | 152.1638
0 | 126.0295 | 0 | 0 | 0 | 0 | -73.5295 | 52.5 | 45.2183 | 3000 | 0 | 3000 | 2691.7768 | 0 | 156.796
0 | 97.7183 | 0 | 0 | 0 | 0 | -45.2183 | 52.5 | 0 | 3000 | 0 | 3000 | 2626.8877 | 0 | 144.006
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2745.851 | 0 | 140.8347
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2713.4065 | 0 | 132.7941
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2767.4807 | 0 | 126.0587
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2816.1475 | 0 | 123.3191
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2783.703 | 0 | 121.5921
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2859.4069 | 0 | 128.7305
0 | 34.55 | 0 | 0 | 0 | 0 | 17.95 | 52.5 | 17.95 | 3000 | 32.0742 | 3032.0742 | 2940.148 | 0 | 130.3368
0 | 36.1198 | 0 | 0 | 0 | 0 | 16.3802 | 52.5 | 34.3302 | 3000 | 29.2693 | 3029.2693 | 2986.0099 | 0 | 143.5076
0 | 38.8722 | 0 | 0 | 0 | 0 | 13.6278 | 52.5 | 47.958 | 3000 | 24.351 | 3024.351 | 3013.5361 | 0 | 157.7285
0 | 54.651 | 0 | 0 | 0 | 0 | -2.151 | 52.5 | 45.807 | 3000 | 0 | 3000 | 3000 | 0 | 164.01
0 | 32.4209 | 0 | 0 | 0 | 0 | 20.0791 | 52.5 | 65.8861 | 3000 | 35.8787 | 3035.8787 | 3035.8787 | 0 | 170.3128
0 | 36.9022 | 0 | 0 | 0 | 0 | 15.5978 | 52.5 | 81.4839 | 3000 | 27.8712 | 3027.8712 | 3027.8712 | 0 | 161.5975
0 | 29.3108 | 0 | 0 | 0 | 0 | 23.1892 | 52.5 | 104.6731 | 3000 | 41.4361 | 3041.4361 | 3041.4361 | 0 | 146.1106
0 | 26.6976 | 0 | 0 | 0 | 0 | 25.8024 | 52.5 | 130.4755 | 3000 | 46.1054 | 3046.1054 | 3046.1054 | 0 | 137.3794
0 | 30.3122 | 0 | 0 | 0 | 0 | 22.1878 | 52.5 | 152.6633 | 3000 | 39.6466 | 3039.6466 | 3039.6466 | 0 | 130.34
0 | 34.2312 | 0 | 0 | 0 | 0 | 18.2688 | 52.5 | 170.932 | 3000 | 32.6438 | 3032.6438 | 3032.6438 | 0 | 128.0079
0 | 35.35 | 0 | 0 | 0 | 0 | 17.15 | 52.5 | 188.0821 | 3000 | 30.6448 | 3030.6448 | 3030.6448 | 0 | 128.8933
0 | 40.0378 | 0 | 0 | 0 | 0 | 12.4622 | 52.5 | 200.5443 | 3000 | 22.2684 | 3022.2684 | 3022.2684 | 0 | 126.9655
0 | 105.7633 | 0 | 0 | 0 | 0 | -53.2633 | 52.5 | 147.281 | 3000 | 0 | 3000 | 3000 | 0 | 129.09
0 | 115.4765 | 0 | 0 | 0 | 0 | -62.9765 | 52.5 | 84.3045 | 3000 | 0 | 3000 | 3000 | 0 | 137.22
0 | 99.3045 | 0 | 0 | 0 | 0 | -46.8045 | 52.5 | 37.5 | 3000 | 0 | 3000 | 2972.9629 | 0 | 177.367
0 | 90 | 0 | 0 | 0 | 0 | -37.5 | 52.5 | 0 | 3000 | 0 | 3000 | 2837.7772 | 0 | 186.3001
0 | 9.7469 | 0 | 0 | 0 | 0 | 0 | 9.7469 | 0 | 556.9648 | 0 | 556.9648 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2248.3679 | 0 | 141.5572
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1902.2927 | 0 | 112.1021
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1826.5887 | 0 | 104.0608
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2059.108 | 0 | 115.2895
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1729.2551 | 0 | 86.9469
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2194.2936 | 0 | 104.6239
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2329.4793 | 0 | 111.1628
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2464.6649 | 0 | 117.6877
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2745.851 | 0 | 150.7472
0 | 43.6449 | 0 | 0 | 0 | 0 | 8.8551 | 52.5 | 8.8551 | 3000 | 15.8229 | 3015.8229 | 2967.156 | 0 | 169.1279
0 | 32.6153 | 0 | 0 | 0 | 0 | 19.8847 | 52.5 | 28.7398 | 3000 | 35.5313 | 3035.5313 | 3035.5313 | 0 | 179.9159
0 | 27.937 | 0 | 0 | 0 | 0 | 24.563 | 52.5 | 53.3027 | 3000 | 43.8908 | 3043.8908 | 3043.8908 | 0 | 180.107
0 | 35.3408 | 0 | 0 | 0 | 0 | 17.1592 | 52.5 | 70.4619 | 3000 | 30.6612 | 3030.6612 | 3030.6612 | 0 | 171.2627
0 | 25.9154 | 0 | 0 | 0 | 0 | 26.5846 | 52.5 | 97.0465 | 3000 | 47.5031 | 3047.5031 | 3047.5031 | 0 | 156.3064
0 | 22.8777 | 0 | 0 | 0 | 0 | 29.6223 | 52.5 | 126.6688 | 3000 | 52.9311 | 3052.9311 | 3052.9311 | 0 | 137.6872
0 | 30.5046 | 0 | 0 | 0 | 0 | 21.9954 | 52.5 | 148.6642 | 3000 | 39.3028 | 3039.3028 | 3039.3028 | 0 | 136.9206
0 | 25.1085 | 0 | 0 | 0 | 0 | 27.3915 | 52.5 | 176.0557 | 3000 | 48.945 | 3048.945 | 3048.945 | 0 | 132.0498
0 | 32.8404 | 0 | 0 | 0 | 0 | 19.6596 | 52.5 | 195.7153 | 3000 | 35.1291 | 3035.1291 | 3035.1291 | 0 | 127.8093
0 | 33.1589 | 0 | 0 | 0 | 0 | 19.3411 | 52.5 | 215.0565 | 3000 | 34.5601 | 3034.5601 | 3034.5601 | 0 | 125.1453
0 | 45.507 | 0 | 0 | 0 | 0 | 6.993 | 52.5 | 222.0495 | 3000 | 12.4956 | 3012.4956 | 3012.4956 | 0 | 126.6754
0 | 116.7942 | 0 | 0 | 0 | 0 | -64.2942 | 52.5 | 157.7553 | 3000 | 0 | 3000 | 3000 | 0 | 135.03
0 | 97.2329 | 0 | 0 | 0 | 0 | -44.7329 | 52.5 | 113.0224 | 3000 | 0 | 3000 | 2983.7777 | 0 | 164.1376
0 | 103.0107 | 0 | 0 | 0 | 0 | -50.5107 | 52.5 | 62.5116 | 3000 | 0 | 3000 | 2864.8144 | 0 | 168.9668
0 | 94.9408 | 0 | 0 | 0 | 0 | -42.4408 | 52.5 | 20.0709 | 3000 | 0 | 3000 | 2502.5169 | 0 | 151.9528
0 | 72.5709 | 0 | 0 | 0 | 0 | -20.0709 | 52.5 | 0 | 3000 | 0 | 3000 | 2302.4421 | 0 | 137.4328
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1902.2927 | 0 | 111.5695
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1983.4041 | 0 | 113.4705
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2048.2932 | 0 | 114.3562
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2091.5526 | 0 | 110.8941
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2059.108 | 0 | 107.1354
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2280.8124 | 0 | 116.8916
0 | 50.9207 | 0 | 0 | 0 | 0 | 1.5793 | 52.5 | 1.5793 | 3000 | 2.8219 | 3002.8219 | 2462.0794 | 0 | 129.333
0 | 38.539 | 0 | 0 | 0 | 0 | 13.961 | 52.5 | 15.5403 | 3000 | 24.9464 | 3024.9464 | 2738.3529 | 0 | 157.4005
0 | 36.8726 | 0 | 0 | 0 | 0 | 15.6274 | 52.5 | 31.1676 | 3000 | 27.924 | 3027.924 | 2979.2572 | 0 | 182.122
0 | 49.2346 | 0 | 0 | 0 | 0 | 3.2654 | 52.5 | 34.4331 | 3000 | 5.8349 | 3005.8349 | 3005.8349 | 0 | 198.6857
0 | 31.0698 | 0 | 0 | 0 | 0 | 21.4302 | 52.5 | 55.8632 | 3000 | 38.2929 | 3038.2929 | 3038.2929 | 0 | 204.8721
0 | 29.9334 | 0 | 0 | 0 | 0 | 22.5666 | 52.5 | 78.4298 | 3000 | 40.3235 | 3040.3235 | 3040.3235 | 0 | 182.1458
0 | 33.2091 | 0 | 0 | 0 | 0 | 19.2909 | 52.5 | 97.7208 | 3000 | 34.4703 | 3034.4703 | 3034.4703 | 0 | 173.0255
0 | 26.9362 | 0 | 0 | 0 | 0 | 25.5638 | 52.5 | 123.2846 | 3000 | 45.6792 | 3045.6792 | 3045.6792 | 0 | 164.4667
0 | 30.2856 | 0 | 0 | 0 | 0 | 22.2144 | 52.5 | 145.499 | 3000 | 39.6942 | 3039.6942 | 3039.6942 | 0 | 166.2713
0 | 23.1214 | 0 | 0 | 0 | 0 | 29.3786 | 52.5 | 174.8776 | 3000 | 52.4957 | 3052.4957 | 3052.4957 | 0 | 144.9935
0 | 30.3581 | 0 | 0 | 0 | 0 | 22.1419 | 52.5 | 197.0196 | 3000 | 39.5647 | 3039.5647 | 3039.5647 | 0 | 143.0723
0 | 30.484 | 0 | 0 | 0 | 0 | 22.016 | 52.5 | 219.0356 | 3000 | 39.3397 | 3039.3397 | 3039.3397 | 0 | 142.545
0 | 34.4877 | 0 | 0 | 0 | 0 | 18.0123 | 52.5 | 237.0479 | 3000 | 32.1857 | 3032.1857 | 3032.1857 | 0 | 141.9973
0 | 27.4982 | 0 | 0 | 0 | 0 | 25.0018 | 52.5 | 262.0498 | 3000 | 44.675 | 3044.675 | 3044.675 | 0 | 142.8866
0 | 52.0543 | 0 | 0 | 0 | 0 | 0.4457 | 52.5 | 262.4955 | 3000 | 0.79641 | 3000.7964 | 2957.537 | 0 | 141.5181
0 | 100.3404 | 0 | 0 | 0 | 0 | -47.8404 | 52.5 | 214.655 | 3000 | 0 | 3000 | 2707.999 | 0 | 148.6691
0 | 106.8015 | 0 | 0 | 0 | 0 | -54.3015 | 52.5 | 160.3536 | 3000 | 0 | 3000 | 2432.2204 | 0 | 137.3961
0 | 110.2962 | 0 | 0 | 0 | 0 | -57.7962 | 52.5 | 102.5573 | 3000 | 0 | 3000 | 2161.8491 | 0 | 122.7282
0 | 90.5478 | 0 | 0 | 0 | 0 | -38.0478 | 52.5 | 64.5096 | 3000 | 0 | 3000 | 1913.1075 | 0 | 98.5059
0 | 50.7867 | 0 | 0 | 0 | 0 | 1.7133 | 52.5 | 66.2229 | 3000 | 3.0615 | 3003.0615 | 1797.2057 | 0 | 85.4392
0 | 48.9304 | 0 | 0 | 0 | 0 | 3.5696 | 52.5 | 69.7925 | 3000 | 6.3784 | 3006.3784 | 1757.2631 | 0 | 81.3261
0 | 46.519 | 0 | 0 | 0 | 0 | 5.981 | 52.5 | 75.7734 | 3000 | 10.6872 | 3010.6872 | 1912.9799 | 0 | 86.1032
0 | 42.8588 | 0 | 0 | 0 | 0 | 9.6412 | 52.5 | 85.4147 | 3000 | 17.2276 | 3017.2276 | 1941.15 | 0 | 83.5277
0 | 40.0344 | 0 | 0 | 0 | 0 | 12.4656 | 52.5 | 97.8803 | 3000 | 22.2744 | 3022.2744 | 2189.5309 | 0 | 94.1936
0 | 56.3426 | 0 | 0 | 0 | 0 | -3.8426 | 52.5 | 94.0377 | 3000 | 0 | 3000 | 2497.1095 | 0 | 112.3699
0 | 39.616 | 0 | 0 | 0 | 0 | 12.884 | 52.5 | 106.9217 | 3000 | 23.022 | 3023.022 | 2860.7993 | 0 | 144.4131
0 | 39.3035 | 0 | 0 | 0 | 0 | 13.1965 | 52.5 | 120.1183 | 3000 | 23.5805 | 3023.5805 | 2985.7285 | 0 | 172.9334
0 | 49.0514 | 0 | 0 | 0 | 0 | 3.4486 | 52.5 | 123.5668 | 3000 | 6.1622 | 3006.1622 | 3006.1622 | 0 | 197.9558
0 | 40.3423 | 0 | 0 | 0 | 0 | 12.1577 | 52.5 | 135.7246 | 3000 | 21.7242 | 3021.7242 | 3021.7242 | 0 | 190.3384
0 | 23.6297 | 0 | 0 | 0 | 0 | 28.8703 | 52.5 | 164.5949 | 3000 | 51.5873 | 3051.5873 | 3051.5873 | 0 | 180.1962
0 | 26.8717 | 0 | 0 | 0 | 0 | 25.6283 | 52.5 | 190.2232 | 3000 | 45.7944 | 3045.7944 | 3045.7944 | 0 | 170.4122
0 | 35.7584 | 0 | 0 | 0 | 0 | 16.7416 | 52.5 | 206.9647 | 3000 | 29.9149 | 3029.9149 | 3029.9149 | 0 | 145.1026
0 | 29.9652 | 0 | 0 | 0 | 0 | 22.5348 | 52.5 | 229.4995 | 3000 | 40.2667 | 3040.2667 | 3040.2667 | 0 | 146.176
0 | 31.8259 | 0 | 0 | 0 | 0 | 20.6741 | 52.5 | 250.1736 | 3000 | 36.9418 | 3036.9418 | 3036.9418 | 0 | 134.8402
0 | 35.8531 | 0 | 0 | 0 | 0 | 16.6469 | 52.5 | 266.8205 | 3000 | 29.7458 | 3029.7458 | 3029.7458 | 0 | 122.2502
0 | 31.2971 | 0 | 0 | 0 | 0 | 21.2029 | 52.5 | 288.0234 | 3000 | 37.8868 | 3037.8868 | 3037.8868 | 0 | 99.825
0 | 30.2419 | 0 | 0 | 0 | 0 | 22.2581 | 52.5 | 310.2816 | 3000 | 39.7723 | 3039.7723 | 3039.7723 | 0 | 96.6648
0 | 25.0304 | 0 | 0 | 0 | 0 | 27.4696 | 52.5 | 337.7512 | 3000 | 49.0845 | 3049.0845 | 3049.0845 | 0 | 103.6689
0 | 28.2945 | 0 | 0 | 0 | 0 | 24.2055 | 52.5 | 361.9567 | 3000 | 43.252 | 3043.252 | 2989.1777 | 0 | 118.1921
0 | 31.4236 | 0 | 0 | 0 | 0 | 21.0764 | 52.5 | 383.0331 | 3000 | 37.6608 | 3037.6608 | 2772.6969 | 0 | 130.7049
0 | 244.0401 | 0 | 0 | 0 | 0 | -191.5401 | 52.5 | 191.493 | 3000 | 0 | 3000 | 2556.5911 | 0 | 110.0612
0 | 31.0235 | 0 | 0 | 0 | 0 | 21.4765 | 52.5 | 212.9695 | 3000 | 38.3756 | 3038.3756 | 2400.2994 | 0 | 113.1741
0 | 47.6541 | 0 | 0 | 0 | 0 | 4.8459 | 52.5 | 217.8153 | 3000 | 8.6589 | 3008.6589 | 2056.9521 | 0 | 88.7781
0 | 39.3486 | 0 | 0 | 0 | 0 | 13.1514 | 52.5 | 230.9667 | 3000 | 23.4998 | 3023.4998 | 1947.4222 | 0 | 77.8969
0 | 54.7768 | 0 | 0 | 0 | 0 | -2.2768 | 52.5 | 228.6899 | 3000 | 0 | 3000 | 1783.3293 | 0 | 76.6832
0 | 49.6179 | 0 | 0 | 0 | 0 | 2.8821 | 52.5 | 231.572 | 3000 | 5.15 | 3005.15 | 2426.5555 | 0 | 109.923
0 | 44.0097 | 0 | 0 | 0 | 0 | 8.4903 | 52.5 | 240.0623 | 3000 | 15.1711 | 3015.1711 | 2333.8355 | 0 | 105.7227
0 | 50.0206 | 0 | 0 | 0 | 0 | 2.4794 | 52.5 | 242.5418 | 3000 | 4.4304 | 3004.4304 | 2761.0963 | 0 | 125.0777
0 | 49.1367 | 0 | 0 | 0 | 0 | 3.3633 | 52.5 | 245.9051 | 3000 | 6.0098 | 3006.0098 | 2941.1207 | 0 | 130.5858
0 | 47.0906 | 0 | 0 | 0 | 0 | 5.4094 | 52.5 | 251.3145 | 3000 | 9.6659 | 3009.6659 | 2950.1843 | 0 | 139.8387
0 | 45.6983 | 0 | 0 | 0 | 0 | 6.8017 | 52.5 | 258.1162 | 3000 | 12.1538 | 3012.1538 | 3001.3389 | 0 | 170.326
0 | 36.1629 | 0 | 0 | 0 | 0 | 16.3371 | 52.5 | 274.4533 | 3000 | 29.1922 | 3029.1922 | 3029.1922 | 0 | 178.6012
0 | 38.8882 | 0 | 0 | 0 | 0 | 13.6118 | 52.5 | 288.0651 | 3000 | 24.3225 | 3024.3225 | 3024.3225 | 0 | 193.2542
0 | 32.1143 | 0 | 0 | 0 | 0 | 20.3857 | 52.5 | 308.4508 | 3000 | 36.4265 | 3036.4265 | 3036.4265 | 0 | 191.2645
0 | 27.5407 | 0 | 0 | 0 | 0 | 24.9593 | 52.5 | 333.4101 | 3000 | 44.5989 | 3044.5989 | 3044.5989 | 0 | 185.4465
0 | 32.0408 | 0 | 0 | 0 | 0 | 20.4592 | 52.5 | 353.8693 | 3000 | 36.5579 | 3036.5579 | 3036.5579 | 0 | 170.5635
0 | 28.4469 | 0 | 0 | 0 | 0 | 24.0531 | 52.5 | 377.9224 | 3000 | 42.9797 | 3042.9797 | 3042.9797 | 0 | 144.3894
0 | 26.3775 | 0 | 0 | 0 | 0 | 26.1225 | 52.5 | 404.0449 | 3000 | 46.6775 | 3046.6775 | 3046.6775 | 0 | 144.9304
0 | 36.9797 | 0 | 0 | 0 | 0 | 15.5203 | 52.5 | 419.5652 | 3000 | 27.7328 | 3027.7328 | 3027.7328 | 0 | 142.5759
0 | 28.3755 | 0 | 0 | 0 | 0 | 24.1245 | 52.5 | 443.6897 | 3000 | 43.1072 | 3043.1072 | 3043.1072 | 0 | 138.2484
0 | 36.5574 | 0 | 0 | 0 | 0 | 15.9426 | 52.5 | 459.6324 | 3000 | 28.4874 | 3028.4874 | 3028.4874 | 0 | 139.0681
0 | 58.5515 | 0 | 0 | 0 | 0 | -6.0515 | 52.5 | 453.5809 | 3000 | 0 | 3000 | 3000 | 0 | 144.9
0 | 87.7705 | 0 | 0 | 0 | 0 | -35.2705 | 52.5 | 418.3103 | 3000 | 0 | 3000 | 2989.1851 | 0 | 189.4546
0 | 38.236 | 0 | 0 | 0 | 0 | 14.264 | 52.5 | 432.5743 | 3000 | 25.4878 | 3025.4878 | 2976.821 | 0 | 201.501
0 | 51.0497 | 0 | 0 | 0 | 0 | -51.0497 | 0 | 381.5246 | 0 | 0 | 0 | 0 | 108.1485 | 0
0 | 50.9909 | 0 | 0 | 0 | 0 | -50.9909 | 0 | 330.5336 | 0 | 0 | 0 | 0 | 173.0376 | 0
0 | 29.7155 | 0 | 0 | 0 | 0 | 22.7845 | 52.5 | 353.3181 | 3000 | 40.7129 | 3040.7129 | 2791.9713 | 0 | 183.6838
0 | 42.3769 | 0 | 0 | 0 | 0 | 10.1231 | 52.5 | 363.4413 | 3000 | 18.0887 | 3018.0887 | 2558.4576 | 0 | 178.2989
0 | 43.889 | 0 | 0 | 0 | 0 | 8.611 | 52.5 | 372.0523 | 3000 | 15.3868 | 3015.3868 | 2436.7923 | 0 | 158.3915
0 | 31.8235 | 0 | 0 | 0 | 0 | 20.6765 | 52.5 | 392.7288 | 3000 | 36.9462 | 3036.9462 | 2647.6116 | 0 | 172.942
0 | 47.4211 | 0 | 0 | 0 | 0 | 5.0789 | 52.5 | 397.8078 | 3000 | 9.0753 | 3009.0753 | 2695.4447 | 0 | 173.5597
0 | 45.4111 | 0 | 0 | 0 | 0 | 7.0889 | 52.5 | 404.8967 | 3000 | 12.667 | 3012.667 | 2726.0734 | 0 | 174.2234
0 | 43.0969 | 0 | 0 | 0 | 0 | 9.4031 | 52.5 | 414.2998 | 3000 | 16.8021 | 3016.8021 | 2616.6527 | 0 | 165.1369
0 | 49.1346 | 0 | 0 | 0 | 0 | 3.3654 | 52.5 | 417.6653 | 3000 | 6.0136 | 3006.0136 | 2876.2354 | 0 | 192.5064
0 | 42.0584 | 0 | 0 | 0 | 0 | -42.0584 | 0 | 375.6069 | 0 | 0 | 0 | 0 | 27.0371 | 0
0 | 35.9723 | 0 | 0 | 0 | 0 | -35.9723 | 0 | 339.6346 | 0 | 0 | 0 | 0 | 0 | 0
0 | 23.0732 | 0 | 0 | 0 | 0 | -23.0732 | 0 | 316.5614 | 0 | 0 | 0 | 0 | 0 | 0
0 | 29.0544 | 0 | 0 | 0 | 0 | 23.4456 | 52.5 | 340.007 | 3000 | 41.8942 | 3041.8942 | 3041.8942 | 0 | 201.0388
0 | 30.1647 | 0 | 0 | 0 | 0 | 22.3353 | 52.5 | 362.3423 | 3000 | 39.9102 | 3039.9102 | 3039.9102 | 0 | 191.0584
0 | 33.9269 | 0 | 0 | 0 | 0 | 18.5731 | 52.5 | 380.9154 | 3000 | 33.1877 | 3033.1877 | 3033.1877 | 0 | 160.7589
0 | 31.0714 | 0 | 0 | 0 | 0 | 21.4286 | 52.5 | 402.344 | 3000 | 38.29 | 3038.29 | 3038.29 | 0 | 157.6265
0 | 33.5038 | 0 | 0 | 0 | 0 | 18.9962 | 52.5 | 421.3402 | 3000 | 33.9437 | 3033.9437 | 3033.9437 | 0 | 145.69
0 | 31.4954 | 0 | 0 | 0 | 0 | 21.0046 | 52.5 | 442.3448 | 3000 | 37.5324 | 3037.5324 | 3037.5324 | 0 | 139.4531
0 | 28.3746 | 0 | 0 | 0 | 0 | 24.1254 | 52.5 | 466.4702 | 3000 | 43.109 | 3043.109 | 3043.109 | 0 | 138.4615
0 | 42.8099 | 0 | 0 | 0 | 0 | 9.6901 | 52.5 | 476.1604 | 3000 | 17.315 | 3017.315 | 3017.315 | 0 | 137.499
0 | 85.9851 | 0 | 0 | 0 | 0 | -33.4851 | 52.5 | 442.6753 | 3000 | 0 | 3000 | 3000 | 0 | 143.64
0 | 109.823 | 0 | 0 | 0 | 0 | -57.323 | 52.5 | 385.3523 | 3000 | 0 | 3000 | 2935.1109 | 0 | 178.7483
0 | 111.7395 | 0 | 0 | 0 | 0 | -59.2395 | 52.5 | 326.1128 | 3000 | 0 | 3000 | 2745.851 | 0 | 180.979
0 | 321.9842 | 0 | 0 | 0 | 0 | -269.4842 | 52.5 | 56.6286 | 3000 | 0 | 3000 | 2524.1466 | 0 | 169.1935
0 | 98.2849 | 0 | 0 | 0 | 0 | -45.7849 | 52.5 | 10.8437 | 3000 | 0 | 3000 | 2518.7392 | 0 | 153.1897
0 | 53.5454 | 0 | 0 | 0 | 0 | -1.0454 | 52.5 | 9.7983 | 3000 | 0 | 3000 | 2269.9976 | 0 | 116.4963
0 | 62.1197 | 0 | 0 | 0 | 0 | -9.6197 | 52.5 | 0.17856 | 3000 | 0 | 3000 | 2778.2956 | 0 | 125.6623
0 | 52.6786 | 0 | 0 | 0 | 0 | -0.17856 | 52.5 | 0 | 3000 | 0 | 3000 | 2405.1832 | 0 | 102.7013
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2426.8129 | 0 | 103.1638
0 | 46.3194 | 0 | 0 | 0 | 0 | 6.1806 | 52.5 | 6.1806 | 3000 | 11.0438 | 3011.0438 | 2427.0419 | 0 | 102.1785
0 | 52.8506 | 0 | 0 | 0 | 0 | -0.35056 | 52.5 | 5.83 | 3000 | 0 | 3000 | 2378.1461 | 0 | 101.0712
0 | 57.5246 | 0 | 0 | 0 | 0 | -5.0246 | 52.5 | 0.80542 | 3000 | 0 | 3000 | 2610.6654 | 0 | 112.2586
0 | 35.6171 | 0 | 0 | 0 | 0 | 16.8829 | 52.5 | 17.6883 | 3000 | 30.1674 | 3030.1674 | 2813.8704 | 0 | 125.8926
0 | 38.6972 | 0 | 0 | 0 | 0 | 13.8028 | 52.5 | 31.4911 | 3000 | 24.6638 | 3024.6638 | 2997.6267 | 0 | 150.8406
0 | 40.2544 | 0 | 0 | 0 | 0 | 12.2456 | 52.5 | 43.7367 | 3000 | 21.8812 | 3021.8812 | 3021.8812 | 0 | 171.4313
0 | 27.6779 | 0 | 0 | 0 | 0 | 24.8221 | 52.5 | 68.5588 | 3000 | 44.3539 | 3044.3539 | 3044.3539 | 0 | 171.458
0 | 24.6802 | 0 | 0 | 0 | 0 | 27.8198 | 52.5 | 96.3786 | 3000 | 49.7102 | 3049.7102 | 3049.7102 | 0 | 157.0906
0 | 30.3023 | 0 | 0 | 0 | 0 | 22.1977 | 52.5 | 118.5763 | 3000 | 39.6644 | 3039.6644 | 3039.6644 | 0 | 146.603
0 | 26.5732 | 0 | 0 | 0 | 0 | 25.9268 | 52.5 | 144.5031 | 3000 | 46.3277 | 3046.3277 | 3046.3277 | 0 | 137.1761
0 | 197.0031 | 0 | 0 | 0 | 0 | -144.5031 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 127.59
0 | 32.6413 | 0 | 0 | 0 | 0 | 19.8587 | 52.5 | 19.8587 | 3000 | 35.4849 | 3035.4849 | 3035.4849 | 0 | 127.976
0 | 23.6857 | 0 | 0 | 0 | 0 | 28.8143 | 52.5 | 48.6731 | 3000 | 51.4874 | 3051.4874 | 3051.4874 | 0 | 128.1625
0 | 37.8372 | 0 | 0 | 0 | 0 | 14.6628 | 52.5 | 63.3359 | 3000 | 26.2005 | 3026.2005 | 3026.2005 | 0 | 126.3136
0 | 32.7116 | 0 | 0 | 0 | 0 | 19.7884 | 52.5 | 83.1243 | 3000 | 35.3593 | 3035.3593 | 3035.3593 | 0 | 129.6098
0 | 45.4285 | 0 | 0 | 0 | 0 | 7.0715 | 52.5 | 90.1959 | 3000 | 12.6359 | 3012.6359 | 3012.6359 | 0 | 136.1109
0 | 84.8469 | 0 | 0 | 0 | 0 | -32.3469 | 52.5 | 57.849 | 3000 | 0 | 3000 | 2972.9629 | 0 | 162.8292
0 | 83.4687 | 0 | 0 | 0 | 0 | -30.9687 | 52.5 | 26.8803 | 3000 | 0 | 3000 | 2859.4069 | 0 | 185.7185
0 | 79.3803 | 0 | 0 | 0 | 0 | -26.8803 | 52.5 | 0 | 3000 | 0 | 3000 | 2507.9243 | 0 | 166.0747
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2480.8872 | 0 | 152.2272
0 | 40.4343 | 0 | 0 | 0 | 0 | 12.0657 | 52.5 | 12.0657 | 3000 | 21.5598 | 3021.5598 | 2378.0762 | 0 | 113.3391
0 | 35.4196 | 0 | 0 | 0 | 0 | 17.0804 | 52.5 | 29.1462 | 3000 | 30.5205 | 3030.5205 | 2349.1849 | 0 | 110.3882
0 | 81.6462 | 0 | 0 | 0 | 0 | -29.1462 | 52.5 | 0 | 3000 | 0 | 3000 | 2248.3679 | 0 | 97.9389
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2199.7011 | 0 | 96.1269
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1988.8115 | 0 | 86.9111
0 | 44.5005 | 0 | 0 | 0 | 0 | 7.9995 | 52.5 | 7.9995 | 3000 | 14.2941 | 3014.2941 | 2651.9966 | 0 | 119.0746
0 | 41.3469 | 0 | 0 | 0 | 0 | 11.1531 | 52.5 | 19.1526 | 3000 | 19.9291 | 3019.9291 | 2630.5945 | 0 | 118.1137
0 | 53.1162 | 0 | 0 | 0 | 0 | -0.61624 | 52.5 | 18.5364 | 3000 | 0 | 3000 | 2826.9624 | 0 | 149.5746
0 | 38.2653 | 0 | 0 | 0 | 0 | 14.2347 | 52.5 | 32.7711 | 3000 | 25.4355 | 3025.4355 | 2992.991 | 0 | 189.4264
0 | 39.5774 | 0 | 0 | 0 | 0 | 12.9226 | 52.5 | 45.6937 | 3000 | 23.091 | 3023.091 | 3023.091 | 0 | 203.3633
0 | 36.7949 | 0 | 0 | 0 | 0 | 15.7051 | 52.5 | 61.3988 | 3000 | 28.0629 | 3028.0629 | 3028.0629 | 0 | 206.423
0 | 36.8393 | 0 | 0 | 0 | 0 | 15.6607 | 52.5 | 77.0594 | 3000 | 27.9835 | 3027.9835 | 3027.9835 | 0 | 190.9749
0 | 31.119 | 0 | 0 | 0 | 0 | 21.381 | 52.5 | 98.4404 | 3000 | 38.205 | 3038.205 | 3038.205 | 0 | 182.8696
0 | 32.1728 | 0 | 0 | 0 | 0 | 20.3272 | 52.5 | 118.7676 | 3000 | 36.322 | 3036.322 | 3036.322 | 0 | 157.8887
0 | 27.5216 | 0 | 0 | 0 | 0 | 24.9784 | 52.5 | 143.746 | 3000 | 44.633 | 3044.633 | 3044.633 | 0 | 147.1776
0 | 32.2637 | 0 | 0 | 0 | 0 | 20.2363 | 52.5 | 163.9822 | 3000 | 36.1595 | 3036.1595 | 3036.1595 | 0 | 140.1188
0 | 29.1257 | 0 | 0 | 0 | 0 | 23.3743 | 52.5 | 187.3565 | 3000 | 41.7667 | 3041.7667 | 3041.7667 | 0 | 139.2521
0 | 25.0153 | 0 | 0 | 0 | 0 | 27.4847 | 52.5 | 214.8411 | 3000 | 49.1114 | 3049.1114 | 3049.1114 | 0 | 135.3805
0 | 29.8607 | 0 | 0 | 0 | 0 | 22.6393 | 52.5 | 237.4804 | 3000 | 40.4533 | 3040.4533 | 3040.4533 | 0 | 141.1682
0 | 55.6309 | 0 | 0 | 0 | 0 | -3.1309 | 52.5 | 234.3495 | 3000 | 0 | 3000 | 3000 | 0 | 148.5
0 | 81.178 | 0 | 0 | 0 | 0 | -28.678 | 52.5 | 205.6716 | 3000 | 0 | 3000 | 2951.3332 | 0 | 188.0885
0 | 42.4177 | 0 | 0 | 0 | 0 | 10.0823 | 52.5 | 215.7539 | 3000 | 18.0158 | 3018.0158 | 2785.4965 | 0 | 186.0433
0 | 60.1485 | 0 | 0 | 0 | 0 | -7.6485 | 52.5 | 208.1054 | 3000 | 0 | 3000 | 2453.8501 | 0 | 169.3157
0 | 53.6021 | 0 | 0 | 0 | 0 | -1.1021 | 52.5 | 207.0033 | 3000 | 0 | 3000 | 2199.7011 | 0 | 147.38
0 | 61.917 | 0 | 0 | 0 | 0 | -9.417 | 52.5 | 197.5863 | 3000 | 0 | 3000 | 1977.9966 | 0 | 128.9456
0 | 100.2407 | 0 | 0 | 0 | 0 | -47.7407 | 52.5 | 149.8457 | 3000 | 0 | 3000 | 2080.7377 | 0 | 123.1797
0 | 39.5349 | 0 | 0 | 0 | 0 | 12.9651 | 52.5 | 162.8108 | 3000 | 23.167 | 3023.167 | 1887.6077 | 0 | 99.5336
0 | 41.0742 | 0 | 0 | 0 | 0 | 11.4258 | 52.5 | 174.2366 | 3000 | 20.4164 | 3020.4164 | 2014.6353 | 0 | 103.3508
0 | 53.6514 | 0 | 0 | 0 | 0 | -1.1514 | 52.5 | 173.0853 | 3000 | 0 | 3000 | 2080.7377 | 0 | 106.1176
0 | 40.1877 | 0 | 0 | 0 | 0 | 12.3123 | 52.5 | 185.3976 | 3000 | 22.0004 | 3022.0004 | 2264.9609 | 0 | 116.3737
0 | 44.2169 | 0 | 0 | 0 | 0 | 8.2831 | 52.5 | 193.6807 | 3000 | 14.8008 | 3014.8008 | 2468.6509 | 0 | 133.0109
0 | 43.1809 | 0 | 0 | 0 | 0 | 9.3191 | 52.5 | 202.9998 | 3000 | 16.6521 | 3016.6521 | 2811.1699 | 0 | 182.726
0 | 40.7652 | 0 | 0 | 0 | 0 | 11.7348 | 52.5 | 214.7346 | 3000 | 20.9685 | 3020.9685 | 2988.5239 | 0 | 200.8288
0 | 50.8278 | 0 | 0 | 0 | 0 | -50.8278 | 0 | 163.9068 | 0 | 0 | 0 | 0 | 0 | 0
0 | 27.7718 | 0 | 0 | 0 | 0 | -27.7718 | 0 | 136.135 | 0 | 0 | 0 | 0 | 0 | 0
0 | 25.7311 | 0 | 0 | 0 | 0 | 26.7689 | 52.5 | 162.9039 | 3000 | 47.8325 | 3047.8325 | 3047.8325 | 0 | 201.8884
0 | 36.6198 | 0 | 0 | 0 | 0 | 15.8802 | 52.5 | 178.7841 | 3000 | 28.3758 | 3028.3758 | 3028.3758 | 0 | 191.0602
0 | 35.0089 | 0 | 0 | 0 | 0 | 17.4911 | 52.5 | 196.2752 | 3000 | 31.2542 | 3031.2542 | 3031.2542 | 0 | 162.4146
0 | 28.641 | 0 | 0 | 0 | 0 | 23.859 | 52.5 | 220.1341 | 3000 | 42.6328 | 3042.6328 | 3042.6328 | 0 | 159.3427
0 | 28.663 | 0 | 0 | 0 | 0 | 23.837 | 52.5 | 243.9712 | 3000 | 42.5936 | 3042.5936 | 3042.5936 | 0 | 145.5273
0 | 30.8788 | 0 | 0 | 0 | 0 | 21.6212 | 52.5 | 265.5924 | 3000 | 38.6343 | 3038.6343 | 3038.6343 | 0 | 139.8379
0 | 30.172 | 0 | 0 | 0 | 0 | 22.328 | 52.5 | 287.9204 | 3000 | 39.8972 | 3039.8972 | 3039.8972 | 0 | 135.3058
0 | 32.5526 | 0 | 0 | 0 | 0 | 19.9474 | 52.5 | 307.8678 | 3000 | 35.6433 | 3035.6433 | 3035.6433 | 0 | 138.3039
0 | 31.6815 | 0 | 0 | 0 | 0 | 20.8185 | 52.5 | 328.6863 | 3000 | 37.1999 | 3037.1999 | 3037.1999 | 0 | 142.5662
0 | 29.6904 | 0 | 0 | 0 | 0 | 22.8096 | 52.5 | 351.4959 | 3000 | 40.7577 | 3040.7577 | 3013.7205 | 0 | 184.8315
0 | 27.6004 | 0 | 0 | 0 | 0 | 24.8996 | 52.5 | 376.3955 | 3000 | 44.4923 | 3044.4923 | 2811.973 | 0 | 192.5358
0 | 52.6045 | 0 | 0 | 0 | 0 | -44.4663 | 8.1382 | 331.9292 | 465.0386 | 0 | 465.0386 | 0 | 0 | 0
0 | 57.1266 | 0 | 0 | 0 | 0 | -4.6266 | 52.5 | 327.3026 | 3000 | 0 | 3000 | 2205.1085 | 0 | 147.9407
0 | 42.2559 | 0 | 0 | 0 | 0 | 10.2441 | 52.5 | 337.5467 | 3000 | 18.3048 | 3018.3048 | 1996.3014 | 0 | 128.7215
0 | 44.8537 | 0 | 0 | 0 | 0 | 7.6463 | 52.5 | 345.193 | 3000 | 13.6629 | 3013.6629 | 1872.6962 | 0 | 105.8448
0 | 46.2067 | 0 | 0 | 0 | 0 | 6.2933 | 52.5 | 351.4862 | 3000 | 11.2452 | 3011.2452 | 1799.982 | 0 | 87.0651
0 | 58.5944 | 0 | 0 | 0 | 0 | -6.0944 | 52.5 | 345.3919 | 3000 | 0 | 3000 | 1853.6259 | 0 | 85.5448
0 | 94.0756 | 0 | 0 | 0 | 0 | -41.5756 | 52.5 | 303.8163 | 3000 | 0 | 3000 | 1994.2189 | 0 | 91.5346
0 | 99.3299 | 0 | 0 | 0 | 0 | -46.8299 | 52.5 | 256.9864 | 3000 | 0 | 3000 | 2215.9233 | 0 | 106.2757
0 | 243.407 | 0 | 0 | 0 | 0 | -190.907 | 52.5 | 66.0794 | 3000 | 0 | 3000 | 2502.5169 | 0 | 122.5733
0 | 32.2483 | 0 | 0 | 0 | 0 | 20.2517 | 52.5 | 86.331 | 3000 | 36.1871 | 3036.1871 | 2825.2975 | 0 | 172.7104
0 | 57.4783 | 0 | 0 | 0 | 0 | -4.9783 | 52.5 | 81.3527 | 3000 | 0 | 3000 | 2978.3703 | 0 | 194.8152
0 | 38.5964 | 0 | 0 | 0 | 0 | -38.5964 | 0 | 42.7563 | 0 | 0 | 0 | 0 | 0 | 0
0 | 34.6348 | 0 | 0 | 0 | 0 | 17.8652 | 52.5 | 60.6216 | 3000 | 31.9228 | 3031.9228 | 3031.9228 | 0 | 200.7739
0 | 31.1164 | 0 | 0 | 0 | 0 | 21.3836 | 52.5 | 82.0051 | 3000 | 38.2096 | 3038.2096 | 3038.2096 | 0 | 179.4974
0 | 33.3049 | 0 | 0 | 0 | 0 | 19.1951 | 52.5 | 101.2002 | 3000 | 34.299 | 3034.299 | 3034.299 | 0 | 162.335
0 | 27.3479 | 0 | 0 | 0 | 0 | 25.1521 | 52.5 | 126.3523 | 3000 | 44.9435 | 3044.9435 | 3044.9435 | 0 | 140.0979
0 | 33.3103 | 0 | 0 | 0 | 0 | 19.1897 | 52.5 | 145.542 | 3000 | 34.2894 | 3034.2894 | 3034.2894 | 0 | 145.8583
0 | 29.4361 | 0 | 0 | 0 | 0 | 23.0639 | 52.5 | 168.6059 | 3000 | 41.2121 | 3041.2121 | 3041.2121 | 0 | 132.0798
0 | 32.2949 | 0 | 0 | 0 | 0 | 20.2051 | 52.5 | 188.811 | 3000 | 36.1038 | 3036.1038 | 3036.1038 | 0 | 129.7024
0 | 34.5334 | 0 | 0 | 0 | 0 | 17.9666 | 52.5 | 206.7777 | 3000 | 32.104 | 3032.104 | 3032.104 | 0 | 122.1635
0 | 29.1793 | 0 | 0 | 0 | 0 | 23.3207 | 52.5 | 230.0983 | 3000 | 41.671 | 3041.671 | 3041.671 | 0 | 125.986
0 | 75.2267 | 0 | 0 | 0 | 0 | -22.7267 | 52.5 | 207.3717 | 3000 | 0 | 3000 | 3000 | 0 | 126.3
0 | 100.0749 | 0 | 0 | 0 | 0 | -47.5749 | 52.5 | 159.7967 | 3000 | 0 | 3000 | 2967.5554 | 0 | 132.0265
0 | 71.762 | 0 | 0 | 0 | 0 | -19.262 | 52.5 | 140.5347 | 3000 | 0 | 3000 | 2729.6287 | 0 | 125.7813
0 | 98.5889 | 0 | 0 | 0 | 0 | -46.0889 | 52.5 | 94.4458 | 3000 | 0 | 3000 | 2459.2575 | 0 | 126.6518
0 | 95.5985 | 0 | 0 | 0 | 0 | -43.0985 | 52.5 | 51.3473 | 3000 | 0 | 3000 | 2178.0714 | 0 | 112.1707
0 | 77.8578 | 0 | 0 | 0 | 0 | -25.3578 | 52.5 | 25.9894 | 3000 | 0 | 3000 | 1967.1818 | 0 | 91.1395
0 | 55.5247 | 0 | 0 | 0 | 0 | -3.0247 | 52.5 | 22.9648 | 3000 | 0 | 3000 | 1842.811 | 0 | 82.6132
0 | 75.4648 | 0 | 0 | 0 | 0 | -22.9648 | 52.5 | 0 | 3000 | 0 | 3000 | 1804.959 | 0 | 77.9381
0 | 48.6013 | 0 | 0 | 0 | 0 | 3.8987 | 52.5 | 3.8987 | 3000 | 6.9664 | 3006.9664 | 1855.1849 | 0 | 78.196
0 | 49.452 | 0 | 0 | 0 | 0 | 3.048 | 52.5 | 6.9467 | 3000 | 5.4464 | 3005.4464 | 1994.2579 | 0 | 83.0608
0 | 54.6022 | 0 | 0 | 0 | 0 | -2.1022 | 52.5 | 4.8445 | 3000 | 0 | 3000 | 2221.3308 | 0 | 93.7402
0 | 53.9555 | 0 | 0 | 0 | 0 | -1.4555 | 52.5 | 3.389 | 3000 | 0 | 3000 | 2502.5169 | 0 | 105.9065
0 | 55.889 | 0 | 0 | 0 | 0 | -3.389 | 52.5 | 0 | 3000 | 0 | 3000 | 2789.1104 | 0 | 136.6664
0 | 43.4066 | 0 | 0 | 0 | 0 | 9.0934 | 52.5 | 9.0934 | 3000 | 16.2486 | 3016.2486 | 2994.6189 | 0 | 174.5863
0 | 42.4333 | 0 | 0 | 0 | 0 | 10.0667 | 52.5 | 19.16 | 3000 | 17.9878 | 3017.9878 | 3017.9878 | 0 | 196.1692
0 | 24.3108 | 0 | 0 | 0 | 0 | 28.1892 | 52.5 | 47.3493 | 3000 | 50.3704 | 3050.3704 | 3050.3704 | 0 | 187.0487
0 | 29.5062 | 0 | 0 | 0 | 0 | 22.9938 | 52.5 | 70.3431 | 3000 | 41.0869 | 3041.0869 | 3041.0869 | 0 | 151.8415
0 | 28.1853 | 0 | 0 | 0 | 0 | 24.3147 | 52.5 | 94.6578 | 3000 | 43.4472 | 3043.4472 | 3043.4472 | 0 | 146.3898
0 | 31.2851 | 0 | 0 | 0 | 0 | 21.2149 | 52.5 | 115.8727 | 3000 | 37.9081 | 3037.9081 | 3037.9081 | 0 | 138.4071
0 | 23.4303 | 0 | 0 | 0 | 0 | 29.0697 | 52.5 | 144.9424 | 3000 | 51.9437 | 3051.9437 | 3051.9437 | 0 | 130.0738
0 | 26.4315 | 0 | 0 | 0 | 0 | 26.0685 | 52.5 | 171.0109 | 3000 | 46.581 | 3046.581 | 3046.581 | 0 | 131.4295
0 | 26.0217 | 0 | 0 | 0 | 0 | 26.4783 | 52.5 | 197.4892 | 3000 | 47.3131 | 3047.3131 | 3047.3131 | 0 | 134.5693
0 | 26.3304 | 0 | 0 | 0 | 0 | 26.1696 | 52.5 | 223.6587 | 3000 | 46.7616 | 3046.7616 | 3046.7616 | 0 | 132.656
0 | 37.6278 | 0 | 0 | 0 | 0 | 14.8722 | 52.5 | 238.5309 | 3000 | 26.5746 | 3026.5746 | 3026.5746 | 0 | 135.8024
0 | 55.3752 | 0 | 0 | 0 | 0 | -2.8752 | 52.5 | 235.6557 | 3000 | 0 | 3000 | 3000 | 0 | 129.63
0 | 104.7936 | 0 | 0 | 0 | 0 | -52.2936 | 52.5 | 183.3621 | 3000 | 0 | 3000 | 2962.148 | 0 | 127.2539
0 | 94.4643 | 0 | 0 | 0 | 0 | -41.9643 | 52.5 | 141.3978 | 3000 | 0 | 3000 | 2735.0362 | 0 | 118.892
0 | 107.5715 | 0 | 0 | 0 | 0 | -55.0715 | 52.5 | 86.3263 | 3000 | 0 | 3000 | 2545.7763 | 0 | 104.3768
0 | 78.6543 | 0 | 0 | 0 | 0 | -26.1543 | 52.5 | 60.172 | 3000 | 0 | 3000 | 2242.9605 | 0 | 96.6043
0 | 44.0778 | 0 | 0 | 0 | 0 | 8.4222 | 52.5 | 68.5942 | 3000 | 15.0493 | 3015.0493 | 2106.6019 | 0 | 86.8763
0 | 41.9865 | 0 | 0 | 0 | 0 | 10.5135 | 52.5 | 79.1077 | 3000 | 18.7862 | 3018.7862 | 2029.2274 | 0 | 85.0449
0 | 69.0027 | 0 | 0 | 0 | 0 | -16.5027 | 52.5 | 62.605 | 3000 | 0 | 3000 | 1902.2927 | 0 | 79.0973
0 | 98.3088 | 0 | 0 | 0 | 0 | -45.8088 | 52.5 | 16.7962 | 3000 | 0 | 3000 | 1891.4778 | 0 | 75.47
0 | 60.6545 | 0 | 0 | 0 | 0 | -8.1545 | 52.5 | 8.6417 | 3000 | 0 | 3000 | 2059.108 | 0 | 82.4673
0 | 46.3062 | 0 | 0 | 0 | 0 | 6.1938 | 52.5 | 14.8355 | 3000 | 11.0675 | 3011.0675 | 2524.3992 | 0 | 104.7373
0 | 58.6439 | 0 | 0 | 0 | 0 | -6.1439 | 52.5 | 8.6916 | 3000 | 0 | 3000 | 2718.8139 | 0 | 114.9243
0 | 35.7291 | 0 | 0 | 0 | 0 | 16.7709 | 52.5 | 25.4626 | 3000 | 29.9674 | 3029.9674 | 2959.6709 | 0 | 147.9539
0 | 44.5818 | 0 | 0 | 0 | 0 | 7.9182 | 52.5 | 33.3808 | 3000 | 14.1488 | 3014.1488 | 3008.7414 | 0 | 162.5021
0 | 38.8529 | 0 | 0 | 0 | 0 | 13.6471 | 52.5 | 47.0278 | 3000 | 24.3855 | 3024.3855 | 3024.3855 | 0 | 169.2749
0 | 37.0449 | 0 | 0 | 0 | 0 | 15.4551 | 52.5 | 62.4829 | 3000 | 27.6162 | 3027.6162 | 3027.6162 | 0 | 161.9775
0 | 31.3802 | 0 | 0 | 0 | 0 | 21.1198 | 52.5 | 83.6027 | 3000 | 37.7382 | 3037.7382 | 3037.7382 | 0 | 150.1858
0 | 23.7302 | 0 | 0 | 0 | 0 | 28.7698 | 52.5 | 112.3725 | 3000 | 51.4077 | 3051.4077 | 3051.4077 | 0 | 147.6881
0 | 25.7037 | 0 | 0 | 0 | 0 | 26.7963 | 52.5 | 139.1688 | 3000 | 47.8815 | 3047.8815 | 3047.8815 | 0 | 143.22
0 | 35.9368 | 0 | 0 | 0 | 0 | 16.5632 | 52.5 | 155.732 | 3000 | 29.5962 | 3029.5962 | 3029.5962 | 0 | 129.2426
0 | 23.4538 | 0 | 0 | 0 | 0 | 29.0462 | 52.5 | 184.7782 | 3000 | 51.9017 | 3051.9017 | 3051.9017 | 0 | 128.7903
0 | 38.6866 | 0 | 0 | 0 | 0 | 13.8134 | 52.5 | 198.5916 | 3000 | 24.6827 | 3024.6827 | 3024.6827 | 0 | 128.1861
0 | 25.1021 | 0 | 0 | 0 | 0 | 27.3979 | 52.5 | 225.9895 | 3000 | 48.9564 | 3048.9564 | 3048.9564 | 0 | 126.0134
0 | 37.7805 | 0 | 0 | 0 | 0 | 14.7195 | 52.5 | 240.709 | 3000 | 26.3018 | 3026.3018 | 3026.3018 | 0 | 122.0508
0 | 30.9258 | 0 | 0 | 0 | 0 | 21.5742 | 52.5 | 262.2833 | 3000 | 38.5503 | 3038.5503 | 3038.5503 | 0 | 140.7153
0 | 33.2887 | 0 | 0 | 0 | 0 | 19.2113 | 52.5 | 281.4946 | 3000 | 34.3281 | 3034.3281 | 3028.9207 | 0 | 161.6535
0 | 31.758 | 0 | 0 | 0 | 0 | 20.742 | 52.5 | 302.2367 | 3000 | 37.0633 | 3037.0633 | 2988.3965 | 0 | 191.2275
0 | 48.3117 | 0 | 0 | 0 | 0 | 4.1883 | 52.5 | 306.425 | 3000 | 7.484 | 3007.484 | 2856.076 | 0 | 185.6449
0 | 254.935 | 0 | 0 | 0 | 0 | -202.435 | 52.5 | 103.99 | 3000 | 0 | 3000 | 2778.2956 | 0 | 180.1447
0 | 43.3252 | 0 | 0 | 0 | 0 | 9.1748 | 52.5 | 113.1648 | 3000 | 16.3942 | 3016.3942 | 2756.8378 | 0 | 179.1669
0 | 49.1025 | 0 | 0 | 0 | 0 | 3.3975 | 52.5 | 116.5623 | 3000 | 6.0709 | 3006.0709 | 2568.0694 | 0 | 165.0498
0 | 57.8031 | 0 | 0 | 0 | 0 | -5.3031 | 52.5 | 111.2592 | 3000 | 0 | 3000 | 2513.3317 | 0 | 152.0063
0 | 37.8575 | 0 | 0 | 0 | 0 | 14.6425 | 52.5 | 125.9017 | 3000 | 26.1641 | 3026.1641 | 2355.6434 | 0 | 137.4989
0 | 39.1035 | 0 | 0 | 0 | 0 | 13.3965 | 52.5 | 139.2982 | 3000 | 23.9378 | 3023.9378 | 2256.0834 | 0 | 124.3779
0 | 35.1047 | 0 | 0 | 0 | 0 | 17.3953 | 52.5 | 156.6935 | 3000 | 31.0831 | 3031.0831 | 2511.9703 | 0 | 139.6404
0 | 37.886 | 0 | 0 | 0 | 0 | 14.614 | 52.5 | 171.3075 | 3000 | 26.1133 | 3026.1133 | 2761.1495 | 0 | 156.5572
0 | 51.7366 | 0 | 0 | 0 | 0 | 0.76336 | 52.5 | 172.0709 | 3000 | 1.364 | 3001.364 | 2898.6229 | 0 | 188.7004
0 | 51.7666 | 0 | 0 | 0 | 0 | 0.73337 | 52.5 | 172.8043 | 3000 | 1.3104 | 3001.3104 | 2990.4956 | 0 | 202.4266
0 | 46.4157 | 0 | 0 | 0 | 0 | -46.4157 | 0 | 126.3885 | 0 | 0 | 0 | 0 | 0 | 0
0 | 33.2741 | 0 | 0 | 0 | 0 | 19.2259 | 52.5 | 145.6145 | 3000 | 34.3542 | 3034.3542 | 3034.3542 | 0 | 205.8809
0 | 26.2245 | 0 | 0 | 0 | 0 | 26.2755 | 52.5 | 171.89 | 3000 | 46.9508 | 3046.9508 | 3046.9508 | 0 | 195.6447
0 | 30.821 | 0 | 0 | 0 | 0 | 21.679 | 52.5 | 193.569 | 3000 | 38.7376 | 3038.7376 | 3038.7376 | 0 | 175.791
0 | 22.033 | 0 | 0 | 0 | 0 | 30.467 | 52.5 | 224.036 | 3000 | 54.4404 | 3054.4404 | 3054.4404 | 0 | 145.7274
0 | 30.603 | 0 | 0 | 0 | 0 | 21.897 | 52.5 | 245.933 | 3000 | 39.1271 | 3039.1271 | 3039.1271 | 0 | 144.9664
0 | 35.4725 | 0 | 0 | 0 | 0 | 17.0275 | 52.5 | 262.9605 | 3000 | 30.4258 | 3030.4258 | 3030.4258 | 0 | 137.5813
0 | 22.9642 | 0 | 0 | 0 | 0 | 29.5358 | 52.5 | 292.4963 | 3000 | 52.7765 | 3052.7765 | 3052.7765 | 0 | 139.6035
0 | 37.0638 | 0 | 0 | 0 | 0 | 15.4362 | 52.5 | 307.9325 | 3000 | 27.5824 | 3027.5824 | 3027.5824 | 0 | 137.0284
0 | 94.9574 | 0 | 0 | 0 | 0 | -42.4574 | 52.5 | 265.4751 | 3000 | 0 | 3000 | 3000 | 0 | 133.86
0 | 116.4975 | 0 | 0 | 0 | 0 | -63.9975 | 52.5 | 201.4776 | 3000 | 0 | 3000 | 3000 | 0 | 142.71
0 | 109.4141 | 0 | 0 | 0 | 0 | -56.9141 | 52.5 | 144.5636 | 3000 | 0 | 3000 | 2983.7777 | 0 | 164.4062
0 | 81.3587 | 0 | 0 | 0 | 0 | -28.8587 | 52.5 | 115.7049 | 3000 | 0 | 3000 | 2881.0366 | 0 | 187.5555
0 | 115.5017 | 0 | 0 | 0 | 0 | -110.1078 | 5.3939 | 5.5971 | 308.2232 | 0 | 308.2232 | 0 | 0 | 0
0 | 58.0971 | 0 | 0 | 0 | 0 | -5.5971 | 52.5 | 0 | 3000 | 0 | 3000 | 2659.3322 | 0 | 180.941
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2540.3689 | 0 | 170.0269
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2140.2194 | 0 | 140.9548
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2226.7382 | 0 | 139.0821
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2735.0362 | 0 | 162.9261
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2870.2218 | 0 | 164.2341
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2891.8515 | 0 | 164.1415
0 | 35.2642 | 0 | 0 | 0 | 0 | 17.2358 | 52.5 | 17.2358 | 3000 | 30.7982 | 3030.7982 | 2955.0942 | 0 | 186.2891
0 | 43.8031 | 0 | 0 | 0 | 0 | 8.6969 | 52.5 | 25.9327 | 3000 | 15.5402 | 3015.5402 | 2988.5031 | 0 | 209.0757
0 | 25.9327 | 0 | 0 | 0 | 0 | -25.9327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 207.18
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 195
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 181.26
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 150.69
0 | 30.8027 | 0 | 0 | 0 | 0 | 21.6973 | 52.5 | 21.6973 | 3000 | 38.7701 | 3038.7701 | 3038.7701 | 0 | 143.43
0 | 24.7373 | 0 | 0 | 0 | 0 | 27.7627 | 52.5 | 49.46 | 3000 | 49.6083 | 3049.6083 | 3049.6083 | 0 | 140.5564
0 | 31.0281 | 0 | 0 | 0 | 0 | 21.4719 | 52.5 | 70.9319 | 3000 | 38.3675 | 3038.3675 | 3038.3675 | 0 | 137.2431
0 | 47.9992 | 0 | 0 | 0 | 0 | 4.5008 | 52.5 | 75.4327 | 3000 | 8.0424 | 3008.0424 | 3008.0424 | 0 | 133.6774
0 | 89.8174 | 0 | 0 | 0 | 0 | -37.3174 | 52.5 | 38.1154 | 3000 | 0 | 3000 | 3000 | 0 | 129.57
0 | 75.1776 | 0 | 0 | 0 | 0 | -22.6776 | 52.5 | 15.4378 | 3000 | 0 | 3000 | 3000 | 0 | 126.66
0 | 58.8746 | 0 | 0 | 0 | 0 | -6.3746 | 52.5 | 9.0632 | 3000 | 0 | 3000 | 3000 | 0 | 137.28
0 | 61.5632 | 0 | 0 | 0 | 0 | -9.0632 | 52.5 | 0 | 3000 | 0 | 3000 | 2989.1851 | 0 | 155.0789
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2902.6663 | 0 | 183.0421
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.8525 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 167.6302 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2751.2584 | 0 | 178.4466
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2578.2208 | 0 | 147.9899
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2610.6654 | 0 | 145.153
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2735.0362 | 0 | 150.1535
0 | 50.1496 | 0 | 0 | 0 | 0 | 2.3504 | 52.5 | 2.3504 | 3000 | 4.1999 | 3004.1999 | 2533.7539 | 0 | 137.2534
0 | 43.1955 | 0 | 0 | 0 | 0 | 9.3045 | 52.5 | 11.6549 | 3000 | 16.6258 | 3016.6258 | 2492.1056 | 0 | 136.8166
0 | 50.9742 | 0 | 0 | 0 | 0 | 1.5258 | 52.5 | 13.1807 | 3000 | 2.7264 | 3002.7264 | 2748.5775 | 0 | 152.8209
0 | 34.7655 | 0 | 0 | 0 | 0 | 17.7345 | 52.5 | 30.9151 | 3000 | 31.6891 | 3031.6891 | 2972.2075 | 0 | 193.1638
0 | 46.4688 | 0 | 0 | 0 | 0 | 6.0312 | 52.5 | 36.9464 | 3000 | 10.777 | 3010.777 | 3005.3696 | 0 | 207.9415
0 | 36.9464 | 0 | 0 | 0 | 0 | -36.9464 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 200.22
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 166.8
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 145.74
0 | 52.0386 | 0 | 0 | 0 | 0 | 0.46136 | 52.5 | 0.46136 | 3000 | 0.82439 | 3000.8244 | 3000.8244 | 0 | 144.9398
0 | 32.7935 | 0 | 0 | 0 | 0 | 19.7065 | 52.5 | 20.1679 | 3000 | 35.2129 | 3035.2129 | 3035.2129 | 0 | 135.4008
0 | 72.6679 | 0 | 0 | 0 | 0 | -20.1679 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 142.71
0 | 23.1164 | 0 | 0 | 0 | 0 | 29.3836 | 52.5 | 29.3836 | 3000 | 52.5045 | 3052.5045 | 3052.5045 | 0 | 137.668
0 | 43.1234 | 0 | 0 | 0 | 0 | 9.3766 | 52.5 | 38.7602 | 3000 | 16.7548 | 3016.7548 | 3016.7548 | 0 | 124.773
0 | 81.2859 | 0 | 0 | 0 | 0 | -28.7859 | 52.5 | 9.9743 | 3000 | 0 | 3000 | 3000 | 0 | 126.09
0 | 62.4743 | 0 | 0 | 0 | 0 | -9.9743 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 136.05
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2989.1851 | 0 | 174.8673
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2924.296 | 0 | 190.9273
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2870.2218 | 0 | 190.8985
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2908.0738 | 0 | 190.1299
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2816.1475 | 0 | 179.3604
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2794.5178 | 0 | 171.3598
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2789.1104 | 0 | 160.0949
0 | 33.186 | 0 | 0 | 0 | 0 | 19.314 | 52.5 | 19.314 | 3000 | 34.5115 | 3034.5115 | 2877.6962 | 0 | 152.3165
0 | 45.2478 | 0 | 0 | 0 | 0 | 7.2522 | 52.5 | 26.5662 | 3000 | 12.9587 | 3012.9587 | 2883.1805 | 0 | 149.3488
0 | 53.3233 | 0 | 0 | 0 | 0 | -0.82334 | 52.5 | 25.7428 | 3000 | 0 | 3000 | 2902.6663 | 0 | 145.4526
0 | 29.6684 | 0 | 0 | 0 | 0 | 22.8316 | 52.5 | 48.5744 | 3000 | 40.797 | 3040.797 | 2975.9079 | 0 | 149.837
0 | 52.556 | 0 | 0 | 0 | 0 | -0.05601 | 52.5 | 48.5184 | 3000 | 0 | 3000 | 2956.7406 | 0 | 166.228
0 | 46.0963 | 0 | 0 | 0 | 0 | 6.4037 | 52.5 | 54.9221 | 3000 | 11.4425 | 3011.4425 | 3006.0351 | 0 | 180.3621
0 | 107.4221 | 0 | 0 | 0 | 0 | -54.9221 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 162
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 154.77
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 144.42
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 136.83
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 134.31
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 132.15
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 128.22
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 127.23
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 119.4
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 117.78
0 | 48.4917 | 0 | 0 | 0 | 0 | 4.0083 | 52.5 | 4.0083 | 3000 | 7.1623 | 3007.1623 | 3007.1623 | 0 | 125.0378
0 | 56.5083 | 0 | 0 | 0 | 0 | -4.0083 | 52.5 | 0 | 3000 | 0 | 3000 | 2989.1851 | 0 | 167.6933
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2918.8886 | 0 | 184.97
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2729.6287 | 0 | 178.2721
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2637.7025 | 0 | 171.5562
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2307.8496 | 0 | 140.4788
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2221.3308 | 0 | 124.7499
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2459.2575 | 0 | 122.1759
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2583.6283 | 0 | 123.2391
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2610.6654 | 0 | 119.3335
0 | 50.7984 | 0 | 0 | 0 | 0 | 1.7016 | 52.5 | 1.7016 | 3000 | 3.0406 | 3003.0406 | 2748.8916 | 0 | 128.8955
0 | 49.8485 | 0 | 0 | 0 | 0 | 2.6515 | 52.5 | 4.3531 | 3000 | 4.7379 | 3004.7379 | 2734.3666 | 0 | 130.3473
0 | 40.4151 | 0 | 0 | 0 | 0 | 12.0849 | 52.5 | 16.438 | 3000 | 21.594 | 3021.594 | 2945.8901 | 0 | 165.2644
0 | 56.2668 | 0 | 0 | 0 | 0 | -3.7668 | 52.5 | 12.6712 | 3000 | 0 | 3000 | 2994.5926 | 0 | 180.0649
0 | 65.1712 | 0 | 0 | 0 | 0 | -12.6712 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 189.87
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 187.47
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 150.42
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 144.24
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 134.97
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 124.5
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 112.5
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 114
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 106.92
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 107.58
0 | 41.5869 | 0 | 0 | 0 | 0 | 10.9131 | 52.5 | 10.9131 | 3000 | 19.5002 | 3019.5002 | 3019.5002 | 0 | 113.9257
0 | 63.4131 | 0 | 0 | 0 | 0 | -10.9131 | 52.5 | 0 | 3000 | 0 | 3000 | 2989.1851 | 0 | 118.9696
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2918.8886 | 0 | 123.936
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2605.258 | 0 | 125.5734
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2405.1832 | 0 | 119.249
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2291.6273 | 0 | 110.3648
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2059.108 | 0 | 97.6429
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2475.4798 | 0 | 113.4512
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2345.7015 | 0 | 103.9615
0 | 47.9185 | 0 | 0 | 0 | 0 | 4.5815 | 52.5 | 4.5815 | 3000 | 8.1866 | 3008.1866 | 2543.148 | 0 | 112.0002
0 | 38.699 | 0 | 0 | 0 | 0 | 13.801 | 52.5 | 18.3826 | 3000 | 24.6606 | 3024.6606 | 2581.2518 | 0 | 113.5235
0 | 39.8558 | 0 | 0 | 0 | 0 | 12.6442 | 52.5 | 31.0268 | 3000 | 22.5935 | 3022.5935 | 2838.741 | 0 | 119.5678
0 | 52.6649 | 0 | 0 | 0 | 0 | -0.16492 | 52.5 | 30.8618 | 3000 | 0 | 3000 | 2886.4441 | 0 | 136.4711
0 | 83.3618 | 0 | 0 | 0 | 0 | -30.8618 | 52.5 | 0 | 3000 | 0 | 3000 | 2994.5926 | 0 | 159.2824
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 176.07
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 149.7
0 | 26.5757 | 0 | 0 | 0 | 0 | 25.9243 | 52.5 | 25.9243 | 3000 | 46.3234 | 3046.3234 | 3046.3234 | 0 | 137.4501
0 | 35.9259 | 0 | 0 | 0 | 0 | 16.5741 | 52.5 | 42.4984 | 3000 | 29.6157 | 3029.6157 | 3029.6157 | 0 | 138.3928
0 | 25.0349 | 0 | 0 | 0 | 0 | 27.4651 | 52.5 | 69.9636 | 3000 | 49.0766 | 3049.0766 | 3049.0766 | 0 | 139.7392
0 | 24.8055 | 0 | 0 | 0 | 0 | 27.6945 | 52.5 | 97.6581 | 3000 | 49.4864 | 3049.4864 | 3049.4864 | 0 | 142.5635
0 | 35.7207 | 0 | 0 | 0 | 0 | 16.7793 | 52.5 | 114.4374 | 3000 | 29.9824 | 3029.9824 | 3029.9824 | 0 | 139.6216
0 | 25.4596 | 0 | 0 | 0 | 0 | 27.0404 | 52.5 | 141.4778 | 3000 | 48.3176 | 3048.3176 | 3048.3176 | 0 | 131.6873
0 | 36.3928 | 0 | 0 | 0 | 0 | 16.1072 | 52.5 | 157.585 | 3000 | 28.7814 | 3028.7814 | 3028.7814 | 0 | 115.0937
0 | 43.0038 | 0 | 0 | 0 | 0 | 9.4962 | 52.5 | 167.0812 | 3000 | 16.9684 | 3016.9684 | 3016.9684 | 0 | 98.2627
0 | 102.8618 | 0 | 0 | 0 | 0 | -50.3618 | 52.5 | 116.7194 | 3000 | 0 | 3000 | 3000 | 0 | 84.24
0 | 113.586 | 0 | 0 | 0 | 0 | -61.086 | 52.5 | 55.6334 | 3000 | 0 | 3000 | 3000 | 0 | 99.33
0 | 108.1334 | 0 | 0 | 0 | 0 | -55.6334 | 52.5 | 0 | 3000 | 0 | 3000 | 2972.9629 | 0 | 113.2402
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2962.148 | 0 | 115.583
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2875.6292 | 0 | 119.6837
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2816.1475 | 0 | 132.3871
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2816.1475 | 0 | 129.2048
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2724.2213 | 0 | 127.4936
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2886.4441 | 0 | 134.5949
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2881.0366 | 0 | 134.4004
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2886.4441 | 0 | 134.364
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2945.9257 | 0 | 137.6337
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2962.148 | 0 | 140.5243
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2994.5926 | 0 | 145.088
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 155.43
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 159
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 147
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 144
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 134.1
0 | 30.6583 | 0 | 0 | 0 | 0 | 21.8417 | 52.5 | 21.8417 | 3000 | 39.0282 | 3039.0282 | 3039.0282 | 0 | 120.0416
0 | 22.2006 | 0 | 0 | 0 | 0 | 30.2994 | 52.5 | 52.1411 | 3000 | 54.141 | 3054.141 | 3054.141 | 0 | 116.0574
0 | 34.0768 | 0 | 0 | 0 | 0 | 18.4232 | 52.5 | 70.5643 | 3000 | 32.9198 | 3032.9198 | 3032.9198 | 0 | 119.497
0 | 30.5159 | 0 | 0 | 0 | 0 | 21.9841 | 52.5 | 92.5483 | 3000 | 39.2826 | 3039.2826 | 3039.2826 | 0 | 122.1792
0 | 27.0941 | 0 | 0 | 0 | 0 | 25.4059 | 52.5 | 117.9542 | 3000 | 45.3969 | 3045.3969 | 3045.3969 | 0 | 121.5113
0 | 43.6206 | 0 | 0 | 0 | 0 | 8.8794 | 52.5 | 126.8337 | 3000 | 15.8664 | 3015.8664 | 3015.8664 | 0 | 117.6188
0 | 113.3714 | 0 | 0 | 0 | 0 | -60.8714 | 52.5 | 65.9622 | 3000 | 0 | 3000 | 2989.1851 | 0 | 134.2144
0 | 92.4617 | 0 | 0 | 0 | 0 | -39.9617 | 52.5 | 26.0005 | 3000 | 0 | 3000 | 2843.1847 | 0 | 172.5813
0 | 78.5005 | 0 | 0 | 0 | 0 | -26.0005 | 52.5 | 0 | 3000 | 0 | 3000 | 2540.3689 | 0 | 149.9326
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2415.9981 | 0 | 153.2226
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2091.5526 | 0 | 96.2114
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2264.5902 | 0 | 97.8303
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 1999.6263 | 0 | 78.9852
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2123.9971 | 0 | 90.0575
0 | 43.8003 | 0 | 0 | 0 | 0 | 8.6997 | 52.5 | 8.6997 | 3000 | 15.5451 | 3015.5451 | 2247.6907 | 0 | 97.1002
0 | 40.278 | 0 | 0 | 0 | 0 | 12.222 | 52.5 | 20.9216 | 3000 | 21.8391 | 3021.8391 | 2475.6891 | 0 | 120.4175
0 | 41.2322 | 0 | 0 | 0 | 0 | 11.2678 | 52.5 | 32.1894 | 3000 | 20.1341 | 3020.1341 | 2647.0217 | 0 | 145.9303
0 | 45.5319 | 0 | 0 | 0 | 0 | 6.9681 | 52.5 | 39.1575 | 3000 | 12.451 | 3012.451 | 2947.5619 | 0 | 194.3033
0 | 39.1575 | 0 | 0 | 0 | 0 | -39.1575 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 25.6447 | 0 | 0 | 0 | 0 | 26.8553 | 52.5 | 26.8553 | 3000 | 47.9868 | 3047.9868 | 3047.9868 | 0 | 195.8941
0 | 34.5652 | 0 | 0 | 0 | 0 | 17.9348 | 52.5 | 44.79 | 3000 | 32.047 | 3032.047 | 3032.047 | 0 | 180.6494
0 | 31.0793 | 0 | 0 | 0 | 0 | 21.4207 | 52.5 | 66.2107 | 3000 | 38.2759 | 3038.2759 | 3038.2759 | 0 | 150.6985
0 | 19.3349 | 0 | 0 | 0 | 0 | 33.1651 | 52.5 | 99.3758 | 3000 | 59.2616 | 3059.2616 | 3059.2616 | 0 | 147.1199
0 | 28.0176 | 0 | 0 | 0 | 0 | 24.4824 | 52.5 | 123.8582 | 3000 | 43.7469 | 3043.7469 | 3043.7469 | 0 | 137.76
0 | 31.1271 | 0 | 0 | 0 | 0 | 21.3729 | 52.5 | 145.2311 | 3000 | 38.1905 | 3038.1905 | 3038.1905 | 0 | 129.6092
0 | 36.0212 | 0 | 0 | 0 | 0 | 16.4788 | 52.5 | 161.7099 | 3000 | 29.4455 | 3029.4455 | 3029.4455 | 0 | 136.9309
0 | 50.2637 | 0 | 0 | 0 | 0 | 2.2363 | 52.5 | 163.9462 | 3000 | 3.9959 | 3003.9959 | 3003.9959 | 0 | 122.563
0 | 108.1155 | 0 | 0 | 0 | 0 | -55.6155 | 52.5 | 108.3307 | 3000 | 0 | 3000 | 3000 | 0 | 144.03
0 | 93.2683 | 0 | 0 | 0 | 0 | -40.7683 | 52.5 | 67.5624 | 3000 | 0 | 3000 | 2994.5926 | 0 | 180.9932
0 | 86.5814 | 0 | 0 | 0 | 0 | -34.0814 | 52.5 | 33.4811 | 3000 | 0 | 3000 | 2978.3703 | 0 | 196.5129
0 | 85.9811 | 0 | 0 | 0 | 0 | -33.4811 | 52.5 | 0 | 3000 | 0 | 3000 | 2924.296 | 0 | 193.1205
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2821.555 | 0 | 182.3571
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2540.3689 | 0 | 157.1472
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2529.554 | 0 | 151.5709
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2675.5545 | 0 | 152.9614
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2691.7768 | 0 | 150.8472
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2637.7025 | 0 | 143.7284
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2908.0738 | 0 | 158.1411
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2956.7406 | 0 | 171.1361
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2972.9629 | 0 | 187.8913
0 | 46.9596 | 0 | 0 | 0 | 0 | 5.5404 | 52.5 | 5.5404 | 3000 | 9.9 | 3009.9 | 3009.9 | 0 | 196.1251
0 | 34.0619 | 0 | 0 | 0 | 0 | 18.4381 | 52.5 | 23.9786 | 3000 | 32.9465 | 3032.9465 | 3032.9465 | 0 | 212.2759
0 | 27.6825 | 0 | 0 | 0 | 0 | 24.8175 | 52.5 | 48.796 | 3000 | 44.3455 | 3044.3455 | 3044.3455 | 0 | 206.7719
0 | 29.9527 | 0 | 0 | 0 | 0 | 22.5473 | 52.5 | 71.3433 | 3000 | 40.289 | 3040.289 | 3040.289 | 0 | 197.6796
0 | 23.0972 | 0 | 0 | 0 | 0 | 29.4028 | 52.5 | 100.7461 | 3000 | 52.539 | 3052.539 | 3052.539 | 0 | 183.3355
0 | 28.9359 | 0 | 0 | 0 | 0 | 23.5641 | 52.5 | 124.3102 | 3000 | 42.1058 | 3042.1058 | 3042.1058 | 0 | 153.4438
0 | 31.3289 | 0 | 0 | 0 | 0 | 21.1711 | 52.5 | 145.4813 | 3000 | 37.8299 | 3037.8299 | 3037.8299 | 0 | 147.3044
0 | 30.4567 | 0 | 0 | 0 | 0 | 22.0433 | 52.5 | 167.5245 | 3000 | 39.3884 | 3039.3884 | 3039.3884 | 0 | 137.198
0 | 21.3122 | 0 | 0 | 0 | 0 | 31.1878 | 52.5 | 198.7123 | 3000 | 55.7284 | 3055.7284 | 3055.7284 | 0 | 135.216
0 | 27.6926 | 0 | 0 | 0 | 0 | 24.8074 | 52.5 | 223.5197 | 3000 | 44.3275 | 3044.3275 | 3044.3275 | 0 | 126.9789
0 | 24.7581 | 0 | 0 | 0 | 0 | 27.7419 | 52.5 | 251.2616 | 3000 | 49.571 | 3049.571 | 3049.571 | 0 | 127.2891
0 | 41.1436 | 0 | 0 | 0 | 0 | 11.3564 | 52.5 | 262.618 | 3000 | 20.2923 | 3020.2923 | 3020.2923 | 0 | 130.4766
0 | 88.9687 | 0 | 0 | 0 | 0 | -36.4687 | 52.5 | 226.1493 | 3000 | 0 | 3000 | 2994.5926 | 0 | 175.9323
0 | 106.0777 | 0 | 0 | 0 | 0 | -53.5777 | 52.5 | 172.5715 | 3000 | 0 | 3000 | 2816.1475 | 0 | 188.0905
0 | 85.7812 | 0 | 0 | 0 | 0 | -33.2812 | 52.5 | 139.2903 | 3000 | 0 | 3000 | 2551.1837 | 0 | 171.9498
0 | 86.687 | 0 | 0 | 0 | 0 | -34.187 | 52.5 | 105.1033 | 3000 | 0 | 3000 | 2253.7753 | 0 | 150.4395
0 | 77.746 | 0 | 0 | 0 | 0 | -25.246 | 52.5 | 79.8573 | 3000 | 0 | 3000 | 2253.7753 | 0 | 146.4954
0 | 61.2557 | 0 | 0 | 0 | 0 | -8.7557 | 52.5 | 71.1015 | 3000 | 0 | 3000 | 2145.6268 | 0 | 131.6986
0 | 47.9081 | 0 | 0 | 0 | 0 | 4.5919 | 52.5 | 75.6934 | 3000 | 8.2051 | 3008.2051 | 2099.7576 | 0 | 109.1034
0 | 128.1934 | 0 | 0 | 0 | 0 | -75.6934 | 52.5 | 0 | 3000 | 0 | 3000 | 2313.257 | 0 | 115.4315
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2280.8124 | 0 | 112.8318
0 | 31.9385 | 0 | 0 | 0 | 0 | 20.5615 | 52.5 | 20.5615 | 3000 | 36.7406 | 3036.7406 | 2544.6649 | 0 | 125.9609
0 | 47.7342 | 0 | 0 | 0 | 0 | 4.7658 | 52.5 | 25.3273 | 3000 | 8.5159 | 3008.5159 | 2727.3298 | 0 | 135.7119
0 | 38.8839 | 0 | 0 | 0 | 0 | 13.6161 | 52.5 | 38.9434 | 3000 | 24.3301 | 3024.3301 | 2964.8484 | 0 | 164.4601
0 | 37.6246 | 0 | 0 | 0 | 0 | 14.8754 | 52.5 | 53.8187 | 3000 | 26.5803 | 3026.5803 | 3026.5803 | 0 | 190.7048
0 | 40.9393 | 0 | 0 | 0 | 0 | 11.5607 | 52.5 | 65.3794 | 3000 | 20.6574 | 3020.6574 | 3020.6574 | 0 | 201.206
0 | 25.3038 | 0 | 0 | 0 | 0 | 27.1962 | 52.5 | 92.5756 | 3000 | 48.596 | 3048.596 | 3048.596 | 0 | 189.5007
0 | 29.722 | 0 | 0 | 0 | 0 | 22.778 | 52.5 | 115.3536 | 3000 | 40.7012 | 3040.7012 | 3040.7012 | 0 | 158.5118
0 | 29.0632 | 0 | 0 | 0 | 0 | 23.4368 | 52.5 | 138.7904 | 3000 | 41.8784 | 3041.8784 | 3041.8784 | 0 | 151.1509
0 | 26.4501 | 0 | 0 | 0 | 0 | 26.0499 | 52.5 | 164.8403 | 3000 | 46.5477 | 3046.5477 | 3046.5477 | 0 | 133.2865
0 | 27.53 | 0 | 0 | 0 | 0 | 24.97 | 52.5 | 189.8102 | 3000 | 44.618 | 3044.618 | 3044.618 | 0 | 125.4687
0 | 28.6478 | 0 | 0 | 0 | 0 | 23.8522 | 52.5 | 213.6625 | 3000 | 42.6208 | 3042.6208 | 3042.6208 | 0 | 125.9949
0 | 24.8045 | 0 | 0 | 0 | 0 | 27.6955 | 52.5 | 241.3579 | 3000 | 49.4881 | 3049.4881 | 3049.4881 | 0 | 122.8944
0 | 35.1009 | 0 | 0 | 0 | 0 | 17.3991 | 52.5 | 258.7571 | 3000 | 31.0899 | 3031.0899 | 3031.0899 | 0 | 122.3045
0 | 102.3566 | 0 | 0 | 0 | 0 | -49.8566 | 52.5 | 208.9005 | 3000 | 0 | 3000 | 3000 | 0 | 124.29
0 | 82.7916 | 0 | 0 | 0 | 0 | -30.2916 | 52.5 | 178.6089 | 3000 | 0 | 3000 | 3000 | 0 | 132.93
0 | 82.6633 | 0 | 0 | 0 | 0 | -30.1633 | 52.5 | 148.4456 | 3000 | 0 | 3000 | 2983.7777 | 0 | 150.1437
0 | 80.2528 | 0 | 0 | 0 | 0 | -27.7528 | 52.5 | 120.6927 | 3000 | 0 | 3000 | 2870.2218 | 0 | 183.6942
0 | 109.9273 | 0 | 0 | 0 | 0 | -57.4273 | 52.5 | 63.2654 | 3000 | 0 | 3000 | 2729.6287 | 0 | 178.7907
0 | 70.7412 | 0 | 0 | 0 | 0 | -63.2654 | 7.4758 | 0 | 427.1866 | 0 | 427.1866 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2069.9229 | 0 | 133.8619
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2172.6639 | 0 | 135.9436
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2318.6644 | 0 | 133.1841
0 | 30.0683 | 0 | 0 | 0 | 0 | 22.4317 | 52.5 | 22.4317 | 3000 | 40.0825 | 3040.0825 | 2045.1162 | 0 | 108.023
0 | 57.4686 | 0 | 0 | 0 | 0 | -4.9686 | 52.5 | 17.4631 | 3000 | 0 | 3000 | 2421.4055 | 0 | 125.2835
0 | 69.9631 | 0 | 0 | 0 | 0 | -17.4631 | 52.5 | 0 | 3000 | 0 | 3000 | 2513.3317 | 0 | 130.3414
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2799.9253 | 0 | 155.1159
0 | 31.032 | 0 | 0 | 0 | 0 | 21.468 | 52.5 | 21.468 | 3000 | 38.3605 | 3038.3605 | 3000.5085 | 0 | 188.822
0 | 55.6354 | 0 | 0 | 0 | 0 | -3.1354 | 52.5 | 18.3327 | 3000 | 0 | 3000 | 3000 | 0 | 198.69
0 | 18.3327 | 0 | 0 | 0 | 0 | -18.3327 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 205.59
0 | 46.5871 | 0 | 0 | 0 | 0 | 5.9129 | 52.5 | 5.9129 | 3000 | 10.5655 | 3010.5655 | 3010.5655 | 0 | 189.8463
0 | 35.5015 | 0 | 0 | 0 | 0 | 16.9985 | 52.5 | 22.9114 | 3000 | 30.374 | 3030.374 | 3030.374 | 0 | 183.6104
0 | 75.4114 | 0 | 0 | 0 | 0 | -22.9114 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 152.79
0 | 27.1956 | 0 | 0 | 0 | 0 | 25.3044 | 52.5 | 25.3044 | 3000 | 45.2156 | 3045.2156 | 3045.2156 | 0 | 159.8434
0 | 57.0243 | 0 | 0 | 0 | 0 | -4.5243 | 52.5 | 20.7801 | 3000 | 0 | 3000 | 3000 | 0 | 136.71
0 | 73.2801 | 0 | 0 | 0 | 0 | -20.7801 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 127.26
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 127.26
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 121.44
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 128.82
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 169.5
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2972.9629 | 0 | 189.5264
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2902.6663 | 0 | 188.8475
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2913.4812 | 0 | 188.3857
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2832.3698 | 0 | 179.7988
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2826.9624 | 0 | 179.0315
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2859.4069 | 0 | 182.6303
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2924.296 | 0 | 181.2186
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2913.4812 | 0 | 172.4781
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2913.4812 | 0 | 178.4799
0 | 44.3285 | 0 | 0 | 0 | 0 | 8.1715 | 52.5 | 8.1715 | 3000 | 14.6014 | 3014.6014 | 2987.5643 | 0 | 182.3908
0 | 50.7905 | 0 | 0 | 0 | 0 | 1.7095 | 52.5 | 9.881 | 3000 | 3.0546 | 3003.0546 | 2981.4249 | 0 | 193.9417
0 | 56.8575 | 0 | 0 | 0 | 0 | -4.3575 | 52.5 | 5.5235 | 3000 | 0 | 3000 | 3000 | 0 | 195.81
0 | 58.0235 | 0 | 0 | 0 | 0 | -5.5235 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 205.56
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 192.66
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 166.5
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 152.61
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 149.7
0 | 44.2426 | 0 | 0 | 0 | 0 | 8.2574 | 52.5 | 8.2574 | 3000 | 14.7549 | 3014.7549 | 3014.7549 | 0 | 137.1713
0 | 25.0061 | 0 | 0 | 0 | 0 | 27.4939 | 52.5 | 35.7513 | 3000 | 49.1279 | 3049.1279 | 3049.1279 | 0 | 145.6263
0 | 47.4966 | 0 | 0 | 0 | 0 | 5.0034 | 52.5 | 40.7547 | 3000 | 8.9404 | 3008.9404 | 3008.9404 | 0 | 133.2359
0 | 86.4489 | 0 | 0 | 0 | 0 | -33.9489 | 52.5 | 6.8058 | 3000 | 0 | 3000 | 3000 | 0 | 130.2
0 | 59.3058 | 0 | 0 | 0 | 0 | -6.8058 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 133.8
0 | 43.5821 | 0 | 0 | 0 | 0 | 8.9179 | 52.5 | 8.9179 | 3000 | 15.9352 | 3015.9352 | 3015.9352 | 0 | 135.1139
0 | 61.4179 | 0 | 0 | 0 | 0 | -8.9179 | 52.5 | 0 | 3000 | 0 | 3000 | 2994.5926 | 0 | 132.6605
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2881.0366 | 0 | 133.997
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2534.9614 | 0 | 131.894
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2232.1456 | 0 | 130.0225
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2021.256 | 0 | 111.0882
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2075.3303 | 0 | 109.3699
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2134.812 | 0 | 111.3945
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2210.5159 | 0 | 113.8637
0 | 44.2145 | 0 | 0 | 0 | 0 | 8.2855 | 52.5 | 8.2855 | 3000 | 14.8051 | 3014.8051 | 2355.0992 | 0 | 118.3202
0 | 46.2553 | 0 | 0 | 0 | 0 | 6.2447 | 52.5 | 14.5302 | 3000 | 11.1584 | 3011.1584 | 2465.0085 | 0 | 125.4443
0 | 30.0573 | 0 | 0 | 0 | 0 | 22.4427 | 52.5 | 36.9729 | 3000 | 40.1022 | 3040.1022 | 2818.3977 | 0 | 149.516
0 | 33.4672 | 0 | 0 | 0 | 0 | 19.0328 | 52.5 | 56.0057 | 3000 | 34.0091 | 3034.0091 | 2963.7126 | 0 | 173.6439
0 | 49.7108 | 0 | 0 | 0 | 0 | 2.7892 | 52.5 | 58.7949 | 3000 | 4.9838 | 3004.9838 | 3004.9838 | 0 | 189.6445
0 | 59.5954 | 0 | 0 | 0 | 0 | -7.0954 | 52.5 | 51.6995 | 3000 | 0 | 3000 | 3000 | 0 | 201.27
0 | 22.7898 | 0 | 0 | 0 | 0 | 29.7102 | 52.5 | 81.4097 | 3000 | 53.0882 | 3053.0882 | 3053.0882 | 0 | 197.6875
0 | 23.2561 | 0 | 0 | 0 | 0 | 29.2439 | 52.5 | 110.6536 | 3000 | 52.2549 | 3052.2549 | 3052.2549 | 0 | 170.9263
0 | 21.7134 | 0 | 0 | 0 | 0 | 30.7866 | 52.5 | 141.4402 | 3000 | 55.0116 | 3055.0116 | 3055.0116 | 0 | 168.0256
0 | 31.6697 | 0 | 0 | 0 | 0 | 20.8303 | 52.5 | 162.2705 | 3000 | 37.221 | 3037.221 | 3037.221 | 0 | 154.5945
0 | 30.4948 | 0 | 0 | 0 | 0 | 22.0052 | 52.5 | 184.2758 | 3000 | 39.3204 | 3039.3204 | 3039.3204 | 0 | 149.5954
0 | 31.2823 | 0 | 0 | 0 | 0 | 21.2177 | 52.5 | 205.4934 | 3000 | 37.9131 | 3037.9131 | 3037.9131 | 0 | 133.4859
0 | 30.8606 | 0 | 0 | 0 | 0 | 21.6394 | 52.5 | 227.1329 | 3000 | 38.6668 | 3038.6668 | 3038.6668 | 0 | 128.9306
0 | 27.7402 | 0 | 0 | 0 | 0 | 24.7598 | 52.5 | 251.8927 | 3000 | 44.2425 | 3044.2425 | 3044.2425 | 0 | 133.9162
0 | 27.9693 | 0 | 0 | 0 | 0 | 24.5307 | 52.5 | 276.4234 | 3000 | 43.8332 | 3043.8332 | 3043.8332 | 0 | 127.841
0 | 31.1947 | 0 | 0 | 0 | 0 | 21.3053 | 52.5 | 297.7288 | 3000 | 38.0698 | 3038.0698 | 3038.0698 | 0 | 127.842
0 | 28.588 | 0 | 0 | 0 | 0 | 23.912 | 52.5 | 321.6407 | 3000 | 42.7275 | 3042.7275 | 3042.7275 | 0 | 128.0988
0 | 229.5781 | 0 | 0 | 0 | 0 | -177.0781 | 52.5 | 144.5626 | 3000 | 0 | 3000 | 2940.5183 | 0 | 129.2946
0 | 55.1298 | 0 | 0 | 0 | 0 | -2.6298 | 52.5 | 141.9329 | 3000 | 0 | 3000 | 2810.7401 | 0 | 126.4833
0 | 47.3007 | 0 | 0 | 0 | 0 | 5.1993 | 52.5 | 147.1322 | 3000 | 9.2905 | 3009.2905 | 2820.0306 | 0 | 140.1555
0 | 41.0464 | 0 | 0 | 0 | 0 | 11.4536 | 52.5 | 158.5858 | 3000 | 20.466 | 3020.466 | 2771.7245 | 0 | 142.8824
0 | 43.6842 | 0 | 0 | 0 | 0 | 8.8158 | 52.5 | 167.4016 | 3000 | 15.7527 | 3015.7527 | 2658.8626 | 0 | 136.9846
0 | 219.9016 | 0 | 0 | 0 | 0 | -167.4016 | 52.5 | 0 | 3000 | 0 | 3000 | 2751.2584 | 0 | 140.5343
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2778.2956 | 0 | 137.6645
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2805.3327 | 0 | 134.656
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2837.7772 | 0 | 124.8622
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2891.8515 | 0 | 127.0101
0 | 38.7473 | 0 | 0 | 0 | 0 | 13.7527 | 52.5 | 13.7527 | 3000 | 24.5742 | 3024.5742 | 3008.3519 | 0 | 151.8014
0 | 41.266 | 0 | 0 | 0 | 0 | 11.234 | 52.5 | 24.9867 | 3000 | 20.0737 | 3020.0737 | 3020.0737 | 0 | 160.3357
0 | 41.4621 | 0 | 0 | 0 | 0 | 11.0379 | 52.5 | 36.0246 | 3000 | 19.7233 | 3019.7233 | 3019.7233 | 0 | 176.2009
0 | 30.5734 | 0 | 0 | 0 | 0 | 21.9266 | 52.5 | 57.9512 | 3000 | 39.18 | 3039.18 | 3039.18 | 0 | 162.3226
0 | 25.8713 | 0 | 0 | 0 | 0 | 26.6287 | 52.5 | 84.5799 | 3000 | 47.5819 | 3047.5819 | 3047.5819 | 0 | 152.1658
0 | 28.2415 | 0 | 0 | 0 | 0 | 24.2585 | 52.5 | 108.8384 | 3000 | 43.3467 | 3043.3467 | 3043.3467 | 0 | 153.2629
0 | 30.5958 | 0 | 0 | 0 | 0 | 21.9042 | 52.5 | 130.7426 | 3000 | 39.1399 | 3039.1399 | 3039.1399 | 0 | 149.1002
0 | 25.812 | 0 | 0 | 0 | 0 | 26.688 | 52.5 | 157.4306 | 3000 | 47.6879 | 3047.6879 | 3047.6879 | 0 | 134.0678
0 | 35.0601 | 0 | 0 | 0 | 0 | 17.4399 | 52.5 | 174.8705 | 3000 | 31.1628 | 3031.1628 | 3031.1628 | 0 | 127.521
0 | 31.8153 | 0 | 0 | 0 | 0 | 20.6847 | 52.5 | 195.5553 | 3000 | 36.9608 | 3036.9608 | 3036.9608 | 0 | 127.5524
0 | 28.196 | 0 | 0 | 0 | 0 | 24.304 | 52.5 | 219.8593 | 3000 | 43.4281 | 3043.4281 | 3043.4281 | 0 | 128.4022
0 | 30.9344 | 0 | 0 | 0 | 0 | 21.5656 | 52.5 | 241.4249 | 3000 | 38.5348 | 3038.5348 | 3038.5348 | 0 | 125.4307
0 | 35.4509 | 0 | 0 | 0 | 0 | 17.0491 | 52.5 | 258.474 | 3000 | 30.4646 | 3030.4646 | 3030.4646 | 0 | 137.0679
0 | 30.9498 | 0 | 0 | 0 | 0 | 21.5502 | 52.5 | 280.0242 | 3000 | 38.5073 | 3038.5073 | 3033.0999 | 0 | 190.7213
0 | 39.804 | 0 | 0 | 0 | 0 | -39.804 | 0 | 240.2202 | 0 | 0 | 0 | 0 | 140.5931 | 0
0 | 95.9802 | 0 | 0 | 0 | 0 | -88.1259 | 7.8543 | 152.0943 | 448.8163 | 0 | 448.8163 | 0 | 0 | 0
0 | 124.1369 | 0 | 0 | 0 | 0 | -112.9706 | 11.1663 | 39.1237 | 638.0762 | 0 | 638.0762 | 0 | 0 | 0
0 | 91.6237 | 0 | 0 | 0 | 0 | -39.1237 | 52.5 | 0 | 3000 | 0 | 3000 | 2221.3308 | 0 | 151.2282
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2205.1085 | 0 | 147.191
0 | 30.3477 | 0 | 0 | 0 | 0 | 22.1523 | 52.5 | 22.1523 | 3000 | 39.5832 | 3039.5832 | 2185.21 | 0 | 141.842
0 | 45.1865 | 0 | 0 | 0 | 0 | 7.3135 | 52.5 | 29.4658 | 3000 | 13.0683 | 3013.0683 | 2391.2144 | 0 | 152.5595
0 | 41.7967 | 0 | 0 | 0 | 0 | 10.7033 | 52.5 | 40.1691 | 3000 | 19.1253 | 3019.1253 | 2754.1615 | 0 | 172.3279
0 | 40.3918 | 0 | 0 | 0 | 0 | 12.1082 | 52.5 | 52.2773 | 3000 | 21.6357 | 3021.6357 | 2908.0798 | 0 | 183.3254
0 | 41.561 | 0 | 0 | 0 | 0 | 10.939 | 52.5 | 63.2163 | 3000 | 19.5466 | 3019.5466 | 2911.3981 | 0 | 185.689
0 | 39.1861 | 0 | 0 | 0 | 0 | 13.3139 | 52.5 | 76.5302 | 3000 | 23.7901 | 3023.7901 | 2996.753 | 0 | 199.2841
0 | 44.9535 | 0 | 0 | 0 | 0 | 7.5465 | 52.5 | 84.0767 | 3000 | 13.4847 | 3013.4847 | 3013.4847 | 0 | 210.6727
0 | 31.2477 | 0 | 0 | 0 | 0 | -31.2477 | 0 | 52.8291 | 0 | 0 | 0 | 0 | 0 | 0
0 | 29.2607 | 0 | 0 | 0 | 0 | 23.2393 | 52.5 | 76.0684 | 3000 | 41.5256 | 3041.5256 | 3041.5256 | 0 | 203.5693
0 | 30.6979 | 0 | 0 | 0 | 0 | 21.8021 | 52.5 | 97.8705 | 3000 | 38.9574 | 3038.9574 | 3038.9574 | 0 | 176.3507
0 | 18.6482 | 0 | 0 | 0 | 0 | 33.8518 | 52.5 | 131.7223 | 3000 | 60.4887 | 3060.4887 | 3060.4887 | 0 | 164.8379
0 | 23.167 | 0 | 0 | 0 | 0 | 29.333 | 52.5 | 161.0553 | 3000 | 52.4142 | 3052.4142 | 3052.4142 | 0 | 130.0328
0 | 20.6548 | 0 | 0 | 0 | 0 | 31.8452 | 52.5 | 192.9005 | 3000 | 56.9031 | 3056.9031 | 3056.9031 | 0 | 139.5171
0 | 32.2396 | 0 | 0 | 0 | 0 | 20.2604 | 52.5 | 213.1609 | 3000 | 36.2027 | 3036.2027 | 3036.2027 | 0 | 130.3442
0 | 24.6803 | 0 | 0 | 0 | 0 | 27.8197 | 52.5 | 240.9806 | 3000 | 49.71 | 3049.71 | 3049.71 | 0 | 121.9884
0 | 22.5225 | 0 | 0 | 0 | 0 | 29.9775 | 52.5 | 270.9581 | 3000 | 53.5658 | 3053.5658 | 3053.5658 | 0 | 115.9744
0 | 26.2137 | 0 | 0 | 0 | 0 | 26.2863 | 52.5 | 297.2444 | 3000 | 46.9702 | 3046.9702 | 3046.9702 | 0 | 111.3668
0 | 45.6169 | 0 | 0 | 0 | 0 | 6.8831 | 52.5 | 304.1275 | 3000 | 12.2992 | 3012.2992 | 3012.2992 | 0 | 118.9858
0 | 81.2296 | 0 | 0 | 0 | 0 | -28.7296 | 52.5 | 275.3979 | 3000 | 0 | 3000 | 3000 | 0 | 136.56
0 | 101.9977 | 0 | 0 | 0 | 0 | -49.4977 | 52.5 | 225.9002 | 3000 | 0 | 3000 | 2956.7406 | 0 | 168.9777
0 | 127.8031 | 0 | 0 | 0 | 0 | -75.3031 | 52.5 | 150.5971 | 3000 | 0 | 3000 | 2853.9995 | 0 | 177.4902
0 | 97.5473 | 0 | 0 | 0 | 0 | -45.0473 | 52.5 | 105.5499 | 3000 | 0 | 3000 | 2816.1475 | 0 | 169.1941
0 | 108.9171 | 0 | 0 | 0 | 0 | -56.4171 | 52.5 | 49.1328 | 3000 | 0 | 3000 | 2735.0362 | 0 | 154.5022
0 | 101.6328 | 0 | 0 | 0 | 0 | -49.1328 | 52.5 | 0 | 3000 | 0 | 3000 | 2756.6659 | 0 | 151.4237
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2697.1842 | 0 | 138.4734
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2751.2584 | 0 | 139.6814
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2762.0733 | 0 | 132.5795
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2778.2956 | 0 | 139.776
0 | 31.3714 | 0 | 0 | 0 | 0 | 21.1286 | 52.5 | 21.1286 | 3000 | 37.754 | 3037.754 | 2907.9758 | 0 | 148.8884
0 | 44.3942 | 0 | 0 | 0 | 0 | 8.1058 | 52.5 | 29.2344 | 3000 | 14.484 | 3014.484 | 2960.4098 | 0 | 164.658
0 | 58.1999 | 0 | 0 | 0 | 0 | -5.6999 | 52.5 | 23.5345 | 3000 | 0 | 3000 | 3000 | 0 | 178.32
0 | 76.0345 | 0 | 0 | 0 | 0 | -23.5345 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 195.45
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 157.5
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 144.48
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 130.5
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 123.9
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 117.57
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 115.89
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 111.75
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 103.32
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 110.76
0 | 42.3462 | 0 | 0 | 0 | 0 | 10.1538 | 52.5 | 10.1538 | 3000 | 18.1435 | 3018.1435 | 3018.1435 | 0 | 121.3897
0 | 62.6538 | 0 | 0 | 0 | 0 | -10.1538 | 52.5 | 0 | 3000 | 0 | 3000 | 2994.5926 | 0 | 137.7513
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2951.3332 | 0 | 172.6825
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2859.4069 | 0 | 173.6518
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2778.2956 | 0 | 172.421
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2686.3693 | 0 | 154.7886
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2702.5916 | 0 | 149.9668
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2513.3317 | 0 | 131.6986
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2626.8877 | 0 | 133.1832
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2621.4802 | 0 | 132.3585
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2740.4436 | 0 | 137.7073
0 | 29.395 | 0 | 0 | 0 | 0 | 23.105 | 52.5 | 23.105 | 3000 | 41.2855 | 3041.2855 | 2922.3221 | 0 | 141.7034
0 | 53.166 | 0 | 0 | 0 | 0 | -0.66603 | 52.5 | 22.4389 | 3000 | 0 | 3000 | 2994.5926 | 0 | 166.8886
0 | 65.8455 | 0 | 0 | 0 | 0 | -13.3455 | 52.5 | 9.0934 | 3000 | 0 | 3000 | 3000 | 0 | 180.3
0 | 61.5934 | 0 | 0 | 0 | 0 | -9.0934 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 199.32
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 174.81
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 159.39
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 147.6
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 129.24
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 116.64
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 113.79
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 110.31
0 | 47.2498 | 0 | 0 | 0 | 0 | 5.2502 | 52.5 | 5.2502 | 3000 | 9.3814 | 3009.3814 | 3009.3814 | 0 | 100.4832
0 | 39.8842 | 0 | 0 | 0 | 0 | 12.6158 | 52.5 | 17.866 | 3000 | 22.5428 | 3022.5428 | 3022.5428 | 0 | 102.6153
0 | 67.5035 | 0 | 0 | 0 | 0 | -15.0035 | 52.5 | 2.8625 | 3000 | 0 | 3000 | 3000 | 0 | 111.6
0 | 55.3625 | 0 | 0 | 0 | 0 | -2.8625 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 149.19
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2913.4812 | 0 | 177.6349
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2713.4065 | 0 | 169.9949
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2475.4798 | 0 | 146.3009
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2313.257 | 0 | 123.7592
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2286.2199 | 0 | 115.9113
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2475.4798 | 0 | 114.4909
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2188.8862 | 0 | 107.343
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2578.2208 | 0 | 116.0199
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2702.5916 | 0 | 126.7245
0 | 39.8207 | 0 | 0 | 0 | 0 | 12.6793 | 52.5 | 12.6793 | 3000 | 22.6563 | 3022.6563 | 2811.7667 | 0 | 124.1676
0 | 49.4039 | 0 | 0 | 0 | 0 | 3.0961 | 52.5 | 15.7754 | 3000 | 5.5323 | 3005.5323 | 2962.2729 | 0 | 153.8901
0 | 53.3114 | 0 | 0 | 0 | 0 | -0.81139 | 52.5 | 14.964 | 3000 | 0 | 3000 | 3000 | 0 | 174.9
0 | 67.464 | 0 | 0 | 0 | 0 | -14.964 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 188.37
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 170.34
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 132
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 130.17
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 120.69
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 115.62
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 112.02
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 97.95
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 82.71
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 88.62
0 | 47.752 | 0 | 0 | 0 | 0 | 4.748 | 52.5 | 4.748 | 3000 | 8.484 | 3008.484 | 3008.484 | 0 | 105.8084
0 | 57.248 | 0 | 0 | 0 | 0 | -4.748 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 122.82
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2978.3703 | 0 | 159.8194
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2918.8886 | 0 | 162.9907
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2886.4441 | 0 | 151.3074
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2751.2584 | 0 | 134.8942
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2718.8139 | 0 | 139.013
0 | 43.5518 | 0 | 0 | 0 | 0 | 8.9482 | 52.5 | 8.9482 | 3000 | 15.9892 | 3015.9892 | 2853.7664 | 0 | 145.2567
0 | 42.0698 | 0 | 0 | 0 | 0 | 10.4302 | 52.5 | 19.3783 | 3000 | 18.6373 | 3018.6373 | 2845.5997 | 0 | 137.4994
0 | 71.8783 | 0 | 0 | 0 | 0 | -19.3783 | 52.5 | 0 | 3000 | 0 | 3000 | 2848.5921 | 0 | 132.602
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2940.5183 | 0 | 126.2659
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2978.3703 | 0 | 118.837
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2994.5926 | 0 | 135.8946
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 145.95
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 149.76
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 138.57
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 119.4
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 117
0 | 43.1868 | 0 | 0 | 0 | 0 | 9.3132 | 52.5 | 9.3132 | 3000 | 16.6415 | 3016.6415 | 3016.6415 | 0 | 114.6324
0 | 47.7848 | 0 | 0 | 0 | 0 | 4.7152 | 52.5 | 14.0284 | 3000 | 8.4254 | 3008.4254 | 3008.4254 | 0 | 98.6764
0 | 66.5284 | 0 | 0 | 0 | 0 | -14.0284 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 109.2
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 111
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 113.1
0 | 37.2265 | 0 | 0 | 0 | 0 | 15.2735 | 52.5 | 15.2735 | 3000 | 27.2918 | 3027.2918 | 3027.2918 | 0 | 108.377
0 | 39.203 | 0 | 0 | 0 | 0 | 13.297 | 52.5 | 28.5706 | 3000 | 23.76 | 3023.76 | 3023.76 | 0 | 120.648
0 | 73.5 | 0 | 0 | 0 | 0 | -21 | 52.5 | 7.5705 | 3000 | 0 | 3000 | 3000 | 0 | 120
0 | 60.0705 | 0 | 0 | 0 | 0 | -7.5705 | 52.5 | 0 | 3000 | 0 | 3000 | 2983.7777 | 0 | 140.7746
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2935.1109 | 0 | 131.0527
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2853.9995 | 0 | 148.9502
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2789.1104 | 0 | 153.1222
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2837.7772 | 0 | 148.6995
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2826.9624 | 0 | 158.3099
0 | 46.8534 | 0 | 0 | 0 | 0 | 5.6466 | 52.5 | 5.6466 | 3000 | 10.0898 | 3010.0898 | 2842.4596 | 0 | 145.8182
0 | 56.0753 | 0 | 0 | 0 | 0 | -3.5753 | 52.5 | 2.0713 | 3000 | 0 | 3000 | 2870.2218 | 0 | 142.076
0 | 38.4401 | 0 | 0 | 0 | 0 | 14.0599 | 52.5 | 16.1313 | 3000 | 25.1232 | 3025.1232 | 2971.049 | 0 | 140.8277
0 | 41.7113 | 0 | 0 | 0 | 0 | 10.7887 | 52.5 | 26.92 | 3000 | 19.278 | 3019.278 | 3003.0557 | 0 | 142.4349
0 | 38.0008 | 0 | 0 | 0 | 0 | 14.4992 | 52.5 | 41.4192 | 3000 | 25.9082 | 3025.9082 | 3020.5007 | 0 | 153.5018
0 | 47.2161 | 0 | 0 | 0 | 0 | 5.2839 | 52.5 | 46.7031 | 3000 | 9.4416 | 3009.4416 | 3009.4416 | 0 | 171.478
0 | 53.4196 | 0 | 0 | 0 | 0 | -0.91957 | 52.5 | 45.7835 | 3000 | 0 | 3000 | 3000 | 0 | 178.95
0 | 79.3618 | 0 | 0 | 0 | 0 | -26.8618 | 52.5 | 18.9217 | 3000 | 0 | 3000 | 3000 | 0 | 165.39
0 | 71.4217 | 0 | 0 | 0 | 0 | -18.9217 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 144.45
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 145.77
0 | 27.8419 | 0 | 0 | 0 | 0 | 24.6581 | 52.5 | 24.6581 | 3000 | 44.0608 | 3044.0608 | 3044.0608 | 0 | 141.6402
0 | 27.6311 | 0 | 0 | 0 | 0 | 24.8689 | 52.5 | 49.527 | 3000 | 44.4374 | 3044.4374 | 3044.4374 | 0 | 141.3837
0 | 29.4128 | 0 | 0 | 0 | 0 | 23.0872 | 52.5 | 72.6143 | 3000 | 41.2538 | 3041.2538 | 3041.2538 | 0 | 123.6574
0 | 37.0411 | 0 | 0 | 0 | 0 | 15.4589 | 52.5 | 88.0731 | 3000 | 27.6229 | 3027.6229 | 3027.6229 | 0 | 118.2287
0 | 32.5209 | 0 | 0 | 0 | 0 | 19.9791 | 52.5 | 108.0522 | 3000 | 35.7 | 3035.7 | 3035.7 | 0 | 109.5888
0 | 19.528 | 0 | 0 | 0 | 0 | 32.972 | 52.5 | 141.0242 | 3000 | 58.9167 | 3058.9167 | 3058.9167 | 0 | 121.1943
0 | 25.4331 | 0 | 0 | 0 | 0 | 27.0669 | 52.5 | 168.0911 | 3000 | 48.3649 | 3048.3649 | 3048.3649 | 0 | 112.9114
0 | 25.9187 | 0 | 0 | 0 | 0 | 26.5813 | 52.5 | 194.6724 | 3000 | 47.4972 | 3047.4972 | 3047.4972 | 0 | 113.0012
0 | 24.9353 | 0 | 0 | 0 | 0 | 27.5647 | 52.5 | 222.2371 | 3000 | 49.2544 | 3049.2544 | 3000.5876 | 0 | 123.6842
0 | 49.0059 | 0 | 0 | 0 | 0 | 3.4941 | 52.5 | 225.7311 | 3000 | 6.2435 | 3006.2435 | 2919.7247 | 0 | 125.1102
0 | 36.6588 | 0 | 0 | 0 | 0 | 15.8412 | 52.5 | 241.5723 | 3000 | 28.3061 | 3028.3061 | 2844.4536 | 0 | 118.2724
0 | 57.383 | 0 | 0 | 0 | 0 | -4.883 | 52.5 | 236.6893 | 3000 | 0 | 3000 | 2610.6654 | 0 | 104.6877
0 | 50.9432 | 0 | 0 | 0 | 0 | 1.5568 | 52.5 | 238.2461 | 3000 | 2.7817 | 3002.7817 | 2608.0397 | 0 | 101.7135
0 | 31.6605 | 0 | 0 | 0 | 0 | 20.8395 | 52.5 | 259.0855 | 3000 | 37.2374 | 3037.2374 | 2296.4202 | 0 | 87.4477
0 | 40.3319 | 0 | 0 | 0 | 0 | 12.1681 | 52.5 | 271.2537 | 3000 | 21.7428 | 3021.7428 | 2124.1102 | 0 | 78.1673
0 | 48.6643 | 0 | 0 | 0 | 0 | 3.8357 | 52.5 | 275.0894 | 3000 | 6.8539 | 3006.8539 | 2568.8525 | 0 | 94.5338
0 | 45.4995 | 0 | 0 | 0 | 0 | 7.0005 | 52.5 | 282.0899 | 3000 | 12.509 | 3012.509 | 2823.2491 | 0 | 103.8956
0 | 47.4845 | 0 | 0 | 0 | 0 | 5.0155 | 52.5 | 287.1054 | 3000 | 8.962 | 3008.962 | 2911.6284 | 0 | 105.663
0 | 38.0533 | 0 | 0 | 0 | 0 | 14.4467 | 52.5 | 301.5521 | 3000 | 25.8143 | 3025.8143 | 3004.1846 | 0 | 128.9997
0 | 33.2022 | 0 | 0 | 0 | 0 | 19.2978 | 52.5 | 320.8499 | 3000 | 34.4826 | 3034.4826 | 3034.4826 | 0 | 136.5517
0 | 32.2221 | 0 | 0 | 0 | 0 | 20.2779 | 52.5 | 341.1278 | 3000 | 36.2339 | 3036.2339 | 3036.2339 | 0 | 189.7646
0 | 27.0654 | 0 | 0 | 0 | 0 | 25.4346 | 52.5 | 366.5625 | 3000 | 45.4483 | 3045.4483 | 3045.4483 | 0 | 144.3542
0 | 32.2988 | 0 | 0 | 0 | 0 | 20.2012 | 52.5 | 386.7637 | 3000 | 36.0969 | 3036.0969 | 3036.0969 | 0 | 121.7475
0 | 33.5457 | 0 | 0 | 0 | 0 | 18.9543 | 52.5 | 405.718 | 3000 | 33.8689 | 3033.8689 | 3033.8689 | 0 | 111.0396
0 | 26.7175 | 0 | 0 | 0 | 0 | 25.7825 | 52.5 | 431.5005 | 3000 | 46.0699 | 3046.0699 | 3046.0699 | 0 | 106.6124
0 | 22.2721 | 0 | 0 | 0 | 0 | 30.2279 | 52.5 | 461.7284 | 3000 | 54.0132 | 3054.0132 | 3054.0132 | 0 | 125.8253
0 | 24.1269 | 0 | 0 | 0 | 0 | 28.3731 | 52.5 | 490.1015 | 3000 | 50.6989 | 3050.6989 | 3050.6989 | 0 | 125.6888
0 | 29.1807 | 0 | 0 | 0 | 0 | 23.3193 | 52.5 | 513.4208 | 3000 | 41.6684 | 3041.6684 | 3041.6684 | 0 | 118.6251
0 | 233.2477 | 0 | 0 | 0 | 0 | -180.7477 | 52.5 | 332.6731 | 3000 | 0 | 3000 | 3000 | 0 | 90.51
0 | 29.4275 | 0 | 0 | 0 | 0 | 23.0725 | 52.5 | 355.7457 | 3000 | 41.2276 | 3041.2276 | 3041.2276 | 0 | 94.2781
0 | 22.974 | 0 | 0 | 0 | 0 | 29.526 | 52.5 | 385.2717 | 3000 | 52.7591 | 3052.7591 | 3052.7591 | 0 | 120.9808
0 | 24.9233 | 0 | 0 | 0 | 0 | 27.5767 | 52.5 | 412.8484 | 3000 | 49.276 | 3049.276 | 3049.276 | 0 | 155.696
0 | 27.0545 | 0 | 0 | 0 | 0 | 25.4455 | 52.5 | 438.2939 | 3000 | 45.4677 | 3045.4677 | 2980.5786 | 0 | 190.5186
0 | 45.4109 | 0 | 0 | 0 | 0 | 7.0891 | 52.5 | 445.383 | 3000 | 12.6672 | 3012.6672 | 2823.4073 | 0 | 184.1991
0 | 50.7082 | 0 | 0 | 0 | 0 | -50.7082 | 0 | 394.6748 | 0 | 0 | 0 | 0 | 264.9638 | 0
0 | 45.1979 | 0 | 0 | 0 | 0 | 7.3021 | 52.5 | 401.9768 | 3000 | 13.0478 | 3013.0478 | 2580.4538 | 0 | 177.6642
0 | 50.1146 | 0 | 0 | 0 | 0 | 2.3854 | 52.5 | 404.3622 | 3000 | 4.2624 | 3004.2624 | 2409.4456 | 0 | 151.7951
0 | 44.3795 | 0 | 0 | 0 | 0 | 8.1205 | 52.5 | 412.4827 | 3000 | 14.5102 | 3014.5102 | 2673.8424 | 0 | 161.099
0 | 39.979 | 0 | 0 | 0 | 0 | 12.521 | 52.5 | 425.0036 | 3000 | 22.3733 | 3022.3733 | 2784.4466 | 0 | 161.4979
0 | 44.5485 | 0 | 0 | 0 | 0 | 7.9515 | 52.5 | 432.9552 | 3000 | 14.2084 | 3014.2084 | 2532.9475 | 0 | 138.0456
0 | 33.6414 | 0 | 0 | 0 | 0 | 18.8586 | 52.5 | 451.8138 | 3000 | 33.6979 | 3033.6979 | 2730.882 | 0 | 158.8827
0 | 40.3088 | 0 | 0 | 0 | 0 | 12.1912 | 52.5 | 464.005 | 3000 | 21.784 | 3021.784 | 2908.2281 | 0 | 178.3907
0 | 38.3995 | 0 | 0 | 0 | 0 | 14.1005 | 52.5 | 478.1054 | 3000 | 25.1956 | 3025.1956 | 3003.5659 | 0 | 190.396
0 | 51.1125 | 0 | 0 | 0 | 0 | 1.3875 | 52.5 | 479.4929 | 3000 | 2.4793 | 3002.4793 | 3002.4793 | 0 | 195.4314
0 | 48.7622 | 0 | 0 | 0 | 0 | 3.7378 | 52.5 | 483.2307 | 3000 | 6.6789 | 3006.6789 | 3006.6789 | 0 | 203.8228
0 | 22.0641 | 0 | 0 | 0 | 0 | 30.4359 | 52.5 | 513.6666 | 3000 | 54.3849 | 3054.3849 | 3054.3849 | 0 | 195.2668
0 | 26.4867 | 0 | 0 | 0 | 0 | 26.0133 | 52.5 | 539.6798 | 3000 | 46.4822 | 3046.4822 | 3046.4822 | 0 | 158.4475
0 | 28.6705 | 0 | 0 | 0 | 0 | 23.8295 | 52.5 | 563.5093 | 3000 | 42.5801 | 3042.5801 | 3042.5801 | 0 | 152.129
0 | 26.0404 | 0 | 0 | 0 | 0 | 26.4596 | 52.5 | 589.9689 | 3000 | 47.2798 | 3047.2798 | 3047.2798 | 0 | 122.4397
0 | 29.8253 | 0 | 0 | 0 | 0 | 22.6747 | 52.5 | 612.6436 | 3000 | 40.5167 | 3040.5167 | 3040.5167 | 0 | 124.6612
0 | 30.3024 | 0 | 0 | 0 | 0 | 22.1976 | 52.5 | 634.8412 | 3000 | 39.6641 | 3039.6641 | 3039.6641 | 0 | 123.7751
0 | 36.0228 | 0 | 0 | 0 | 0 | 16.4772 | 52.5 | 651.3184 | 3000 | 29.4426 | 3029.4426 | 3029.4426 | 0 | 121.1777
0 | 24.7591 | 0 | 0 | 0 | 0 | 27.7409 | 52.5 | 679.0593 | 3000 | 49.5693 | 3049.5693 | 3049.5693 | 0 | 119.7566
0 | 40.7969 | 0 | 0 | 0 | 0 | 11.7031 | 52.5 | 690.7625 | 3000 | 20.9119 | 3020.9119 | 3020.9119 | 0 | 120.8365
0 | 111.3337 | 0 | 0 | 0 | 0 | -58.8337 | 52.5 | 631.9288 | 3000 | 0 | 3000 | 3000 | 0 | 134.97
0 | 69.6671 | 0 | 0 | 0 | 0 | -17.1671 | 52.5 | 614.7617 | 3000 | 0 | 3000 | 3000 | 0 | 166.83
0 | 37.127 | 0 | 0 | 0 | 0 | 15.373 | 52.5 | 630.1347 | 3000 | 27.4695 | 3027.4695 | 2973.3952 | 0 | 201.1205
0 | 67.6624 | 0 | 0 | 0 | 0 | -67.6624 | 0 | 562.4723 | 0 | 0 | 0 | 0 | 135.1856 | 0
0 | 40.881 | 0 | 0 | 0 | 0 | 11.619 | 52.5 | 574.0913 | 3000 | 20.7615 | 3020.7615 | 2923.4279 | 0 | 204.0553
0 | 45.3446 | 0 | 0 | 0 | 0 | 7.1554 | 52.5 | 581.2467 | 3000 | 12.7857 | 3012.7857 | 2785.6739 | 0 | 185.9716
0 | 62.3046 | 0 | 0 | 0 | 0 | -9.8046 | 52.5 | 571.4421 | 3000 | 0 | 3000 | 2621.4802 | 0 | 172.0215
0 | 104.4882 | 0 | 0 | 0 | 0 | -51.9882 | 52.5 | 519.4538 | 3000 | 0 | 3000 | 2697.1842 | 0 | 169.6529
0 | 51.13 | 0 | 0 | 0 | 0 | 1.37 | 52.5 | 520.8239 | 3000 | 2.448 | 3002.448 | 2678.0025 | 0 | 165.0721
0 | 45.1363 | 0 | 0 | 0 | 0 | 7.3637 | 52.5 | 528.1875 | 3000 | 13.1579 | 3013.1579 | 2531.8971 | 0 | 150.8504
0 | 47.2666 | 0 | 0 | 0 | 0 | 5.2334 | 52.5 | 533.4209 | 3000 | 9.3513 | 3009.3513 | 2852.536 | 0 | 171.6941
0 | 37.2904 | 0 | 0 | 0 | 0 | 15.2096 | 52.5 | 548.6305 | 3000 | 27.1776 | 3027.1776 | 2983.9182 | 0 | 184.9433
0 | 45.044 | 0 | 0 | 0 | 0 | 7.456 | 52.5 | 556.0865 | 3000 | 13.3228 | 3013.3228 | 3007.9154 | 0 | 202.6433
0 | 82.7858 | 0 | 0 | 0 | 0 | -82.7858 | 0 | 473.3008 | 0 | 0 | 0 | 0 | 0 | 0
0 | 100.2412 | 0 | 0 | 0 | 0 | -100.2412 | 0 | 373.0596 | 0 | 0 | 0 | 0 | 0 | 0
0 | 67.248 | 0 | 0 | 0 | 0 | -67.248 | 0 | 305.8115 | 0 | 0 | 0 | 0 | 0 | 0
0 | 90.3573 | 0 | 0 | 0 | 0 | -37.8573 | 52.5 | 267.9543 | 3000 | 0 | 3000 | 3000 | 0 | 182.91
0 | 86.7187 | 0 | 0 | 0 | 0 | -34.2187 | 52.5 | 233.7355 | 3000 | 0 | 3000 | 3000 | 0 | 163.5
0 | 74.6858 | 0 | 0 | 0 | 0 | -22.1858 | 52.5 | 211.5497 | 3000 | 0 | 3000 | 3000 | 0 | 134.55
0 | 63.3195 | 0 | 0 | 0 | 0 | -10.8195 | 52.5 | 200.7302 | 3000 | 0 | 3000 | 3000 | 0 | 149.43
0 | 107.4662 | 0 | 0 | 0 | 0 | -54.9662 | 52.5 | 145.7641 | 3000 | 0 | 3000 | 3000 | 0 | 144.06
0 | 92.3769 | 0 | 0 | 0 | 0 | -39.8769 | 52.5 | 105.8872 | 3000 | 0 | 3000 | 3000 | 0 | 132.75
0 | 63.0677 | 0 | 0 | 0 | 0 | -10.5677 | 52.5 | 95.3195 | 3000 | 0 | 3000 | 3000 | 0 | 130.2
0 | 26.9963 | 0 | 0 | 0 | 0 | 25.5037 | 52.5 | 120.8233 | 3000 | 45.5718 | 3045.5718 | 3045.5718 | 0 | 133.0915
0 | 33.4624 | 0 | 0 | 0 | 0 | 19.0376 | 52.5 | 139.8609 | 3000 | 34.0177 | 3034.0177 | 3034.0177 | 0 | 137.441
0 | 62.8829 | 0 | 0 | 0 | 0 | -10.3829 | 52.5 | 129.478 | 3000 | 0 | 3000 | 3000 | 0 | 161.04
0 | 108.0447 | 0 | 0 | 0 | 0 | -55.5447 | 52.5 | 73.9333 | 3000 | 0 | 3000 | 2978.3703 | 0 | 193.5047
0 | 82.6931 | 0 | 0 | 0 | 0 | -30.1931 | 52.5 | 43.7402 | 3000 | 0 | 3000 | 2908.0738 | 0 | 192.8053
0 | 37.1581 | 0 | 0 | 0 | 0 | 15.3419 | 52.5 | 59.0821 | 3000 | 27.4139 | 3027.4139 | 2627.2645 | 0 | 171.14
0 | 42.2265 | 0 | 0 | 0 | 0 | 10.2735 | 52.5 | 69.3556 | 3000 | 18.3574 | 3018.3574 | 2342.4293 | 0 | 145.2072
0 | 77.7593 | 0 | 0 | 0 | 0 | -25.2593 | 52.5 | 44.0963 | 3000 | 0 | 3000 | 2361.9238 | 0 | 136.0232
0 | 96.5712 | 0 | 0 | 0 | 0 | -44.0712 | 52.5 | 0.025078 | 3000 | 0 | 3000 | 2637.7025 | 0 | 134.5228
0 | 43.4895 | 0 | 0 | 0 | 0 | 9.0105 | 52.5 | 9.0356 | 3000 | 16.1006 | 3016.1006 | 2794.3962 | 0 | 142.5142
0 | 38.9228 | 0 | 0 | 0 | 0 | 13.5772 | 52.5 | 22.6128 | 3000 | 24.2606 | 3024.2606 | 2829.5933 | 0 | 144.5639
0 | 40.964 | 0 | 0 | 0 | 0 | 11.536 | 52.5 | 34.1488 | 3000 | 20.6133 | 3020.6133 | 2917.8722 | 0 | 151.671
0 | 86.6488 | 0 | 0 | 0 | 0 | -34.1488 | 52.5 | 0 | 3000 | 0 | 3000 | 2972.9629 | 0 | 157.6562
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2994.5926 | 0 | 185.6348
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 195.21
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 187.29
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 165
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 144.18
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 146.58
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 137.61
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 127.95
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 129.3
0 | 52.2683 | 0 | 0 | 0 | 0 | 0.2317 | 52.5 | 0.2317 | 3000 | 0.41402 | 3000.414 | 3000.414 | 0 | 124.8172
0 | 37.4909 | 0 | 0 | 0 | 0 | 15.0091 | 52.5 | 15.2408 | 3000 | 26.8192 | 3026.8192 | 3026.8192 | 0 | 125.1287
0 | 31.1444 | 0 | 0 | 0 | 0 | 21.3556 | 52.5 | 36.5964 | 3000 | 38.1596 | 3038.1596 | 3038.1596 | 0 | 131.9473
0 | 29.3703 | 0 | 0 | 0 | 0 | 23.1297 | 52.5 | 59.726 | 3000 | 41.3297 | 3041.3297 | 3041.3297 | 0 | 140.7831
0 | 29.4322 | 0 | 0 | 0 | 0 | 23.0678 | 52.5 | 82.7938 | 3000 | 41.219 | 3041.219 | 3041.219 | 0 | 166.4763
0 | 71.8366 | 0 | 0 | 0 | 0 | -19.3366 | 52.5 | 63.4572 | 3000 | 0 | 3000 | 2972.9629 | 0 | 199.575
0 | 93.7782 | 0 | 0 | 0 | 0 | -41.2782 | 52.5 | 22.1789 | 3000 | 0 | 3000 | 2897.2589 | 0 | 201.1277
0 | 74.6789 | 0 | 0 | 0 | 0 | -22.1789 | 52.5 | 0 | 3000 | 0 | 3000 | 2735.0362 | 0 | 188.7995
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2605.258 | 0 | 173.0673
0 | 41.8344 | 0 | 0 | 0 | 0 | 10.6656 | 52.5 | 10.6656 | 3000 | 19.058 | 3019.058 | 2581.0565 | 0 | 168.8785
0 | 56.6674 | 0 | 0 | 0 | 0 | -4.1674 | 52.5 | 6.4981 | 3000 | 0 | 3000 | 2578.2208 | 0 | 164.2327
0 | 44.9013 | 0 | 0 | 0 | 0 | 7.5987 | 52.5 | 14.0968 | 3000 | 13.5779 | 3013.5779 | 2467.428 | 0 | 143.1108
0 | 36.5082 | 0 | 0 | 0 | 0 | 15.9918 | 52.5 | 30.0886 | 3000 | 28.5752 | 3028.5752 | 2531.0921 | 0 | 142.8801
0 | 43.7947 | 0 | 0 | 0 | 0 | 8.7053 | 52.5 | 38.794 | 3000 | 15.5553 | 3015.5553 | 2691.1097 | 0 | 160.8476
0 | 48.6596 | 0 | 0 | 0 | 0 | 3.8404 | 52.5 | 42.6344 | 3000 | 6.8624 | 3006.8624 | 2931.1584 | 0 | 186.2165
0 | 79.0277 | 0 | 0 | 0 | 0 | -26.5277 | 52.5 | 16.1067 | 3000 | 0 | 3000 | 2989.1851 | 0 | 199.7672
0 | 16.1067 | 0 | 0 | 0 | 0 | -16.1067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 208.02
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 181.59
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 160.8
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 148.32
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 144.45
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 138.15
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 129.93
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 127.5
0 | 30.3901 | 0 | 0 | 0 | 0 | 22.1099 | 52.5 | 22.1099 | 3000 | 39.5075 | 3039.5075 | 3039.5075 | 0 | 125.8356
0 | 36.4985 | 0 | 0 | 0 | 0 | 16.0015 | 52.5 | 38.1114 | 3000 | 28.5925 | 3028.5925 | 3028.5925 | 0 | 135.0147
0 | 59.4287 | 0 | 0 | 0 | 0 | -6.9287 | 52.5 | 31.1827 | 3000 | 0 | 3000 | 3000 | 0 | 159.6
0 | 83.6827 | 0 | 0 | 0 | 0 | -31.1827 | 52.5 | 0 | 3000 | 0 | 3000 | 2972.9629 | 0 | 184.4426
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2724.2213 | 0 | 181.0517
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2735.0362 | 0 | 169.5722
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2718.8139 | 0 | 146.0003
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2826.9624 | 0 | 144.1751
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2551.1837 | 0 | 109.0886
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2816.1475 | 0 | 117.1517
0 | 36.8127 | 0 | 0 | 0 | 0 | 15.6873 | 52.5 | 15.6873 | 3000 | 28.0312 | 3028.0312 | 2681.956 | 0 | 113.3395
0 | 40.2571 | 0 | 0 | 0 | 0 | 12.2429 | 52.5 | 27.9302 | 3000 | 21.8764 | 3021.8764 | 2762.32 | 0 | 119.056
0 | 41.9283 | 0 | 0 | 0 | 0 | 10.5717 | 52.5 | 38.5019 | 3000 | 18.8902 | 3018.8902 | 2905.3343 | 0 | 127.1955
0 | 80.144 | 0 | 0 | 0 | 0 | -27.644 | 52.5 | 10.8579 | 3000 | 0 | 3000 | 2983.7777 | 0 | 153.4259
0 | 63.3579 | 0 | 0 | 0 | 0 | -10.8579 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 155.37
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 156.09
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 134.7
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 132
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 128.4
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 128.7
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 126.12
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 127.68
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 121.2
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 116.7
0 | 26.6706 | 0 | 0 | 0 | 0 | 25.8294 | 52.5 | 25.8294 | 3000 | 46.1537 | 3046.1537 | 3046.1537 | 0 | 119.4092
0 | 32.9224 | 0 | 0 | 0 | 0 | 19.5776 | 52.5 | 45.407 | 3000 | 34.9826 | 3034.9826 | 3034.9826 | 0 | 121.6725
0 | 58.0467 | 0 | 0 | 0 | 0 | -5.5467 | 52.5 | 39.8603 | 3000 | 0 | 3000 | 3000 | 0 | 125.67
0 | 92.3603 | 0 | 0 | 0 | 0 | -39.8603 | 52.5 | 0 | 3000 | 0 | 3000 | 2967.5554 | 0 | 132.6497
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2897.2589 | 0 | 138.9815
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2908.0738 | 0 | 145.8108
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2745.851 | 0 | 140.0384
0 | 43.2943 | 0 | 0 | 0 | 0 | 9.2057 | 52.5 | 9.2057 | 3000 | 16.4494 | 3016.4494 | 2838.0043 | 0 | 146.2424
0 | 50.5996 | 0 | 0 | 0 | 0 | 1.9004 | 52.5 | 11.1061 | 3000 | 3.3957 | 3003.3957 | 2657.3205 | 0 | 133.3975
0 | 63.6061 | 0 | 0 | 0 | 0 | -11.1061 | 52.5 | 0 | 3000 | 0 | 3000 | 2529.554 | 0 | 124.1505
0 | 35.6299 | 0 | 0 | 0 | 0 | 16.8701 | 52.5 | 16.8701 | 3000 | 30.1446 | 3030.1446 | 2813.8476 | 0 | 135.9088
0 | 41.9257 | 0 | 0 | 0 | 0 | 10.5743 | 52.5 | 27.4444 | 3000 | 18.8949 | 3018.8949 | 2813.4127 | 0 | 135.2407
0 | 42.7631 | 0 | 0 | 0 | 0 | 9.7369 | 52.5 | 37.1813 | 3000 | 17.3986 | 3017.3986 | 2893.0278 | 0 | 144.7671
0 | 43.9162 | 0 | 0 | 0 | 0 | 8.5838 | 52.5 | 45.7651 | 3000 | 15.338 | 3015.338 | 3004.5232 | 0 | 160.6819
0 | 48.4675 | 0 | 0 | 0 | 0 | 4.0325 | 52.5 | 49.7976 | 3000 | 7.2055 | 3007.2055 | 3007.2055 | 0 | 177.6657
0 | 48.302 | 0 | 0 | 0 | 0 | 4.198 | 52.5 | 53.9956 | 3000 | 7.5012 | 3007.5012 | 3007.5012 | 0 | 189.1718
0 | 22.3415 | 0 | 0 | 0 | 0 | 30.1585 | 52.5 | 84.154 | 3000 | 53.8892 | 3053.8892 | 3053.8892 | 0 | 165.4903
0 | 28.8539 | 0 | 0 | 0 | 0 | 23.6461 | 52.5 | 107.8002 | 3000 | 42.2525 | 3042.2525 | 3042.2525 | 0 | 152.2952
0 | 26.0853 | 0 | 0 | 0 | 0 | 26.4147 | 52.5 | 134.2148 | 3000 | 47.1995 | 3047.1995 | 3047.1995 | 0 | 152.5123
0 | 32.3885 | 0 | 0 | 0 | 0 | 20.1115 | 52.5 | 154.3264 | 3000 | 35.9366 | 3035.9366 | 3035.9366 | 0 | 146.2714
0 | 30.9539 | 0 | 0 | 0 | 0 | 21.5461 | 52.5 | 175.8725 | 3000 | 38.5 | 3038.5 | 3038.5 | 0 | 136.7021
0 | 29.4739 | 0 | 0 | 0 | 0 | 23.0261 | 52.5 | 198.8985 | 3000 | 41.1445 | 3041.1445 | 3041.1445 | 0 | 124.7173
0 | 24.9906 | 0 | 0 | 0 | 0 | 27.5094 | 52.5 | 226.408 | 3000 | 49.1557 | 3049.1557 | 3049.1557 | 0 | 128.095
0 | 24.1783 | 0 | 0 | 0 | 0 | 28.3217 | 52.5 | 254.7297 | 3000 | 50.6071 | 3050.6071 | 3050.6071 | 0 | 127.8204
0 | 32.9888 | 0 | 0 | 0 | 0 | 19.5112 | 52.5 | 274.2409 | 3000 | 34.864 | 3034.864 | 3034.864 | 0 | 125.9772
0 | 59.8491 | 0 | 0 | 0 | 0 | -7.3491 | 52.5 | 266.8918 | 3000 | 0 | 3000 | 3000 | 0 | 123.9
0 | 78.448 | 0 | 0 | 0 | 0 | -25.948 | 52.5 | 240.9438 | 3000 | 0 | 3000 | 3000 | 0 | 126.09
0 | 59.1858 | 0 | 0 | 0 | 0 | -6.6858 | 52.5 | 234.258 | 3000 | 0 | 3000 | 2967.5554 | 0 | 133.3619
0 | 36.5546 | 0 | 0 | 0 | 0 | 15.9454 | 52.5 | 250.2034 | 3000 | 28.4923 | 3028.4923 | 2823.0102 | 0 | 131.9475
0 | 42.2579 | 0 | 0 | 0 | 0 | 10.2421 | 52.5 | 260.4455 | 3000 | 18.3013 | 3018.3013 | 2856.0785 | 0 | 146.7168
0 | 37.6022 | 0 | 0 | 0 | 0 | 14.8978 | 52.5 | 275.3434 | 3000 | 26.6204 | 3026.6204 | 2864.3977 | 0 | 150.2949
0 | 37.8842 | 0 | 0 | 0 | 0 | 14.6158 | 52.5 | 289.9592 | 3000 | 26.1165 | 3026.1165 | 2853.0788 | 0 | 152.1262
0 | 44.2301 | 0 | 0 | 0 | 0 | 8.2699 | 52.5 | 298.2291 | 3000 | 14.7773 | 3014.7773 | 2841.7397 | 0 | 150.328
0 | 37.3519 | 0 | 0 | 0 | 0 | 15.1481 | 52.5 | 313.3772 | 3000 | 27.0677 | 3027.0677 | 2875.6598 | 0 | 143.8405
0 | 42.28 | 0 | 0 | 0 | 0 | 10.22 | 52.5 | 323.5972 | 3000 | 18.2617 | 3018.2617 | 2839.8167 | 0 | 130.7452
0 | 40.7745 | 0 | 0 | 0 | 0 | 11.7255 | 52.5 | 335.3227 | 3000 | 20.9519 | 3020.9519 | 2907.396 | 0 | 138.9735
0 | 38.834 | 0 | 0 | 0 | 0 | 13.666 | 52.5 | 348.9887 | 3000 | 24.4194 | 3024.4194 | 2954.1229 | 0 | 149.8627
0 | 36.2922 | 0 | 0 | 0 | 0 | 16.2078 | 52.5 | 365.1965 | 3000 | 28.9612 | 3028.9612 | 3018.1464 | 0 | 167.1449
0 | 32.8364 | 0 | 0 | 0 | 0 | 19.6636 | 52.5 | 384.8601 | 3000 | 35.1362 | 3035.1362 | 3035.1362 | 0 | 189.9388
0 | 50.3601 | 0 | 0 | 0 | 0 | 2.1399 | 52.5 | 387.0001 | 3000 | 3.8237 | 3003.8237 | 3003.8237 | 0 | 198.4326
0 | 31.0844 | 0 | 0 | 0 | 0 | 21.4156 | 52.5 | 408.4157 | 3000 | 38.2668 | 3038.2668 | 3038.2668 | 0 | 188.6764
0 | 31.0859 | 0 | 0 | 0 | 0 | 21.4141 | 52.5 | 429.8298 | 3000 | 38.2642 | 3038.2642 | 3038.2642 | 0 | 165.95
0 | 28.0035 | 0 | 0 | 0 | 0 | 24.4965 | 52.5 | 454.3264 | 3000 | 43.7721 | 3043.7721 | 3043.7721 | 0 | 161.5939
0 | 24.2706 | 0 | 0 | 0 | 0 | 28.2294 | 52.5 | 482.5557 | 3000 | 50.4421 | 3050.4421 | 3050.4421 | 0 | 155.5725
0 | 24.0249 | 0 | 0 | 0 | 0 | 28.4751 | 52.5 | 511.0308 | 3000 | 50.8812 | 3050.8812 | 3050.8812 | 0 | 138.327
0 | 24.115 | 0 | 0 | 0 | 0 | 28.385 | 52.5 | 539.4158 | 3000 | 50.7202 | 3050.7202 | 3050.7202 | 0 | 128.4658
0 | 26.6407 | 0 | 0 | 0 | 0 | 25.8593 | 52.5 | 565.2751 | 3000 | 46.2072 | 3046.2072 | 3046.2072 | 0 | 125.7474
0 | 26.0407 | 0 | 0 | 0 | 0 | 26.4593 | 52.5 | 591.7345 | 3000 | 47.2793 | 3047.2793 | 3047.2793 | 0 | 124.2985
0 | 32.6589 | 0 | 0 | 0 | 0 | 19.8411 | 52.5 | 611.5756 | 3000 | 35.4534 | 3035.4534 | 3035.4534 | 0 | 123.543
0 | 27.2326 | 0 | 0 | 0 | 0 | 25.2674 | 52.5 | 636.843 | 3000 | 45.1495 | 3045.1495 | 3045.1495 | 0 | 126.0387
0 | 26.1635 | 0 | 0 | 0 | 0 | 26.3365 | 52.5 | 663.1795 | 3000 | 47.0598 | 3047.0598 | 3047.0598 | 0 | 161.5246
0 | 29.5122 | 0 | 0 | 0 | 0 | 22.9878 | 52.5 | 686.1673 | 3000 | 41.0761 | 3041.0761 | 3030.2612 | 0 | 202.8154
0 | 47.5376 | 0 | 0 | 0 | 0 | 4.9624 | 52.5 | 691.1296 | 3000 | 8.8671 | 3008.8671 | 2976.4225 | 0 | 200.7002
0 | 37.5792 | 0 | 0 | 0 | 0 | 14.9208 | 52.5 | 706.0504 | 3000 | 26.6615 | 3026.6615 | 2923.9204 | 0 | 195.4348
0 | 41.5015 | 0 | 0 | 0 | 0 | 10.9985 | 52.5 | 717.049 | 3000 | 19.6529 | 3019.6529 | 2700.6148 | 0 | 174.4597
0 | 44.5524 | 0 | 0 | 0 | 0 | 7.9476 | 52.5 | 724.9966 | 3000 | 14.2013 | 3014.2013 | 2495.0885 | 0 | 160.7586
0 | 44.2604 | 0 | 0 | 0 | 0 | 8.2396 | 52.5 | 733.2362 | 3000 | 14.7231 | 3014.7231 | 2679.4627 | 0 | 160.0979
0 | 43.2611 | 0 | 0 | 0 | 0 | 9.2389 | 52.5 | 742.4751 | 3000 | 16.5087 | 3016.5087 | 2740.73 | 0 | 160.9631
0 | 49.197 | 0 | 0 | 0 | 0 | 3.303 | 52.5 | 745.7781 | 3000 | 5.9021 | 3005.9021 | 2843.6793 | 0 | 171.0757
0 | 37.2394 | 0 | 0 | 0 | 0 | 15.2606 | 52.5 | 761.0387 | 3000 | 27.2686 | 3027.2686 | 2838.0087 | 0 | 177.9715
0 | 38.9525 | 0 | 0 | 0 | 0 | 13.5475 | 52.5 | 774.5861 | 3000 | 24.2075 | 3024.2075 | 2986.3556 | 0 | 194.2027
0 | 35.2611 | 0 | 0 | 0 | 0 | 17.2389 | 52.5 | 791.825 | 3000 | 30.8036 | 3030.8036 | 3025.3962 | 0 | 209.0851
0 | 31.2298 | 0 | 0 | 0 | 0 | -31.2298 | 0 | 760.5952 | 0 | 0 | 0 | 0 | 0 | 0
0 | 41.8899 | 0 | 0 | 0 | 0 | -41.8899 | 0 | 718.7053 | 0 | 0 | 0 | 0 | 0 | 0
0 | 223.2946 | 0 | 0 | 0 | 0 | -170.7946 | 52.5 | 547.9106 | 3000 | 0 | 3000 | 3000 | 0 | 201.6
0 | 26.9843 | 0 | 0 | 0 | 0 | 25.5157 | 52.5 | 573.4264 | 3000 | 45.5932 | 3045.5932 | 3045.5932 | 0 | 194.6134
0 | 22.5587 | 0 | 0 | 0 | 0 | 29.9413 | 52.5 | 603.3677 | 3000 | 53.5012 | 3053.5012 | 3053.5012 | 0 | 170.7518
0 | 30.7523 | 0 | 0 | 0 | 0 | 21.7477 | 52.5 | 625.1154 | 3000 | 38.8603 | 3038.8603 | 3038.8603 | 0 | 154.0094
0 | 36.2401 | 0 | 0 | 0 | 0 | 16.2599 | 52.5 | 641.3753 | 3000 | 29.0542 | 3029.0542 | 3029.0542 | 0 | 163.0237
0 | 34.5315 | 0 | 0 | 0 | 0 | 17.9685 | 52.5 | 659.3437 | 3000 | 32.1072 | 3032.1072 | 3032.1072 | 0 | 154.2736
0 | 41.1613 | 0 | 0 | 0 | 0 | 11.3387 | 52.5 | 670.6824 | 3000 | 20.2608 | 3020.2608 | 3020.2608 | 0 | 149.9257
0 | 77.0778 | 0 | 0 | 0 | 0 | -24.5778 | 52.5 | 646.1046 | 3000 | 0 | 3000 | 3000 | 0 | 140.52
0 | 115.3156 | 0 | 0 | 0 | 0 | -62.8156 | 52.5 | 583.2891 | 3000 | 0 | 3000 | 3000 | 0 | 145.65
0 | 120.2782 | 0 | 0 | 0 | 0 | -67.7782 | 52.5 | 515.5109 | 3000 | 0 | 3000 | 3000 | 0 | 153.6
0 | 117.6863 | 0 | 0 | 0 | 0 | -65.1863 | 52.5 | 450.3246 | 3000 | 0 | 3000 | 3000 | 0 | 185.97
0 | 90.3953 | 0 | 0 | 0 | 0 | -90.3953 | 0 | 359.9293 | 0 | 0 | 0 | 0 | 27.0371 | 0
0 | 100.0508 | 0 | 0 | 0 | 0 | -100.0508 | 0 | 259.8785 | 0 | 0 | 0 | 0 | 118.9634 | 0
0 | 259.8785 | 0 | 0 | 0 | 0 | -259.8785 | 0 | 0 | 0 | 0 | 0 | 0 | 183.8525 | 0
0 | 7.8543 | 0 | 0 | 0 | 0 | 0 | 7.8543 | 0 | 448.8163 | 0 | 448.8163 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2599.8505 | 0 | 176.0619
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2599.8505 | 0 | 155.5231
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2648.5174 | 0 | 145.6685
0 | 40.3442 | 0 | 0 | 0 | 0 | 12.1558 | 52.5 | 12.1558 | 3000 | 21.7207 | 3021.7207 | 2767.5718 | 0 | 157.7516
0 | 39.426 | 0 | 0 | 0 | 0 | 13.074 | 52.5 | 25.2298 | 3000 | 23.3616 | 3023.3616 | 2715.1383 | 0 | 157.1522
0 | 44.965 | 0 | 0 | 0 | 0 | 7.535 | 52.5 | 32.7648 | 3000 | 13.464 | 3013.464 | 2932.3526 | 0 | 179.5773
0 | 66.983 | 0 | 0 | 0 | 0 | -14.483 | 52.5 | 18.2818 | 3000 | 0 | 3000 | 2994.5926 | 0 | 200.4281
0 | 18.2818 | 0 | 0 | 0 | 0 | -18.2818 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 200.91
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 180.45
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 163.5
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 154.44
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 151.56
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 141.93
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 139.08
0 | 24.2775 | 0 | 0 | 0 | 0 | 28.2225 | 52.5 | 28.2225 | 3000 | 50.4298 | 3050.4298 | 3050.4298 | 0 | 137.5439
0 | 29.237 | 0 | 0 | 0 | 0 | 23.263 | 52.5 | 51.4855 | 3000 | 41.568 | 3041.568 | 3041.568 | 0 | 138.0568
0 | 42.0361 | 0 | 0 | 0 | 0 | 10.4639 | 52.5 | 61.9495 | 3000 | 18.6976 | 3018.6976 | 3018.6976 | 0 | 149.1237
0 | 107.4987 | 0 | 0 | 0 | 0 | -54.9987 | 52.5 | 6.9507 | 3000 | 0 | 3000 | 3000 | 0 | 167.1
0 | 59.4507 | 0 | 0 | 0 | 0 | -6.9507 | 52.5 | 0 | 3000 | 0 | 3000 | 2983.7777 | 0 | 201.1066
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2965 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 183.8525 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2751.2584 | 0 | 190.1395
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2567.406 | 0 | 170.0393
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2432.2204 | 0 | 138.6609
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2291.6273 | 0 | 124.802
0 | 52.4764 | 0 | 0 | 0 | 0 | 0.023595 | 52.5 | 0.023595 | 3000 | 0.042162 | 3000.0422 | 2453.8922 | 0 | 132.1912
0 | 33.3966 | 0 | 0 | 0 | 0 | 19.1034 | 52.5 | 19.127 | 3000 | 34.1352 | 3034.1352 | 2693.4674 | 0 | 152.9889
0 | 52.1502 | 0 | 0 | 0 | 0 | 0.34983 | 52.5 | 19.4768 | 3000 | 0.6251 | 3000.6251 | 2892.4766 | 0 | 176.0651
0 | 71.9768 | 0 | 0 | 0 | 0 | -19.4768 | 52.5 | 0 | 3000 | 0 | 3000 | 2994.5926 | 0 | 196.6549
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 205.47
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 166.35
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 159.51
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 157.14
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 146.25
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 145.65
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 138.12
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 135.06
0 | 23.2677 | 0 | 0 | 0 | 0 | 29.2323 | 52.5 | 29.2323 | 3000 | 52.2342 | 3052.2342 | 3052.2342 | 0 | 135.5497
0 | 27.7044 | 0 | 0 | 0 | 0 | 24.7956 | 52.5 | 54.0279 | 3000 | 44.3065 | 3044.3065 | 3044.3065 | 0 | 137.1765
0 | 46.1264 | 0 | 0 | 0 | 0 | 6.3736 | 52.5 | 60.4015 | 3000 | 11.3887 | 3011.3887 | 3011.3887 | 0 | 144.2154
0 | 71.1711 | 0 | 0 | 0 | 0 | -18.6711 | 52.5 | 41.7304 | 3000 | 0 | 3000 | 3000 | 0 | 163.65
0 | 94.2304 | 0 | 0 | 0 | 0 | -41.7304 | 52.5 | 0 | 3000 | 0 | 3000 | 2983.7777 | 0 | 190.9021
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2886.4441 | 0 | 199.4821
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2816.1475 | 0 | 194.624
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2686.3693 | 0 | 177.5153
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2497.1095 | 0 | 154.646
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2610.6654 | 0 | 153.1416
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2610.6654 | 0 | 144.6048
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2486.2946 | 0 | 131.699
0 | 52.166 | 0 | 0 | 0 | 0 | 0.33401 | 52.5 | 0.33401 | 3000 | 0.59684 | 3000.5968 | 2600.4474 | 0 | 134.6512
0 | 43.1708 | 0 | 0 | 0 | 0 | 9.3292 | 52.5 | 9.6632 | 3000 | 16.67 | 3016.67 | 2930.1512 | 0 | 154.7413
0 | 62.1632 | 0 | 0 | 0 | 0 | -9.6632 | 52.5 | 0 | 3000 | 0 | 3000 | 2994.5926 | 0 | 164.4031
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 175.23
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 159.39
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 152.01
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 135.21
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 135.63
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 123.09
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 126
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 120.81
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 120.6
0 | 33.81 | 0 | 0 | 0 | 0 | 18.69 | 52.5 | 18.69 | 3000 | 33.3965 | 3033.3965 | 3033.3965 | 0 | 119.5765
0 | 35.8182 | 0 | 0 | 0 | 0 | 16.6818 | 52.5 | 35.3718 | 3000 | 29.8081 | 3029.8081 | 3029.8081 | 0 | 121.7983
0 | 40.564 | 0 | 0 | 0 | 0 | 11.936 | 52.5 | 47.3078 | 3000 | 21.3281 | 3021.3281 | 3021.3281 | 0 | 130.5818
0 | 99.8078 | 0 | 0 | 0 | 0 | -47.3078 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 153.18
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2983.7777 | 0 | 187.6796
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2870.2218 | 0 | 190.9272
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2686.3693 | 0 | 165.6953
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2643.1099 | 0 | 157.2386
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2448.4426 | 0 | 134.0767
0 | 45.9221 | 0 | 0 | 0 | 0 | 6.5779 | 52.5 | 6.5779 | 3000 | 11.7537 | 3011.7537 | 2314.1959 | 0 | 117.214
0 | 53.1132 | 0 | 0 | 0 | 0 | -0.61316 | 52.5 | 5.9647 | 3000 | 0 | 3000 | 2518.7392 | 0 | 128.632
0 | 51.7072 | 0 | 0 | 0 | 0 | 0.79278 | 52.5 | 6.7575 | 3000 | 1.4166 | 3001.4166 | 2541.7854 | 0 | 126.5301
0 | 45.0031 | 0 | 0 | 0 | 0 | 7.4969 | 52.5 | 14.2544 | 3000 | 13.3961 | 3013.3961 | 2715.9877 | 0 | 136.6957
0 | 42.9198 | 0 | 0 | 0 | 0 | 9.5802 | 52.5 | 23.8346 | 3000 | 17.1186 | 3017.1186 | 2919.7849 | 0 | 151.5952
0 | 57.1109 | 0 | 0 | 0 | 0 | -4.6109 | 52.5 | 19.2237 | 3000 | 0 | 3000 | 2994.5926 | 0 | 176.1719
0 | 71.7237 | 0 | 0 | 0 | 0 | -19.2237 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 189.33
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 185.07
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 153.15
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 144.63
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 136.05
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 121.53
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 122.4
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 123
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 116.7
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 105
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 96
0 | 47.3788 | 0 | 0 | 0 | 0 | 5.1212 | 52.5 | 5.1212 | 3000 | 9.1509 | 3009.1509 | 3009.1509 | 0 | 117.056
0 | 57.6212 | 0 | 0 | 0 | 0 | -5.1212 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 120.6
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2989.1851 | 0 | 124.9479
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2924.296 | 0 | 135.9798
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2794.5178 | 0 | 142.8837
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2453.8501 | 0 | 108.7546
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2443.0352 | 0 | 107.4935
0 | 38.1132 | 0 | 0 | 0 | 0 | 14.3868 | 52.5 | 14.3868 | 3000 | 25.7072 | 3025.7072 | 2306.5197 | 0 | 96.4125
0 | 38.0873 | 0 | 0 | 0 | 0 | 14.4127 | 52.5 | 28.7995 | 3000 | 25.7536 | 3025.7536 | 2317.3809 | 0 | 108.4534
0 | 39.402 | 0 | 0 | 0 | 0 | 13.098 | 52.5 | 41.8975 | 3000 | 23.4044 | 3023.4044 | 2477.2545 | 0 | 115.9355
0 | 35.8612 | 0 | 0 | 0 | 0 | 16.6388 | 52.5 | 58.5363 | 3000 | 29.7313 | 3029.7313 | 2818.8417 | 0 | 118.3914
0 | 45.7346 | 0 | 0 | 0 | 0 | 6.7654 | 52.5 | 65.3017 | 3000 | 12.0888 | 3012.0888 | 2963.422 | 0 | 134.9542
0 | 34.6347 | 0 | 0 | 0 | 0 | 17.8653 | 52.5 | 83.1669 | 3000 | 31.9229 | 3031.9229 | 3031.9229 | 0 | 155.2951
0 | 49.8154 | 0 | 0 | 0 | 0 | 2.6846 | 52.5 | 85.8515 | 3000 | 4.797 | 3004.797 | 3004.797 | 0 | 159.1641
0 | 42.5464 | 0 | 0 | 0 | 0 | 9.9536 | 52.5 | 95.8051 | 3000 | 17.7857 | 3017.7857 | 3017.7857 | 0 | 158.0414
0 | 34.5287 | 0 | 0 | 0 | 0 | 17.9713 | 52.5 | 113.7764 | 3000 | 32.1123 | 3032.1123 | 3032.1123 | 0 | 153.9403
0 | 29.3466 | 0 | 0 | 0 | 0 | 23.1534 | 52.5 | 136.9298 | 3000 | 41.3721 | 3041.3721 | 3041.3721 | 0 | 152.2207
0 | 189.4298 | 0 | 0 | 0 | 0 | -136.9298 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 140.46
0 | 28.9788 | 0 | 0 | 0 | 0 | 23.5212 | 52.5 | 23.5212 | 3000 | 42.0293 | 3042.0293 | 3042.0293 | 0 | 127.1872
0 | 26.4533 | 0 | 0 | 0 | 0 | 26.0467 | 52.5 | 49.5679 | 3000 | 46.542 | 3046.542 | 3046.542 | 0 | 143.8272
0 | 32.4034 | 0 | 0 | 0 | 0 | 20.0966 | 52.5 | 69.6645 | 3000 | 35.91 | 3035.91 | 3035.91 | 0 | 127.8422
0 | 26.0941 | 0 | 0 | 0 | 0 | 26.4059 | 52.5 | 96.0704 | 3000 | 47.1838 | 3047.1838 | 3047.1838 | 0 | 121.8874
0 | 29.3239 | 0 | 0 | 0 | 0 | 23.1761 | 52.5 | 119.2464 | 3000 | 41.4125 | 3041.4125 | 3041.4125 | 0 | 123.7855
0 | 26.43 | 0 | 0 | 0 | 0 | 26.07 | 52.5 | 145.3164 | 3000 | 46.5835 | 3046.5835 | 3046.5835 | 0 | 115.3437
0 | 28.7398 | 0 | 0 | 0 | 0 | 23.7602 | 52.5 | 169.0766 | 3000 | 42.4563 | 3042.4563 | 3042.4563 | 0 | 95.7461
0 | 22.2975 | 0 | 0 | 0 | 0 | 30.2025 | 52.5 | 199.279 | 3000 | 53.9678 | 3053.9678 | 3053.9678 | 0 | 105.026
0 | 31.2356 | 0 | 0 | 0 | 0 | 21.2644 | 52.5 | 220.5435 | 3000 | 37.9967 | 3037.9967 | 3027.1818 | 0 | 109.0996
0 | 40.6398 | 0 | 0 | 0 | 0 | 11.8602 | 52.5 | 232.4037 | 3000 | 21.1926 | 3021.1926 | 2902.2293 | 0 | 121.023
0 | 48.5771 | 0 | 0 | 0 | 0 | 3.9229 | 52.5 | 236.3266 | 3000 | 7.0098 | 3007.0098 | 2763.6756 | 0 | 121.5465
0 | 42.1429 | 0 | 0 | 0 | 0 | 10.3571 | 52.5 | 246.6837 | 3000 | 18.5067 | 3018.5067 | 2591.3201 | 0 | 126.1973
0 | 24.6166 | 0 | 0 | 0 | 0 | 27.8834 | 52.5 | 274.5671 | 3000 | 49.824 | 3049.824 | 2541.526 | 0 | 129.7957
0 | 43.3395 | 0 | 0 | 0 | 0 | 9.1605 | 52.5 | 283.7276 | 3000 | 16.3686 | 3016.3686 | 2416.1444 | 0 | 108.7265
0 | 37.3828 | 0 | 0 | 0 | 0 | 15.1172 | 52.5 | 298.8447 | 3000 | 27.0124 | 3027.0124 | 2599.8258 | 0 | 112.9364
0 | 52.6353 | 0 | 0 | 0 | 0 | -0.13534 | 52.5 | 298.7094 | 3000 | 0 | 3000 | 2534.9614 | 0 | 109.0033
0 | 34.5462 | 0 | 0 | 0 | 0 | 17.9538 | 52.5 | 316.6632 | 3000 | 32.081 | 3032.081 | 2669.7836 | 0 | 114.8007
0 | 33.8554 | 0 | 0 | 0 | 0 | 18.6446 | 52.5 | 335.3078 | 3000 | 33.3154 | 3033.3154 | 2908.9446 | 0 | 134.1023
0 | 49.1857 | 0 | 0 | 0 | 0 | 3.3143 | 52.5 | 338.622 | 3000 | 5.9221 | 3005.9221 | 3000.5147 | 0 | 153.9264
0 | 247.8575 | 0 | 0 | 0 | 0 | -195.3575 | 52.5 | 143.2646 | 3000 | 0 | 3000 | 3000 | 0 | 178.32
0 | 33.678 | 0 | 0 | 0 | 0 | 18.822 | 52.5 | 162.0865 | 3000 | 33.6324 | 3033.6324 | 3033.6324 | 0 | 174.5249
0 | 25.3151 | 0 | 0 | 0 | 0 | 27.1849 | 52.5 | 189.2714 | 3000 | 48.5757 | 3048.5757 | 3048.5757 | 0 | 171.6958
0 | 23.8891 | 0 | 0 | 0 | 0 | 28.6109 | 52.5 | 217.8823 | 3000 | 51.1238 | 3051.1238 | 3051.1238 | 0 | 155.7904
0 | 29.1804 | 0 | 0 | 0 | 0 | 23.3196 | 52.5 | 241.2019 | 3000 | 41.6691 | 3041.6691 | 3041.6691 | 0 | 149.2243
0 | 28.3537 | 0 | 0 | 0 | 0 | 24.1463 | 52.5 | 265.3482 | 3000 | 43.1463 | 3043.1463 | 3043.1463 | 0 | 136.4851
0 | 18.9772 | 0 | 0 | 0 | 0 | 33.5228 | 52.5 | 298.871 | 3000 | 59.9008 | 3059.9008 | 3059.9008 | 0 | 124.9051
0 | 25.7376 | 0 | 0 | 0 | 0 | 26.7624 | 52.5 | 325.6335 | 3000 | 47.8209 | 3047.8209 | 3047.8209 | 0 | 126.1798
0 | 26.595 | 0 | 0 | 0 | 0 | 25.905 | 52.5 | 351.5385 | 3000 | 46.2889 | 3046.2889 | 3046.2889 | 0 | 126.7256
0 | 37.069 | 0 | 0 | 0 | 0 | 15.431 | 52.5 | 366.9695 | 3000 | 27.5732 | 3027.5732 | 3027.5732 | 0 | 126.8553
0 | 28.1545 | 0 | 0 | 0 | 0 | 24.3455 | 52.5 | 391.315 | 3000 | 43.5021 | 3043.5021 | 3043.5021 | 0 | 129.7749
0 | 34.6607 | 0 | 0 | 0 | 0 | 17.8393 | 52.5 | 409.1543 | 3000 | 31.8765 | 3031.8765 | 3031.8765 | 0 | 130.1585
0 | 78.9795 | 0 | 0 | 0 | 0 | -26.4795 | 52.5 | 382.6748 | 3000 | 0 | 3000 | 3000 | 0 | 137.91
0 | 124.9615 | 0 | 0 | 0 | 0 | -72.4615 | 52.5 | 310.2133 | 3000 | 0 | 3000 | 2978.3703 | 0 | 161.6362
0 | 126.881 | 0 | 0 | 0 | 0 | -74.381 | 52.5 | 235.8323 | 3000 | 0 | 3000 | 2794.5178 | 0 | 177.368
0 | 134.353 | 0 | 0 | 0 | 0 | -81.853 | 52.5 | 153.9793 | 3000 | 0 | 3000 | 2561.9986 | 0 | 156.1026
0 | 94.5451 | 0 | 0 | 0 | 0 | -42.0451 | 52.5 | 111.9343 | 3000 | 0 | 3000 | 2410.5907 | 0 | 142.249
0 | 53.5131 | 0 | 0 | 0 | 0 | -1.0131 | 52.5 | 110.9211 | 3000 | 0 | 3000 | 2529.554 | 0 | 146.8659
0 | 38.9138 | 0 | 0 | 0 | 0 | 13.5862 | 52.5 | 124.5074 | 3000 | 24.2768 | 3024.2768 | 2602.4976 | 0 | 149.2012
0 | 66.1475 | 0 | 0 | 0 | 0 | -13.6475 | 52.5 | 110.8599 | 3000 | 0 | 3000 | 2486.2946 | 0 | 138.1883
0 | 128.2643 | 0 | 0 | 0 | 0 | -75.7643 | 52.5 | 35.0956 | 3000 | 0 | 3000 | 2626.8877 | 0 | 150.4419
0 | 41.3978 | 0 | 0 | 0 | 0 | 11.1022 | 52.5 | 46.1978 | 3000 | 19.8382 | 3019.8382 | 2738.6521 | 0 | 174.8082
0 | 71.427 | 0 | 0 | 0 | 0 | -18.927 | 52.5 | 27.2708 | 3000 | 0 | 3000 | 2902.6663 | 0 | 190.2698
0 | 79.7708 | 0 | 0 | 0 | 0 | -27.2708 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 209.97
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 29.5488 | 0 | 0 | 0 | 0 | 22.9512 | 52.5 | 22.9512 | 3000 | 41.0108 | 3041.0108 | 3041.0108 | 0 | 193.682
0 | 39.9719 | 0 | 0 | 0 | 0 | 12.5281 | 52.5 | 35.4794 | 3000 | 22.3861 | 3022.3861 | 3022.3861 | 0 | 170.8253
0 | 30.5866 | 0 | 0 | 0 | 0 | 21.9134 | 52.5 | 57.3927 | 3000 | 39.1563 | 3039.1563 | 3039.1563 | 0 | 166.1203
0 | 109.8927 | 0 | 0 | 0 | 0 | -57.3927 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 152.55
0 | 29.838 | 0 | 0 | 0 | 0 | 22.662 | 52.5 | 22.662 | 3000 | 40.4939 | 3040.4939 | 3040.4939 | 0 | 157.8624
0 | 27.1719 | 0 | 0 | 0 | 0 | 25.3281 | 52.5 | 47.99 | 3000 | 45.2579 | 3045.2579 | 3045.2579 | 0 | 156.8308
0 | 21.755 | 0 | 0 | 0 | 0 | 30.745 | 52.5 | 78.735 | 3000 | 54.9372 | 3054.9372 | 3054.9372 | 0 | 155.2825
0 | 29.5593 | 0 | 0 | 0 | 0 | 22.9407 | 52.5 | 101.6757 | 3000 | 40.9919 | 3040.9919 | 3040.9919 | 0 | 152.6578
0 | 31.4505 | 0 | 0 | 0 | 0 | 21.0495 | 52.5 | 122.7252 | 3000 | 37.6126 | 3037.6126 | 3037.6126 | 0 | 152.397
0 | 32.4684 | 0 | 0 | 0 | 0 | 20.0316 | 52.5 | 142.7567 | 3000 | 35.7937 | 3035.7937 | 3035.7937 | 0 | 154.8255
0 | 18.938 | 0 | 0 | 0 | 0 | 33.562 | 52.5 | 176.3187 | 3000 | 59.9708 | 3059.9708 | 3043.7485 | 0 | 177.3288
0 | 41.863 | 0 | 0 | 0 | 0 | 10.637 | 52.5 | 186.9557 | 3000 | 19.0068 | 3019.0068 | 2835.1544 | 0 | 194.2081
0 | 49.5587 | 0 | 0 | 0 | 0 | -42.1776 | 7.3811 | 144.7781 | 421.7792 | 0 | 421.7792 | 0 | 0 | 0
0 | 69.0118 | 0 | 0 | 0 | 0 | -58.3186 | 10.6932 | 86.4595 | 611.0391 | 0 | 611.0391 | 0 | 0 | 0
0 | 56.4516 | 0 | 0 | 0 | 0 | -3.9516 | 52.5 | 82.5078 | 3000 | 0 | 3000 | 2280.8124 | 0 | 149.0967
0 | 135.0078 | 0 | 0 | 0 | 0 | -82.5078 | 52.5 | 0 | 3000 | 0 | 3000 | 2129.4045 | 0 | 138.9862
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2502.5169 | 0 | 150.4013
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2659.3322 | 0 | 163.9212
0 | 50.1345 | 0 | 0 | 0 | 0 | 2.3655 | 52.5 | 2.3655 | 3000 | 4.2268 | 3004.2268 | 2739.263 | 0 | 184.3524
0 | 2.3655 | 0 | 0 | 0 | 0 | -2.3655 | 0 | 0 | 0 | 0 | 0 | 0 | 86.5188 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 34.1003 | 0 | 0 | 0 | 0 | 18.3997 | 52.5 | 18.3997 | 3000 | 32.8778 | 3032.8778 | 3032.8778 | 0 | 208.8136
0 | 21.3491 | 0 | 0 | 0 | 0 | 31.1509 | 52.5 | 49.5506 | 3000 | 55.6626 | 3055.6626 | 3055.6626 | 0 | 185.6621
0 | 26.8991 | 0 | 0 | 0 | 0 | 25.6009 | 52.5 | 75.1515 | 3000 | 45.7453 | 3045.7453 | 3045.7453 | 0 | 167.8815
0 | 20.7257 | 0 | 0 | 0 | 0 | 31.7743 | 52.5 | 106.9258 | 3000 | 56.7765 | 3056.7765 | 3056.7765 | 0 | 159.9917
0 | 35.9204 | 0 | 0 | 0 | 0 | 16.5796 | 52.5 | 123.5055 | 3000 | 29.6256 | 3029.6256 | 3029.6256 | 0 | 158.9039
0 | 19.5208 | 0 | 0 | 0 | 0 | 32.9792 | 52.5 | 156.4847 | 3000 | 58.9295 | 3058.9295 | 3058.9295 | 0 | 157.1984
0 | 18.6993 | 0 | 0 | 0 | 0 | 33.8007 | 52.5 | 190.2854 | 3000 | 60.3974 | 3060.3974 | 3060.3974 | 0 | 156.5087
0 | 28.5435 | 0 | 0 | 0 | 0 | 23.9565 | 52.5 | 214.2419 | 3000 | 42.8072 | 3042.8072 | 3042.8072 | 0 | 153.9052
0 | 229.0389 | 0 | 0 | 0 | 0 | -176.5389 | 52.5 | 37.703 | 3000 | 0 | 3000 | 3000 | 0 | 153.45
0 | 51.7201 | 0 | 0 | 0 | 0 | 0.77992 | 52.5 | 38.483 | 3000 | 1.3936 | 3001.3936 | 3001.3936 | 0 | 158.2335
0 | 90.983 | 0 | 0 | 0 | 0 | -38.483 | 52.5 | 0 | 3000 | 0 | 3000 | 2983.7777 | 0 | 178.7283
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2778.2956 | 0 | 192.0358
0 | 7.0026 | 0 | 0 | 0 | 0 | 0 | 7.0026 | 0 | 400.1495 | 0 | 400.1495 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2405.1832 | 0 | 165.7652
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2291.6273 | 0 | 138.6435
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2242.9605 | 0 | 128.9254
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2302.4421 | 0 | 124.8154
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2475.4798 | 0 | 134.171
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2680.9619 | 0 | 152.4931
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2918.8886 | 0 | 196.4704
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 30.8161 | 0 | 0 | 0 | 0 | 21.6839 | 52.5 | 21.6839 | 3000 | 38.7463 | 3038.7463 | 3038.7463 | 0 | 203.9607
0 | 33.1834 | 0 | 0 | 0 | 0 | 19.3166 | 52.5 | 41.0005 | 3000 | 34.5161 | 3034.5161 | 3034.5161 | 0 | 177.2764
0 | 27.3514 | 0 | 0 | 0 | 0 | 25.1486 | 52.5 | 66.1491 | 3000 | 44.9372 | 3044.9372 | 3044.9372 | 0 | 166.7408
0 | 31.4089 | 0 | 0 | 0 | 0 | 21.0911 | 52.5 | 87.2402 | 3000 | 37.6869 | 3037.6869 | 3037.6869 | 0 | 145.5052
0 | 25.3325 | 0 | 0 | 0 | 0 | 27.1675 | 52.5 | 114.4076 | 3000 | 48.5446 | 3048.5446 | 3048.5446 | 0 | 150.1408
0 | 25.6153 | 0 | 0 | 0 | 0 | 26.8847 | 52.5 | 141.2923 | 3000 | 48.0394 | 3048.0394 | 3048.0394 | 0 | 150.055
0 | 24.1831 | 0 | 0 | 0 | 0 | 28.3169 | 52.5 | 169.6092 | 3000 | 50.5985 | 3050.5985 | 3050.5985 | 0 | 149.2353
0 | 25.0701 | 0 | 0 | 0 | 0 | 27.4299 | 52.5 | 197.0391 | 3000 | 49.0136 | 3049.0136 | 3049.0136 | 0 | 146.8405
0 | 31.063 | 0 | 0 | 0 | 0 | 21.437 | 52.5 | 218.4761 | 3000 | 38.305 | 3038.305 | 3038.305 | 0 | 146.9628
0 | 41.6125 | 0 | 0 | 0 | 0 | 10.8875 | 52.5 | 229.3636 | 3000 | 19.4545 | 3019.4545 | 3019.4545 | 0 | 151.6672
0 | 107.4451 | 0 | 0 | 0 | 0 | -54.9451 | 52.5 | 174.4185 | 3000 | 0 | 3000 | 2989.1851 | 0 | 164.1063
0 | 132.3404 | 0 | 0 | 0 | 0 | -79.8404 | 52.5 | 94.5781 | 3000 | 0 | 3000 | 2837.7772 | 0 | 170.8058
0 | 90.1291 | 0 | 0 | 0 | 0 | -37.6291 | 52.5 | 56.949 | 3000 | 0 | 3000 | 2594.4431 | 0 | 154.525
0 | 48.8946 | 0 | 0 | 0 | 0 | 3.6054 | 52.5 | 60.5544 | 3000 | 6.4424 | 3006.4424 | 2395.4033 | 0 | 144.2272
0 | 57.7205 | 0 | 0 | 0 | 0 | -5.2205 | 52.5 | 55.334 | 3000 | 0 | 3000 | 2264.5902 | 0 | 125.73
0 | 80.4198 | 0 | 0 | 0 | 0 | -27.9198 | 52.5 | 27.4141 | 3000 | 0 | 3000 | 2242.9605 | 0 | 120.7161
0 | 79.9141 | 0 | 0 | 0 | 0 | -27.4141 | 52.5 | 0 | 3000 | 0 | 3000 | 2318.6644 | 0 | 120.6633
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2486.2946 | 0 | 131.9974
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2691.7768 | 0 | 155.3424
0 | 37.8236 | 0 | 0 | 0 | 0 | 14.6764 | 52.5 | 14.6764 | 3000 | 26.2247 | 3026.2247 | 2955.9282 | 0 | 182.3808
0 | 44.1697 | 0 | 0 | 0 | 0 | 8.3303 | 52.5 | 23.0067 | 3000 | 14.8852 | 3014.8852 | 3014.8852 | 0 | 199.2236
0 | 23.0067 | 0 | 0 | 0 | 0 | -23.0067 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 27.544 | 0 | 0 | 0 | 0 | 24.956 | 52.5 | 24.956 | 3000 | 44.5931 | 3044.5931 | 3044.5931 | 0 | 188.6734
0 | 25.7924 | 0 | 0 | 0 | 0 | 26.7076 | 52.5 | 51.6636 | 3000 | 47.7229 | 3047.7229 | 3047.7229 | 0 | 182.5586
0 | 32.8468 | 0 | 0 | 0 | 0 | 19.6532 | 52.5 | 71.3168 | 3000 | 35.1176 | 3035.1176 | 3035.1176 | 0 | 173.2445
0 | 28.7697 | 0 | 0 | 0 | 0 | 23.7303 | 52.5 | 95.0471 | 3000 | 42.4029 | 3042.4029 | 3042.4029 | 0 | 164.0768
0 | 147.5471 | 0 | 0 | 0 | 0 | -95.0471 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 153.12
0 | 29.9476 | 0 | 0 | 0 | 0 | 22.5524 | 52.5 | 22.5524 | 3000 | 40.2981 | 3040.2981 | 3040.2981 | 0 | 154.8728
0 | 29.5769 | 0 | 0 | 0 | 0 | 22.9231 | 52.5 | 45.4755 | 3000 | 40.9605 | 3040.9605 | 3040.9605 | 0 | 147.4562
0 | 36.1266 | 0 | 0 | 0 | 0 | 16.3734 | 52.5 | 61.8489 | 3000 | 29.2571 | 3029.2571 | 3029.2571 | 0 | 133.257
0 | 114.3489 | 0 | 0 | 0 | 0 | -61.8489 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 126.36
0 | 26.5849 | 0 | 0 | 0 | 0 | 25.9151 | 52.5 | 25.9151 | 3000 | 46.3069 | 3046.3069 | 3046.3069 | 0 | 125.4165
0 | 37.2112 | 0 | 0 | 0 | 0 | 15.2888 | 52.5 | 41.2039 | 3000 | 27.3191 | 3027.3191 | 3027.3191 | 0 | 124.5439
0 | 70.2345 | 0 | 0 | 0 | 0 | -17.7345 | 52.5 | 23.4695 | 3000 | 0 | 3000 | 2994.5926 | 0 | 132.0615
0 | 75.9695 | 0 | 0 | 0 | 0 | -23.4695 | 52.5 | 0 | 3000 | 0 | 3000 | 2951.3332 | 0 | 147.3306
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2908.0738 | 0 | 143.2808
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2881.0366 | 0 | 144.2535
0 | 48.7099 | 0 | 0 | 0 | 0 | 3.7901 | 52.5 | 3.7901 | 3000 | 6.7725 | 3006.7725 | 2871.5868 | 0 | 153.515
0 | 50.4119 | 0 | 0 | 0 | 0 | 2.0881 | 52.5 | 5.8782 | 3000 | 3.7311 | 3003.7311 | 2803.6564 | 0 | 137.4913
0 | 38.5563 | 0 | 0 | 0 | 0 | 13.9437 | 52.5 | 19.8219 | 3000 | 24.9155 | 3024.9155 | 2895.1373 | 0 | 147.3625
0 | 49.4493 | 0 | 0 | 0 | 0 | 3.0507 | 52.5 | 22.8726 | 3000 | 5.4511 | 3005.4511 | 2929.7472 | 0 | 141.8877
0 | 52.7903 | 0 | 0 | 0 | 0 | -0.29031 | 52.5 | 22.5823 | 3000 | 0 | 3000 | 2956.7406 | 0 | 137.4884
0 | 39.0602 | 0 | 0 | 0 | 0 | 13.4398 | 52.5 | 36.0221 | 3000 | 24.0152 | 3024.0152 | 3007.7929 | 0 | 139.9225
0 | 20.7648 | 0 | 0 | 0 | 0 | 31.7352 | 52.5 | 67.7573 | 3000 | 56.7066 | 3056.7066 | 3056.7066 | 0 | 142.412
0 | 55.943 | 0 | 0 | 0 | 0 | -3.443 | 52.5 | 64.3143 | 3000 | 0 | 3000 | 3000 | 0 | 159
0 | 59.9599 | 0 | 0 | 0 | 0 | -7.4599 | 52.5 | 56.8544 | 3000 | 0 | 3000 | 3000 | 0 | 159.24
0 | 32.9781 | 0 | 0 | 0 | 0 | 19.5219 | 52.5 | 76.3763 | 3000 | 34.883 | 3034.883 | 3034.883 | 0 | 157.8443
0 | 34.1425 | 0 | 0 | 0 | 0 | 18.3575 | 52.5 | 94.7338 | 3000 | 32.8023 | 3032.8023 | 3032.8023 | 0 | 142.4811
0 | 30.2502 | 0 | 0 | 0 | 0 | 22.2498 | 52.5 | 116.9836 | 3000 | 39.7575 | 3039.7575 | 3039.7575 | 0 | 137.1235
0 | 32.3278 | 0 | 0 | 0 | 0 | 20.1722 | 52.5 | 137.1558 | 3000 | 36.045 | 3036.045 | 3036.045 | 0 | 138.1097
0 | 32.5252 | 0 | 0 | 0 | 0 | 19.9748 | 52.5 | 157.1306 | 3000 | 35.6923 | 3035.6923 | 3035.6923 | 0 | 130.7169
0 | 27.5971 | 0 | 0 | 0 | 0 | 24.9029 | 52.5 | 182.0334 | 3000 | 44.4981 | 3044.4981 | 3044.4981 | 0 | 141.5692
0 | 37.5691 | 0 | 0 | 0 | 0 | 14.9309 | 52.5 | 196.9643 | 3000 | 26.6796 | 3026.6796 | 3026.6796 | 0 | 136.4124
0 | 25.5084 | 0 | 0 | 0 | 0 | 26.9916 | 52.5 | 223.9559 | 3000 | 48.2303 | 3048.2303 | 3048.2303 | 0 | 125.2823
0 | 33.4642 | 0 | 0 | 0 | 0 | 19.0358 | 52.5 | 242.9917 | 3000 | 34.0144 | 3034.0144 | 3034.0144 | 0 | 121.3606
0 | 26.7852 | 0 | 0 | 0 | 0 | 25.7148 | 52.5 | 268.7065 | 3000 | 45.949 | 3045.949 | 3045.949 | 0 | 103.5318
0 | 28.9048 | 0 | 0 | 0 | 0 | 23.5952 | 52.5 | 292.3016 | 3000 | 42.1614 | 3042.1614 | 3042.1614 | 0 | 112.1341
0 | 24.8524 | 0 | 0 | 0 | 0 | 27.6476 | 52.5 | 319.9492 | 3000 | 49.4026 | 3049.4026 | 3043.9952 | 0 | 124.7429
0 | 55.2962 | 0 | 0 | 0 | 0 | -2.7962 | 52.5 | 317.153 | 3000 | 0 | 3000 | 2929.7035 | 0 | 148.536
0 | 61.4029 | 0 | 0 | 0 | 0 | -8.9029 | 52.5 | 308.2502 | 3000 | 0 | 3000 | 2832.3698 | 0 | 146.122
0 | 71.0691 | 0 | 0 | 0 | 0 | -18.5691 | 52.5 | 289.6811 | 3000 | 0 | 3000 | 2772.8881 | 0 | 146.8244
0 | 44.8909 | 0 | 0 | 0 | 0 | 7.6091 | 52.5 | 297.2902 | 3000 | 13.5964 | 3013.5964 | 2856.7811 | 0 | 152.6378
0 | 41.7023 | 0 | 0 | 0 | 0 | 10.7977 | 52.5 | 308.0879 | 3000 | 19.294 | 3019.294 | 2483.9589 | 0 | 129.4143
0 | 51.443 | 0 | 0 | 0 | 0 | 1.057 | 52.5 | 309.1448 | 3000 | 1.8886 | 3001.8886 | 2396.257 | 0 | 108.5504
0 | 44.8028 | 0 | 0 | 0 | 0 | 7.6972 | 52.5 | 316.842 | 3000 | 13.7539 | 3013.7539 | 2548.7153 | 0 | 114.6922
0 | 40.2523 | 0 | 0 | 0 | 0 | 12.2477 | 52.5 | 329.0898 | 3000 | 21.885 | 3021.885 | 2794.7732 | 0 | 119.0573
0 | 53.8849 | 0 | 0 | 0 | 0 | -1.3849 | 52.5 | 327.7048 | 3000 | 0 | 3000 | 2940.5183 | 0 | 126.2659
0 | 43.1972 | 0 | 0 | 0 | 0 | 9.3028 | 52.5 | 337.0077 | 3000 | 16.6229 | 3016.6229 | 3016.6229 | 0 | 135.748
0 | 36.1383 | 0 | 0 | 0 | 0 | 16.3617 | 52.5 | 353.3693 | 3000 | 29.2361 | 3029.2361 | 3029.2361 | 0 | 148.1599
0 | 50.4902 | 0 | 0 | 0 | 0 | 2.0098 | 52.5 | 355.3791 | 3000 | 3.5913 | 3003.5913 | 3003.5913 | 0 | 163.5155
0 | 29.4296 | 0 | 0 | 0 | 0 | 23.0704 | 52.5 | 378.4495 | 3000 | 41.2237 | 3041.2237 | 3041.2237 | 0 | 159.0864
0 | 21.3992 | 0 | 0 | 0 | 0 | 31.1008 | 52.5 | 409.5502 | 3000 | 55.5729 | 3055.5729 | 3055.5729 | 0 | 158.5231
0 | 33.3301 | 0 | 0 | 0 | 0 | 19.1699 | 52.5 | 428.7201 | 3000 | 34.2541 | 3034.2541 | 3034.2541 | 0 | 130.0178
0 | 232.3984 | 0 | 0 | 0 | 0 | -179.8984 | 52.5 | 248.8218 | 3000 | 0 | 3000 | 3000 | 0 | 131.43
0 | 36.7762 | 0 | 0 | 0 | 0 | 15.7238 | 52.5 | 264.5455 | 3000 | 28.0963 | 3028.0963 | 3028.0963 | 0 | 133.2362
0 | 35.9334 | 0 | 0 | 0 | 0 | 16.5666 | 52.5 | 281.1121 | 3000 | 29.6023 | 3029.6023 | 3029.6023 | 0 | 109.0657
0 | 35.6906 | 0 | 0 | 0 | 0 | 16.8094 | 52.5 | 297.9215 | 3000 | 30.0362 | 3030.0362 | 3030.0362 | 0 | 123.3225
0 | 43.1616 | 0 | 0 | 0 | 0 | 9.3384 | 52.5 | 307.2599 | 3000 | 16.6865 | 3016.6865 | 3016.6865 | 0 | 125.7958
0 | 79.9973 | 0 | 0 | 0 | 0 | -27.4973 | 52.5 | 279.7627 | 3000 | 0 | 3000 | 3000 | 0 | 125.1
0 | 99.3603 | 0 | 0 | 0 | 0 | -46.8603 | 52.5 | 232.9024 | 3000 | 0 | 3000 | 3000 | 0 | 120
0 | 115.1287 | 0 | 0 | 0 | 0 | -62.6287 | 52.5 | 170.2737 | 3000 | 0 | 3000 | 3000 | 0 | 122.58
0 | 92.8322 | 0 | 0 | 0 | 0 | -40.3322 | 52.5 | 129.9415 | 3000 | 0 | 3000 | 2994.5926 | 0 | 129.8156
0 | 105.9819 | 0 | 0 | 0 | 0 | -53.4819 | 52.5 | 76.4595 | 3000 | 0 | 3000 | 2935.1109 | 0 | 118.5785
0 | 96.6991 | 0 | 0 | 0 | 0 | -44.1991 | 52.5 | 32.2605 | 3000 | 0 | 3000 | 2767.4807 | 0 | 108.4852
0 | 84.7605 | 0 | 0 | 0 | 0 | -32.2605 | 52.5 | 0 | 3000 | 0 | 3000 | 2567.406 | 0 | 113.2483
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2415.9981 | 0 | 108.0676
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2659.3322 | 0 | 130.5998
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2853.9995 | 0 | 150.577
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2799.9253 | 0 | 143.5242
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2902.6663 | 0 | 147.8038
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2978.3703 | 0 | 151.8373
0 | 36.9867 | 0 | 0 | 0 | 0 | 15.5133 | 52.5 | 15.5133 | 3000 | 27.7203 | 3027.7203 | 3027.7203 | 0 | 161.0444
0 | 42.0269 | 0 | 0 | 0 | 0 | 10.4731 | 52.5 | 25.9865 | 3000 | 18.7141 | 3018.7141 | 3018.7141 | 0 | 169.7121
0 | 44.4824 | 0 | 0 | 0 | 0 | 8.0176 | 52.5 | 34.0041 | 3000 | 14.3264 | 3014.3264 | 3014.3264 | 0 | 174.3185
0 | 34.6967 | 0 | 0 | 0 | 0 | 17.8033 | 52.5 | 51.8074 | 3000 | 31.8121 | 3031.8121 | 3031.8121 | 0 | 169.9028
0 | 31.3369 | 0 | 0 | 0 | 0 | 21.1631 | 52.5 | 72.9705 | 3000 | 37.8156 | 3037.8156 | 3037.8156 | 0 | 161.8852
0 | 27.2075 | 0 | 0 | 0 | 0 | 25.2925 | 52.5 | 98.263 | 3000 | 45.1944 | 3045.1944 | 3045.1944 | 0 | 150.1281
0 | 27.8101 | 0 | 0 | 0 | 0 | 24.6899 | 52.5 | 122.9529 | 3000 | 44.1176 | 3044.1176 | 3044.1176 | 0 | 141.1557
0 | 24.8407 | 0 | 0 | 0 | 0 | 27.6593 | 52.5 | 150.6122 | 3000 | 49.4235 | 3049.4235 | 3049.4235 | 0 | 126.4291
0 | 28.5969 | 0 | 0 | 0 | 0 | 23.9031 | 52.5 | 174.5153 | 3000 | 42.7116 | 3042.7116 | 3042.7116 | 0 | 126.8202
0 | 39.9679 | 0 | 0 | 0 | 0 | 12.5321 | 52.5 | 187.0474 | 3000 | 22.3932 | 3022.3932 | 3022.3932 | 0 | 120.7144
0 | 27.8145 | 0 | 0 | 0 | 0 | 24.6855 | 52.5 | 211.7328 | 3000 | 44.1096 | 3044.1096 | 3044.1096 | 0 | 114.1846
0 | 31.063 | 0 | 0 | 0 | 0 | 21.437 | 52.5 | 233.1698 | 3000 | 38.305 | 3038.305 | 3038.305 | 0 | 102.7555
0 | 23.0629 | 0 | 0 | 0 | 0 | 29.4371 | 52.5 | 262.6069 | 3000 | 52.6002 | 3052.6002 | 3052.6002 | 0 | 101.5295
0 | 243.9404 | 0 | 0 | 0 | 0 | -191.4404 | 52.5 | 71.1665 | 3000 | 0 | 3000 | 3000 | 0 | 116.43
0 | 78.0076 | 0 | 0 | 0 | 0 | -25.5076 | 52.5 | 45.659 | 3000 | 0 | 3000 | 2994.5926 | 0 | 151.2269
0 | 98.159 | 0 | 0 | 0 | 0 | -45.659 | 52.5 | 0 | 3000 | 0 | 3000 | 2940.5183 | 0 | 172.1968
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2881.0366 | 0 | 173.8706
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2745.851 | 0 | 164.9433
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2388.9609 | 0 | 140.877
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2583.6283 | 0 | 150.703
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2702.5916 | 0 | 153.264
0 | 34.5977 | 0 | 0 | 0 | 0 | 17.9023 | 52.5 | 17.9023 | 3000 | 31.9891 | 3031.9891 | 2767.0253 | 0 | 162.286
0 | 40.6678 | 0 | 0 | 0 | 0 | 11.8322 | 52.5 | 29.7346 | 3000 | 21.1426 | 3021.1426 | 2923.809 | 0 | 173.645
0 | 34.4673 | 0 | 0 | 0 | 0 | 18.0327 | 52.5 | 47.7673 | 3000 | 32.2221 | 3032.2221 | 3015.9998 | 0 | 185.1221
0 | 40.7859 | 0 | 0 | 0 | 0 | 11.7141 | 52.5 | 59.4814 | 3000 | 20.9315 | 3020.9315 | 3020.9315 | 0 | 189.9864
0 | 54.7552 | 0 | 0 | 0 | 0 | -2.2552 | 52.5 | 57.2262 | 3000 | 0 | 3000 | 3000 | 0 | 203.67
0 | 41.2777 | 0 | 0 | 0 | 0 | 11.2223 | 52.5 | 68.4485 | 3000 | 20.0528 | 3020.0528 | 3020.0528 | 0 | 205.122
0 | 30.9184 | 0 | 0 | 0 | 0 | 21.5816 | 52.5 | 90.0301 | 3000 | 38.5634 | 3038.5634 | 3038.5634 | 0 | 194.1946
0 | 31.7379 | 0 | 0 | 0 | 0 | 20.7621 | 52.5 | 110.7922 | 3000 | 37.0992 | 3037.0992 | 3037.0992 | 0 | 179.8266
0 | 25.9366 | 0 | 0 | 0 | 0 | 26.5634 | 52.5 | 137.3556 | 3000 | 47.4653 | 3047.4653 | 3047.4653 | 0 | 161.3633
0 | 33.9189 | 0 | 0 | 0 | 0 | 18.5811 | 52.5 | 155.9368 | 3000 | 33.202 | 3033.202 | 3033.202 | 0 | 153.1767
0 | 29.7543 | 0 | 0 | 0 | 0 | 22.7457 | 52.5 | 178.6825 | 3000 | 40.6436 | 3040.6436 | 3040.6436 | 0 | 136.829
0 | 32.8132 | 0 | 0 | 0 | 0 | 19.6868 | 52.5 | 198.3693 | 3000 | 35.1777 | 3035.1777 | 3035.1777 | 0 | 125.9599
0 | 28.3296 | 0 | 0 | 0 | 0 | 24.1704 | 52.5 | 222.5398 | 3000 | 43.1893 | 3043.1893 | 3043.1893 | 0 | 123.6752
0 | 26.132 | 0 | 0 | 0 | 0 | 26.368 | 52.5 | 248.9078 | 3000 | 47.1162 | 3047.1162 | 3047.1162 | 0 | 124.8403
0 | 40.3223 | 0 | 0 | 0 | 0 | 12.1777 | 52.5 | 261.0854 | 3000 | 21.7599 | 3021.7599 | 3021.7599 | 0 | 120.8402
0 | 35.5741 | 0 | 0 | 0 | 0 | 16.9259 | 52.5 | 278.0113 | 3000 | 30.2443 | 3030.2443 | 3030.2443 | 0 | 124.3612
0 | 60.2364 | 0 | 0 | 0 | 0 | -7.7364 | 52.5 | 270.2749 | 3000 | 0 | 3000 | 3000 | 0 | 128.82
0 | 112.2448 | 0 | 0 | 0 | 0 | -59.7448 | 52.5 | 210.5301 | 3000 | 0 | 3000 | 2994.5926 | 0 | 161.4684
0 | 137.3911 | 0 | 0 | 0 | 0 | -84.8911 | 52.5 | 125.639 | 3000 | 0 | 3000 | 2972.9629 | 0 | 179.9237
0 | 89.6171 | 0 | 0 | 0 | 0 | -37.1171 | 52.5 | 88.5218 | 3000 | 0 | 3000 | 2945.9257 | 0 | 185.5049
0 | 56.2558 | 0 | 0 | 0 | 0 | -3.7558 | 52.5 | 84.766 | 3000 | 0 | 3000 | 2918.8886 | 0 | 182.2262
0 | 45.7266 | 0 | 0 | 0 | 0 | 6.7734 | 52.5 | 91.5394 | 3000 | 12.1031 | 3012.1031 | 2849.8804 | 0 | 179.4855
0 | 78.6419 | 0 | 0 | 0 | 0 | -26.1419 | 52.5 | 65.3975 | 3000 | 0 | 3000 | 2648.5174 | 0 | 167.9955
0 | 87.8541 | 0 | 0 | 0 | 0 | -35.3541 | 52.5 | 30.0435 | 3000 | 0 | 3000 | 2524.1466 | 0 | 156.3961
0 | 82.5435 | 0 | 0 | 0 | 0 | -30.0435 | 52.5 | 0 | 3000 | 0 | 3000 | 2821.555 | 0 | 178.7173
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2918.8886 | 0 | 189.4651
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2967.5554 | 0 | 192.8911
0 | 25.824 | 0 | 0 | 0 | 0 | 26.676 | 52.5 | 26.676 | 3000 | 47.6665 | 3047.6665 | 3047.6665 | 0 | 198.2202
0 | 26.676 | 0 | 0 | 0 | 0 | -26.676 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 25.9044 | 0 | 0 | 0 | 0 | 26.5956 | 52.5 | 26.5956 | 3000 | 47.5228 | 3047.5228 | 3047.5228 | 0 | 205.0983
0 | 35.9118 | 0 | 0 | 0 | 0 | 16.5882 | 52.5 | 43.1838 | 3000 | 29.6409 | 3029.6409 | 3029.6409 | 0 | 189.5343
0 | 28.0375 | 0 | 0 | 0 | 0 | 24.4625 | 52.5 | 67.6463 | 3000 | 43.7112 | 3043.7112 | 3043.7112 | 0 | 177.4484
0 | 120.1463 | 0 | 0 | 0 | 0 | -67.6463 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 168.63
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 159.9
0 | 36.1666 | 0 | 0 | 0 | 0 | 16.3334 | 52.5 | 16.3334 | 3000 | 29.1856 | 3029.1856 | 3029.1856 | 0 | 157.4268
0 | 20.8905 | 0 | 0 | 0 | 0 | 31.6095 | 52.5 | 47.9429 | 3000 | 56.482 | 3056.482 | 3056.482 | 0 | 155.1165
0 | 33.822 | 0 | 0 | 0 | 0 | 18.678 | 52.5 | 66.6208 | 3000 | 33.3751 | 3033.3751 | 3033.3751 | 0 | 149.4544
0 | 35.9867 | 0 | 0 | 0 | 0 | 16.5133 | 52.5 | 83.1341 | 3000 | 29.507 | 3029.507 | 3029.507 | 0 | 147.8096
0 | 28.8914 | 0 | 0 | 0 | 0 | 23.6086 | 52.5 | 106.7427 | 3000 | 42.1854 | 3042.1854 | 3042.1854 | 0 | 150.4361
0 | 45.2386 | 0 | 0 | 0 | 0 | 7.2614 | 52.5 | 114.004 | 3000 | 12.9751 | 3012.9751 | 3012.9751 | 0 | 158.9043
0 | 71.3303 | 0 | 0 | 0 | 0 | -18.8303 | 52.5 | 95.1738 | 3000 | 0 | 3000 | 2994.5926 | 0 | 181.5621
0 | 95.1738 | 0 | 0 | 0 | 0 | -95.1738 | 0 | 0 | 0 | 0 | 0 | 0 | 54.0743 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 275.7787 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 270.3713 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 297.4084 | 0
0 | 11.3556 | 0 | 0 | 0 | 0 | 0 | 11.3556 | 0 | 648.891 | 0 | 648.891 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2756.6659 | 0 | 191.3677
0 | 6.1509 | 0 | 0 | 0 | 0 | 0 | 6.1509 | 0 | 351.4826 | 0 | 351.4826 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173.0376 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 32.4446 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 21.9828 | 0 | 0 | 0 | 0 | 30.5172 | 52.5 | 30.5172 | 3000 | 54.5302 | 3054.5302 | 3054.5302 | 0 | 212.1982
0 | 29.2315 | 0 | 0 | 0 | 0 | 23.2685 | 52.5 | 53.7857 | 3000 | 41.5777 | 3041.5777 | 3041.5777 | 0 | 190.1594
0 | 37.9827 | 0 | 0 | 0 | 0 | 14.5173 | 52.5 | 68.303 | 3000 | 25.9405 | 3025.9405 | 3025.9405 | 0 | 180.3158
0 | 29.7178 | 0 | 0 | 0 | 0 | 22.7822 | 52.5 | 91.0852 | 3000 | 40.7087 | 3040.7087 | 3040.7087 | 0 | 168.1512
0 | 25.1595 | 0 | 0 | 0 | 0 | 27.3405 | 52.5 | 118.4256 | 3000 | 48.8538 | 3048.8538 | 3048.8538 | 0 | 164.8515
0 | 19.3781 | 0 | 0 | 0 | 0 | 33.1219 | 52.5 | 151.5475 | 3000 | 59.1844 | 3059.1844 | 3059.1844 | 0 | 155.8654
0 | 34.3279 | 0 | 0 | 0 | 0 | 18.1721 | 52.5 | 169.7197 | 3000 | 32.4712 | 3032.4712 | 3032.4712 | 0 | 146.7716
0 | 37.2497 | 0 | 0 | 0 | 0 | 15.2503 | 52.5 | 184.97 | 3000 | 27.2503 | 3027.2503 | 3027.2503 | 0 | 144.309
0 | 34.5213 | 0 | 0 | 0 | 0 | 17.9787 | 52.5 | 202.9486 | 3000 | 32.1255 | 3032.1255 | 3032.1255 | 0 | 145.2388
0 | 64.7443 | 0 | 0 | 0 | 0 | -12.2443 | 52.5 | 190.7043 | 3000 | 0 | 3000 | 3000 | 0 | 150.75
0 | 118.423 | 0 | 0 | 0 | 0 | -65.923 | 52.5 | 124.7813 | 3000 | 0 | 3000 | 3000 | 0 | 172.47
0 | 111.3641 | 0 | 0 | 0 | 0 | -58.8641 | 52.5 | 65.9172 | 3000 | 0 | 3000 | 2967.5554 | 0 | 187.3121
0 | 118.4172 | 0 | 0 | 0 | 0 | -65.9172 | 52.5 | 0 | 3000 | 0 | 3000 | 2918.8886 | 0 | 193.4931
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2908.0738 | 0 | 184.8372
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2794.5178 | 0 | 174.7691
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2789.1104 | 0 | 171.1398
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2789.1104 | 0 | 164.3065
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2945.9257 | 0 | 175.4888
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2924.296 | 0 | 177.2416
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2989.1851 | 0 | 184.8213
0 | 38.9165 | 0 | 0 | 0 | 0 | 13.5835 | 52.5 | 13.5835 | 3000 | 24.2719 | 3024.2719 | 3024.2719 | 0 | 192.5856
0 | 44.0999 | 0 | 0 | 0 | 0 | 8.4001 | 52.5 | 21.9836 | 3000 | 15.0098 | 3015.0098 | 3015.0098 | 0 | 199.5032
0 | 46.6819 | 0 | 0 | 0 | 0 | 5.8181 | 52.5 | 27.8016 | 3000 | 10.3961 | 3010.3961 | 3010.3961 | 0 | 190.2269
0 | 37.9768 | 0 | 0 | 0 | 0 | 14.5232 | 52.5 | 42.3248 | 3000 | 25.951 | 3025.951 | 3025.951 | 0 | 186.7617
0 | 27.7712 | 0 | 0 | 0 | 0 | 24.7288 | 52.5 | 67.0536 | 3000 | 44.1871 | 3044.1871 | 3044.1871 | 0 | 182.5903
0 | 25.4629 | 0 | 0 | 0 | 0 | 27.0371 | 52.5 | 94.0907 | 3000 | 48.3116 | 3048.3116 | 3048.3116 | 0 | 160.9509
0 | 24.926 | 0 | 0 | 0 | 0 | 27.574 | 52.5 | 121.6647 | 3000 | 49.2711 | 3049.2711 | 3049.2711 | 0 | 159.4769
0 | 30.2592 | 0 | 0 | 0 | 0 | 22.2408 | 52.5 | 143.9055 | 3000 | 39.7413 | 3039.7413 | 3039.7413 | 0 | 149.2513
0 | 25.7509 | 0 | 0 | 0 | 0 | 26.7491 | 52.5 | 170.6546 | 3000 | 47.7971 | 3047.7971 | 3047.7971 | 0 | 139.6501
0 | 31.6884 | 0 | 0 | 0 | 0 | 20.8116 | 52.5 | 191.4662 | 3000 | 37.1875 | 3037.1875 | 3037.1875 | 0 | 141.5329
0 | 26.2972 | 0 | 0 | 0 | 0 | 26.2028 | 52.5 | 217.669 | 3000 | 46.8209 | 3046.8209 | 3046.8209 | 0 | 143.4139
0 | 31.6963 | 0 | 0 | 0 | 0 | 20.8037 | 52.5 | 238.4727 | 3000 | 37.1734 | 3037.1734 | 3037.1734 | 0 | 142.2005
0 | 35.2749 | 0 | 0 | 0 | 0 | 17.2251 | 52.5 | 255.6978 | 3000 | 30.7789 | 3030.7789 | 3030.7789 | 0 | 146.0532
0 | 62.4036 | 0 | 0 | 0 | 0 | -9.9036 | 52.5 | 245.7942 | 3000 | 0 | 3000 | 3000 | 0 | 150.66
0 | 40.6545 | 0 | 0 | 0 | 0 | 11.8455 | 52.5 | 257.6397 | 3000 | 21.1664 | 3021.1664 | 3015.7589 | 0 | 180.644
0 | 248.5891 | 0 | 0 | 0 | 0 | -196.0891 | 52.5 | 61.5506 | 3000 | 0 | 3000 | 2908.0738 | 0 | 193.3578
0 | 41.9814 | 0 | 0 | 0 | 0 | 10.5186 | 52.5 | 72.0692 | 3000 | 18.7953 | 3018.7953 | 2678.1275 | 0 | 185.6478
0 | 49.1528 | 0 | 0 | 0 | 0 | -40.0683 | 9.0845 | 32.0008 | 519.1128 | 0 | 519.1128 | 0 | 0 | 0
0 | 70.2473 | 0 | 0 | 0 | 0 | -17.7473 | 52.5 | 14.2535 | 3000 | 0 | 3000 | 2351.109 | 0 | 164.1309
0 | 66.7535 | 0 | 0 | 0 | 0 | -14.2535 | 52.5 | 0 | 3000 | 0 | 3000 | 2318.6644 | 0 | 159.5705
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2383.5535 | 0 | 160.7468
0 | 51.6903 | 0 | 0 | 0 | 0 | 0.80971 | 52.5 | 0.80971 | 3000 | 1.4468 | 3001.4468 | 2531.0008 | 0 | 170.8932
0 | 53.3097 | 0 | 0 | 0 | 0 | -0.80971 | 52.5 | 0 | 3000 | 0 | 3000 | 2756.6659 | 0 | 187.4808
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2967.5554 | 0 | 199.3901
0 | 39.2255 | 0 | 0 | 0 | 0 | 13.2745 | 52.5 | 13.2745 | 3000 | 23.7198 | 3023.7198 | 3023.7198 | 0 | 209.5438
0 | 13.2745 | 0 | 0 | 0 | 0 | -13.2745 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 35.6358 | 0 | 0 | 0 | 0 | 16.8642 | 52.5 | 16.8642 | 3000 | 30.134 | 3030.134 | 3030.134 | 0 | 202.9281
0 | 31.0768 | 0 | 0 | 0 | 0 | 21.4232 | 52.5 | 38.2873 | 3000 | 38.2804 | 3038.2804 | 3038.2804 | 0 | 186.5808
0 | 27.6618 | 0 | 0 | 0 | 0 | 24.8382 | 52.5 | 63.1255 | 3000 | 44.3825 | 3044.3825 | 3044.3825 | 0 | 178.6748
0 | 33.8777 | 0 | 0 | 0 | 0 | 18.6223 | 52.5 | 81.7478 | 3000 | 33.2755 | 3033.2755 | 3033.2755 | 0 | 178.3566
0 | 34.4261 | 0 | 0 | 0 | 0 | 18.0739 | 52.5 | 99.8217 | 3000 | 32.2957 | 3032.2957 | 3032.2957 | 0 | 164.7749
0 | 28.6679 | 0 | 0 | 0 | 0 | 23.8321 | 52.5 | 123.6538 | 3000 | 42.5848 | 3042.5848 | 3042.5848 | 0 | 175.3442
0 | 39.3313 | 0 | 0 | 0 | 0 | 13.1687 | 52.5 | 136.8225 | 3000 | 23.5306 | 3023.5306 | 3023.5306 | 0 | 165.629
0 | 31.6504 | 0 | 0 | 0 | 0 | 20.8496 | 52.5 | 157.672 | 3000 | 37.2554 | 3037.2554 | 3037.2554 | 0 | 163.4347
0 | 30.6089 | 0 | 0 | 0 | 0 | 21.8911 | 52.5 | 179.5631 | 3000 | 39.1164 | 3039.1164 | 3039.1164 | 0 | 157.8517
0 | 31.7271 | 0 | 0 | 0 | 0 | 20.7729 | 52.5 | 200.336 | 3000 | 37.1183 | 3037.1183 | 3037.1183 | 0 | 155.5005
0 | 43.5231 | 0 | 0 | 0 | 0 | 8.9769 | 52.5 | 209.3129 | 3000 | 16.0405 | 3016.0405 | 3016.0405 | 0 | 154.2102
0 | 93.9625 | 0 | 0 | 0 | 0 | -41.4625 | 52.5 | 167.8504 | 3000 | 0 | 3000 | 2994.5926 | 0 | 163.4149
0 | 120.2883 | 0 | 0 | 0 | 0 | -67.7883 | 52.5 | 100.0621 | 3000 | 0 | 3000 | 2972.9629 | 0 | 168.1508
0 | 104.4503 | 0 | 0 | 0 | 0 | -51.9503 | 52.5 | 48.1118 | 3000 | 0 | 3000 | 2935.1109 | 0 | 167.36
0 | 100.6118 | 0 | 0 | 0 | 0 | -48.1118 | 52.5 | 0 | 3000 | 0 | 3000 | 2837.7772 | 0 | 169.0464
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2729.6287 | 0 | 161.4575
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2881.0366 | 0 | 165.8037
0 | 46.9771 | 0 | 0 | 0 | 0 | 5.5229 | 52.5 | 5.5229 | 3000 | 9.8688 | 3009.8688 | 2863.8683 | 0 | 161.5794
0 | 52.2101 | 0 | 0 | 0 | 0 | 0.2899 | 52.5 | 5.8129 | 3000 | 0.51802 | 3000.518 | 2908.5918 | 0 | 160.0016
0 | 58.3129 | 0 | 0 | 0 | 0 | -5.8129 | 52.5 | 0 | 3000 | 0 | 3000 | 2935.1109 | 0 | 161.3137
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2972.9629 | 0 | 168.4778
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 176.43
0 | 45.6798 | 0 | 0 | 0 | 0 | 6.8202 | 52.5 | 6.8202 | 3000 | 12.1868 | 3012.1868 | 3012.1868 | 0 | 195.6415
0 | 45.3623 | 0 | 0 | 0 | 0 | 7.1377 | 52.5 | 13.9579 | 3000 | 12.7541 | 3012.7541 | 3012.7541 | 0 | 198.8418
0 | 24.8606 | 0 | 0 | 0 | 0 | 27.6394 | 52.5 | 41.5974 | 3000 | 49.388 | 3049.388 | 3049.388 | 0 | 193.4837
0 | 30.9704 | 0 | 0 | 0 | 0 | 21.5296 | 52.5 | 63.127 | 3000 | 38.4706 | 3038.4706 | 3038.4706 | 0 | 175.4717
0 | 29.8339 | 0 | 0 | 0 | 0 | 22.6661 | 52.5 | 85.7931 | 3000 | 40.5013 | 3040.5013 | 3040.5013 | 0 | 168.3222
0 | 21.1899 | 0 | 0 | 0 | 0 | 31.3101 | 52.5 | 117.1032 | 3000 | 55.9469 | 3055.9469 | 3055.9469 | 0 | 167.0381
0 | 33.0359 | 0 | 0 | 0 | 0 | 19.4641 | 52.5 | 136.5673 | 3000 | 34.7798 | 3034.7798 | 3034.7798 | 0 | 156.8071
0 | 32.692 | 0 | 0 | 0 | 0 | 19.808 | 52.5 | 156.3753 | 3000 | 35.3942 | 3035.3942 | 3035.3942 | 0 | 159.5707
0 | 34.4012 | 0 | 0 | 0 | 0 | 18.0988 | 52.5 | 174.474 | 3000 | 32.3401 | 3032.3401 | 3032.3401 | 0 | 152.5267
0 | 27.8654 | 0 | 0 | 0 | 0 | 24.6346 | 52.5 | 199.1087 | 3000 | 44.0188 | 3044.0188 | 3044.0188 | 0 | 152.5967
0 | 33.547 | 0 | 0 | 0 | 0 | 18.953 | 52.5 | 218.0617 | 3000 | 33.8665 | 3033.8665 | 3033.8665 | 0 | 149.3269
0 | 31.7972 | 0 | 0 | 0 | 0 | 20.7028 | 52.5 | 238.7645 | 3000 | 36.9932 | 3036.9932 | 3036.9932 | 0 | 148.3875
0 | 29.4134 | 0 | 0 | 0 | 0 | 23.0866 | 52.5 | 261.8511 | 3000 | 41.2526 | 3041.2526 | 3041.2526 | 0 | 152.093
0 | 36.1598 | 0 | 0 | 0 | 0 | 16.3402 | 52.5 | 278.1913 | 3000 | 29.1977 | 3029.1977 | 3023.7903 | 0 | 153.0038
0 | 60.78 | 0 | 0 | 0 | 0 | -8.28 | 52.5 | 269.9113 | 3000 | 0 | 3000 | 2918.8886 | 0 | 153.3
0 | 143.5386 | 0 | 0 | 0 | 0 | -91.0386 | 52.5 | 178.8726 | 3000 | 0 | 3000 | 2680.9619 | 0 | 140.8041
0 | 126.0388 | 0 | 0 | 0 | 0 | -73.5388 | 52.5 | 105.3338 | 3000 | 0 | 3000 | 2507.9243 | 0 | 135.7289
0 | 53.7213 | 0 | 0 | 0 | 0 | -1.2213 | 52.5 | 104.1125 | 3000 | 0 | 3000 | 2361.9238 | 0 | 126.1267
0 | 49.1809 | 0 | 0 | 0 | 0 | 3.3191 | 52.5 | 107.4316 | 3000 | 5.9308 | 3005.9308 | 2335.4101 | 0 | 125.7385
0 | 56.9321 | 0 | 0 | 0 | 0 | -4.4321 | 52.5 | 102.9995 | 3000 | 0 | 3000 | 2383.5535 | 0 | 131.3338
0 | 48.8614 | 0 | 0 | 0 | 0 | 3.6386 | 52.5 | 106.6381 | 3000 | 6.5017 | 3006.5017 | 2541.4632 | 0 | 134.1893
0 | 45.7273 | 0 | 0 | 0 | 0 | 6.7727 | 52.5 | 113.4108 | 3000 | 12.1019 | 3012.1019 | 2768.7677 | 0 | 151.3962
0 | 52.5011 | 0 | 0 | 0 | 0 | -0.0010893 | 52.5 | 113.4097 | 3000 | 0 | 3000 | 2978.3703 | 0 | 167.8312
0 | 60.6622 | 0 | 0 | 0 | 0 | -8.1622 | 52.5 | 105.2476 | 3000 | 0 | 3000 | 3000 | 0 | 184.23
0 | 38.2643 | 0 | 0 | 0 | 0 | 14.2357 | 52.5 | 119.4833 | 3000 | 25.4374 | 3025.4374 | 3025.4374 | 0 | 203.2186
0 | 60.1314 | 0 | 0 | 0 | 0 | -7.6314 | 52.5 | 111.8519 | 3000 | 0 | 3000 | 3000 | 0 | 204.27
0 | 164.3519 | 0 | 0 | 0 | 0 | -111.8519 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 202.53
0 | 36.5487 | 0 | 0 | 0 | 0 | 15.9513 | 52.5 | 15.9513 | 3000 | 28.5029 | 3028.5029 | 3028.5029 | 0 | 199.9115
0 | 32.3256 | 0 | 0 | 0 | 0 | 20.1744 | 52.5 | 36.1257 | 3000 | 36.049 | 3036.049 | 3036.049 | 0 | 188.235
0 | 24.8793 | 0 | 0 | 0 | 0 | 27.6207 | 52.5 | 63.7464 | 3000 | 49.3545 | 3049.3545 | 3049.3545 | 0 | 180.1559
0 | 28.6356 | 0 | 0 | 0 | 0 | 23.8644 | 52.5 | 87.6108 | 3000 | 42.6424 | 3042.6424 | 3042.6424 | 0 | 164.3027
0 | 32.4244 | 0 | 0 | 0 | 0 | 20.0756 | 52.5 | 107.6864 | 3000 | 35.8724 | 3035.8724 | 3035.8724 | 0 | 153.7973
0 | 25.7623 | 0 | 0 | 0 | 0 | 26.7377 | 52.5 | 134.4241 | 3000 | 47.7768 | 3047.7768 | 3047.7768 | 0 | 154.8271
0 | 28.4187 | 0 | 0 | 0 | 0 | 24.0813 | 52.5 | 158.5053 | 3000 | 43.03 | 3043.03 | 3043.03 | 0 | 155.0119
0 | 30.9751 | 0 | 0 | 0 | 0 | 21.5249 | 52.5 | 180.0303 | 3000 | 38.4622 | 3038.4622 | 3038.4622 | 0 | 151.1635
0 | 35.4105 | 0 | 0 | 0 | 0 | 17.0895 | 52.5 | 197.1198 | 3000 | 30.5367 | 3030.5367 | 3030.5367 | 0 | 150.9207
0 | 47.7419 | 0 | 0 | 0 | 0 | 4.7581 | 52.5 | 201.8779 | 3000 | 8.5021 | 3008.5021 | 3008.5021 | 0 | 155.1785
0 | 98.6856 | 0 | 0 | 0 | 0 | -46.1856 | 52.5 | 155.6922 | 3000 | 0 | 3000 | 3000 | 0 | 174
0 | 121.8375 | 0 | 0 | 0 | 0 | -69.3375 | 52.5 | 86.3548 | 3000 | 0 | 3000 | 2967.5554 | 0 | 185.2645
0 | 98.4054 | 0 | 0 | 0 | 0 | -45.9054 | 52.5 | 40.4494 | 3000 | 0 | 3000 | 2897.2589 | 0 | 191.2191
0 | 54.116 | 0 | 0 | 0 | 0 | -1.616 | 52.5 | 38.8333 | 3000 | 0 | 3000 | 2843.1847 | 0 | 184.3805
0 | 45.9238 | 0 | 0 | 0 | 0 | 6.5762 | 52.5 | 45.4095 | 3000 | 11.7508 | 3011.7508 | 2784.6389 | 0 | 175.4323
0 | 59.0882 | 0 | 0 | 0 | 0 | -6.5882 | 52.5 | 38.8213 | 3000 | 0 | 3000 | 2778.2956 | 0 | 173.06
0 | 35.5762 | 0 | 0 | 0 | 0 | 16.9238 | 52.5 | 55.7451 | 3000 | 30.2405 | 3030.2405 | 2824.7584 | 0 | 169.4855
0 | 46.5687 | 0 | 0 | 0 | 0 | 5.9313 | 52.5 | 61.6764 | 3000 | 10.5985 | 3010.5985 | 2940.302 | 0 | 178.1823
0 | 57.3224 | 0 | 0 | 0 | 0 | -4.8224 | 52.5 | 56.854 | 3000 | 0 | 3000 | 2967.5554 | 0 | 174.4032
0 | 49.5976 | 0 | 0 | 0 | 0 | 2.9024 | 52.5 | 59.7564 | 3000 | 5.1862 | 3005.1862 | 2988.9639 | 0 | 176.1098
0 | 112.2564 | 0 | 0 | 0 | 0 | -59.7564 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 178.11
0 | 52.48 | 0 | 0 | 0 | 0 | 0.019954 | 52.5 | 0.019954 | 3000 | 0.035655 | 3000.0357 | 3000.0357 | 0 | 190.1723
0 | 41.4256 | 0 | 0 | 0 | 0 | 11.0744 | 52.5 | 11.0944 | 3000 | 19.7885 | 3019.7885 | 3019.7885 | 0 | 182.365
0 | 31.9894 | 0 | 0 | 0 | 0 | 20.5106 | 52.5 | 31.6049 | 3000 | 36.6497 | 3036.6497 | 3036.6497 | 0 | 168.1089
0 | 24.7666 | 0 | 0 | 0 | 0 | 27.7334 | 52.5 | 59.3383 | 3000 | 49.5559 | 3049.5559 | 3049.5559 | 0 | 153.2707
0 | 23.195 | 0 | 0 | 0 | 0 | 29.305 | 52.5 | 88.6433 | 3000 | 52.3641 | 3052.3641 | 3052.3641 | 0 | 153.8391
0 | 27.2583 | 0 | 0 | 0 | 0 | 25.2417 | 52.5 | 113.885 | 3000 | 45.1036 | 3045.1036 | 3045.1036 | 0 | 150.7326
0 | 30.0595 | 0 | 0 | 0 | 0 | 22.4405 | 52.5 | 136.3256 | 3000 | 40.0983 | 3040.0983 | 3040.0983 | 0 | 150.7889
0 | 26.9289 | 0 | 0 | 0 | 0 | 25.5711 | 52.5 | 161.8967 | 3000 | 45.6921 | 3045.6921 | 3045.6921 | 0 | 159.2897
0 | 29.8086 | 0 | 0 | 0 | 0 | 22.6914 | 52.5 | 184.5881 | 3000 | 40.5466 | 3040.5466 | 3040.5466 | 0 | 155.0679
0 | 32.087 | 0 | 0 | 0 | 0 | 20.413 | 52.5 | 205.0011 | 3000 | 36.4753 | 3036.4753 | 3036.4753 | 0 | 149.6982
0 | 31.0886 | 0 | 0 | 0 | 0 | 21.4114 | 52.5 | 226.4125 | 3000 | 38.2593 | 3038.2593 | 3038.2593 | 0 | 144.6211
0 | 45.1117 | 0 | 0 | 0 | 0 | 7.3883 | 52.5 | 233.8007 | 3000 | 13.2019 | 3013.2019 | 3013.2019 | 0 | 142.5244
0 | 87.3167 | 0 | 0 | 0 | 0 | -34.8167 | 52.5 | 198.984 | 3000 | 0 | 3000 | 3000 | 0 | 150.9
0 | 86.2395 | 0 | 0 | 0 | 0 | -33.7395 | 52.5 | 165.2445 | 3000 | 0 | 3000 | 3000 | 0 | 166.26
0 | 38.842 | 0 | 0 | 0 | 0 | 13.658 | 52.5 | 178.9025 | 3000 | 24.405 | 3024.405 | 3002.7753 | 0 | 176.7734
0 | 65.0956 | 0 | 0 | 0 | 0 | -12.5956 | 52.5 | 166.3068 | 3000 | 0 | 3000 | 2935.1109 | 0 | 173.1422
0 | 103.1454 | 0 | 0 | 0 | 0 | -50.6454 | 52.5 | 115.6614 | 3000 | 0 | 3000 | 2929.7035 | 0 | 169.9228
0 | 83.9511 | 0 | 0 | 0 | 0 | -31.4511 | 52.5 | 84.2103 | 3000 | 0 | 3000 | 2924.296 | 0 | 167.9131
0 | 39.3919 | 0 | 0 | 0 | 0 | 13.1081 | 52.5 | 97.3184 | 3000 | 23.4225 | 3023.4225 | 2726.0141 | 0 | 155.4646
0 | 47.1515 | 0 | 0 | 0 | 0 | 5.3485 | 52.5 | 102.6669 | 3000 | 9.5571 | 3009.5571 | 2782.4452 | 0 | 154.4257
0 | 56.7169 | 0 | 0 | 0 | 0 | -4.2169 | 52.5 | 98.4501 | 3000 | 0 | 3000 | 2875.6292 | 0 | 161.064
0 | 44.2901 | 0 | 0 | 0 | 0 | 8.2099 | 52.5 | 106.66 | 3000 | 14.67 | 3014.67 | 2803.7804 | 0 | 167.4978
0 | 35.7805 | 0 | 0 | 0 | 0 | 16.7195 | 52.5 | 123.3795 | 3000 | 29.8756 | 3029.8756 | 3002.8384 | 0 | 198.3075
0 | 43.0155 | 0 | 0 | 0 | 0 | 9.4845 | 52.5 | 132.864 | 3000 | 16.9475 | 3016.9475 | 3016.9475 | 0 | 199.2392
0 | 50.9854 | 0 | 0 | 0 | 0 | -50.9854 | 0 | 81.8786 | 0 | 0 | 0 | 0 | 0 | 0
0 | 38.8429 | 0 | 0 | 0 | 0 | 13.6571 | 52.5 | 95.5357 | 3000 | 24.4034 | 3024.4034 | 3024.4034 | 0 | 196.5862
0 | 36.5223 | 0 | 0 | 0 | 0 | 15.9777 | 52.5 | 111.5134 | 3000 | 28.5501 | 3028.5501 | 3028.5501 | 0 | 175.6559
0 | 27.2675 | 0 | 0 | 0 | 0 | 25.2325 | 52.5 | 136.7458 | 3000 | 45.087 | 3045.087 | 3045.087 | 0 | 171.682
0 | 29.1051 | 0 | 0 | 0 | 0 | 23.3949 | 52.5 | 160.1407 | 3000 | 41.8035 | 3041.8035 | 3041.8035 | 0 | 166.2041
0 | 26.8262 | 0 | 0 | 0 | 0 | 25.6738 | 52.5 | 185.8145 | 3000 | 45.8757 | 3045.8757 | 3045.8757 | 0 | 165.2692
0 | 36.6188 | 0 | 0 | 0 | 0 | 15.8812 | 52.5 | 201.6957 | 3000 | 28.3775 | 3028.3775 | 3028.3775 | 0 | 150.2075
0 | 28.6884 | 0 | 0 | 0 | 0 | 23.8116 | 52.5 | 225.5073 | 3000 | 42.5482 | 3042.5482 | 3042.5482 | 0 | 149.0849
0 | 32.9564 | 0 | 0 | 0 | 0 | 19.5436 | 52.5 | 245.0509 | 3000 | 34.9218 | 3034.9218 | 3034.9218 | 0 | 148.4077
0 | 31.2248 | 0 | 0 | 0 | 0 | 21.2752 | 52.5 | 266.3261 | 3000 | 38.0159 | 3038.0159 | 3038.0159 | 0 | 149.7742
0 | 33.7269 | 0 | 0 | 0 | 0 | 18.7731 | 52.5 | 285.0992 | 3000 | 33.545 | 3033.545 | 3033.545 | 0 | 150.7065
0 | 33.1125 | 0 | 0 | 0 | 0 | 19.3875 | 52.5 | 304.4866 | 3000 | 34.6428 | 3034.6428 | 3034.6428 | 0 | 150.8824
0 | 26.2036 | 0 | 0 | 0 | 0 | 26.2964 | 52.5 | 330.7831 | 3000 | 46.9882 | 3046.9882 | 3046.9882 | 0 | 152.0447
0 | 28.9945 | 0 | 0 | 0 | 0 | 23.5055 | 52.5 | 354.2886 | 3000 | 42.0013 | 3042.0013 | 3042.0013 | 0 | 169.4699
0 | 233.3785 | 0 | 0 | 0 | 0 | -180.8785 | 52.5 | 173.4101 | 3000 | 0 | 3000 | 2967.5554 | 0 | 186.0657
0 | 35.1557 | 0 | 0 | 0 | 0 | 17.3443 | 52.5 | 190.7544 | 3000 | 30.9919 | 3030.9919 | 2895.8063 | 0 | 194.2507
0 | 57.1766 | 0 | 0 | 0 | 0 | -4.6766 | 52.5 | 186.0777 | 3000 | 0 | 3000 | 2616.0728 | 0 | 174.1258
0 | 33.4304 | 0 | 0 | 0 | 0 | 19.0696 | 52.5 | 205.1473 | 3000 | 34.0748 | 3034.0748 | 2606.8882 | 0 | 169.7606
0 | 35.7367 | 0 | 0 | 0 | 0 | 16.7633 | 52.5 | 221.9106 | 3000 | 29.9537 | 3029.9537 | 2618.9894 | 0 | 171.7795
0 | 40.8494 | 0 | 0 | 0 | 0 | 11.6506 | 52.5 | 233.5612 | 3000 | 20.8182 | 3020.8182 | 2831.5583 | 0 | 181.1348
0 | 49.2613 | 0 | 0 | 0 | 0 | -49.2613 | 0 | 184.3 | 0 | 0 | 0 | 0 | 140.5931 | 0
0 | 54.0157 | 0 | 0 | 0 | 0 | -54.0157 | 0 | 130.2842 | 0 | 0 | 0 | 0 | 183.8525 | 0
0 | 47.6742 | 0 | 0 | 0 | 0 | -47.6742 | 0 | 82.61 | 0 | 0 | 0 | 0 | 16.2223 | 0
0 | 30.0754 | 0 | 0 | 0 | 0 | -30.0754 | 0 | 52.5346 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.5346 | 0 | 0 | 0 | 0 | -52.5346 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 23.5152 | 0 | 0 | 0 | 0 | 28.9848 | 52.5 | 28.9848 | 3000 | 51.792 | 3051.792 | 3051.792 | 0 | 207.3388
0 | 29.9571 | 0 | 0 | 0 | 0 | 22.5429 | 52.5 | 51.5277 | 3000 | 40.2811 | 3040.2811 | 3040.2811 | 0 | 186.126
0 | 35.9772 | 0 | 0 | 0 | 0 | 16.5228 | 52.5 | 68.0505 | 3000 | 29.524 | 3029.524 | 3029.524 | 0 | 175.4397
0 | 19.0507 | 0 | 0 | 0 | 0 | 33.4493 | 52.5 | 101.4997 | 3000 | 59.7694 | 3059.7694 | 3059.7694 | 0 | 168.7157
0 | 29.209 | 0 | 0 | 0 | 0 | 23.291 | 52.5 | 124.7907 | 3000 | 41.6179 | 3041.6179 | 3041.6179 | 0 | 161.2057
0 | 32.0449 | 0 | 0 | 0 | 0 | 20.4551 | 52.5 | 145.2458 | 3000 | 36.5505 | 3036.5505 | 3036.5505 | 0 | 157.9614
0 | 30.5209 | 0 | 0 | 0 | 0 | 21.9791 | 52.5 | 167.2249 | 3000 | 39.2737 | 3039.2737 | 3039.2737 | 0 | 160.6256
0 | 31.2207 | 0 | 0 | 0 | 0 | 21.2793 | 52.5 | 188.5042 | 3000 | 38.0233 | 3038.0233 | 3038.0233 | 0 | 156.4886
0 | 30.7258 | 0 | 0 | 0 | 0 | 21.7742 | 52.5 | 210.2784 | 3000 | 38.9075 | 3038.9075 | 3038.9075 | 0 | 153.0698
0 | 41.1546 | 0 | 0 | 0 | 0 | 11.3454 | 52.5 | 221.6238 | 3000 | 20.2728 | 3020.2728 | 3020.2728 | 0 | 153.3392
0 | 274.1238 | 0 | 0 | 0 | 0 | -221.6238 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 159.42
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 178.26
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2967.5554 | 0 | 196.5115
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2918.8886 | 0 | 196.4996
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2832.3698 | 0 | 181.5549
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2778.2956 | 0 | 172.9211
0 | 37.7022 | 0 | 0 | 0 | 0 | 14.7978 | 52.5 | 14.7978 | 3000 | 26.4417 | 3026.4417 | 2610.07 | 0 | 164.3039
0 | 39.4028 | 0 | 0 | 0 | 0 | 13.0972 | 52.5 | 27.895 | 3000 | 23.4029 | 3023.4029 | 2644.8831 | 0 | 168.3204
0 | 46.1118 | 0 | 0 | 0 | 0 | 6.3882 | 52.5 | 34.2832 | 3000 | 11.4149 | 3011.4149 | 2805.9327 | 0 | 184.1253
0 | 39.7949 | 0 | 0 | 0 | 0 | 12.7051 | 52.5 | 46.9883 | 3000 | 22.7023 | 3022.7023 | 2957.8132 | 0 | 203.2018
0 | 41.7663 | 0 | 0 | 0 | 0 | 10.7337 | 52.5 | 57.7219 | 3000 | 19.1796 | 3019.1796 | 3008.3648 | 0 | 207.9382
0 | 56.4393 | 0 | 0 | 0 | 0 | -56.4393 | 0 | 1.2827 | 0 | 0 | 0 | 0 | 0 | 0
0 | 1.2827 | 0 | 0 | 0 | 0 | -1.2827 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 50.3662 | 0 | 0 | 0 | 0 | 2.1338 | 52.5 | 2.1338 | 3000 | 3.8128 | 3003.8128 | 3003.8128 | 0 | 194.6471
0 | 39.3826 | 0 | 0 | 0 | 0 | 13.1174 | 52.5 | 15.2512 | 3000 | 23.4391 | 3023.4391 | 3023.4391 | 0 | 181.7087
0 | 38.0705 | 0 | 0 | 0 | 0 | 14.4295 | 52.5 | 29.6807 | 3000 | 25.7836 | 3025.7836 | 3025.7836 | 0 | 174.5575
0 | 19.2964 | 0 | 0 | 0 | 0 | 33.2036 | 52.5 | 62.8843 | 3000 | 59.3303 | 3059.3303 | 3059.3303 | 0 | 174.5348
0 | 24.1137 | 0 | 0 | 0 | 0 | 28.3863 | 52.5 | 91.2705 | 3000 | 50.7225 | 3050.7225 | 3050.7225 | 0 | 163.6713
0 | 32.51 | 0 | 0 | 0 | 0 | 19.99 | 52.5 | 111.2605 | 3000 | 35.7194 | 3035.7194 | 3035.7194 | 0 | 152.9395
0 | 24.575 | 0 | 0 | 0 | 0 | 27.925 | 52.5 | 139.1855 | 3000 | 49.8983 | 3049.8983 | 3049.8983 | 0 | 144.5652
0 | 28.0736 | 0 | 0 | 0 | 0 | 24.4264 | 52.5 | 163.6119 | 3000 | 43.6467 | 3043.6467 | 3043.6467 | 0 | 143.3558
0 | 29.2988 | 0 | 0 | 0 | 0 | 23.2012 | 52.5 | 186.8131 | 3000 | 41.4574 | 3041.4574 | 3041.4574 | 0 | 136.8656
0 | 37.505 | 0 | 0 | 0 | 0 | 14.995 | 52.5 | 201.808 | 3000 | 26.7941 | 3026.7941 | 3026.7941 | 0 | 145.2861
0 | 36.632 | 0 | 0 | 0 | 0 | 15.868 | 52.5 | 217.6761 | 3000 | 28.354 | 3028.354 | 3028.354 | 0 | 145.361
0 | 57.8522 | 0 | 0 | 0 | 0 | -5.3522 | 52.5 | 212.3239 | 3000 | 0 | 3000 | 3000 | 0 | 144
0 | 85.9333 | 0 | 0 | 0 | 0 | -33.4333 | 52.5 | 178.8905 | 3000 | 0 | 3000 | 3000 | 0 | 153.3
0 | 55.3683 | 0 | 0 | 0 | 0 | -2.8683 | 52.5 | 176.0222 | 3000 | 0 | 3000 | 2978.3703 | 0 | 163.0062
0 | 55.445 | 0 | 0 | 0 | 0 | -2.945 | 52.5 | 173.0773 | 3000 | 0 | 3000 | 2918.8886 | 0 | 163.0491
0 | 66.4433 | 0 | 0 | 0 | 0 | -13.9433 | 52.5 | 159.134 | 3000 | 0 | 3000 | 2935.1109 | 0 | 163.2215
0 | 123.3241 | 0 | 0 | 0 | 0 | -70.8241 | 52.5 | 88.3099 | 3000 | 0 | 3000 | 2891.8515 | 0 | 160.1507
0 | 119.4514 | 0 | 0 | 0 | 0 | -66.9514 | 52.5 | 21.3586 | 3000 | 0 | 3000 | 2924.296 | 0 | 162.2984
0 | 66.7282 | 0 | 0 | 0 | 0 | -14.2282 | 52.5 | 7.1304 | 3000 | 0 | 3000 | 2924.296 | 0 | 160.8948
0 | 50.1831 | 0 | 0 | 0 | 0 | 2.3169 | 52.5 | 9.4473 | 3000 | 4.14 | 3004.14 | 2950.0657 | 0 | 162.6076
0 | 61.9473 | 0 | 0 | 0 | 0 | -9.4473 | 52.5 | 0 | 3000 | 0 | 3000 | 2956.7406 | 0 | 168.9482
0 | 42.5458 | 0 | 0 | 0 | 0 | 9.9542 | 52.5 | 9.9542 | 3000 | 17.7869 | 3017.7869 | 3001.5646 | 0 | 181.3245
0 | 45.8326 | 0 | 0 | 0 | 0 | 6.6674 | 52.5 | 16.6216 | 3000 | 11.9137 | 3011.9137 | 3011.9137 | 0 | 192.7625
0 | 16.6216 | 0 | 0 | 0 | 0 | -16.6216 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 182.73
0 | 26.9247 | 0 | 0 | 0 | 0 | 25.5753 | 52.5 | 25.5753 | 3000 | 45.6996 | 3045.6996 | 3045.6996 | 0 | 179.0871
0 | 30.7728 | 0 | 0 | 0 | 0 | 21.7272 | 52.5 | 47.3025 | 3000 | 38.8237 | 3038.8237 | 3038.8237 | 0 | 176.0087
0 | 28.2423 | 0 | 0 | 0 | 0 | 24.2577 | 52.5 | 71.5602 | 3000 | 43.3454 | 3043.3454 | 3043.3454 | 0 | 171.4925
0 | 30.9308 | 0 | 0 | 0 | 0 | 21.5692 | 52.5 | 93.1295 | 3000 | 38.5413 | 3038.5413 | 3038.5413 | 0 | 167.2413
0 | 29.5766 | 0 | 0 | 0 | 0 | 22.9234 | 52.5 | 116.0528 | 3000 | 40.961 | 3040.961 | 3040.961 | 0 | 162.5698
0 | 25.9963 | 0 | 0 | 0 | 0 | 26.5037 | 52.5 | 142.5565 | 3000 | 47.3585 | 3047.3585 | 3047.3585 | 0 | 158.4017
0 | 20.7816 | 0 | 0 | 0 | 0 | 31.7184 | 52.5 | 174.2749 | 3000 | 56.6766 | 3056.6766 | 3056.6766 | 0 | 159.1611
0 | 33.7249 | 0 | 0 | 0 | 0 | 18.7751 | 52.5 | 193.05 | 3000 | 33.5485 | 3033.5485 | 3033.5485 | 0 | 156.3188
0 | 31.8284 | 0 | 0 | 0 | 0 | 20.6716 | 52.5 | 213.7215 | 3000 | 36.9373 | 3036.9373 | 3036.9373 | 0 | 158.4978
0 | 35.2388 | 0 | 0 | 0 | 0 | 17.2612 | 52.5 | 230.9827 | 3000 | 30.8434 | 3030.8434 | 3030.8434 | 0 | 158.5737
0 | 38.6 | 0 | 0 | 0 | 0 | 13.9 | 52.5 | 244.8826 | 3000 | 24.8374 | 3024.8374 | 3024.8374 | 0 | 158.7737
0 | 70.2341 | 0 | 0 | 0 | 0 | -17.7341 | 52.5 | 227.1485 | 3000 | 0 | 3000 | 3000 | 0 | 160.26
0 | 85.4308 | 0 | 0 | 0 | 0 | -32.9308 | 52.5 | 194.2177 | 3000 | 0 | 3000 | 2983.7777 | 0 | 161.1538
0 | 46.2153 | 0 | 0 | 0 | 0 | 6.2847 | 52.5 | 200.5023 | 3000 | 11.2299 | 3011.2299 | 2935.5259 | 0 | 168.7047
0 | 50.1238 | 0 | 0 | 0 | 0 | 2.3762 | 52.5 | 202.8786 | 3000 | 4.246 | 3004.246 | 2814.9861 | 0 | 163.6351
0 | 255.3786 | 0 | 0 | 0 | 0 | -202.8786 | 52.5 | 0 | 3000 | 0 | 3000 | 2794.5178 | 0 | 157.9182
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2843.1847 | 0 | 161.7772
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2881.0366 | 0 | 155.4895
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2908.0738 | 0 | 156.8615
0 | 44.7119 | 0 | 0 | 0 | 0 | 7.7881 | 52.5 | 7.7881 | 3000 | 13.9162 | 3013.9162 | 2943.6197 | 0 | 162.2523
0 | 44.453 | 0 | 0 | 0 | 0 | 8.047 | 52.5 | 15.8351 | 3000 | 14.3789 | 3014.3789 | 2998.1567 | 0 | 165.4683
0 | 44.4818 | 0 | 0 | 0 | 0 | 8.0182 | 52.5 | 23.8533 | 3000 | 14.3275 | 3014.3275 | 3014.3275 | 0 | 173.6554
0 | 60.069 | 0 | 0 | 0 | 0 | -7.569 | 52.5 | 16.2843 | 3000 | 0 | 3000 | 3000 | 0 | 176.61
0 | 34.6083 | 0 | 0 | 0 | 0 | 17.8917 | 52.5 | 34.176 | 3000 | 31.9702 | 3031.9702 | 3031.9702 | 0 | 173.4287
0 | 24.7697 | 0 | 0 | 0 | 0 | 27.7303 | 52.5 | 61.9064 | 3000 | 49.5504 | 3049.5504 | 3049.5504 | 0 | 165.6516
0 | 25.8281 | 0 | 0 | 0 | 0 | 26.6719 | 52.5 | 88.5783 | 3000 | 47.6591 | 3047.6591 | 3047.6591 | 0 | 158.4783
0 | 26.386 | 0 | 0 | 0 | 0 | 26.114 | 52.5 | 114.6923 | 3000 | 46.6623 | 3046.6623 | 3046.6623 | 0 | 149.9872
0 | 33.3159 | 0 | 0 | 0 | 0 | 19.1841 | 52.5 | 133.8764 | 3000 | 34.2795 | 3034.2795 | 3034.2795 | 0 | 149.59
0 | 28.5631 | 0 | 0 | 0 | 0 | 23.9369 | 52.5 | 157.8134 | 3000 | 42.7721 | 3042.7721 | 3042.7721 | 0 | 151.2258
0 | 36.0936 | 0 | 0 | 0 | 0 | 16.4064 | 52.5 | 174.2198 | 3000 | 29.3161 | 3029.3161 | 3029.3161 | 0 | 145.1042
0 | 31.5521 | 0 | 0 | 0 | 0 | 20.9479 | 52.5 | 195.1677 | 3000 | 37.4311 | 3037.4311 | 3037.4311 | 0 | 144.278
0 | 27.6437 | 0 | 0 | 0 | 0 | 24.8563 | 52.5 | 220.024 | 3000 | 44.4149 | 3044.4149 | 3044.4149 | 0 | 151.3074
0 | 31.0488 | 0 | 0 | 0 | 0 | 21.4512 | 52.5 | 241.4752 | 3000 | 38.3304 | 3038.3304 | 3038.3304 | 0 | 143.5003
0 | 31.8122 | 0 | 0 | 0 | 0 | 20.6878 | 52.5 | 262.163 | 3000 | 36.9663 | 3036.9663 | 3036.9663 | 0 | 145.3492
0 | 31.4294 | 0 | 0 | 0 | 0 | 21.0706 | 52.5 | 283.2336 | 3000 | 37.6503 | 3037.6503 | 3037.6503 | 0 | 148.0855
0 | 31.04 | 0 | 0 | 0 | 0 | 21.46 | 52.5 | 304.6936 | 3000 | 38.3462 | 3038.3462 | 3038.3462 | 0 | 144.2911
0 | 31.4515 | 0 | 0 | 0 | 0 | 21.0485 | 52.5 | 325.7421 | 3000 | 37.6109 | 3037.6109 | 3005.1664 | 0 | 146.8925
0 | 39.3074 | 0 | 0 | 0 | 0 | 13.1926 | 52.5 | 338.9347 | 3000 | 23.5735 | 3023.5735 | 2899.2027 | 0 | 150.3237
0 | 45.3059 | 0 | 0 | 0 | 0 | 7.1941 | 52.5 | 346.1289 | 3000 | 12.855 | 3012.855 | 2796.558 | 0 | 150.4828
0 | 42.0826 | 0 | 0 | 0 | 0 | 10.4174 | 52.5 | 356.5463 | 3000 | 18.6145 | 3018.6145 | 2596.8354 | 0 | 142.0988
0 | 31.4685 | 0 | 0 | 0 | 0 | 21.0315 | 52.5 | 377.5778 | 3000 | 37.5806 | 3037.5806 | 2507.6529 | 0 | 139.8267
0 | 45.546 | 0 | 0 | 0 | 0 | 6.954 | 52.5 | 384.5318 | 3000 | 12.4258 | 3012.4258 | 2644.7209 | 0 | 145.8564
0 | 63.7221 | 0 | 0 | 0 | 0 | -11.2221 | 52.5 | 373.3096 | 3000 | 0 | 3000 | 2729.6287 | 0 | 148.0824
0 | 35.2826 | 0 | 0 | 0 | 0 | 17.2174 | 52.5 | 390.527 | 3000 | 30.7652 | 3030.7652 | 2900.987 | 0 | 156.8274
0 | 248.191 | 0 | 0 | 0 | 0 | -195.691 | 52.5 | 194.836 | 3000 | 0 | 3000 | 2978.3703 | 0 | 163.304
0 | 43.15 | 0 | 0 | 0 | 0 | 9.35 | 52.5 | 204.186 | 3000 | 16.7072 | 3016.7072 | 3016.7072 | 0 | 169.3881
0 | 33.5766 | 0 | 0 | 0 | 0 | 18.9234 | 52.5 | 223.1095 | 3000 | 33.8136 | 3033.8136 | 3033.8136 | 0 | 183.3637
0 | 47.0915 | 0 | 0 | 0 | 0 | 5.4085 | 52.5 | 228.518 | 3000 | 9.6643 | 3009.6643 | 3009.6643 | 0 | 176.577
0 | 39.7662 | 0 | 0 | 0 | 0 | 12.7338 | 52.5 | 241.2518 | 3000 | 22.7536 | 3022.7536 | 3022.7536 | 0 | 174.1106
0 | 39.8557 | 0 | 0 | 0 | 0 | 12.6443 | 52.5 | 253.8961 | 3000 | 22.5936 | 3022.5936 | 3022.5936 | 0 | 166.7867
0 | 84.661 | 0 | 0 | 0 | 0 | -32.161 | 52.5 | 221.7351 | 3000 | 0 | 3000 | 3000 | 0 | 160.8
0 | 109.2149 | 0 | 0 | 0 | 0 | -56.7149 | 52.5 | 165.0201 | 3000 | 0 | 3000 | 3000 | 0 | 150.18
0 | 98.1766 | 0 | 0 | 0 | 0 | -45.6766 | 52.5 | 119.3435 | 3000 | 0 | 3000 | 3000 | 0 | 141.9
0 | 58.6321 | 0 | 0 | 0 | 0 | -6.1321 | 52.5 | 113.2115 | 3000 | 0 | 3000 | 3000 | 0 | 119.28
0 | 35.0815 | 0 | 0 | 0 | 0 | 17.4185 | 52.5 | 130.63 | 3000 | 31.1245 | 3031.1245 | 3031.1245 | 0 | 129.8231
0 | 28.1672 | 0 | 0 | 0 | 0 | 24.3328 | 52.5 | 154.9628 | 3000 | 43.4795 | 3043.4795 | 3043.4795 | 0 | 126.3044
0 | 27.4681 | 0 | 0 | 0 | 0 | 25.0319 | 52.5 | 179.9947 | 3000 | 44.7287 | 3044.7287 | 3044.7287 | 0 | 131.4105
0 | 26.002 | 0 | 0 | 0 | 0 | 26.498 | 52.5 | 206.4927 | 3000 | 47.3484 | 3047.3484 | 3047.3484 | 0 | 136.8259
0 | 44.6933 | 0 | 0 | 0 | 0 | 7.8067 | 52.5 | 214.2994 | 3000 | 13.9495 | 3013.9495 | 3013.9495 | 0 | 147.6835
0 | 257.5457 | 0 | 0 | 0 | 0 | -205.0457 | 52.5 | 9.2537 | 3000 | 0 | 3000 | 3000 | 0 | 165.06
0 | 61.3251 | 0 | 0 | 0 | 0 | -8.8251 | 52.5 | 0.42859 | 3000 | 0 | 3000 | 2994.5926 | 0 | 169.9731
0 | 48.8612 | 0 | 0 | 0 | 0 | 3.6388 | 52.5 | 4.0674 | 3000 | 6.502 | 3006.502 | 2979.4649 | 0 | 181.36
0 | 45.6877 | 0 | 0 | 0 | 0 | 6.8123 | 52.5 | 10.8797 | 3000 | 12.1727 | 3012.1727 | 2947.2836 | 0 | 180.8748
0 | 52.1863 | 0 | 0 | 0 | 0 | 0.31373 | 52.5 | 11.1934 | 3000 | 0.56059 | 3000.5606 | 2876.1898 | 0 | 182.2929
0 | 47.2096 | 0 | 0 | 0 | 0 | 5.2904 | 52.5 | 16.4838 | 3000 | 9.4532 | 3009.4532 | 2912.1196 | 0 | 188.6762
0 | 48.903 | 0 | 0 | 0 | 0 | 3.597 | 52.5 | 20.0808 | 3000 | 6.4273 | 3006.4273 | 2941.5382 | 0 | 187.6996
0 | 42.6739 | 0 | 0 | 0 | 0 | 9.8261 | 52.5 | 29.9069 | 3000 | 17.5579 | 3017.5579 | 2979.7059 | 0 | 198.3888
0 | 47.0891 | 0 | 0 | 0 | 0 | 5.4109 | 52.5 | 35.3178 | 3000 | 9.6686 | 3009.6686 | 2993.4463 | 0 | 193.9753
0 | 49.5706 | 0 | 0 | 0 | 0 | 2.9294 | 52.5 | 38.2472 | 3000 | 5.2344 | 3005.2344 | 2999.827 | 0 | 203.5983
0 | 38.2472 | 0 | 0 | 0 | 0 | -38.2472 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 41.4073 | 0 | 0 | 0 | 0 | 11.0927 | 52.5 | 11.0927 | 3000 | 19.8212 | 3019.8212 | 3019.8212 | 0 | 211.2063
0 | 63.5927 | 0 | 0 | 0 | 0 | -11.0927 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 176.01
0 | 30.1671 | 0 | 0 | 0 | 0 | 22.3329 | 52.5 | 22.3329 | 3000 | 39.9059 | 3039.9059 | 3039.9059 | 0 | 172.1195
0 | 25.1202 | 0 | 0 | 0 | 0 | 27.3798 | 52.5 | 49.7127 | 3000 | 48.924 | 3048.924 | 3048.924 | 0 | 165.831
0 | 24.6219 | 0 | 0 | 0 | 0 | 27.8781 | 52.5 | 77.5908 | 3000 | 49.8144 | 3049.8144 | 3049.8144 | 0 | 153.4057
0 | 28.6463 | 0 | 0 | 0 | 0 | 23.8537 | 52.5 | 101.4444 | 3000 | 42.6233 | 3042.6233 | 3042.6233 | 0 | 148.7539
0 | 34.8741 | 0 | 0 | 0 | 0 | 17.6259 | 52.5 | 119.0704 | 3000 | 31.4952 | 3031.4952 | 3031.4952 | 0 | 144.9055
0 | 26.0877 | 0 | 0 | 0 | 0 | 26.4123 | 52.5 | 145.4827 | 3000 | 47.1953 | 3047.1953 | 3047.1953 | 0 | 144.1323
0 | 30.9787 | 0 | 0 | 0 | 0 | 21.5213 | 52.5 | 167.004 | 3000 | 38.4558 | 3038.4558 | 3038.4558 | 0 | 145.2382
0 | 31.8299 | 0 | 0 | 0 | 0 | 20.6701 | 52.5 | 187.6742 | 3000 | 36.9348 | 3036.9348 | 3036.9348 | 0 | 143.3433
0 | 32.2773 | 0 | 0 | 0 | 0 | 20.2227 | 52.5 | 207.8968 | 3000 | 36.1352 | 3036.1352 | 3036.1352 | 0 | 142.6984
0 | 41.4936 | 0 | 0 | 0 | 0 | 11.0064 | 52.5 | 218.9033 | 3000 | 19.667 | 3019.667 | 3019.667 | 0 | 141.9243
0 | 44.9198 | 0 | 0 | 0 | 0 | 7.5802 | 52.5 | 226.4834 | 3000 | 13.5448 | 3013.5448 | 3013.5448 | 0 | 151.2799
0 | 70.6285 | 0 | 0 | 0 | 0 | -18.1285 | 52.5 | 208.355 | 3000 | 0 | 3000 | 3000 | 0 | 160.08
0 | 90.1098 | 0 | 0 | 0 | 0 | -37.6098 | 52.5 | 170.7452 | 3000 | 0 | 3000 | 2972.9629 | 0 | 173.3832
0 | 72.4189 | 0 | 0 | 0 | 0 | -19.9189 | 52.5 | 150.8263 | 3000 | 0 | 3000 | 2859.4069 | 0 | 171.1641
0 | 43.2534 | 0 | 0 | 0 | 0 | 9.2466 | 52.5 | 160.0729 | 3000 | 16.5224 | 3016.5224 | 2708.2992 | 0 | 158.1105
0 | 43.8925 | 0 | 0 | 0 | 0 | 8.6075 | 52.5 | 168.6804 | 3000 | 15.3804 | 3015.3804 | 2566.5641 | 0 | 149.066
0 | 38.2879 | 0 | 0 | 0 | 0 | 14.2121 | 52.5 | 182.8925 | 3000 | 25.3952 | 3025.3952 | 2473.8378 | 0 | 143.8537
0 | 51.0693 | 0 | 0 | 0 | 0 | 1.4307 | 52.5 | 184.3232 | 3000 | 2.5564 | 3002.5564 | 2542.9253 | 0 | 148.3797
0 | 33.9756 | 0 | 0 | 0 | 0 | 18.5244 | 52.5 | 202.8475 | 3000 | 33.1006 | 3033.1006 | 2746.507 | 0 | 172.9475
0 | 52.3471 | 0 | 0 | 0 | 0 | 0.15295 | 52.5 | 203.0005 | 3000 | 0.2733 | 3000.2733 | 2870.4951 | 0 | 200.6476
0 | 51.2766 | 0 | 0 | 0 | 0 | -51.2766 | 0 | 151.7239 | 0 | 0 | 0 | 0 | 16.2223 | 0
0 | 41.4369 | 0 | 0 | 0 | 0 | -41.4369 | 0 | 110.287 | 0 | 0 | 0 | 0 | 0 | 0
0 | 53.8859 | 0 | 0 | 0 | 0 | -53.8859 | 0 | 56.401 | 0 | 0 | 0 | 0 | 0 | 0
0 | 49.368 | 0 | 0 | 0 | 0 | -49.368 | 0 | 7.0331 | 0 | 0 | 0 | 0 | 0 | 0
0 | 7.0331 | 0 | 0 | 0 | 0 | -7.0331 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 185.85
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 166.89
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 159.09
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 151.5
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 145.2
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 146.1
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 150.84
0 | 37.3121 | 0 | 0 | 0 | 0 | 15.1879 | 52.5 | 15.1879 | 3000 | 27.1388 | 3027.1388 | 3027.1388 | 0 | 154.6868
0 | 32.9336 | 0 | 0 | 0 | 0 | 19.5664 | 52.5 | 34.7544 | 3000 | 34.9626 | 3034.9626 | 3034.9626 | 0 | 160.853
0 | 31.2511 | 0 | 0 | 0 | 0 | 21.2489 | 52.5 | 56.0033 | 3000 | 37.969 | 3037.969 | 3037.969 | 0 | 197.6199
0 | 40.8721 | 0 | 0 | 0 | 0 | -40.8721 | 0 | 15.1312 | 0 | 0 | 0 | 0 | 27.0371 | 0
0 | 15.1312 | 0 | 0 | 0 | 0 | -15.1312 | 0 | 0 | 0 | 0 | 0 | 0 | 91.9262 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 156.8153 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189.2599 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 173.0376 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 162.2228 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102.7411 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 37.852 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8149 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 25.9534 | 0 | 0 | 0 | 0 | 26.5466 | 52.5 | 26.5466 | 3000 | 47.4353 | 3047.4353 | 3047.4353 | 0 | 198.388
0 | 35.1038 | 0 | 0 | 0 | 0 | 17.3962 | 52.5 | 43.9429 | 3000 | 31.0848 | 3031.0848 | 3031.0848 | 0 | 192.9589
0 | 77.4934 | 0 | 0 | 0 | 0 | -24.9934 | 52.5 | 18.9494 | 3000 | 0 | 3000 | 3000 | 0 | 169.86
0 | 71.4494 | 0 | 0 | 0 | 0 | -18.9494 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 151.2
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 154.8
0 | 27.0296 | 0 | 0 | 0 | 0 | 25.4704 | 52.5 | 25.4704 | 3000 | 45.5123 | 3045.5123 | 3045.5123 | 0 | 152.2756
0 | 40.8405 | 0 | 0 | 0 | 0 | 11.6595 | 52.5 | 37.1299 | 3000 | 20.8339 | 3020.8339 | 3020.8339 | 0 | 151.0417
0 | 87.1819 | 0 | 0 | 0 | 0 | -34.6819 | 52.5 | 2.448 | 3000 | 0 | 3000 | 3000 | 0 | 152.58
0 | 54.948 | 0 | 0 | 0 | 0 | -2.448 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 145.5
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 153.63
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 160.71
0 | 23.3644 | 0 | 0 | 0 | 0 | 29.1356 | 52.5 | 29.1356 | 3000 | 52.0614 | 3052.0614 | 3052.0614 | 0 | 178.5761
0 | 29.1356 | 0 | 0 | 0 | 0 | -29.1356 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8149 | 0
0 | 39.4637 | 0 | 0 | 0 | 0 | 13.0363 | 52.5 | 13.0363 | 3000 | 23.2941 | 3023.2941 | 2969.2198 | 0 | 198.1063
0 | 65.3546 | 0 | 0 | 0 | 0 | -12.8546 | 52.5 | 0.18171 | 3000 | 0 | 3000 | 2853.9995 | 0 | 197.7536
0 | 0.18171 | 0 | 0 | 0 | 0 | -0.18171 | 0 | 0 | 0 | 0 | 0 | 0 | 210.8896 | 0
0 | 6.4348 | 0 | 0 | 0 | 0 | 0 | 6.4348 | 0 | 367.7049 | 0 | 367.7049 | 0 | 0 | 0
0 | 46.8974 | 0 | 0 | 0 | 0 | 5.6026 | 52.5 | 5.6026 | 3000 | 10.0112 | 3010.0112 | 2669.3434 | 0 | 182.3962
0 | 5.6026 | 0 | 0 | 0 | 0 | -5.6026 | 0 | 0 | 0 | 0 | 0 | 0 | 264.9638 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 151.4079 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.2223 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 37.523 | 0 | 0 | 0 | 0 | 14.977 | 52.5 | 14.977 | 3000 | 26.7619 | 3026.7619 | 3026.7619 | 0 | 206.1528
0 | 45.8686 | 0 | 0 | 0 | 0 | 6.6314 | 52.5 | 21.6084 | 3000 | 11.8493 | 3011.8493 | 3011.8493 | 0 | 195.1076
0 | 74.1084 | 0 | 0 | 0 | 0 | -21.6084 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 175.65
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 165.57
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 158.76
0 | 26.291 | 0 | 0 | 0 | 0 | 26.209 | 52.5 | 26.209 | 3000 | 46.8319 | 3046.8319 | 3046.8319 | 0 | 156.9118
0 | 63.2486 | 0 | 0 | 0 | 0 | -10.7486 | 52.5 | 15.4603 | 3000 | 0 | 3000 | 3000 | 0 | 145.5
0 | 67.9603 | 0 | 0 | 0 | 0 | -15.4603 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 148.5
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 147.6
0 | 35.8144 | 0 | 0 | 0 | 0 | 16.6856 | 52.5 | 16.6856 | 3000 | 29.815 | 3029.815 | 3029.815 | 0 | 149.9758
0 | 35.3185 | 0 | 0 | 0 | 0 | 17.1815 | 52.5 | 33.8672 | 3000 | 30.7011 | 3030.7011 | 3030.7011 | 0 | 152.7473
0 | 27.2263 | 0 | 0 | 0 | 0 | 25.2737 | 52.5 | 59.1409 | 3000 | 45.1607 | 3045.1607 | 3045.1607 | 0 | 157.8307
0 | 27.5208 | 0 | 0 | 0 | 0 | 24.9792 | 52.5 | 84.1201 | 3000 | 44.6345 | 3044.6345 | 3044.6345 | 0 | 153.48
0 | 49.7684 | 0 | 0 | 0 | 0 | 2.7316 | 52.5 | 86.8516 | 3000 | 4.881 | 3004.881 | 2983.2513 | 0 | 196.2084
0 | 36.9307 | 0 | 0 | 0 | 0 | 15.5693 | 52.5 | 102.4209 | 3000 | 27.8202 | 3027.8202 | 2952.1163 | 0 | 196.5519
0 | 52.0194 | 0 | 0 | 0 | 0 | 0.48058 | 52.5 | 102.9015 | 3000 | 0.85873 | 3000.8587 | 2789.9691 | 0 | 181.069
0 | 44.2276 | 0 | 0 | 0 | 0 | 8.2724 | 52.5 | 111.1739 | 3000 | 14.7817 | 3014.7817 | 2647.0768 | 0 | 168.5923
0 | 33.2576 | 0 | 0 | 0 | 0 | 19.2424 | 52.5 | 130.4163 | 3000 | 34.3836 | 3034.3836 | 2493.6411 | 0 | 155.1793
0 | 34.6031 | 0 | 0 | 0 | 0 | 17.8969 | 52.5 | 148.3132 | 3000 | 31.9794 | 3031.9794 | 2566.9408 | 0 | 154.2731
0 | 50.8065 | 0 | 0 | 0 | 0 | 1.6935 | 52.5 | 150.0067 | 3000 | 3.026 | 3003.026 | 2716.4325 | 0 | 165.4579
0 | 52.7072 | 0 | 0 | 0 | 0 | -0.20722 | 52.5 | 149.7994 | 3000 | 0 | 3000 | 2886.4441 | 0 | 184.819
0 | 41.294 | 0 | 0 | 0 | 0 | 11.206 | 52.5 | 161.0055 | 3000 | 20.0237 | 3020.0237 | 3003.8014 | 0 | 193.7452
0 | 34.7065 | 0 | 0 | 0 | 0 | 17.7935 | 52.5 | 178.7989 | 3000 | 31.7946 | 3031.7946 | 3031.7946 | 0 | 194.1561
0 | 36.4124 | 0 | 0 | 0 | 0 | 16.0876 | 52.5 | 194.8865 | 3000 | 28.7464 | 3028.7464 | 3028.7464 | 0 | 202.6534
0 | 44.0608 | 0 | 0 | 0 | 0 | 8.4392 | 52.5 | 203.3257 | 3000 | 15.0797 | 3015.0797 | 3015.0797 | 0 | 176.2314
0 | 27.889 | 0 | 0 | 0 | 0 | 24.611 | 52.5 | 227.9367 | 3000 | 43.9766 | 3043.9766 | 3043.9766 | 0 | 162.8527
0 | 21.448 | 0 | 0 | 0 | 0 | 31.052 | 52.5 | 258.9887 | 3000 | 55.4858 | 3055.4858 | 3055.4858 | 0 | 166.7073
0 | 229.2915 | 0 | 0 | 0 | 0 | -176.7915 | 52.5 | 82.1972 | 3000 | 0 | 3000 | 3000 | 0 | 162.81
0 | 27.3676 | 0 | 0 | 0 | 0 | 25.1324 | 52.5 | 107.3297 | 3000 | 44.9083 | 3044.9083 | 3044.9083 | 0 | 162.3545
0 | 26.7612 | 0 | 0 | 0 | 0 | 25.7388 | 52.5 | 133.0684 | 3000 | 45.9918 | 3045.9918 | 3045.9918 | 0 | 153.7921
0 | 29.8994 | 0 | 0 | 0 | 0 | 22.6006 | 52.5 | 155.669 | 3000 | 40.3842 | 3040.3842 | 3040.3842 | 0 | 150.0734
0 | 26.1769 | 0 | 0 | 0 | 0 | 26.3231 | 52.5 | 181.9921 | 3000 | 47.0359 | 3047.0359 | 3047.0359 | 0 | 153.8753
0 | 34.1428 | 0 | 0 | 0 | 0 | 18.3572 | 52.5 | 200.3493 | 3000 | 32.8019 | 3032.8019 | 3032.8019 | 0 | 153.1565
0 | 34.6804 | 0 | 0 | 0 | 0 | 17.8196 | 52.5 | 218.1689 | 3000 | 31.8412 | 3031.8412 | 3031.8412 | 0 | 146.0438
0 | 31.6646 | 0 | 0 | 0 | 0 | 20.8354 | 52.5 | 239.0043 | 3000 | 37.23 | 3037.23 | 3037.23 | 0 | 136.7665
0 | 227.634 | 0 | 0 | 0 | 0 | -175.134 | 52.5 | 63.8703 | 3000 | 0 | 3000 | 3000 | 0 | 129.66
0 | 30.2594 | 0 | 0 | 0 | 0 | 22.2406 | 52.5 | 86.1109 | 3000 | 39.741 | 3039.741 | 3039.741 | 0 | 144.0533
0 | 35.6897 | 0 | 0 | 0 | 0 | 16.8103 | 52.5 | 102.9211 | 3000 | 30.0377 | 3030.0377 | 3003.0006 | 0 | 153.5734
0 | 36.3388 | 0 | 0 | 0 | 0 | 16.1612 | 52.5 | 119.0824 | 3000 | 28.878 | 3028.878 | 2899.0998 | 0 | 152.0578
0 | 39.9169 | 0 | 0 | 0 | 0 | 12.5831 | 52.5 | 131.6655 | 3000 | 22.4843 | 3022.4843 | 2849.4467 | 0 | 170.9098
0 | 52.3062 | 0 | 0 | 0 | 0 | 0.19383 | 52.5 | 131.8593 | 3000 | 0.34635 | 3000.3463 | 2773.2345 | 0 | 186.0563
0 | 45.7819 | 0 | 0 | 0 | 0 | 6.7181 | 52.5 | 138.5774 | 3000 | 12.0044 | 3012.0044 | 2644.2995 | 0 | 178.834
0 | 42.5619 | 0 | 0 | 0 | 0 | -42.5619 | 0 | 96.0155 | 0 | 0 | 0 | 0 | 275.7787 | 0
0 | 53.1192 | 0 | 0 | 0 | 0 | -0.61922 | 52.5 | 95.3962 | 3000 | 0 | 3000 | 2832.3698 | 0 | 184.104
0 | 43.0474 | 0 | 0 | 0 | 0 | 9.4526 | 52.5 | 104.8489 | 3000 | 16.8906 | 3016.8906 | 2946.594 | 0 | 189.8196
0 | 44.8514 | 0 | 0 | 0 | 0 | 7.6486 | 52.5 | 112.4974 | 3000 | 13.667 | 3013.667 | 3002.8521 | 0 | 189.8703
0 | 38.6824 | 0 | 0 | 0 | 0 | 13.8176 | 52.5 | 126.315 | 3000 | 24.6901 | 3024.6901 | 3024.6901 | 0 | 199.9925
0 | 35.0889 | 0 | 0 | 0 | 0 | -35.0889 | 0 | 91.2261 | 0 | 0 | 0 | 0 | 0 | 0
0 | 42.9227 | 0 | 0 | 0 | 0 | 9.5773 | 52.5 | 100.8034 | 3000 | 17.1134 | 3017.1134 | 3017.1134 | 0 | 208.1808
0 | 153.3034 | 0 | 0 | 0 | 0 | -100.8034 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 164.7
0 | 27.729 | 0 | 0 | 0 | 0 | 24.771 | 52.5 | 24.771 | 3000 | 44.2624 | 3044.2624 | 3044.2624 | 0 | 159.9455
0 | 33.866 | 0 | 0 | 0 | 0 | 18.634 | 52.5 | 43.405 | 3000 | 33.2965 | 3033.2965 | 3033.2965 | 0 | 166.528
0 | 34.9543 | 0 | 0 | 0 | 0 | 17.5457 | 52.5 | 60.9506 | 3000 | 31.3518 | 3031.3518 | 3031.3518 | 0 | 157.4484
0 | 22.8426 | 0 | 0 | 0 | 0 | 29.6574 | 52.5 | 90.608 | 3000 | 52.9938 | 3052.9938 | 3052.9938 | 0 | 156.008
0 | 33.1975 | 0 | 0 | 0 | 0 | 19.3025 | 52.5 | 109.9105 | 3000 | 34.491 | 3034.491 | 3034.491 | 0 | 156.5797
0 | 38.8726 | 0 | 0 | 0 | 0 | 13.6274 | 52.5 | 123.5379 | 3000 | 24.3504 | 3024.3504 | 3024.3504 | 0 | 160.2906
0 | 32.9414 | 0 | 0 | 0 | 0 | 19.5586 | 52.5 | 143.0965 | 3000 | 34.9487 | 3034.9487 | 3034.9487 | 0 | 157.0282
0 | 36.7806 | 0 | 0 | 0 | 0 | 15.7194 | 52.5 | 158.8159 | 3000 | 28.0885 | 3028.0885 | 3028.0885 | 0 | 152.6157
0 | 30.9469 | 0 | 0 | 0 | 0 | 21.5531 | 52.5 | 180.369 | 3000 | 38.5125 | 3038.5125 | 3038.5125 | 0 | 165.9028
0 | 30.6113 | 0 | 0 | 0 | 0 | 21.8887 | 52.5 | 202.2577 | 3000 | 39.1122 | 3039.1122 | 3039.1122 | 0 | 161.9847
0 | 30.7641 | 0 | 0 | 0 | 0 | 21.7359 | 52.5 | 223.9936 | 3000 | 38.8392 | 3038.8392 | 3038.8392 | 0 | 156.2875
0 | 49.5769 | 0 | 0 | 0 | 0 | 2.9231 | 52.5 | 226.9168 | 3000 | 5.2233 | 3005.2233 | 2983.5936 | 0 | 188.8913
0 | 54.1933 | 0 | 0 | 0 | 0 | -1.6933 | 52.5 | 225.2235 | 3000 | 0 | 3000 | 2859.4069 | 0 | 171.9075
0 | 46.7958 | 0 | 0 | 0 | 0 | 5.7042 | 52.5 | 230.9277 | 3000 | 10.1927 | 3010.1927 | 2691.1546 | 0 | 179.9037
0 | 42.1222 | 0 | 0 | 0 | 0 | 10.3778 | 52.5 | 241.3055 | 3000 | 18.5437 | 3018.5437 | 2634.6165 | 0 | 138.4491
0 | 45.0494 | 0 | 0 | 0 | 0 | 7.4506 | 52.5 | 248.7561 | 3000 | 13.3132 | 3013.3132 | 2645.6082 | 0 | 145.0058
0 | 36.5013 | 0 | 0 | 0 | 0 | 15.9987 | 52.5 | 264.7547 | 3000 | 28.5875 | 3028.5875 | 2655.4752 | 0 | 145.5466
0 | 41.0888 | 0 | 0 | 0 | 0 | 11.4112 | 52.5 | 276.1659 | 3000 | 20.3902 | 3020.3902 | 2793.2784 | 0 | 152.9599
0 | 61.1831 | 0 | 0 | 0 | 0 | -8.6831 | 52.5 | 267.4828 | 3000 | 0 | 3000 | 2891.8515 | 0 | 159.1964
0 | 33.6377 | 0 | 0 | 0 | 0 | 18.8623 | 52.5 | 286.3451 | 3000 | 33.7044 | 3033.7044 | 3017.4821 | 0 | 171.0309
0 | 38.3498 | 0 | 0 | 0 | 0 | 14.1502 | 52.5 | 300.4952 | 3000 | 25.2844 | 3025.2844 | 3025.2844 | 0 | 181.5473
0 | 49.6059 | 0 | 0 | 0 | 0 | 2.8941 | 52.5 | 303.3893 | 3000 | 5.1714 | 3005.1714 | 3005.1714 | 0 | 195.3361
0 | 28.0957 | 0 | 0 | 0 | 0 | 24.4043 | 52.5 | 327.7936 | 3000 | 43.6073 | 3043.6073 | 3043.6073 | 0 | 203.2217
0 | 38.6519 | 0 | 0 | 0 | 0 | 13.8481 | 52.5 | 341.6418 | 3000 | 24.7448 | 3024.7448 | 3024.7448 | 0 | 196.9411
0 | 36.7002 | 0 | 0 | 0 | 0 | 15.7998 | 52.5 | 357.4416 | 3000 | 28.2321 | 3028.2321 | 3028.2321 | 0 | 196.714
0 | 31.31 | 0 | 0 | 0 | 0 | 21.19 | 52.5 | 378.6316 | 3000 | 37.8637 | 3037.8637 | 3037.8637 | 0 | 184.3983
0 | 29.9526 | 0 | 0 | 0 | 0 | 22.5474 | 52.5 | 401.179 | 3000 | 40.2892 | 3040.2892 | 3040.2892 | 0 | 181.3228
0 | 38.3635 | 0 | 0 | 0 | 0 | 14.1365 | 52.5 | 415.3155 | 3000 | 25.2601 | 3025.2601 | 3025.2601 | 0 | 165.7843
0 | 28.0026 | 0 | 0 | 0 | 0 | 24.4974 | 52.5 | 439.8129 | 3000 | 43.7737 | 3043.7737 | 3043.7737 | 0 | 161.8983
0 | 28.5372 | 0 | 0 | 0 | 0 | 23.9628 | 52.5 | 463.7758 | 3000 | 42.8184 | 3042.8184 | 3042.8184 | 0 | 156.0966
0 | 238.1225 | 0 | 0 | 0 | 0 | -185.6225 | 52.5 | 278.1533 | 3000 | 0 | 3000 | 3000 | 0 | 153.06
0 | 33.8072 | 0 | 0 | 0 | 0 | 18.6928 | 52.5 | 296.846 | 3000 | 33.4015 | 3033.4015 | 3033.4015 | 0 | 152.8834
0 | 34.899 | 0 | 0 | 0 | 0 | 17.601 | 52.5 | 314.447 | 3000 | 31.4506 | 3031.4506 | 3031.4506 | 0 | 152.7245
0 | 28.6953 | 0 | 0 | 0 | 0 | 23.8047 | 52.5 | 338.2517 | 3000 | 42.5358 | 3042.5358 | 3042.5358 | 0 | 160.7676
0 | 31.7043 | 0 | 0 | 0 | 0 | 20.7957 | 52.5 | 359.0473 | 3000 | 37.1591 | 3037.1591 | 3037.1591 | 0 | 197.4153
0 | 37.7427 | 0 | 0 | 0 | 0 | -37.7427 | 0 | 321.3046 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 51.7849 | 0 | 0 | 0 | 0 | -51.7849 | 0 | 269.5196 | 0 | 0 | 0 | 0 | 27.0371 | 0
0 | 42.0773 | 0 | 0 | 0 | 0 | -42.0773 | 0 | 227.4423 | 0 | 0 | 0 | 0 | 135.1856 | 0
0 | 42.3079 | 0 | 0 | 0 | 0 | -35.9677 | 6.3402 | 191.4746 | 362.2975 | 0 | 362.2975 | 0 | 0 | 0
0 | 46.4353 | 0 | 0 | 0 | 0 | -37.8239 | 8.6113 | 153.6507 | 492.0757 | 0 | 492.0757 | 0 | 0 | 0
0 | 40.6664 | 0 | 0 | 0 | 0 | -33.4745 | 7.1919 | 120.1762 | 410.9643 | 0 | 410.9643 | 0 | 0 | 0
0 | 45.4039 | 0 | 0 | 0 | 0 | -45.4039 | 0 | 74.7723 | 0 | 0 | 0 | 0 | 156.8153 | 0
0 | 22.7957 | 0 | 0 | 0 | 0 | -22.7957 | 0 | 51.9765 | 0 | 0 | 0 | 0 | 86.5188 | 0
0 | 35.4015 | 0 | 0 | 0 | 0 | -35.4015 | 0 | 16.5751 | 0 | 0 | 0 | 0 | 16.2223 | 0
0 | 16.5751 | 0 | 0 | 0 | 0 | -16.5751 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 31.0298 | 0 | 0 | 0 | 0 | 21.4702 | 52.5 | 21.4702 | 3000 | 38.3643 | 3038.3643 | 3038.3643 | 0 | 209.4345
0 | 33.9101 | 0 | 0 | 0 | 0 | 18.5899 | 52.5 | 40.06 | 3000 | 33.2176 | 3033.2176 | 3033.2176 | 0 | 197.6748
0 | 32.9192 | 0 | 0 | 0 | 0 | 19.5808 | 52.5 | 59.6408 | 3000 | 34.9882 | 3034.9882 | 3034.9882 | 0 | 182.9491
0 | 26.615 | 0 | 0 | 0 | 0 | 25.885 | 52.5 | 85.5258 | 3000 | 46.2531 | 3046.2531 | 3046.2531 | 0 | 165.8685
0 | 31.599 | 0 | 0 | 0 | 0 | 20.901 | 52.5 | 106.4267 | 3000 | 37.3472 | 3037.3472 | 3037.3472 | 0 | 164.2294
0 | 23.6654 | 0 | 0 | 0 | 0 | 28.8346 | 52.5 | 135.2613 | 3000 | 51.5236 | 3051.5236 | 3051.5236 | 0 | 163.0429
0 | 35.2585 | 0 | 0 | 0 | 0 | 17.2415 | 52.5 | 152.5028 | 3000 | 30.8082 | 3030.8082 | 3030.8082 | 0 | 155.1774
0 | 29.261 | 0 | 0 | 0 | 0 | 23.239 | 52.5 | 175.7418 | 3000 | 41.525 | 3041.525 | 3041.525 | 0 | 154.844
0 | 38.9636 | 0 | 0 | 0 | 0 | 13.5364 | 52.5 | 189.2782 | 3000 | 24.1878 | 3024.1878 | 3024.1878 | 0 | 154.1731
0 | 80.078 | 0 | 0 | 0 | 0 | -27.578 | 52.5 | 161.7003 | 3000 | 0 | 3000 | 3000 | 0 | 159.03
0 | 103.7026 | 0 | 0 | 0 | 0 | -51.2026 | 52.5 | 110.4976 | 3000 | 0 | 3000 | 3000 | 0 | 180.63
0 | 162.9976 | 0 | 0 | 0 | 0 | -110.4976 | 52.5 | 0 | 3000 | 0 | 3000 | 2989.1851 | 0 | 204.4304
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2945.9257 | 0 | 205.5962
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2913.4812 | 0 | 202.72
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2859.4069 | 0 | 199.558
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2870.2218 | 0 | 198.1888
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2848.5921 | 0 | 193.4479
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2918.8886 | 0 | 197.2877
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2962.148 | 0 | 201.3964
0 | 39.6906 | 0 | 0 | 0 | 0 | 12.8094 | 52.5 | 12.8094 | 3000 | 22.8887 | 3022.8887 | 3017.4813 | 0 | 203.1972
0 | 49.1222 | 0 | 0 | 0 | 0 | 3.3778 | 52.5 | 16.1872 | 3000 | 6.0357 | 3006.0357 | 3006.0357 | 0 | 202.697
0 | 39.8737 | 0 | 0 | 0 | 0 | 12.6263 | 52.5 | 28.8135 | 3000 | 22.5615 | 3022.5615 | 3022.5615 | 0 | 210.2192
0 | 46.6794 | 0 | 0 | 0 | 0 | 5.8206 | 52.5 | 34.6341 | 3000 | 10.4007 | 3010.4007 | 3010.4007 | 0 | 209.2831
0 | 25.0972 | 0 | 0 | 0 | 0 | 27.4028 | 52.5 | 62.037 | 3000 | 48.9652 | 3048.9652 | 3048.9652 | 0 | 207.0247
0 | 40.8663 | 0 | 0 | 0 | 0 | 11.6337 | 52.5 | 73.6707 | 3000 | 20.7879 | 3020.7879 | 3020.7879 | 0 | 188.8294
0 | 35.8207 | 0 | 0 | 0 | 0 | 16.6793 | 52.5 | 90.35 | 3000 | 29.8037 | 3029.8037 | 3029.8037 | 0 | 177.3344
0 | 27.2684 | 0 | 0 | 0 | 0 | 25.2316 | 52.5 | 115.5815 | 3000 | 45.0854 | 3045.0854 | 3045.0854 | 0 | 174.4225
0 | 25.8486 | 0 | 0 | 0 | 0 | 26.6514 | 52.5 | 142.2329 | 3000 | 47.6225 | 3047.6225 | 3047.6225 | 0 | 160.7316
0 | 24.9965 | 0 | 0 | 0 | 0 | 27.5035 | 52.5 | 169.7365 | 3000 | 49.1451 | 3049.1451 | 3049.1451 | 0 | 156.1162
0 | 31.1324 | 0 | 0 | 0 | 0 | 21.3676 | 52.5 | 191.104 | 3000 | 38.181 | 3038.181 | 3038.181 | 0 | 152.8813
0 | 25.0338 | 0 | 0 | 0 | 0 | 27.4662 | 52.5 | 218.5702 | 3000 | 49.0784 | 3049.0784 | 3049.0784 | 0 | 145.8679
0 | 31.3079 | 0 | 0 | 0 | 0 | 21.1921 | 52.5 | 239.7623 | 3000 | 37.8675 | 3037.8675 | 3037.8675 | 0 | 137.4027
0 | 33.5983 | 0 | 0 | 0 | 0 | 18.9017 | 52.5 | 258.6641 | 3000 | 33.7749 | 3033.7749 | 3033.7749 | 0 | 141.5256
0 | 22.4201 | 0 | 0 | 0 | 0 | 30.0799 | 52.5 | 288.744 | 3000 | 53.7488 | 3053.7488 | 3053.7488 | 0 | 152.0767
0 | 244.2084 | 0 | 0 | 0 | 0 | -191.7084 | 52.5 | 97.0356 | 3000 | 0 | 3000 | 3000 | 0 | 170.82
0 | 110.6002 | 0 | 0 | 0 | 0 | -58.1002 | 52.5 | 38.9354 | 3000 | 0 | 3000 | 2994.5926 | 0 | 196.6848
0 | 90.4532 | 0 | 0 | 0 | 0 | -37.9532 | 52.5 | 0.98221 | 3000 | 0 | 3000 | 2972.9629 | 0 | 194.848
0 | 53.4822 | 0 | 0 | 0 | 0 | -0.98221 | 52.5 | 0 | 3000 | 0 | 3000 | 2864.8144 | 0 | 195.409
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2805.3327 | 0 | 177.4653
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2718.8139 | 0 | 164.162
0 | 44.7534 | 0 | 0 | 0 | 0 | 7.7466 | 52.5 | 7.7466 | 3000 | 13.8422 | 3013.8422 | 2884.064 | 0 | 170.5059
0 | 42.2736 | 0 | 0 | 0 | 0 | 10.2264 | 52.5 | 17.973 | 3000 | 18.2733 | 3018.2733 | 2947.9767 | 0 | 173.5474
0 | 47.1691 | 0 | 0 | 0 | 0 | 5.3309 | 52.5 | 23.3039 | 3000 | 9.5256 | 3009.5256 | 2950.0439 | 0 | 173.0791
0 | 43.3254 | 0 | 0 | 0 | 0 | 9.1746 | 52.5 | 32.4785 | 3000 | 16.3938 | 3016.3938 | 3010.9864 | 0 | 177.3471
0 | 54.1189 | 0 | 0 | 0 | 0 | -1.6189 | 52.5 | 30.8596 | 3000 | 0 | 3000 | 3000 | 0 | 179.64
0 | 59.6648 | 0 | 0 | 0 | 0 | -7.1648 | 52.5 | 23.6948 | 3000 | 0 | 3000 | 3000 | 0 | 186.57
0 | 62.7277 | 0 | 0 | 0 | 0 | -10.2277 | 52.5 | 13.4671 | 3000 | 0 | 3000 | 3000 | 0 | 188.16
0 | 27.6988 | 0 | 0 | 0 | 0 | 24.8012 | 52.5 | 38.2683 | 3000 | 44.3165 | 3044.3165 | 3044.3165 | 0 | 179.6147
0 | 27.0133 | 0 | 0 | 0 | 0 | 25.4867 | 52.5 | 63.755 | 3000 | 45.5414 | 3045.5414 | 3045.5414 | 0 | 175.2709
0 | 24.853 | 0 | 0 | 0 | 0 | 27.647 | 52.5 | 91.402 | 3000 | 49.4015 | 3049.4015 | 3049.4015 | 0 | 165.8874
0 | 32.3343 | 0 | 0 | 0 | 0 | 20.1657 | 52.5 | 111.5678 | 3000 | 36.0335 | 3036.0335 | 3036.0335 | 0 | 163.9458
0 | 29.0225 | 0 | 0 | 0 | 0 | 23.4775 | 52.5 | 135.0452 | 3000 | 41.9511 | 3041.9511 | 3041.9511 | 0 | 162.9877
0 | 29.0298 | 0 | 0 | 0 | 0 | 23.4702 | 52.5 | 158.5155 | 3000 | 41.9382 | 3041.9382 | 3041.9382 | 0 | 168.3409
0 | 29.3035 | 0 | 0 | 0 | 0 | 23.1965 | 52.5 | 181.7119 | 3000 | 41.449 | 3041.449 | 3041.449 | 0 | 156.0568
0 | 27.619 | 0 | 0 | 0 | 0 | 24.881 | 52.5 | 206.5929 | 3000 | 44.459 | 3044.459 | 3044.459 | 0 | 149.1785
0 | 238.7478 | 0 | 0 | 0 | 0 | -186.2478 | 52.5 | 20.3451 | 3000 | 0 | 3000 | 3000 | 0 | 140.85
0 | 35.7435 | 0 | 0 | 0 | 0 | 16.7565 | 52.5 | 37.1016 | 3000 | 29.9416 | 3029.9416 | 3029.9416 | 0 | 130.2875
0 | 89.6016 | 0 | 0 | 0 | 0 | -37.1016 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 130.62
0 | 29.8057 | 0 | 0 | 0 | 0 | 22.6943 | 52.5 | 22.6943 | 3000 | 40.5516 | 3040.5516 | 3040.5516 | 0 | 161.21
0 | 58.3936 | 0 | 0 | 0 | 0 | -5.8936 | 52.5 | 16.8006 | 3000 | 0 | 3000 | 2994.5926 | 0 | 194.6485
0 | 40.0255 | 0 | 0 | 0 | 0 | 12.4745 | 52.5 | 29.2751 | 3000 | 22.2903 | 3022.2903 | 3000.6606 | 0 | 197.8936
0 | 62.4043 | 0 | 0 | 0 | 0 | -9.9043 | 52.5 | 19.3709 | 3000 | 0 | 3000 | 2940.5183 | 0 | 196.8089
0 | 71.8709 | 0 | 0 | 0 | 0 | -19.3709 | 52.5 | 0 | 3000 | 0 | 3000 | 2913.4812 | 0 | 186.6085
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2821.555 | 0 | 181.3413
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2783.703 | 0 | 173.1463
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2886.4441 | 0 | 175.7267
0 | 42.6396 | 0 | 0 | 0 | 0 | 9.8604 | 52.5 | 9.8604 | 3000 | 17.6191 | 3017.6191 | 2985.1746 | 0 | 177.0209
0 | 41.3381 | 0 | 0 | 0 | 0 | 11.1619 | 52.5 | 21.0223 | 3000 | 19.9449 | 3019.9449 | 3014.5375 | 0 | 188.077
0 | 35.5733 | 0 | 0 | 0 | 0 | 16.9267 | 52.5 | 37.949 | 3000 | 30.2458 | 3030.2458 | 3030.2458 | 0 | 189.9964
0 | 37.949 | 0 | 0 | 0 | 0 | -37.949 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 32.106 | 0 | 0 | 0 | 0 | 20.394 | 52.5 | 20.394 | 3000 | 36.4413 | 3036.4413 | 3036.4413 | 0 | 211.0327
0 | 20.394 | 0 | 0 | 0 | 0 | -20.394 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 25.8465 | 0 | 0 | 0 | 0 | 26.6535 | 52.5 | 26.6535 | 3000 | 47.6263 | 3047.6263 | 3047.6263 | 0 | 197.7909
0 | 30.5977 | 0 | 0 | 0 | 0 | 21.9023 | 52.5 | 48.5559 | 3000 | 39.1365 | 3039.1365 | 3039.1365 | 0 | 180.7982
0 | 33.8666 | 0 | 0 | 0 | 0 | 18.6334 | 52.5 | 67.1892 | 3000 | 33.2953 | 3033.2953 | 3033.2953 | 0 | 169.0152
0 | 22.6988 | 0 | 0 | 0 | 0 | 29.8012 | 52.5 | 96.9905 | 3000 | 53.2508 | 3053.2508 | 3053.2508 | 0 | 172.7224
0 | 28.3818 | 0 | 0 | 0 | 0 | 24.1182 | 52.5 | 121.1086 | 3000 | 43.096 | 3043.096 | 3043.096 | 0 | 160.4929
0 | 26.5517 | 0 | 0 | 0 | 0 | 25.9483 | 52.5 | 147.0569 | 3000 | 46.3662 | 3046.3662 | 3046.3662 | 0 | 159.5991
0 | 25.3069 | 0 | 0 | 0 | 0 | 27.1931 | 52.5 | 174.2501 | 3000 | 48.5905 | 3048.5905 | 3048.5905 | 0 | 160.0205
0 | 32.1122 | 0 | 0 | 0 | 0 | 20.3878 | 52.5 | 194.6379 | 3000 | 36.4303 | 3036.4303 | 3036.4303 | 0 | 158.8053
0 | 34.6043 | 0 | 0 | 0 | 0 | 17.8957 | 52.5 | 212.5336 | 3000 | 31.9772 | 3031.9772 | 3031.9772 | 0 | 156.1468
0 | 36.7169 | 0 | 0 | 0 | 0 | 15.7831 | 52.5 | 228.3166 | 3000 | 28.2022 | 3028.2022 | 3028.2022 | 0 | 179.7238
0 | 46.9833 | 0 | 0 | 0 | 0 | 5.5167 | 52.5 | 233.8333 | 3000 | 9.8575 | 3009.8575 | 2988.2278 | 0 | 208.3094
0 | 60.0715 | 0 | 0 | 0 | 0 | -60.0715 | 0 | 173.7618 | 0 | 0 | 0 | 0 | 173.0376 | 0
0 | 99.5774 | 0 | 0 | 0 | 0 | -94.0889 | 5.4885 | 79.6729 | 313.6307 | 0 | 313.6307 | 0 | 0 | 0
0 | 72.4534 | 0 | 0 | 0 | 0 | -65.0723 | 7.3811 | 14.6006 | 421.7792 | 0 | 421.7792 | 0 | 0 | 0
0 | 43.0479 | 0 | 0 | 0 | 0 | 9.4521 | 52.5 | 24.0528 | 3000 | 16.8897 | 3016.8897 | 2708.6665 | 0 | 176.0633
0 | 46.2468 | 0 | 0 | 0 | 0 | 6.2532 | 52.5 | 30.306 | 3000 | 11.1736 | 3011.1736 | 2654.2835 | 0 | 150.3652
0 | 37.1769 | 0 | 0 | 0 | 0 | 15.3231 | 52.5 | 45.629 | 3000 | 27.3803 | 3027.3803 | 2875.9724 | 0 | 168.5895
0 | 46.3824 | 0 | 0 | 0 | 0 | 6.1176 | 52.5 | 51.7466 | 3000 | 10.9313 | 3010.9313 | 2935.2274 | 0 | 184.6552
0 | 39.6724 | 0 | 0 | 0 | 0 | 12.8276 | 52.5 | 64.5742 | 3000 | 22.9213 | 3022.9213 | 3012.1064 | 0 | 198.9195
0 | 49.4594 | 0 | 0 | 0 | 0 | 3.0406 | 52.5 | 67.6148 | 3000 | 5.4331 | 3005.4331 | 3005.4331 | 0 | 201.7848
0 | 42.2761 | 0 | 0 | 0 | 0 | 10.2239 | 52.5 | 77.8387 | 3000 | 18.2688 | 3018.2688 | 3018.2688 | 0 | 208.6529
0 | 45.0568 | 0 | 0 | 0 | 0 | 7.4432 | 52.5 | 85.282 | 3000 | 13.3001 | 3013.3001 | 3013.3001 | 0 | 208.0081
0 | 29.4885 | 0 | 0 | 0 | 0 | 23.0115 | 52.5 | 108.2935 | 3000 | 41.1185 | 3041.1185 | 3041.1185 | 0 | 195.0269
0 | 31.2603 | 0 | 0 | 0 | 0 | 21.2397 | 52.5 | 129.5332 | 3000 | 37.9525 | 3037.9525 | 3037.9525 | 0 | 199.3201
0 | 31.954 | 0 | 0 | 0 | 0 | 20.546 | 52.5 | 150.0792 | 3000 | 36.713 | 3036.713 | 3036.713 | 0 | 175.4613
0 | 28.1556 | 0 | 0 | 0 | 0 | 24.3444 | 52.5 | 174.4236 | 3000 | 43.5002 | 3043.5002 | 3043.5002 | 0 | 174.21
0 | 30.5478 | 0 | 0 | 0 | 0 | 21.9522 | 52.5 | 196.3758 | 3000 | 39.2257 | 3039.2257 | 3039.2257 | 0 | 164.9692
0 | 38.8641 | 0 | 0 | 0 | 0 | 13.6359 | 52.5 | 210.0117 | 3000 | 24.3656 | 3024.3656 | 3024.3656 | 0 | 155.1197
0 | 35.1662 | 0 | 0 | 0 | 0 | 17.3338 | 52.5 | 227.3455 | 3000 | 30.9732 | 3030.9732 | 3030.9732 | 0 | 163.036
0 | 30.6817 | 0 | 0 | 0 | 0 | 21.8183 | 52.5 | 249.1638 | 3000 | 38.9864 | 3038.9864 | 3038.9864 | 0 | 156.3255
0 | 23.762 | 0 | 0 | 0 | 0 | 28.738 | 52.5 | 277.9019 | 3000 | 51.3511 | 3051.3511 | 3051.3511 | 0 | 153.7576
0 | 34.5546 | 0 | 0 | 0 | 0 | 17.9454 | 52.5 | 295.8473 | 3000 | 32.0661 | 3032.0661 | 3032.0661 | 0 | 152.7858
0 | 57.3131 | 0 | 0 | 0 | 0 | -4.8131 | 52.5 | 291.0342 | 3000 | 0 | 3000 | 3000 | 0 | 153.09
0 | 92.921 | 0 | 0 | 0 | 0 | -40.421 | 52.5 | 250.6132 | 3000 | 0 | 3000 | 3000 | 0 | 154.68
0 | 294.2266 | 0 | 0 | 0 | 0 | -241.7266 | 52.5 | 8.8866 | 3000 | 0 | 3000 | 2978.3703 | 0 | 175.9621
0 | 55.2979 | 0 | 0 | 0 | 0 | -2.7979 | 52.5 | 6.0887 | 3000 | 0 | 3000 | 2810.7401 | 0 | 161.0273
0 | 58.5887 | 0 | 0 | 0 | 0 | -6.0887 | 52.5 | 0 | 3000 | 0 | 3000 | 2648.5174 | 0 | 159.838
0 | 43.8652 | 0 | 0 | 0 | 0 | 8.6348 | 52.5 | 8.6348 | 3000 | 15.4292 | 3015.4292 | 2561.2054 | 0 | 151.1111
0 | 36.663 | 0 | 0 | 0 | 0 | 15.837 | 52.5 | 24.4718 | 3000 | 28.2986 | 3028.2986 | 2530.8155 | 0 | 146.0281
0 | 52.0332 | 0 | 0 | 0 | 0 | 0.46683 | 52.5 | 24.9386 | 3000 | 0.83416 | 3000.8342 | 2535.7956 | 0 | 143.2725
0 | 42.0041 | 0 | 0 | 0 | 0 | 10.4959 | 52.5 | 35.4345 | 3000 | 18.7548 | 3018.7548 | 2699.7167 | 0 | 150.5632
0 | 41.6567 | 0 | 0 | 0 | 0 | 10.8433 | 52.5 | 46.2778 | 3000 | 19.3756 | 3019.3756 | 2938.2642 | 0 | 164.9542
0 | 98.7778 | 0 | 0 | 0 | 0 | -46.2778 | 52.5 | 0 | 3000 | 0 | 3000 | 2994.5926 | 0 | 173.7463
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 191.28
0 | 38.0254 | 0 | 0 | 0 | 0 | 14.4746 | 52.5 | 14.4746 | 3000 | 25.8641 | 3025.8641 | 3025.8641 | 0 | 205.4562
0 | 47.9217 | 0 | 0 | 0 | 0 | 4.5783 | 52.5 | 19.0529 | 3000 | 8.1809 | 3008.1809 | 3008.1809 | 0 | 204.8571
0 | 34.2123 | 0 | 0 | 0 | 0 | 18.2877 | 52.5 | 37.3406 | 3000 | 32.6777 | 3032.6777 | 3032.6777 | 0 | 197.1544
0 | 31.2418 | 0 | 0 | 0 | 0 | 21.2582 | 52.5 | 58.5988 | 3000 | 37.9856 | 3037.9856 | 3037.9856 | 0 | 189.4184
0 | 29.7912 | 0 | 0 | 0 | 0 | 22.7088 | 52.5 | 81.3076 | 3000 | 40.5776 | 3040.5776 | 3040.5776 | 0 | 174.59
0 | 30.3659 | 0 | 0 | 0 | 0 | 22.1341 | 52.5 | 103.4417 | 3000 | 39.5507 | 3039.5507 | 3039.5507 | 0 | 173.072
0 | 29.6777 | 0 | 0 | 0 | 0 | 22.8223 | 52.5 | 126.264 | 3000 | 40.7804 | 3040.7804 | 3040.7804 | 0 | 167.6382
0 | 28.2908 | 0 | 0 | 0 | 0 | 24.2092 | 52.5 | 150.4731 | 3000 | 43.2585 | 3043.2585 | 3043.2585 | 0 | 162.9665
0 | 24.5351 | 0 | 0 | 0 | 0 | 27.9649 | 52.5 | 178.438 | 3000 | 49.9695 | 3049.9695 | 3049.9695 | 0 | 158.8119
0 | 33.687 | 0 | 0 | 0 | 0 | 18.813 | 52.5 | 197.251 | 3000 | 33.6164 | 3033.6164 | 3033.6164 | 0 | 155.5032
0 | 24.7622 | 0 | 0 | 0 | 0 | 27.7378 | 52.5 | 224.9888 | 3000 | 49.5638 | 3049.5638 | 3049.5638 | 0 | 155.3143
0 | 27.1313 | 0 | 0 | 0 | 0 | 25.3687 | 52.5 | 250.3576 | 3000 | 45.3306 | 3045.3306 | 3045.3306 | 0 | 154.8855
0 | 28.1201 | 0 | 0 | 0 | 0 | 24.3799 | 52.5 | 274.7375 | 3000 | 43.5637 | 3043.5637 | 3043.5637 | 0 | 154.9783
0 | 27.1903 | 0 | 0 | 0 | 0 | 25.3097 | 52.5 | 300.0472 | 3000 | 45.225 | 3045.225 | 3045.225 | 0 | 155.7024
0 | 51.2714 | 0 | 0 | 0 | 0 | 1.2286 | 52.5 | 301.2758 | 3000 | 2.1953 | 3002.1953 | 2991.3805 | 0 | 155.6714
0 | 48.916 | 0 | 0 | 0 | 0 | 3.584 | 52.5 | 304.8598 | 3000 | 6.4042 | 3006.4042 | 2946.9225 | 0 | 158.3676
0 | 46.3907 | 0 | 0 | 0 | 0 | 6.1093 | 52.5 | 310.9691 | 3000 | 10.9166 | 3010.9166 | 2875.731 | 0 | 164.2618
0 | 31.4223 | 0 | 0 | 0 | 0 | 21.0777 | 52.5 | 332.0468 | 3000 | 37.663 | 3037.663 | 2864.6254 | 0 | 171.2187
0 | 39.6988 | 0 | 0 | 0 | 0 | 12.8012 | 52.5 | 344.8481 | 3000 | 22.8741 | 3022.8741 | 2866.0588 | 0 | 180.5617
0 | 42.6225 | 0 | 0 | 0 | 0 | 9.8775 | 52.5 | 354.7255 | 3000 | 17.6497 | 3017.6497 | 2839.2047 | 0 | 179.2958
0 | 43.2301 | 0 | 0 | 0 | 0 | 9.2699 | 52.5 | 363.9955 | 3000 | 16.5641 | 3016.5641 | 2875.9711 | 0 | 174.744
0 | 40.0618 | 0 | 0 | 0 | 0 | 12.4382 | 52.5 | 376.4336 | 3000 | 22.2253 | 3022.2253 | 2957.3362 | 0 | 176.553
0 | 47.6455 | 0 | 0 | 0 | 0 | 4.8545 | 52.5 | 381.2881 | 3000 | 8.6744 | 3008.6744 | 3003.267 | 0 | 180.136
0 | 56.1782 | 0 | 0 | 0 | 0 | -3.6782 | 52.5 | 377.6099 | 3000 | 0 | 3000 | 3000 | 0 | 188.37
0 | 38.245 | 0 | 0 | 0 | 0 | 14.255 | 52.5 | 391.8649 | 3000 | 25.4718 | 3025.4718 | 3025.4718 | 0 | 198.0171
0 | 52.1455 | 0 | 0 | 0 | 0 | 0.35454 | 52.5 | 392.2194 | 3000 | 0.63351 | 3000.6335 | 3000.6335 | 0 | 202.2427
0 | 30.3934 | 0 | 0 | 0 | 0 | 22.1066 | 52.5 | 414.326 | 3000 | 39.5015 | 3039.5015 | 3039.5015 | 0 | 197.8715
0 | 33.0622 | 0 | 0 | 0 | 0 | 19.4378 | 52.5 | 433.7638 | 3000 | 34.7328 | 3034.7328 | 3034.7328 | 0 | 177.5319
0 | 22.7403 | 0 | 0 | 0 | 0 | 29.7597 | 52.5 | 463.5235 | 3000 | 53.1766 | 3053.1766 | 3053.1766 | 0 | 174.2448
0 | 27.8354 | 0 | 0 | 0 | 0 | 24.6646 | 52.5 | 488.1881 | 3000 | 44.0724 | 3044.0724 | 3044.0724 | 0 | 167.1196
0 | 31.6087 | 0 | 0 | 0 | 0 | 20.8913 | 52.5 | 509.0794 | 3000 | 37.33 | 3037.33 | 3037.33 | 0 | 160.4621
0 | 22.9288 | 0 | 0 | 0 | 0 | 29.5712 | 52.5 | 538.6506 | 3000 | 52.8398 | 3052.8398 | 3052.8398 | 0 | 155.7864
0 | 31.6874 | 0 | 0 | 0 | 0 | 20.8126 | 52.5 | 559.4632 | 3000 | 37.1893 | 3037.1893 | 3037.1893 | 0 | 157.7212
0 | 29.4703 | 0 | 0 | 0 | 0 | 23.0297 | 52.5 | 582.4929 | 3000 | 41.1511 | 3041.1511 | 3041.1511 | 0 | 153.274
0 | 28.5082 | 0 | 0 | 0 | 0 | 23.9918 | 52.5 | 606.4848 | 3000 | 42.8702 | 3042.8702 | 3042.8702 | 0 | 150.5004
0 | 28.4166 | 0 | 0 | 0 | 0 | 24.0834 | 52.5 | 630.5682 | 3000 | 43.0338 | 3043.0338 | 3043.0338 | 0 | 153.3689
0 | 27.2532 | 0 | 0 | 0 | 0 | 25.2468 | 52.5 | 655.815 | 3000 | 45.1127 | 3045.1127 | 3045.1127 | 0 | 156.2143
0 | 27.8336 | 0 | 0 | 0 | 0 | 24.6664 | 52.5 | 680.4814 | 3000 | 44.0756 | 3044.0756 | 3044.0756 | 0 | 181.7922
0 | 41.3769 | 0 | 0 | 0 | 0 | 11.1231 | 52.5 | 691.6045 | 3000 | 19.8755 | 3019.8755 | 3003.6532 | 0 | 204.1583
0 | 36.4575 | 0 | 0 | 0 | 0 | -36.4575 | 0 | 655.147 | 0 | 0 | 0 | 0 | 124.3708 | 0
0 | 43.6981 | 0 | 0 | 0 | 0 | 8.8019 | 52.5 | 663.9489 | 3000 | 15.7279 | 3015.7279 | 2739.9492 | 0 | 189.3031
0 | 39.581 | 0 | 0 | 0 | 0 | 12.919 | 52.5 | 676.868 | 3000 | 23.0846 | 3023.0846 | 2639.1574 | 0 | 163.1263
0 | 54.0255 | 0 | 0 | 0 | 0 | -1.5255 | 52.5 | 675.3425 | 3000 | 0 | 3000 | 2540.3689 | 0 | 152.4983
0 | 49.4244 | 0 | 0 | 0 | 0 | 3.0756 | 52.5 | 678.4181 | 3000 | 5.4957 | 3005.4957 | 2594.5314 | 0 | 147.7845
0 | 40.4802 | 0 | 0 | 0 | 0 | 12.0198 | 52.5 | 690.4379 | 3000 | 21.4778 | 3021.4778 | 2734.8843 | 0 | 162.1239
0 | 41.9061 | 0 | 0 | 0 | 0 | 10.5939 | 52.5 | 701.0318 | 3000 | 18.93 | 3018.93 | 2954.0409 | 0 | 191.156
0 | 48.7207 | 0 | 0 | 0 | 0 | 3.7793 | 52.5 | 704.8111 | 3000 | 6.7531 | 3006.7531 | 3001.3456 | 0 | 203.9414
0 | 51.9698 | 0 | 0 | 0 | 0 | -51.9698 | 0 | 652.8413 | 0 | 0 | 0 | 0 | 0 | 0
0 | 43.2024 | 0 | 0 | 0 | 0 | -43.2024 | 0 | 609.6389 | 0 | 0 | 0 | 0 | 0 | 0
0 | 45.3357 | 0 | 0 | 0 | 0 | -45.3357 | 0 | 564.3032 | 0 | 0 | 0 | 0 | 0 | 0
0 | 32.606 | 0 | 0 | 0 | 0 | -32.606 | 0 | 531.6972 | 0 | 0 | 0 | 0 | 0 | 0
0 | 27.6226 | 0 | 0 | 0 | 0 | 24.8774 | 52.5 | 556.5746 | 3000 | 44.4526 | 3044.4526 | 3044.4526 | 0 | 211.3763
0 | 27.8942 | 0 | 0 | 0 | 0 | 24.6058 | 52.5 | 581.1804 | 3000 | 43.9672 | 3043.9672 | 3043.9672 | 0 | 195.8184
0 | 31.9871 | 0 | 0 | 0 | 0 | 20.5129 | 52.5 | 601.6932 | 3000 | 36.6538 | 3036.6538 | 3036.6538 | 0 | 176.0956
0 | 19.9958 | 0 | 0 | 0 | 0 | 32.5042 | 52.5 | 634.1974 | 3000 | 58.0806 | 3058.0806 | 3058.0806 | 0 | 169.9681
0 | 32.9392 | 0 | 0 | 0 | 0 | 19.5608 | 52.5 | 653.7582 | 3000 | 34.9525 | 3034.9525 | 3034.9525 | 0 | 167.0438
0 | 31.1069 | 0 | 0 | 0 | 0 | 21.3931 | 52.5 | 675.1512 | 3000 | 38.2266 | 3038.2266 | 3038.2266 | 0 | 158.96
0 | 33.9164 | 0 | 0 | 0 | 0 | 18.5836 | 52.5 | 693.7348 | 3000 | 33.2065 | 3033.2065 | 3033.2065 | 0 | 161.4879
0 | 23.4937 | 0 | 0 | 0 | 0 | 29.0063 | 52.5 | 722.7412 | 3000 | 51.8304 | 3051.8304 | 3051.8304 | 0 | 162.2353
0 | 45.5594 | 0 | 0 | 0 | 0 | 6.9406 | 52.5 | 729.6818 | 3000 | 12.4019 | 3012.4019 | 3012.4019 | 0 | 163.9349
0 | 101.3945 | 0 | 0 | 0 | 0 | -48.8945 | 52.5 | 680.7872 | 3000 | 0 | 3000 | 3000 | 0 | 173.43
0 | 316.6724 | 0 | 0 | 0 | 0 | -316.6724 | 0 | 364.1148 | 0 | 0 | 0 | 0 | 0 | 0
0 | 126.1754 | 0 | 0 | 0 | 0 | -126.1754 | 0 | 237.9395 | 0 | 0 | 0 | 0 | 16.2223 | 0
0 | 123.3389 | 0 | 0 | 0 | 0 | -123.3389 | 0 | 114.6006 | 0 | 0 | 0 | 0 | 135.1856 | 0
0 | 86.6956 | 0 | 0 | 0 | 0 | -80.9232 | 5.7724 | 33.6774 | 329.8529 | 0 | 329.8529 | 0 | 0 | 0
0 | 40.3961 | 0 | 0 | 0 | 0 | -33.6774 | 6.7187 | 0 | 383.9272 | 0 | 383.9272 | 0 | 0 | 0
0 | 7.3811 | 0 | 0 | 0 | 0 | 0 | 7.3811 | 0 | 421.7792 | 0 | 421.7792 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 259.5564 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2751.2584 | 0 | 187.911
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 81.1114 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8149 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 194.7
0 | 34.3077 | 0 | 0 | 0 | 0 | 18.1923 | 52.5 | 18.1923 | 3000 | 32.5073 | 3032.5073 | 3032.5073 | 0 | 188.9859
0 | 36.6758 | 0 | 0 | 0 | 0 | 15.8242 | 52.5 | 34.0166 | 3000 | 28.2758 | 3028.2758 | 3028.2758 | 0 | 174.6407
0 | 32.0411 | 0 | 0 | 0 | 0 | 20.4589 | 52.5 | 54.4755 | 3000 | 36.5574 | 3036.5574 | 3036.5574 | 0 | 171.5048
0 | 27.3272 | 0 | 0 | 0 | 0 | 25.1728 | 52.5 | 79.6483 | 3000 | 44.9804 | 3044.9804 | 3044.9804 | 0 | 162.8151
0 | 24.5054 | 0 | 0 | 0 | 0 | 27.9946 | 52.5 | 107.6429 | 3000 | 50.0227 | 3050.0227 | 3050.0227 | 0 | 158.7537
0 | 30.1717 | 0 | 0 | 0 | 0 | 22.3283 | 52.5 | 129.9712 | 3000 | 39.8977 | 3039.8977 | 3039.8977 | 0 | 151.9949
0 | 33.3525 | 0 | 0 | 0 | 0 | 19.1475 | 52.5 | 149.1187 | 3000 | 34.2141 | 3034.2141 | 3034.2141 | 0 | 151.7107
0 | 29.8805 | 0 | 0 | 0 | 0 | 22.6195 | 52.5 | 171.7382 | 3000 | 40.418 | 3040.418 | 3040.418 | 0 | 152.7506
0 | 26.9201 | 0 | 0 | 0 | 0 | 25.5799 | 52.5 | 197.318 | 3000 | 45.7078 | 3045.7078 | 3045.7078 | 0 | 154.0519
0 | 33.6598 | 0 | 0 | 0 | 0 | 18.8402 | 52.5 | 216.1583 | 3000 | 33.665 | 3033.665 | 3033.665 | 0 | 155.5967
0 | 49.3436 | 0 | 0 | 0 | 0 | 3.1564 | 52.5 | 219.3147 | 3000 | 5.6401 | 3005.6401 | 3005.6401 | 0 | 156.1129
0 | 99.2338 | 0 | 0 | 0 | 0 | -46.7338 | 52.5 | 172.5809 | 3000 | 0 | 3000 | 3000 | 0 | 174.78
0 | 92.4654 | 0 | 0 | 0 | 0 | -39.9654 | 52.5 | 132.6155 | 3000 | 0 | 3000 | 2989.1851 | 0 | 204.4603
0 | 66.6108 | 0 | 0 | 0 | 0 | -14.1108 | 52.5 | 118.5047 | 3000 | 0 | 3000 | 2870.2218 | 0 | 200.2267
0 | 77.5106 | 0 | 0 | 0 | 0 | -71.8328 | 5.6778 | 46.6719 | 324.4455 | 0 | 324.4455 | 0 | 0 | 0
0 | 54.337 | 0 | 0 | 0 | 0 | -46.6719 | 7.665 | 0 | 438.0014 | 0 | 438.0014 | 0 | 0 | 0
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2540.3689 | 0 | 170.3825
0 | 41.6356 | 0 | 0 | 0 | 0 | 10.8644 | 52.5 | 10.8644 | 3000 | 19.4133 | 3019.4133 | 2597.6341 | 0 | 168.5865
0 | 63.3644 | 0 | 0 | 0 | 0 | -10.8644 | 52.5 | 0 | 3000 | 0 | 3000 | 2718.8139 | 0 | 180.7739
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 70.2965 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 31.5501 | 0 | 0 | 0 | 0 | 20.9499 | 52.5 | 20.9499 | 3000 | 37.4347 | 3037.4347 | 3037.4347 | 0 | 206.3329
0 | 30.6926 | 0 | 0 | 0 | 0 | 21.8074 | 52.5 | 42.7574 | 3000 | 38.967 | 3038.967 | 3038.967 | 0 | 182.338
0 | 29.1855 | 0 | 0 | 0 | 0 | 23.3145 | 52.5 | 66.0719 | 3000 | 41.66 | 3041.66 | 3041.66 | 0 | 169.2075
0 | 32.5775 | 0 | 0 | 0 | 0 | 19.9225 | 52.5 | 85.9944 | 3000 | 35.5988 | 3035.5988 | 3035.5988 | 0 | 159.5814
0 | 29.318 | 0 | 0 | 0 | 0 | 23.182 | 52.5 | 109.1764 | 3000 | 41.4232 | 3041.4232 | 3041.4232 | 0 | 155.5992
0 | 34.4811 | 0 | 0 | 0 | 0 | 18.0189 | 52.5 | 127.1952 | 3000 | 32.1973 | 3032.1973 | 3032.1973 | 0 | 153.8234
0 | 31.2504 | 0 | 0 | 0 | 0 | 21.2496 | 52.5 | 148.4449 | 3000 | 37.9703 | 3037.9703 | 3037.9703 | 0 | 154.5112
0 | 29.9184 | 0 | 0 | 0 | 0 | 22.5816 | 52.5 | 171.0265 | 3000 | 40.3504 | 3040.3504 | 3040.3504 | 0 | 154.2978
0 | 26.1197 | 0 | 0 | 0 | 0 | 26.3803 | 52.5 | 197.4068 | 3000 | 47.1381 | 3047.1381 | 3047.1381 | 0 | 154.0633
0 | 30.329 | 0 | 0 | 0 | 0 | 22.171 | 52.5 | 219.5778 | 3000 | 39.6166 | 3039.6166 | 3039.6166 | 0 | 155.0204
0 | 27.0454 | 0 | 0 | 0 | 0 | 25.4546 | 52.5 | 245.0324 | 3000 | 45.4841 | 3045.4841 | 3045.4841 | 0 | 158.7915
0 | 38.3166 | 0 | 0 | 0 | 0 | 14.1834 | 52.5 | 259.2159 | 3000 | 25.3439 | 3025.3439 | 3014.529 | 0 | 190.8197
0 | 52.0312 | 0 | 0 | 0 | 0 | -52.0312 | 0 | 207.1847 | 0 | 0 | 0 | 0 | 48.6668 | 0
0 | 53.5876 | 0 | 0 | 0 | 0 | -53.5876 | 0 | 153.5971 | 0 | 0 | 0 | 0 | 81.1114 | 0
0 | 55.2992 | 0 | 0 | 0 | 0 | -55.2992 | 0 | 98.2979 | 0 | 0 | 0 | 0 | 140.5931 | 0
0 | 105.9109 | 0 | 0 | 0 | 0 | -53.4109 | 52.5 | 44.887 | 3000 | 0 | 3000 | 2816.1475 | 0 | 170.9965
0 | 97.387 | 0 | 0 | 0 | 0 | -44.887 | 52.5 | 0 | 3000 | 0 | 3000 | 2697.1842 | 0 | 153.6046
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2778.2956 | 0 | 157.9739
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2945.9257 | 0 | 163.1454
0 | 37.3672 | 0 | 0 | 0 | 0 | 15.1328 | 52.5 | 15.1328 | 3000 | 27.0404 | 3027.0404 | 3021.633 | 0 | 174.4691
0 | 38.1744 | 0 | 0 | 0 | 0 | 14.3256 | 52.5 | 29.4584 | 3000 | 25.5979 | 3025.5979 | 3025.5979 | 0 | 181.2333
0 | 47.2404 | 0 | 0 | 0 | 0 | 5.2596 | 52.5 | 34.718 | 3000 | 9.3982 | 3009.3982 | 3009.3982 | 0 | 180.263
0 | 39.0389 | 0 | 0 | 0 | 0 | 13.4611 | 52.5 | 48.1791 | 3000 | 24.0532 | 3024.0532 | 3024.0532 | 0 | 167.5628
0 | 31.5322 | 0 | 0 | 0 | 0 | 20.9678 | 52.5 | 69.1469 | 3000 | 37.4666 | 3037.4666 | 3037.4666 | 0 | 166.7569
0 | 30.3893 | 0 | 0 | 0 | 0 | 22.1107 | 52.5 | 91.2576 | 3000 | 39.5089 | 3039.5089 | 3039.5089 | 0 | 165.1973
0 | 33.1121 | 0 | 0 | 0 | 0 | 19.3879 | 52.5 | 110.6455 | 3000 | 34.6436 | 3034.6436 | 3034.6436 | 0 | 156.1324
0 | 31.7411 | 0 | 0 | 0 | 0 | 20.7589 | 52.5 | 131.4044 | 3000 | 37.0934 | 3037.0934 | 3037.0934 | 0 | 152.5532
0 | 29.3927 | 0 | 0 | 0 | 0 | 23.1073 | 52.5 | 154.5117 | 3000 | 41.2897 | 3041.2897 | 3041.2897 | 0 | 142.9406
0 | 207.0117 | 0 | 0 | 0 | 0 | -154.5117 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 145.65
0 | 23.0173 | 0 | 0 | 0 | 0 | 29.4827 | 52.5 | 29.4827 | 3000 | 52.6817 | 3052.6817 | 3052.6817 | 0 | 141.0339
0 | 33.434 | 0 | 0 | 0 | 0 | 19.066 | 52.5 | 48.5488 | 3000 | 34.0685 | 3034.0685 | 3034.0685 | 0 | 112.2605
0 | 30.2474 | 0 | 0 | 0 | 0 | 22.2526 | 52.5 | 70.8014 | 3000 | 39.7625 | 3039.7625 | 3039.7625 | 0 | 92.4088
0 | 34.2763 | 0 | 0 | 0 | 0 | 18.2237 | 52.5 | 89.0251 | 3000 | 32.5633 | 3032.5633 | 3032.5633 | 0 | 109.5968
0 | 64.3302 | 0 | 0 | 0 | 0 | -11.8302 | 52.5 | 77.1949 | 3000 | 0 | 3000 | 3000 | 0 | 128.01
0 | 56.9391 | 0 | 0 | 0 | 0 | -4.4391 | 52.5 | 72.7558 | 3000 | 0 | 3000 | 3000 | 0 | 143.7
0 | 68.0157 | 0 | 0 | 0 | 0 | -15.5157 | 52.5 | 57.2402 | 3000 | 0 | 3000 | 3000 | 0 | 167.1
0 | 109.7402 | 0 | 0 | 0 | 0 | -57.2402 | 52.5 | 0 | 3000 | 0 | 3000 | 2983.7777 | 0 | 168.0165
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2972.9629 | 0 | 192.9453
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2951.3332 | 0 | 194.1977
0 | 49.7329 | 0 | 0 | 0 | 0 | 2.7671 | 52.5 | 2.7671 | 3000 | 4.9444 | 3004.9444 | 2950.8702 | 0 | 187.3803
0 | 55.2671 | 0 | 0 | 0 | 0 | -2.7671 | 52.5 | 0 | 3000 | 0 | 3000 | 2956.7406 | 0 | 176.0739
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2972.9629 | 0 | 174.2156
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2989.1851 | 0 | 165.84
0 | 40.7098 | 0 | 0 | 0 | 0 | 11.7902 | 52.5 | 11.7902 | 3000 | 21.0675 | 3021.0675 | 3021.0675 | 0 | 172.9561
0 | 36.5845 | 0 | 0 | 0 | 0 | 15.9155 | 52.5 | 27.7057 | 3000 | 28.4389 | 3028.4389 | 3028.4389 | 0 | 180.6767
0 | 35.5267 | 0 | 0 | 0 | 0 | 16.9733 | 52.5 | 44.679 | 3000 | 30.3291 | 3030.3291 | 3030.3291 | 0 | 179.0924
0 | 40.5244 | 0 | 0 | 0 | 0 | 11.9756 | 52.5 | 56.6546 | 3000 | 21.3988 | 3021.3988 | 3021.3988 | 0 | 163.1253
0 | 33.7389 | 0 | 0 | 0 | 0 | 18.7611 | 52.5 | 75.4157 | 3000 | 33.5236 | 3033.5236 | 3033.5236 | 0 | 158.2893
0 | 29.2295 | 0 | 0 | 0 | 0 | 23.2705 | 52.5 | 98.6862 | 3000 | 41.5813 | 3041.5813 | 3041.5813 | 0 | 152.3832
0 | 31.4255 | 0 | 0 | 0 | 0 | 21.0745 | 52.5 | 119.7607 | 3000 | 37.6573 | 3037.6573 | 3037.6573 | 0 | 154.8598
0 | 28.8397 | 0 | 0 | 0 | 0 | 23.6603 | 52.5 | 143.421 | 3000 | 42.2778 | 3042.2778 | 3042.2778 | 0 | 155.1562
0 | 22.4818 | 0 | 0 | 0 | 0 | 30.0182 | 52.5 | 173.4392 | 3000 | 53.6386 | 3053.6386 | 3053.6386 | 0 | 147.4907
0 | 225.9392 | 0 | 0 | 0 | 0 | -173.4392 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 137.1
0 | 24.629 | 0 | 0 | 0 | 0 | 27.871 | 52.5 | 27.871 | 3000 | 49.8017 | 3049.8017 | 3049.8017 | 0 | 149.1353
0 | 31.2314 | 0 | 0 | 0 | 0 | 21.2686 | 52.5 | 49.1396 | 3000 | 38.0041 | 3038.0041 | 3038.0041 | 0 | 136.7102
0 | 28.3642 | 0 | 0 | 0 | 0 | 24.1358 | 52.5 | 73.2753 | 3000 | 43.1274 | 3043.1274 | 3043.1274 | 0 | 130.4284
0 | 25.9622 | 0 | 0 | 0 | 0 | 26.5378 | 52.5 | 99.8131 | 3000 | 47.4195 | 3047.4195 | 3047.4195 | 0 | 123.4205
0 | 56.1556 | 0 | 0 | 0 | 0 | -3.6556 | 52.5 | 96.1575 | 3000 | 0 | 3000 | 3000 | 0 | 139.5
0 | 68.781 | 0 | 0 | 0 | 0 | -16.281 | 52.5 | 79.8765 | 3000 | 0 | 3000 | 3000 | 0 | 142.5
0 | 40.6777 | 0 | 0 | 0 | 0 | 11.8223 | 52.5 | 91.6988 | 3000 | 21.1248 | 3021.1248 | 3015.7174 | 0 | 147.4686
0 | 76.9439 | 0 | 0 | 0 | 0 | -24.4439 | 52.5 | 67.2549 | 3000 | 0 | 3000 | 2967.5554 | 0 | 142.4427
0 | 98.7766 | 0 | 0 | 0 | 0 | -46.2766 | 52.5 | 20.9783 | 3000 | 0 | 3000 | 2902.6663 | 0 | 165.3068
0 | 73.1009 | 0 | 0 | 0 | 0 | -20.6009 | 52.5 | 0.37738 | 3000 | 0 | 3000 | 2853.9995 | 0 | 154.9436
0 | 44.4203 | 0 | 0 | 0 | 0 | 8.0797 | 52.5 | 8.457 | 3000 | 14.4373 | 3014.4373 | 2879.2516 | 0 | 155.9403
0 | 45.9892 | 0 | 0 | 0 | 0 | 6.5108 | 52.5 | 14.9678 | 3000 | 11.6339 | 3011.6339 | 2925.1151 | 0 | 153.5685
0 | 49.6195 | 0 | 0 | 0 | 0 | 2.8805 | 52.5 | 17.8483 | 3000 | 5.147 | 3005.147 | 2945.6654 | 0 | 150.9948
0 | 47.3053 | 0 | 0 | 0 | 0 | 5.1947 | 52.5 | 23.043 | 3000 | 9.2823 | 3009.2823 | 2982.2451 | 0 | 161.2798
0 | 45.3752 | 0 | 0 | 0 | 0 | 7.1248 | 52.5 | 30.1678 | 3000 | 12.7311 | 3012.7311 | 3012.7311 | 0 | 163.9227
0 | 32.2655 | 0 | 0 | 0 | 0 | 20.2345 | 52.5 | 50.4023 | 3000 | 36.1564 | 3036.1564 | 3036.1564 | 0 | 181.3193
0 | 47.1129 | 0 | 0 | 0 | 0 | 5.3871 | 52.5 | 55.7895 | 3000 | 9.6261 | 3009.6261 | 3009.6261 | 0 | 190.9909
0 | 45.766 | 0 | 0 | 0 | 0 | 6.734 | 52.5 | 62.5235 | 3000 | 12.0328 | 3012.0328 | 3012.0328 | 0 | 199.999
0 | 27.1511 | 0 | 0 | 0 | 0 | 25.3489 | 52.5 | 87.8724 | 3000 | 45.2952 | 3045.2952 | 3045.2952 | 0 | 177.023
0 | 29.3748 | 0 | 0 | 0 | 0 | 23.1252 | 52.5 | 110.9977 | 3000 | 41.3217 | 3041.3217 | 3041.3217 | 0 | 152.5831
0 | 29.2252 | 0 | 0 | 0 | 0 | 23.2748 | 52.5 | 134.2725 | 3000 | 41.589 | 3041.589 | 3041.589 | 0 | 152.2315
0 | 24.4113 | 0 | 0 | 0 | 0 | 28.0887 | 52.5 | 162.3612 | 3000 | 50.1908 | 3050.1908 | 3050.1908 | 0 | 155.7732
0 | 32.989 | 0 | 0 | 0 | 0 | 19.511 | 52.5 | 181.8722 | 3000 | 34.8636 | 3034.8636 | 3034.8636 | 0 | 138.0256
0 | 33.56 | 0 | 0 | 0 | 0 | 18.94 | 52.5 | 200.8122 | 3000 | 33.8433 | 3033.8433 | 3033.8433 | 0 | 112.1612
0 | 28.4302 | 0 | 0 | 0 | 0 | 24.0698 | 52.5 | 224.882 | 3000 | 43.0095 | 3043.0095 | 3043.0095 | 0 | 108.818
0 | 28.8917 | 0 | 0 | 0 | 0 | 23.6083 | 52.5 | 248.4903 | 3000 | 42.185 | 3042.185 | 3042.185 | 0 | 67.2019
0 | 28.4869 | 0 | 0 | 0 | 0 | 24.0131 | 52.5 | 272.5034 | 3000 | 42.9082 | 3042.9082 | 3042.9082 | 0 | 49.1125
0 | 36.3331 | 0 | 0 | 0 | 0 | 16.1669 | 52.5 | 288.6703 | 3000 | 28.8881 | 3028.8881 | 3028.8881 | 0 | 45.4636
0 | 23.9321 | 0 | 0 | 0 | 0 | 28.5679 | 52.5 | 317.2383 | 3000 | 51.0471 | 3051.0471 | 3051.0471 | 0 | 45.7657
0 | 29.2262 | 0 | 0 | 0 | 0 | 23.2738 | 52.5 | 340.512 | 3000 | 41.5872 | 3041.5872 | 3041.5872 | 0 | 45.6542
0 | 51.1169 | 0 | 0 | 0 | 0 | 1.3831 | 52.5 | 341.8951 | 3000 | 2.4713 | 3002.4713 | 3002.4713 | 0 | 51.7026
0 | 50.6221 | 0 | 0 | 0 | 0 | 1.8779 | 52.5 | 343.773 | 3000 | 3.3555 | 3003.3555 | 2992.5406 | 0 | 134.3651
0 | 33.1795 | 0 | 0 | 0 | 0 | 19.3205 | 52.5 | 363.0935 | 3000 | 34.5232 | 3034.5232 | 3007.4861 | 0 | 140.6
0 | 34.3774 | 0 | 0 | 0 | 0 | 18.1226 | 52.5 | 381.2161 | 3000 | 32.3826 | 3032.3826 | 2967.4935 | 0 | 153.6865
0 | 46.2181 | 0 | 0 | 0 | 0 | 6.2819 | 52.5 | 387.498 | 3000 | 11.2249 | 3011.2249 | 2903.0764 | 0 | 150.6987
0 | 229.0288 | 0 | 0 | 0 | 0 | -176.5288 | 52.5 | 210.9692 | 3000 | 0 | 3000 | 2891.8515 | 0 | 149.393
0 | 40.9918 | 0 | 0 | 0 | 0 | 11.5082 | 52.5 | 222.4774 | 3000 | 20.5636 | 3020.5636 | 2901.6002 | 0 | 149.9257
0 | 41.3867 | 0 | 0 | 0 | 0 | 11.1133 | 52.5 | 233.5906 | 3000 | 19.8579 | 3019.8579 | 2949.5614 | 0 | 152.8758
0 | 46.5739 | 0 | 0 | 0 | 0 | 5.9261 | 52.5 | 239.5167 | 3000 | 10.5891 | 3010.5891 | 3005.1817 | 0 | 163.572
0 | 38.8844 | 0 | 0 | 0 | 0 | 13.6156 | 52.5 | 253.1323 | 3000 | 24.3293 | 3024.3293 | 3024.3293 | 0 | 162.4972
0 | 36.9608 | 0 | 0 | 0 | 0 | -36.9608 | 0 | 216.1715 | 0 | 0 | 0 | 0 | 0 | 0
0 | 42.7004 | 0 | 0 | 0 | 0 | 9.7996 | 52.5 | 225.971 | 3000 | 17.5105 | 3017.5105 | 3017.5105 | 0 | 181.0506
0 | 21.037 | 0 | 0 | 0 | 0 | 31.463 | 52.5 | 257.434 | 3000 | 56.2202 | 3056.2202 | 3056.2202 | 0 | 177.2608
0 | 24.9416 | 0 | 0 | 0 | 0 | 27.5584 | 52.5 | 284.9925 | 3000 | 49.2433 | 3049.2433 | 3049.2433 | 0 | 156.1213
0 | 27.6453 | 0 | 0 | 0 | 0 | 24.8547 | 52.5 | 309.8472 | 3000 | 44.412 | 3044.412 | 3044.412 | 0 | 152.2206
0 | 24.7286 | 0 | 0 | 0 | 0 | 27.7714 | 52.5 | 337.6186 | 3000 | 49.6238 | 3049.6238 | 3049.6238 | 0 | 152.1762
0 | 28.167 | 0 | 0 | 0 | 0 | 24.333 | 52.5 | 361.9516 | 3000 | 43.4798 | 3043.4798 | 3043.4798 | 0 | 138.7827
0 | 26.1845 | 0 | 0 | 0 | 0 | 26.3155 | 52.5 | 388.2671 | 3000 | 47.0223 | 3047.0223 | 3047.0223 | 0 | 113.0445
0 | 23.5792 | 0 | 0 | 0 | 0 | 28.9208 | 52.5 | 417.1879 | 3000 | 51.6777 | 3051.6777 | 3051.6777 | 0 | 100.9495
0 | 33.0241 | 0 | 0 | 0 | 0 | 19.4759 | 52.5 | 436.6638 | 3000 | 34.8009 | 3034.8009 | 3034.8009 | 0 | 86.6132
0 | 30.2973 | 0 | 0 | 0 | 0 | 22.2027 | 52.5 | 458.8665 | 3000 | 39.6732 | 3039.6732 | 3039.6732 | 0 | 45.5951
0 | 31.6869 | 0 | 0 | 0 | 0 | 20.8131 | 52.5 | 479.6796 | 3000 | 37.1903 | 3037.1903 | 3037.1903 | 0 | 35.0188
0 | 31.3366 | 0 | 0 | 0 | 0 | 21.1634 | 52.5 | 500.843 | 3000 | 37.8161 | 3037.8161 | 3037.8161 | 0 | 45.871
0 | 25.2587 | 0 | 0 | 0 | 0 | 27.2413 | 52.5 | 528.0843 | 3000 | 48.6766 | 3048.6766 | 3048.6766 | 0 | 137.1904
0 | 42.1952 | 0 | 0 | 0 | 0 | 10.3048 | 52.5 | 538.3891 | 3000 | 18.4133 | 3018.4133 | 3013.0058 | 0 | 171.44
0 | 42.2931 | 0 | 0 | 0 | 0 | 10.2069 | 52.5 | 548.596 | 3000 | 18.2384 | 3018.2384 | 2974.979 | 0 | 173.5305
0 | 44.5054 | 0 | 0 | 0 | 0 | 7.9946 | 52.5 | 556.5906 | 3000 | 14.2853 | 3014.2853 | 2900.7294 | 0 | 177.3796
0 | 38.962 | 0 | 0 | 0 | 0 | 13.538 | 52.5 | 570.1286 | 3000 | 24.1906 | 3024.1906 | 2737.5971 | 0 | 167.7326
0 | 29.1008 | 0 | 0 | 0 | 0 | 23.3992 | 52.5 | 593.5278 | 3000 | 41.8112 | 3041.8112 | 2787.6622 | 0 | 165.0296
0 | 51.4698 | 0 | 0 | 0 | 0 | 1.0302 | 52.5 | 594.558 | 3000 | 1.8408 | 3001.8408 | 2758.5067 | 0 | 155.1108
0 | 45.8119 | 0 | 0 | 0 | 0 | 6.6881 | 52.5 | 601.2461 | 3000 | 11.9508 | 3011.9508 | 2898.3949 | 0 | 163.0347
0 | 35.4448 | 0 | 0 | 0 | 0 | 17.0552 | 52.5 | 618.3013 | 3000 | 30.4754 | 3030.4754 | 3003.4382 | 0 | 169.0635
0 | 29.1325 | 0 | 0 | 0 | 0 | 23.3675 | 52.5 | 641.6688 | 3000 | 41.7545 | 3041.7545 | 3036.3471 | 0 | 169.7014
0 | 35.9972 | 0 | 0 | 0 | 0 | 16.5028 | 52.5 | 658.1715 | 3000 | 29.4883 | 3029.4883 | 3029.4883 | 0 | 171.1358
0 | 34.3837 | 0 | 0 | 0 | 0 | 18.1163 | 52.5 | 676.2879 | 3000 | 32.3715 | 3032.3715 | 3032.3715 | 0 | 189.038
0 | 43.9461 | 0 | 0 | 0 | 0 | 8.5539 | 52.5 | 684.8418 | 3000 | 15.2847 | 3015.2847 | 3015.2847 | 0 | 165.3582
0 | 29.23 | 0 | 0 | 0 | 0 | 23.27 | 52.5 | 708.1118 | 3000 | 41.5804 | 3041.5804 | 3041.5804 | 0 | 163.0895
0 | 27.0872 | 0 | 0 | 0 | 0 | 25.4128 | 52.5 | 733.5246 | 3000 | 45.4093 | 3045.4093 | 3045.4093 | 0 | 149.5905
0 | 31.7995 | 0 | 0 | 0 | 0 | 20.7005 | 52.5 | 754.2251 | 3000 | 36.989 | 3036.989 | 3036.989 | 0 | 144.5607
0 | 27.4459 | 0 | 0 | 0 | 0 | 25.0541 | 52.5 | 779.2792 | 3000 | 44.7684 | 3044.7684 | 3044.7684 | 0 | 142.9519
0 | 27.9838 | 0 | 0 | 0 | 0 | 24.5162 | 52.5 | 803.7954 | 3000 | 43.8072 | 3043.8072 | 3043.8072 | 0 | 138.1888
0 | 32.9931 | 0 | 0 | 0 | 0 | 19.5069 | 52.5 | 823.3023 | 3000 | 34.8563 | 3034.8563 | 3034.8563 | 0 | 138.3894
0 | 31.492 | 0 | 0 | 0 | 0 | 21.008 | 52.5 | 844.3103 | 3000 | 37.5385 | 3037.5385 | 3037.5385 | 0 | 139.7268
0 | 24.0464 | 0 | 0 | 0 | 0 | 28.4536 | 52.5 | 872.7639 | 3000 | 50.8427 | 3050.8427 | 3050.8427 | 0 | 140.3388
0 | 26.1831 | 0 | 0 | 0 | 0 | 26.3169 | 52.5 | 899.0807 | 3000 | 47.0247 | 3047.0247 | 3047.0247 | 0 | 141.5343
0 | 46.7822 | 0 | 0 | 0 | 0 | 5.7178 | 52.5 | 904.7985 | 3000 | 10.2169 | 3010.2169 | 3010.2169 | 0 | 141.7511
0 | 75.6236 | 0 | 0 | 0 | 0 | -23.1236 | 52.5 | 881.6749 | 3000 | 0 | 3000 | 3000 | 0 | 149.79
0 | 123.9454 | 0 | 0 | 0 | 0 | -71.4454 | 52.5 | 810.2295 | 3000 | 0 | 3000 | 3000 | 0 | 183.33
0 | 507.4551 | 0 | 0 | 0 | 0 | -454.9551 | 52.5 | 355.2744 | 3000 | 0 | 3000 | 2983.7777 | 0 | 203.1953
0 | 111.8511 | 0 | 0 | 0 | 0 | -111.8511 | 0 | 243.4233 | 0 | 0 | 0 | 0 | 102.7411 | 0
0 | 80.9954 | 0 | 0 | 0 | 0 | -28.4954 | 52.5 | 214.9278 | 3000 | 0 | 3000 | 2745.851 | 0 | 192.0174
0 | 128.7525 | 0 | 0 | 0 | 0 | -76.2525 | 52.5 | 138.6753 | 3000 | 0 | 3000 | 2578.2208 | 0 | 170.1626
0 | 76.1561 | 0 | 0 | 0 | 0 | -23.6561 | 52.5 | 115.0192 | 3000 | 0 | 3000 | 2561.9986 | 0 | 166.2737
0 | 61.2088 | 0 | 0 | 0 | 0 | -8.7088 | 52.5 | 106.3104 | 3000 | 0 | 3000 | 2578.2208 | 0 | 160.7263
0 | 118.3478 | 0 | 0 | 0 | 0 | -65.8478 | 52.5 | 40.4626 | 3000 | 0 | 3000 | 2810.7401 | 0 | 174.2378
0 | 83.9583 | 0 | 0 | 0 | 0 | -31.4583 | 52.5 | 9.0043 | 3000 | 0 | 3000 | 2935.1109 | 0 | 181.4779
0 | 40.7168 | 0 | 0 | 0 | 0 | 11.7832 | 52.5 | 20.7875 | 3000 | 21.0551 | 3021.0551 | 3015.6476 | 0 | 184.6179
0 | 44.1286 | 0 | 0 | 0 | 0 | 8.3714 | 52.5 | 29.1589 | 3000 | 14.9586 | 3014.9586 | 3014.9586 | 0 | 182.1337
0 | 55.6957 | 0 | 0 | 0 | 0 | -3.1957 | 52.5 | 25.9632 | 3000 | 0 | 3000 | 3000 | 0 | 186.63
0 | 34.3015 | 0 | 0 | 0 | 0 | 18.1985 | 52.5 | 44.1617 | 3000 | 32.5182 | 3032.5182 | 3032.5182 | 0 | 145.2576
0 | 35.6065 | 0 | 0 | 0 | 0 | 16.8935 | 52.5 | 61.0553 | 3000 | 30.1865 | 3030.1865 | 3030.1865 | 0 | 140.2976
0 | 26.5942 | 0 | 0 | 0 | 0 | 25.9058 | 52.5 | 86.9611 | 3000 | 46.2902 | 3046.2902 | 3046.2902 | 0 | 146.953
0 | 30.761 | 0 | 0 | 0 | 0 | 21.739 | 52.5 | 108.7001 | 3000 | 38.8448 | 3038.8448 | 3038.8448 | 0 | 151.9422
0 | 23.7392 | 0 | 0 | 0 | 0 | 28.7608 | 52.5 | 137.4609 | 3000 | 51.3918 | 3051.3918 | 3051.3918 | 0 | 137.6178
0 | 26.0438 | 0 | 0 | 0 | 0 | 26.4562 | 52.5 | 163.9171 | 3000 | 47.2737 | 3047.2737 | 3047.2737 | 0 | 121.7081
0 | 23.3794 | 0 | 0 | 0 | 0 | 29.1206 | 52.5 | 193.0376 | 3000 | 52.0346 | 3052.0346 | 3052.0346 | 0 | 137.3416
0 | 27.8011 | 0 | 0 | 0 | 0 | 24.6989 | 52.5 | 217.7365 | 3000 | 44.1336 | 3044.1336 | 3044.1336 | 0 | 91.6284
0 | 27.7697 | 0 | 0 | 0 | 0 | 24.7303 | 52.5 | 242.4668 | 3000 | 44.1897 | 3044.1897 | 3044.1897 | 0 | 109.5908
0 | 32.0897 | 0 | 0 | 0 | 0 | 20.4103 | 52.5 | 262.8771 | 3000 | 36.4705 | 3036.4705 | 3036.4705 | 0 | 137.461
0 | 32.5094 | 0 | 0 | 0 | 0 | 19.9906 | 52.5 | 282.8677 | 3000 | 35.7205 | 3035.7205 | 3035.7205 | 0 | 137.5485
0 | 35.7483 | 0 | 0 | 0 | 0 | 16.7517 | 52.5 | 299.6195 | 3000 | 29.9331 | 3029.9331 | 3029.9331 | 0 | 148.8
0 | 94.7816 | 0 | 0 | 0 | 0 | -42.2816 | 52.5 | 257.3378 | 3000 | 0 | 3000 | 3000 | 0 | 156.42
0 | 104.2469 | 0 | 0 | 0 | 0 | -51.7469 | 52.5 | 205.5909 | 3000 | 0 | 3000 | 3000 | 0 | 162.51
0 | 72.3961 | 0 | 0 | 0 | 0 | -19.8961 | 52.5 | 185.6948 | 3000 | 0 | 3000 | 2983.7777 | 0 | 198.8389
0 | 68.5425 | 0 | 0 | 0 | 0 | -16.0425 | 52.5 | 169.6524 | 3000 | 0 | 3000 | 2913.4812 | 0 | 198.2041
0 | 92.6883 | 0 | 0 | 0 | 0 | -40.1883 | 52.5 | 129.464 | 3000 | 0 | 3000 | 2886.4441 | 0 | 196.3648
0 | 59.5459 | 0 | 0 | 0 | 0 | -7.0459 | 52.5 | 122.4182 | 3000 | 0 | 3000 | 2821.555 | 0 | 181.6517
0 | 174.9182 | 0 | 0 | 0 | 0 | -122.4182 | 52.5 | 0 | 3000 | 0 | 3000 | 2843.1847 | 0 | 183.7835
0 | 47.2646 | 0 | 0 | 0 | 0 | 5.2354 | 52.5 | 5.2354 | 3000 | 9.355 | 3009.355 | 2879.5768 | 0 | 192.4133
0 | 47.8032 | 0 | 0 | 0 | 0 | 4.6968 | 52.5 | 9.9322 | 3000 | 8.3926 | 3008.3926 | 2938.0961 | 0 | 194.7664
0 | 60.1917 | 0 | 0 | 0 | 0 | -7.6917 | 52.5 | 2.2405 | 3000 | 0 | 3000 | 2994.5926 | 0 | 200.0088
0 | 50.6268 | 0 | 0 | 0 | 0 | 1.8732 | 52.5 | 4.1137 | 3000 | 3.3472 | 3003.3472 | 3003.3472 | 0 | 203.8071
0 | 4.1137 | 0 | 0 | 0 | 0 | -4.1137 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
0 | 25.3493 | 0 | 0 | 0 | 0 | 27.1507 | 52.5 | 27.1507 | 3000 | 48.5146 | 3048.5146 | 3048.5146 | 0 | 208.7013
0 | 32.606 | 0 | 0 | 0 | 0 | 19.894 | 52.5 | 47.0447 | 3000 | 35.548 | 3035.548 | 3035.548 | 0 | 188.8718
0 | 23.6054 | 0 | 0 | 0 | 0 | 28.8946 | 52.5 | 75.9393 | 3000 | 51.6308 | 3051.6308 | 3051.6308 | 0 | 182.1824
0 | 29.3469 | 0 | 0 | 0 | 0 | 23.1531 | 52.5 | 99.0924 | 3000 | 41.3716 | 3041.3716 | 3041.3716 | 0 | 160.0674
0 | 24.3486 | 0 | 0 | 0 | 0 | 28.1514 | 52.5 | 127.2438 | 3000 | 50.3028 | 3050.3028 | 3050.3028 | 0 | 159.1343
0 | 22.4066 | 0 | 0 | 0 | 0 | 30.0934 | 52.5 | 157.3372 | 3000 | 53.7729 | 3053.7729 | 3053.7729 | 0 | 158.7962
0 | 30.7442 | 0 | 0 | 0 | 0 | 21.7558 | 52.5 | 179.093 | 3000 | 38.8748 | 3038.8748 | 3038.8748 | 0 | 154.466
0 | 26.9075 | 0 | 0 | 0 | 0 | 25.5925 | 52.5 | 204.6855 | 3000 | 45.7304 | 3045.7304 | 3045.7304 | 0 | 152.3474
0 | 26.7397 | 0 | 0 | 0 | 0 | 25.7603 | 52.5 | 230.4458 | 3000 | 46.0302 | 3046.0302 | 3046.0302 | 0 | 151.2354
0 | 25.3055 | 0 | 0 | 0 | 0 | 27.1945 | 52.5 | 257.6403 | 3000 | 48.5929 | 3048.5929 | 3048.5929 | 0 | 152.9784
0 | 29.818 | 0 | 0 | 0 | 0 | 22.682 | 52.5 | 280.3223 | 3000 | 40.5297 | 3040.5297 | 3040.5297 | 0 | 158.0467
0 | 24.0943 | 0 | 0 | 0 | 0 | 28.4057 | 52.5 | 308.728 | 3000 | 50.7572 | 3050.7572 | 3050.7572 | 0 | 195.2485
0 | 39.8028 | 0 | 0 | 0 | 0 | -39.8028 | 0 | 268.9252 | 0 | 0 | 0 | 0 | 5.4074 | 0
0 | 248.47 | 0 | 0 | 0 | 0 | -248.47 | 0 | 20.4552 | 0 | 0 | 0 | 0 | 86.5188 | 0
0 | 20.4552 | 0 | 0 | 0 | 0 | -20.4552 | 0 | 0 | 0 | 0 | 0 | 0 | 183.8525 | 0
0 | 34.8017 | 0 | 0 | 0 | 0 | 17.6983 | 52.5 | 17.6983 | 3000 | 31.6245 | 3031.6245 | 2772.0681 | 0 | 191.2727
0 | 54.5515 | 0 | 0 | 0 | 0 | -2.0515 | 52.5 | 15.6468 | 3000 | 0 | 3000 | 2702.5916 | 0 | 174.8307
0 | 47.7432 | 0 | 0 | 0 | 0 | 4.7568 | 52.5 | 20.4036 | 3000 | 8.4998 | 3008.4998 | 2684.0543 | 0 | 171.7795
0 | 38.006 | 0 | 0 | 0 | 0 | 14.494 | 52.5 | 34.8977 | 3000 | 25.8989 | 3025.8989 | 2793.3796 | 0 | 172.8264
0 | 49.7609 | 0 | 0 | 0 | 0 | 2.7391 | 52.5 | 37.6368 | 3000 | 4.8944 | 3004.8944 | 2923.783 | 0 | 181.7131
0 | 45.9172 | 0 | 0 | 0 | 0 | 6.5828 | 52.5 | 44.2196 | 3000 | 11.7625 | 3011.7625 | 3006.3551 | 0 | 191.6551
0 | 37.8507 | 0 | 0 | 0 | 0 | 14.6493 | 52.5 | 58.8689 | 3000 | 26.1764 | 3026.1764 | 3026.1764 | 0 | 189.711
0 | 56.7122 | 0 | 0 | 0 | 0 | -4.2122 | 52.5 | 54.6566 | 3000 | 0 | 3000 | 3000 | 0 | 201.39
0 | 71.7553 | 0 | 0 | 0 | 0 | -19.2553 | 52.5 | 35.4013 | 3000 | 0 | 3000 | 3000 | 0 | 186.15
0 | 46.9771 | 0 | 0 | 0 | 0 | 5.5229 | 52.5 | 40.9242 | 3000 | 9.8686 | 3009.8686 | 3009.8686 | 0 | 166.6263
0 | 92.5952 | 0 | 0 | 0 | 0 | -40.0952 | 52.5 | 0.82898 | 3000 | 0 | 3000 | 3000 | 0 | 159.12
0 | 53.329 | 0 | 0 | 0 | 0 | -0.82898 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 153.39
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 150.21
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 147.81
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 135.3
0 | 41.5008 | 0 | 0 | 0 | 0 | 10.9992 | 52.5 | 10.9992 | 3000 | 19.6541 | 3019.6541 | 3019.6541 | 0 | 131.1134
0 | 22.3141 | 0 | 0 | 0 | 0 | 30.1859 | 52.5 | 41.1851 | 3000 | 53.9383 | 3053.9383 | 3053.9383 | 0 | 134.3733
0 | 93.6851 | 0 | 0 | 0 | 0 | -41.1851 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 104.7
0 | 35.9158 | 0 | 0 | 0 | 0 | 16.5842 | 52.5 | 16.5842 | 3000 | 29.6338 | 3029.6338 | 3029.6338 | 0 | 109.0668
0 | 56.3058 | 0 | 0 | 0 | 0 | -3.8058 | 52.5 | 12.7784 | 3000 | 0 | 3000 | 3000 | 0 | 127.8
0 | 65.2784 | 0 | 0 | 0 | 0 | -12.7784 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 143.49
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2994.5926 | 0 | 164.0138
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 2972.9629 | 0 | 178.3778
0 | 47.7123 | 0 | 0 | 0 | 0 | 4.7877 | 52.5 | 4.7877 | 3000 | 8.555 | 3008.555 | 2965.2956 | 0 | 174.6559
0 | 29.5372 | 0 | 0 | 0 | 0 | 22.9628 | 52.5 | 27.7505 | 3000 | 41.0314 | 3041.0314 | 2976.1423 | 0 | 166.1283
0 | 48.6551 | 0 | 0 | 0 | 0 | 3.8449 | 52.5 | 31.5953 | 3000 | 6.8702 | 3006.8702 | 2931.1663 | 0 | 166.0506
0 | 84.0953 | 0 | 0 | 0 | 0 | -31.5953 | 52.5 | 0 | 3000 | 0 | 3000 | 2913.4812 | 0 | 169.7685
0 | 38.5047 | 0 | 0 | 0 | 0 | 13.9953 | 52.5 | 13.9953 | 3000 | 25.0078 | 3025.0078 | 2992.5632 | 0 | 166.985
0 | 42.1089 | 0 | 0 | 0 | 0 | 10.3911 | 52.5 | 24.3864 | 3000 | 18.5674 | 3018.5674 | 3002.3452 | 0 | 159.3645
0 | 38.0305 | 0 | 0 | 0 | 0 | 14.4695 | 52.5 | 38.8558 | 3000 | 25.855 | 3025.855 | 3025.855 | 0 | 162.6094
0 | 42.1431 | 0 | 0 | 0 | 0 | 10.3569 | 52.5 | 49.2127 | 3000 | 18.5064 | 3018.5064 | 3018.5064 | 0 | 167.678
0 | 33.3574 | 0 | 0 | 0 | 0 | 19.1426 | 52.5 | 68.3554 | 3000 | 34.2053 | 3034.2053 | 3034.2053 | 0 | 198.9225
0 | 60.5675 | 0 | 0 | 0 | 0 | -8.0675 | 52.5 | 60.2878 | 3000 | 0 | 3000 | 3000 | 0 | 184.77
0 | 75.353 | 0 | 0 | 0 | 0 | -22.853 | 52.5 | 37.4348 | 3000 | 0 | 3000 | 3000 | 0 | 173.37
0 | 45.4028 | 0 | 0 | 0 | 0 | 7.0972 | 52.5 | 44.532 | 3000 | 12.6817 | 3012.6817 | 3012.6817 | 0 | 161.6002
0 | 92.3505 | 0 | 0 | 0 | 0 | -39.8505 | 52.5 | 4.6815 | 3000 | 0 | 3000 | 3000 | 0 | 154.53
0 | 40.9489 | 0 | 0 | 0 | 0 | 11.5511 | 52.5 | 16.2326 | 3000 | 20.6403 | 3020.6403 | 3020.6403 | 0 | 151.1528
0 | 68.7326 | 0 | 0 | 0 | 0 | -16.2326 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 146.88
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 148.17
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 142.86
0 | 52.5 | 0 | 0 | 0 | 0 | 0 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 140.49
0 | 20.859 | 0 | 0 | 0 | 0 | 31.641 | 52.5 | 31.641 | 3000 | 56.5382 | 3056.5382 | 3056.5382 | 0 | 123.7898
0 | 22.7528 | 0 | 0 | 0 | 0 | 29.7472 | 52.5 | 61.3882 | 3000 | 53.1543 | 3053.1543 | 3053.1543 | 0 | 112.7225
0 | 34.4105 | 0 | 0 | 0 | 0 | 18.0895 | 52.5 | 79.4776 | 3000 | 32.3235 | 3032.3235 | 3032.3235 | 0 | 105.8887
0 | 70.8516 | 0 | 0 | 0 | 0 | -18.3516 | 52.5 | 61.1261 | 3000 | 0 | 3000 | 3000 | 0 | 111.75
0 | 45.1337 | 0 | 0 | 0 | 0 | 7.3663 | 52.5 | 68.4924 | 3000 | 13.1626 | 3013.1626 | 3007.7552 | 0 | 129.7846
0 | 69.3587 | 0 | 0 | 0 | 0 | -16.8587 | 52.5 | 51.6337 | 3000 | 0 | 3000 | 2929.7035 | 0 | 143.2332
0 | 92.436 | 0 | 0 | 0 | 0 | -39.936 | 52.5 | 11.6977 | 3000 | 0 | 3000 | 2767.4807 | 0 | 139.9238
0 | 59.1146 | 0 | 0 | 0 | 0 | -6.6146 | 52.5 | 5.0831 | 3000 | 0 | 3000 | 2799.9253 | 0 | 140.8362
0 | 47.9237 | 0 | 0 | 0 | 0 | 4.5763 | 52.5 | 9.6593 | 3000 | 8.1772 | 3008.1772 | 2597.2128 | 0 | 130.0165
0 | 47.8645 | 0 | 0 | 0 | 0 | 4.6355 | 52.5 | 14.2949 | 3000 | 8.2831 | 3008.2831 | 2770.3564 | 0 | 139.8476
0 | 46.0715 | 0 | 0 | 0 | 0 | 6.4285 | 52.5 | 20.7234 | 3000 | 11.4869 | 3011.4869 | 2876.3013 | 0 | 146.6338
0 | 49.7895 | 0 | 0 | 0 | 0 | 2.7105 | 52.5 | 23.4339 | 3000 | 4.8433 | 3004.8433 | 2972.3988 | 0 | 151.1168
0 | 45.333 | 0 | 0 | 0 | 0 | 7.167 | 52.5 | 30.6009 | 3000 | 12.8065 | 3012.8065 | 3012.8065 | 0 | 153.7134
0 | 31.6848 | 0 | 0 | 0 | 0 | 20.8152 | 52.5 | 51.4161 | 3000 | 37.1941 | 3037.1941 | 3037.1941 | 0 | 155.9599
0 | 51.8175 | 0 | 0 | 0 | 0 | 0.68249 | 52.5 | 52.0986 | 3000 | 1.2195 | 3001.2195 | 3001.2195 | 0 | 167.0779
0 | 34.8412 | 0 | 0 | 0 | 0 | 17.6588 | 52.5 | 69.7574 | 3000 | 31.5539 | 3031.5539 | 3031.5539 | 0 | 166.7658
0 | 34.0304 | 0 | 0 | 0 | 0 | 18.4696 | 52.5 | 88.227 | 3000 | 33.0027 | 3033.0027 | 3033.0027 | 0 | 163.7821
0 | 28.7348 | 0 | 0 | 0 | 0 | 23.7652 | 52.5 | 111.9922 | 3000 | 42.4653 | 3042.4653 | 3042.4653 | 0 | 165.2059
0 | 164.4922 | 0 | 0 | 0 | 0 | -111.9922 | 52.5 | 0 | 3000 | 0 | 3000 | 3000 | 0 | 150.06
0 | 29.0594 | 0 | 0 | 0 | 0 | 23.4406 | 52.5 | 23.4406 | 3000 | 41.8853 | 3041.8853 | 3041.8853 | 0 | 149.0524
0 | 34.0048 | 0 | 0 | 0 | 0 | 18.4952 | 52.5 | 41.9358 | 3000 | 33.0485 | 3033.0485 | 3033.0485 | 0 | 151.6524
0 | 24.2617 | 0 | 0 | 0 | 0 | 28.2383 | 52.5 | 70.1741 | 3000 | 50.4581 | 3050.4581 | 3050.4581 | 0 | 152.2179
0 | 27.2138 | 0 | 0 | 0 | 0 | 25.2862 | 52.5 | 95.4603 | 3000 | 45.183 | 3045.183 | 3045.183 | 0 | 152.2592
0 | 30.0893 | 0 | 0 | 0 | 0 | 22.4107 | 52.5 | 117.871 | 3000 | 40.0449 | 3040.0449 | 3040.0449 | 0 | 136.498
0 | 25.1933 | 0 | 0 | 0 | 0 | 27.3067 | 52.5 | 145.1777 | 3000 | 48.7935 | 3048.7935 | 3048.7935 | 0 | 96.1589
0 | 35.9141 | 0 | 0 | 0 | 0 | 16.5859 | 52.5 | 161.7637 | 3000 | 29.6368 | 3029.6368 | 3029.6368 | 0 | 81.5275
0 | 24.8427 | 0 | 0 | 0 | 0 | 27.6573 | 52.5 | 189.421 | 3000 | 49.4199 | 3049.4199 | 3049.4199 | 0 | 93.6172
0 | 35.7937 | 0 | 0 | 0 | 0 | 16.7063 | 52.5 | 206.1272 | 3000 | 29.8519 | 3029.8519 | 3029.8519 | 0 | 127.072
0 | 32.3465 | 0 | 0 | 0 | 0 | 20.1535 | 52.5 | 226.2807 | 3000 | 36.0116 | 3036.0116 | 3030.6042 | 0 | 141.1655
0 | 36.1303 | 0 | 0 | 0 | 0 | 16.3697 | 52.5 | 242.6504 | 3000 | 29.2504 | 3029.2504 | 2937.3242 | 0 | 129.536
0 | 44.1971 | 0 | 0 | 0 | 0 | 8.3029 | 52.5 | 250.9533 | 3000 | 14.8361 | 3014.8361 | 2728.2426 | 0 | 134.0931
0 | 60.3616 | 0 | 0 | 0 | 0 | -7.8616 | 52.5 | 243.0917 | 3000 | 0 | 3000 | 2594.4431 | 0 | 130.9156
0 | 43.367 | 0 | 0 | 0 | 0 | 9.133 | 52.5 | 252.2247 | 3000 | 16.3195 | 3016.3195 | 2621.5774 | 0 | 132.2586
0 | 33.8472 | 0 | 0 | 0 | 0 | 18.6528 | 52.5 | 270.8775 | 3000 | 33.3301 | 3033.3301 | 2827.8479 | 0 | 142.6649
0 | 29.8309 | 0 | 0 | 0 | 0 | 22.6691 | 52.5 | 293.5467 | 3000 | 40.5067 | 3040.5067 | 2948.5805 | 0 | 148.8443
0 | 49.0767 | 0 | 0 | 0 | 0 | 3.4233 | 52.5 | 296.9699 | 3000 | 6.1169 | 3006.1169 | 2935.8204 | 0 | 155.7746
0 | 31.9156 | 0 | 0 | 0 | 0 | 20.5844 | 52.5 | 317.5543 | 3000 | 36.7816 | 3036.7816 | 3036.7816 | 0 | 177.8339
0 | 48.3795 | 0 | 0 | 0 | 0 | 4.1205 | 52.5 | 321.6748 | 3000 | 7.3628 | 3007.3628 | 3007.3628 | 0 | 148.8645
0 | 39.0937 | 0 | 0 | 0 | 0 | 13.4063 | 52.5 | 335.0811 | 3000 | 23.9552 | 3023.9552 | 3023.9552 | 0 | 163.596
0 | 35.8524 | 0 | 0 | 0 | 0 | 16.6476 | 52.5 | 351.7287 | 3000 | 29.747 | 3029.747 | 3029.747 | 0 | 172.7259
0 | 230.2328 | 0 | 0 | 0 | 0 | -177.7328 | 52.5 | 173.9959 | 3000 | 0 | 3000 | 3000 | 0 | 172.2
0 | 36.0743 | 0 | 0 | 0 | 0 | 16.4257 | 52.5 | 190.4216 | 3000 | 29.3506 | 3029.3506 | 3029.3506 | 0 | 159.0106
0 | 32.9147 | 0 | 0 | 0 | 0 | 19.5853 | 52.5 | 210.0069 | 3000 | 34.9963 | 3034.9963 | 3034.9963 | 0 | 152.721
0 | 31.3635 | 0 | 0 | 0 | 0 | 21.1365 | 52.5 | 231.1435 | 3000 | 37.7682 | 3037.7682 | 3037.7682 | 0 | 147.028
0 | 27.0581 | 0 | 0 | 0 | 0 | 25.4419 | 52.5 | 256.5854 | 3000 | 45.4613 | 3045.4613 | 3045.4613 | 0 | 152.5776
0 | 23.002 | 0 | 0 | 0 | 0 | 29.498 | 52.5 | 286.0833 | 3000 | 52.7089 | 3052.7089 | 3052.7089 | 0 | 153.3376
0 | 31.3266 | 0 | 0 | 0 | 0 | 21.1734 | 52.5 | 307.2568 | 3000 | 37.8341 | 3037.8341 | 3037.8341 | 0 | 147.8818
0 | 33.0835 | 0 | 0 | 0 | 0 | 19.4165 | 52.5 | 326.6732 | 3000 | 34.6947 | 3034.6947 | 3034.6947 | 0 | 139.3228
0 | 39.5893 | 0 | 0 | 0 | 0 | 12.9107 | 52.5 | 339.5839 | 3000 | 23.0696 | 3023.0696 | 3023.0696 | 0 | 134.4964
0 | 31.1118 | 0 | 0 | 0 | 0 | 21.3882 | 52.5 | 360.9721 | 3000 | 38.2178 | 3038.2178 | 3038.2178 | 0 | 134.2588
0 | 24.6647 | 0 | 0 | 0 | 0 | 27.8353 | 52.5 | 388.8073 | 3000 | 49.7379 | 3049.7379 | 3049.7379 | 0 | 142.6362
0 | 26.877 | 0 | 0 | 0 | 0 | 25.623 | 52.5 | 414.4303 | 3000 | 45.7849 | 3045.7849 | 3045.7849 | 0 | 164.0764
0 | 44.5563 | 0 | 0 | 0 | 0 | 7.9437 | 52.5 | 422.3741 | 3000 | 14.1944 | 3014.1944 | 3014.1944 | 0 | 195.9528
0 | 41.9036 | 0 | 0 | 0 | 0 | 10.5964 | 52.5 | 432.9705 | 3000 | 18.9344 | 3018.9344 | 2975.675 | 0 | 176.8444
0 | 56.3217 | 0 | 0 | 0 | 0 | -3.8217 | 52.5 | 429.1488 | 3000 | 0 | 3000 | 2918.8886 | 0 | 178.3441
0 | 47.2389 | 0 | 0 | 0 | 0 | 5.2611 | 52.5 | 434.4099 | 3000 | 9.4009 | 3009.4009 | 2912.0673 | 0 | 167.6186
0 | 42.7711 | 0 | 0 | 0 | 0 | 9.7289 | 52.5 | 444.1388 | 3000 | 17.3842 | 3017.3842 | 2936.2729 | 0 | 184.9852
0 | 50.0367 | 0 | 0 | 0 | 0 | 2.4633 | 52.5 | 446.6021 | 3000 | 4.4015 | 3004.4015 | 2907.0678 | 0 | 172.2147
0 | 55.0605 | 0 | 0 | 0 | 0 | -2.5605 | 52.5 | 444.0416 | 3000 | 0 | 3000 | 2918.8886 | 0 | 174.316
0 | 30.9086 | 0 | 0 | 0 | 0 | 21.5914 | 52.5 | 465.6329 | 3000 | 38.5809 | 3038.5809 | 3006.1363 | 0 | 183.4645
0 | 42.1939 | 0 | 0 | 0 | 0 | 10.3061 | 52.5 | 475.9391 | 3000 | 18.4157 | 3018.4157 | 3018.4157 | 0 | 188.168
0 | 44.5434 | 0 | 0 | 0 | 0 | 7.9566 | 52.5 | 483.8957 | 3000 | 14.2174 | 3014.2174 | 3014.2174 | 0 | 195.9241
0 | 44.5631 | 0 | 0 | 0 | 0 | 7.9369 | 52.5 | 491.8326 | 3000 | 14.1822 | 3014.1822 | 3014.1822 | 0 | 201.9804
0 | 249.9315 | 0 | 0 | 0 | 0 | -197.4315 | 52.5 | 294.4011 | 3000 | 0 | 3000 | 3000 | 0 | 200.88
0 | 225.6579 | 0 | 0 | 0 | 0 | -173.1579 | 52.5 | 121.2432 | 3000 | 0 | 3000 | 3000 | 0 | 187.65
0 | 24.3545 | 0 | 0 | 0 | 0 | 28.1455 | 52.5 | 149.3887 | 3000 | 50.2923 | 3050.2923 | 3050.2923 | 0 | 174.3852
0 | 27.479 | 0 | 0 | 0 | 0 | 25.021 | 52.5 | 174.4097 | 3000 | 44.7092 | 3044.7092 | 3044.7092 | 0 | 167.7635
0 | 32.3054 | 0 | 0 | 0 | 0 | 20.1946 | 52.5 | 194.6043 | 3000 | 36.0851 | 3036.0851 | 3036.0851 | 0 | 161.1554
0 | 22.1729 | 0 | 0 | 0 | 0 | 30.3271 | 52.5 | 224.9314 | 3000 | 54.1905 | 3054.1905 | 3054.1905 | 0 | 155.7637
0 | 33.5682 | 0 | 0 | 0 | 0 | 18.9318 | 52.5 | 243.8632 | 3000 | 33.8286 | 3033.8286 | 3033.8286 | 0 | 144.744
0 | 31.6343 | 0 | 0 | 0 | 0 | 20.8657 | 52.5 | 264.7289 | 3000 | 37.2842 | 3037.2842 | 3037.2842 | 0 | 142.4486
0 | 27.7329 | 0 | 0 | 0 | 0 | 24.7671 | 52.5 | 289.496 | 3000 | 44.2556 | 3044.2556 | 3044.2556 | 0 | 138.5136
0 | 29.0675 | 0 | 0 | 0 | 0 | 23.4325 | 52.5 | 312.9286 | 3000 | 41.8708 | 3041.8708 | 3041.8708 | 0 | 134.4203
0 | 24.8192 | 0 | 0 | 0 | 0 | 27.6808 | 52.5 | 340.6094 | 3000 | 49.462 | 3049.462 | 3049.462 | 0 | 135.3961
0 | 18.7299 | 0 | 0 | 0 | 0 | 33.7701 | 52.5 | 374.3795 | 3000 | 60.3427 | 3060.3427 | 3060.3427 | 0 | 141.6021
0 | 34.2367 | 0 | 0 | 0 | 0 | 18.2633 | 52.5 | 392.6429 | 3000 | 32.6342 | 3032.6342 | 3032.6342 | 0 | 153.8759
0 | 39.7738 | 0 | 0 | 0 | 0 | 12.7262 | 52.5 | 405.369 | 3000 | 22.74 | 3022.74 | 3017.3326 | 0 | 178.5356
0 | 47.8207 | 0 | 0 | 0 | 0 | 4.6793 | 52.5 | 410.0483 | 3000 | 8.3613 | 3008.3613 | 2965.1019 | 0 | 191.2491
0 | 46.8767 | 0 | 0 | 0 | 0 | 5.6233 | 52.5 | 415.6717 | 3000 | 10.0482 | 3010.0482 | 2934.3442 | 0 | 168.8128
0 | 46.8111 | 0 | 0 | 0 | 0 | 5.6889 | 52.5 | 421.3606 | 3000 | 10.1653 | 3010.1653 | 2907.4243 | 0 | 159.8502
0 | 44.9998 | 0 | 0 | 0 | 0 | 7.5002 | 52.5 | 428.8608 | 3000 | 13.4018 | 3013.4018 | 2791.6974 | 0 | 147.7366
0 | 42.3736 | 0 | 0 | 0 | 0 | 10.1264 | 52.5 | 438.9872 | 3000 | 18.0945 | 3018.0945 | 2720.6861 | 0 | 135.2181
0 | 36.4147 | 0 | 0 | 0 | 0 | 16.0853 | 52.5 | 455.0725 | 3000 | 28.7423 | 3028.7423 | 2780.0007 | 0 | 140.0008
0 | 44.8942 | 0 | 0 | 0 | 0 | 7.6058 | 52.5 | 462.6782 | 3000 | 13.5905 | 3013.5905 | 2954.1089 | 0 | 156.5678
0 | 41.7302 | 0 | 0 | 0 | 0 | 10.7698 | 52.5 | 473.448 | 3000 | 19.2441 | 3019.2441 | 3013.8367 | 0 | 173.3559
0 | 42.064 | 0 | 0 | 0 | 0 | 10.436 | 52.5 | 483.884 | 3000 | 18.6478 | 3018.6478 | 3018.6478 | 0 | 173.7836
0 | 36.5816 | 0 | 0 | 0 | 0 | 15.9184 | 52.5 | 499.8024 | 3000 | 28.444 | 3028.444 | 3028.444 | 0 | 175.1349
0 | 46.6379 | 0 | 0 | 0 | 0 | 5.8621 | 52.5 | 505.6645 | 3000 | 10.4748 | 3010.4748 | 3010.4748 | 0 | 161.9334
0 | 25.4059 | 0 | 0 | 0 | 0 | 27.0941 | 52.5 | 532.7586 | 3000 | 48.4136 | 3048.4136 | 3048.4136 | 0 | 157.7249
0 | 28.2553 | 0 | 0 | 0 | 0 | 24.2447 | 52.5 | 557.0033 | 3000 | 43.322 | 3043.322 | 3043.322 | 0 | 149.7314
0 | 27.3932 | 0 | 0 | 0 | 0 | 25.1068 | 52.5 | 582.1101 | 3000 | 44.8625 | 3044.8625 | 3044.8625 | 0 | 147.3409
0 | 22.0562 | 0 | 0 | 0 | 0 | 30.4438 | 52.5 | 612.5539 | 3000 | 54.399 | 3054.399 | 3054.399 | 0 | 143.2513
0 | 28.5045 | 0 | 0 | 0 | 0 | 23.9955 | 52.5 | 636.5494 | 3000 | 42.8768 | 3042.8768 | 3042.8768 | 0 | 137.2337
0 | 30.391 | 0 | 0 | 0 | 0 | 22.109 | 52.5 | 658.6584 | 3000 | 39.5058 | 3039.5058 | 3039.5058 | 0 | 148.723
0 | 25.2601 | 0 | 0 | 0 | 0 | 27.2399 | 52.5 | 685.8983 | 3000 | 48.6741 | 3048.6741 | 3048.6741 | 0 | 138.7147
0 | 34.7213 | 0 | 0 | 0 | 0 | 17.7787 | 52.5 | 703.677 | 3000 | 31.7681 | 3031.7681 | 3031.7681 | 0 | 136.4296
0 | 229.1656 | 0 | 0 | 0 | 0 | -176.6656 | 52.5 | 527.0113 | 3000 | 0 | 3000 | 3000 | 0 | 125.49
0 | 31.2092 | 0 | 0 | 0 | 0 | 21.2908 | 52.5 | 548.3021 | 3000 | 38.0438 | 3038.0438 | 3038.0438 | 0 | 131.8207
0 | 22.4246 | 0 | 0 | 0 | 0 | 30.0754 | 52.5 | 578.3775 | 3000 | 53.7407 | 3053.7407 | 3053.7407 | 0 | 138.0902
0 | 25.3983 | 0 | 0 | 0 | 0 | 27.1017 | 52.5 | 605.4791 | 3000 | 48.4271 | 3048.4271 | 3048.4271 | 0 | 156.049
0 | 42.3557 | 0 | 0 | 0 | 0 | 10.1443 | 52.5 | 615.6235 | 3000 | 18.1266 | 3018.1266 | 3018.1266 | 0 | 172.1841
0 | 43.7652 | 0 | 0 | 0 | 0 | 8.7348 | 52.5 | 624.3582 | 3000 | 15.6079 | 3015.6079 | 2988.5708 | 0 | 200.5331
0 | 51.1337 | 0 | 0 | 0 | 0 | 1.3663 | 52.5 | 625.7245 | 3000 | 2.4414 | 3002.4414 | 2872.6632 | 0 | 192.3823
0 | 36.5882 | 0 | 0 | 0 | 0 | 15.9118 | 52.5 | 641.6363 | 3000 | 28.4322 | 3028.4322 | 2893.2466 | 0 | 172.0903
0 | 41.8076 | 0 | 0 | 0 | 0 | 10.6924 | 52.5 | 652.3287 | 3000 | 19.1059 | 3019.1059 | 2856.8832 | 0 | 180.0693
0 | 36.7775 | 0 | 0 | 0 | 0 | 15.7225 | 52.5 | 668.0512 | 3000 | 28.094 | 3028.094 | 2865.8712 | 0 | 175.7066
0 | 36.3739 | 0 | 0 | 0 | 0 | 16.1261 | 52.5 | 684.1774 | 3000 | 28.8153 | 3028.8153 | 2861.1851 | 0 | 176.5065
0 | 48.6655 | 0 | 0 | 0 | 0 | 3.8345 | 52.5 | 688.0119 | 3000 | 6.8517 | 3006.8517 | 2914.9255 | 0 | 182.6201
0 | 39.8838 | 0 | 0 | 0 | 0 | 12.6162 | 52.5 | 700.6281 | 3000 | 22.5435 | 3022.5435 | 3017.1361 | 0 | 186.3082
0 | 50.4673 | 0 | 0 | 0 | 0 | 2.0327 | 52.5 | 702.6608 | 3000 | 3.6321 | 3003.6321 | 3003.6321 | 0 | 196.4075
0 | 50.7687 | 0 | 0 | 0 | 0 | 1.7313 | 52.5 | 704.3921 | 3000 | 3.0936 | 3003.0936 | 3003.0936 | 0 | 207.784
0 | 54.9389 | 0 | 0 | 0 | 0 | -2.4389 | 52.5 | 701.9532 | 3000 | 0 | 3000 | 3000 | 0 | 198
0 | 28.1306 | 0 | 0 | 0 | 0 | 24.3694 | 52.5 | 726.3225 | 3000 | 43.5448 | 3043.5448 | 3043.5448 | 0 | 186.5693
0 | 32.5704 | 0 | 0 | 0 | 0 | 19.9296 | 52.5 | 746.2521 | 3000 | 35.6116 | 3035.6116 | 3035.6116 | 0 | 178.6457
0 | 24.8277 | 0 | 0 | 0 | 0 | 27.6723 | 52.5 | 773.9244 | 3000 | 49.4467 | 3049.4467 | 3049.4467 | 0 | 165.1275
0 | 31.2916 | 0 | 0 | 0 | 0 | 21.2084 | 52.5 | 795.1328 | 3000 | 37.8966 | 3037.8966 | 3037.8966 | 0 | 154.6289
0 | 22.9259 | 0 | 0 | 0 | 0 | 29.5741 | 52.5 | 824.7069 | 3000 | 52.8449 | 3052.8449 | 3052.8449 | 0 | 143.3921
0 | 23.5626 | 0 | 0 | 0 | 0 | 28.9374 | 52.5 | 853.6443 | 3000 | 51.7073 | 3051.7073 | 3051.7073 | 0 | 129.3314
0 | 20.4631 | 0 | 0 | 0 | 0 | 32.0369 | 52.5 | 885.6812 | 3000 | 57.2457 | 3057.2457 | 3057.2457 | 0 | 120.3332
0 | 16.6457 | 0 | 0 | 0 | 0 | 35.8543 | 52.5 | 921.5355 | 3000 | 64.0668 | 3064.0668 | 3064.0668 | 0 | 120.6017
0 | 28.1539 | 0 | 0 | 0 | 0 | 24.3461 | 52.5 | 945.8816 | 3000 | 43.5032 | 3043.5032 | 3043.5032 | 0 | 113.827
0 | 29.6454 | 0 | 0 | 0 | 0 | 22.8546 | 52.5 | 968.7361 | 3000 | 40.8381 | 3040.8381 | 3040.8381 | 0 | 93.2321
0 | 30.6985 | 0 | 0 | 0 | 0 | 21.8015 | 52.5 | 990.5376 | 3000 | 38.9564 | 3038.9564 | 3038.9564 | 0 | 101.1061
0 | 28.7949 | 0 | 0 | 0 | 0 | 23.7051 | 52.5 | 1014.2427 | 3000 | 42.3579 | 3042.3579 | 3042.3579 | 0 | 139.4617
0 | 50.6918 | 0 | 0 | 0 | 0 | 1.8082 | 52.5 | 1016.0509 | 3000 | 3.231 | 3003.231 | 2997.8236 | 0 | 164.8803
0 | 33.1516 | 0 | 0 | 0 | 0 | 19.3484 | 52.5 | 1035.3993 | 3000 | 34.573 | 3034.573 | 2937.2393 | 0 | 170.213
0 | 39.9027 | 0 | 0 | 0 | 0 | 12.5973 | 52.5 | 1047.9966 | 3000 | 22.5096 | 3022.5096 | 2757.5458 | 0 | 150.6172
0 | 46.0946 | 0 | 0 | 0 | 0 | 6.4054 | 52.5 | 1054.4019 | 3000 | 11.4455 | 3011.4455 | 2643.7406 | 0 | 139.7481
0 | 42.3205 | 0 | 0 | 0 | 0 | 10.1795 | 52.5 | 1064.5814 | 3000 | 18.1894 | 3018.1894 | 2596.4102 | 0 | 136.8049
0 | 44.2668 | 0 | 0 | 0 | 0 | 8.2332 | 52.5 | 1072.8146 | 3000 | 14.7116 | 3014.7116 | 2630.7844 | 0 | 136.4588
0 | 37.0788 | 0 | 0 | 0 | 0 | 15.4212 | 52.5 | 1088.2359 | 3000 | 27.5557 | 3027.5557 | 2773.4067 | 0 | 144.5222
0 | 31.7223 | 0 | 0 | 0 | 0 | 20.7777 | 52.5 | 1109.0136 | 3000 | 37.127 | 3037.127 | 2977.6453 | 0 | 154.242
0 | 36.4735 | 0 | 0 | 0 | 0 | 16.0265 | 52.5 | 1125.0401 | 3000 | 28.6373 | 3028.6373 | 3028.6373 | 0 | 162.6984
0 | 36.6568 | 0 | 0 | 0 | 0 | 15.8432 | 52.5 | 1140.8833 | 3000 | 28.3097 | 3028.3097 | 3028.3097 | 0 | 165.0126
0 | 250.1009 | 0 | 0 | 0 | 0 | -197.6009 | 52.5 | 943.2825 | 3000 | 0 | 3000 | 3000 | 0 | 165.93
0 | 55.969 | 0 | 0 | 0 | 0 | -3.469 | 52.5 | 939.8135 | 3000 | 0 | 3000 | 3000 | 0 | 164.73
0 | 28.5456 | 0 | 0 | 0 | 0 | 23.9544 | 52.5 | 963.7679 | 3000 | 42.8034 | 3042.8034 | 3042.8034 | 0 | 164.2201
0 | 28.9498 | 0 | 0 | 0 | 0 | 23.5502 | 52.5 | 987.3181 | 3000 | 42.081 | 3042.081 | 3042.081 | 0 | 154.1727
0 | 30.2361 | 0 | 0 | 0 | 0 | 22.2639 | 52.5 | 1009.582 | 3000 | 39.7827 | 3039.7827 | 3039.7827 | 0 | 152.2627
0 | 24.6219 | 0 | 0 | 0 | 0 | 27.8781 | 52.5 | 1037.4601 | 3000 | 49.8145 | 3049.8145 | 3049.8145 | 0 | 149.8679
0 | 34.991 | 0 | 0 | 0 | 0 | 17.509 | 52.5 | 1054.9691 | 3000 | 31.2862 | 3031.2862 | 3031.2862 | 0 | 137.6204
0 | 31.5389 | 0 | 0 | 0 | 0 | 20.9611 | 52.5 | 1075.9302 | 3000 | 37.4547 | 3037.4547 | 3037.4547 | 0 | 126.2366
0 | 220.376 | 0 | 0 | 0 | 0 | -167.876 | 52.5 | 908.0542 | 3000 | 0 | 3000 | 3000 | 0 | 122.85
0 | 37.4758 | 0 | 0 | 0 | 0 | 15.0242 | 52.5 | 923.0784 | 3000 | 26.8463 | 3026.8463 | 3026.8463 | 0 | 123.4348
0 | 28.1803 | 0 | 0 | 0 | 0 | 24.3197 | 52.5 | 947.3981 | 3000 | 43.4561 | 3043.4561 | 3043.4561 | 0 | 95.9906
0 | 29.4713 | 0 | 0 | 0 | 0 | 23.0287 | 52.5 | 970.4268 | 3000 | 41.1492 | 3041.1492 | 3041.1492 | 0 | 110.1504
0 | 30.8986 | 0 | 0 | 0 | 0 | 21.6014 | 52.5 | 992.0281 | 3000 | 38.5988 | 3038.5988 | 3038.5988 | 0 | 134.3365
0 | 31.3883 | 0 | 0 | 0 | 0 | 21.1117 | 52.5 | 1013.1399 | 3000 | 37.7239 | 3037.7239 | 3037.7239 | 0 | 149.1522
0 | 41.8055 | 0 | 0 | 0 | 0 | 10.6945 | 52.5 | 1023.8344 | 3000 | 19.1097 | 3019.1097 | 3019.1097 | 0 | 158.6844
0 | 45.9715 | 0 | 0 | 0 | 0 | 6.5285 | 52.5 | 1030.363 | 3000 | 11.6656 | 3011.6656 | 2979.221 | 0 | 162.0398
0 | 49.1325 | 0 | 0 | 0 | 0 | 3.3675 | 52.5 | 1033.7304 | 3000 | 6.0172 | 3006.0172 | 2941.1281 | 0 | 176.1736
0 | 40.9107 | 0 | 0 | 0 | 0 | 11.5893 | 52.5 | 1045.3197 | 3000 | 20.7085 | 3020.7085 | 2923.3749 | 0 | 158.4177
0 | 45.2558 | 0 | 0 | 0 | 0 | 7.2442 | 52.5 | 1052.5639 | 3000 | 12.9444 | 3012.9444 | 2899.3885 | 0 | 179.7621
0 | 40.4082 | 0 | 0 | 0 | 0 | 12.0918 | 52.5 | 1064.6558 | 3000 | 21.6065 | 3021.6065 | 2962.1248 | 0 | 160.014
0 | 42.4241 | 0 | 0 | 0 | 0 | 10.0759 | 52.5 | 1074.7316 | 3000 | 18.0042 | 3018.0042 | 2888.226 | 0 | 199.2876
0 | 41.3167 | 0 | 0 | 0 | 0 | 11.1833 | 52.5 | 1085.9149 | 3000 | 19.9831 | 3019.9831 | 2982.1311 | 0 | 178.6297
0 | 35.3661 | 0 | 0 | 0 | 0 | 17.1339 | 52.5 | 1103.0489 | 3000 | 30.6161 | 3030.6161 | 3030.6161 | 0 | 162.6229
0 | 38.1434 | 0 | 0 | 0 | 0 | 14.3566 | 52.5 | 1117.4054 | 3000 | 25.6533 | 3025.6533 | 3025.6533 | 0 | 162.4473
0 | 39.7012 | 0 | 0 | 0 | 0 | 12.7988 | 52.5 | 1130.2043 | 3000 | 22.8698 | 3022.8698 | 3022.8698 | 0 | 196.1843
0 | 24.2799 | 0 | 0 | 0 | 0 | 28.2201 | 52.5 | 1158.4244 | 3000 | 50.4256 | 3050.4256 | 3050.4256 | 0 | 163.8384
0 | 26.1027 | 0 | 0 | 0 | 0 | 26.3973 | 52.5 | 1184.8216 | 3000 | 47.1684 | 3047.1684 | 3047.1684 | 0 | 158.4528
0 | 35.8309 | 0 | 0 | 0 | 0 | 16.6691 | 52.5 | 1201.4907 | 3000 | 29.7855 | 3029.7855 | 3029.7855 | 0 | 148.4898
0 | 25.6945 | 0 | 0 | 0 | 0 | 26.8055 | 52.5 | 1228.2962 | 3000 | 47.8979 | 3047.8979 | 3047.8979 | 0 | 152.273
0 | 35.7209 | 0 | 0 | 0 | 0 | 16.7791 | 52.5 | 1245.0754 | 3000 | 29.9821 | 3029.9821 | 3029.9821 | 0 | 142.4092
0 | 24.6707 | 0 | 0 | 0 | 0 | 27.8293 | 52.5 | 1272.9046 | 3000 | 49.7272 | 3049.7272 | 3049.7272 | 0 | 136.9328
0 | 35.8777 | 0 | 0 | 0 | 0 | 16.6223 | 52.5 | 1289.5269 | 3000 | 29.7018 | 3029.7018 | 3029.7018 | 0 | 128.4594
0 | 22.2563 | 0 | 0 | 0 | 0 | 30.2437 | 52.5 | 1319.7706 | 3000 | 54.0414 | 3054.0414 | 3054.0414 | 0 | 129.7968
0 | 23.4637 | 0 | 0 | 0 | 0 | 29.0363 | 52.5 | 1348.8069 | 3000 | 51.8839 | 3051.8839 | 3051.8839 | 0 | 76.2971
0 | 30.9654 | 0 | 0 | 0 | 0 | 21.5346 | 52.5 | 1370.3415 | 3000 | 38.4795 | 3038.4795 | 3038.4795 | 0 | 139.2535
0 | 29.2584 | 0 | 0 | 0 | 0 | 23.2416 | 52.5 | 1393.5831 | 3000 | 41.5297 | 3041.5297 | 3041.5297 | 0 | 141.9482
0 | 30.9499 | 0 | 0 | 0 | 0 | 21.5501 | 52.5 | 1415.1332 | 3000 | 38.5072 | 3038.5072 | 3038.5072 | 0 | 138.5559
0 | 31.3643 | 0 | 0 | 0 | 0 | 21.1357 | 52.5 | 1436.2689 | 3000 | 37.7666 | 3037.7666 | 3037.7666 | 0 | 136.3957
0 | 47.931 | 0 | 0 | 0 | 0 | 4.569 | 52.5 | 1440.8379 | 3000 | 8.1642 | 3008.1642 | 3002.7568 | 0 | 147.6756
0 | 38.9205 | 0 | 0 | 0 | 0 | 13.5795 | 52.5 | 1454.4174 | 3000 | 24.2648 | 3024.2648 | 2943.1534 | 0 | 135.3262
0 | 51.9111 | 0 | 0 | 0 | 0 | 0.58892 | 52.5 | 1455.0063 | 3000 | 1.0523 | 3001.0523 | 2730.6811 | 0 | 135.8787
0 | 41.3684 | 0 | 0 | 0 | 0 | 11.1316 | 52.5 | 1466.1379 | 3000 | 19.8907 | 3019.8907 | 2846.8531 | 0 | 145.1895
0 | 45.0167 | 0 | 0 | 0 | 0 | 7.4833 | 52.5 | 1473.6212 | 3000 | 13.3717 | 3013.3717 | 2818.7044 | 0 | 144.6559
0 | 38.3206 | 0 | 0 | 0 | 0 | 14.1794 | 52.5 | 1487.8006 | 3000 | 25.3367 | 3025.3367 | 2944.2253 | 0 | 150.8327
0 | 42.7647 | 0 | 0 | 0 | 0 | 9.7353 | 52.5 | 1497.536 | 3000 | 17.3958 | 3017.3958 | 2784.8765 | 0 | 139.2438
0 | 42.2361 | 0 | 0 | 0 | 0 | 2.464 | 44.7001 | 1500 | 2554.2929 | 4.4029 | 2558.6958 | 2493.8067 | 0 | 126.1866
0 | 34.5109 | 0 | 0 | 0 | 0 | 9.2371e-14 | 34.5109 | 1500 | 1972.0495 | 1.6505e-13 | 1972.0495 | 1966.642 | 0 | 102.2457
0 | 48.5598 | 0 | 0 | 0 | 0 | 0 | 48.5598 | 1500 | 2774.8431 | 1.2696e-14 | 2774.8431 | 2774.8431 | 0 | 144.1531
0 | 42.5681 | 0 | 0 | 0 | 0 | 0 | 42.5681 | 1500 | 2432.461 | 5.0786e-14 | 2432.461 | 2432.461 | 0 | 133.6151
0 | 53.7892 | 0 | 0 | 0 | 0 | -1.2892 | 52.5 | 1498.7108 | 3000 | 0 | 3000 | 3000 | 0 | 158.28
0 | 227.2957 | 0 | 0 | 0 | 0 | -174.7957 | 52.5 | 1323.9151 | 3000 | 0 | 3000 | 3000 | 0 | 155.76
0 | 23.9718 | 0 | 0 | 0 | 0 | 28.5282 | 52.5 | 1352.4433 | 3000 | 50.9761 | 3050.9761 | 3050.9761 | 0 | 140.3449
0 | 31.336 | 0 | 0 | 0 | 0 | 21.164 | 52.5 | 1373.6074 | 3000 | 37.8173 | 3037.8173 | 3037.8173 | 0 | 137.3093
0 | 33.1202 | 0 | 0 | 0 | 0 | 19.3798 | 52.5 | 1392.9872 | 3000 | 34.6292 | 3034.6292 | 3034.6292 | 0 | 133.5237
0 | 22.7966 | 0 | 0 | 0 | 0 | 29.7034 | 52.5 | 1422.6906 | 3000 | 53.076 | 3053.076 | 3053.076 | 0 | 134.3353
0 | 32.804 | 0 | 0 | 0 | 0 | 19.696 | 52.5 | 1442.3865 | 3000 | 35.194 | 3035.194 | 3035.194 | 0 | 101.4665
0 | 34.0441 | 0 | 0 | 0 | 0 | 18.4559 | 52.5 | 1460.8424 | 3000 | 32.9782 | 3032.9782 | 3032.9782 | 0 | 118.2861
0 | 25.5485 | 0 | 0 | 0 | 0 | 26.9515 | 52.5 | 1487.7939 | 3000 | 48.1587 | 3048.1587 | 3048.1587 | 0 | 100.8941
0 | 34.7565 | 0 | 0 | 0 | 0 | 12.2061 | 46.9626 | 1500 | 2683.575 | 21.8107 | 2705.3857 | 2705.3857 | 0 | 117.6843
0 | 32.7634 | 0 | 0 | 0 | 0 | 0 | 32.7634 | 1500 | 1872.1924 | 3.8089e-14 | 1872.1924 | 1872.1924 | 0 | 79.5682
0 | 31.8909 | 0 | 0 | 0 | 0 | 0 | 31.8909 | 1500 | 1822.34 | 3.8089e-14 | 1822.34 | 1822.34 | 0 | 69.2489
0 | 35.1234 | 0 | 0 | 0 | 0 | 9.2371e-14 | 35.1234 | 1500 | 2007.0488 | 1.6505e-13 | 2007.0488 | 2007.0488 | 0 | 88.3101
0 | 42.681 | 0 | 0 | 0 | 0 | 1.0658e-13 | 42.681 | 1500 | 2438.9131 | 1.9045e-13 | 2438.9131 | 2438.9131 | 0 | 101.2149
0 | 54.7089 | 0 | 0 | 0 | 0 | -2.2089 | 52.5 | 1497.7911 | 3000 | 0 | 3000 | 2962.148 | 0 | 136.2588
0 | 46.1754 | 0 | 0 | 0 | 0 | 2.2089 | 48.3843 | 1500 | 2764.8158 | 3.947 | 2768.7628 | 2633.5772 | 0 | 131.6789
0 | 42.0573 | 0 | 0 | 0 | 0 | -1.0658e-13 | 42.0573 | 1500 | 2403.2721 | 0 | 2403.2721 | 2300.531 | 0 | 123.5615
0 | 41.8355 | 0 | 0 | 0 | 0 | -9.9476e-14 | 41.8355 | 1500 | 2390.602 | 0 | 2390.602 | 2277.0461 | 0 | 125.5563
0 | 37.9495 | 0 | 0 | 0 | 0 | 0 | 37.9495 | 1500 | 2168.5402 | 8.8875e-14 | 2168.5402 | 1984.6878 | 0 | 99.2344
0 | 37.6448 | 0 | 0 | 0 | 0 | -9.9476e-14 | 37.6448 | 1500 | 2151.1311 | 0 | 2151.1311 | 2107.8717 | 0 | 107.2696
0 | 37.3127 | 0 | 0 | 0 | 0 | 9.9476e-14 | 37.3127 | 1500 | 2132.1521 | 1.7775e-13 | 2132.1521 | 2110.5224 | 0 | 107.9321
0 | 44.4715 | 0 | 0 | 0 | 0 | 0 | 44.4715 | 1500 | 2541.2275 | 0 | 2541.2275 | 2535.8201 | 0 | 135.1085
0 | 50.7947 | 0 | 0 | 0 | 0 | 0 | 50.7947 | 1500 | 2902.5561 | 0 | 2902.5561 | 2902.5561 | 0 | 152.4422
0 | 37.594 | 0 | 0 | 0 | 0 | -7.1054e-14 | 37.594 | 1500 | 2148.2306 | 0 | 2148.2306 | 2148.2306 | 0 | 121.3535
0 | 38.9118 | 0 | 0 | 0 | 0 | 0 | 38.9118 | 1500 | 2223.5307 | 7.6179e-14 | 2223.5307 | 2223.5307 | 0 | 119.3591
0 | 24.9614 | 0 | 0 | 0 | 0 | -7.4607e-14 | 24.9614 | 1500 | 1426.3663 | 0 | 1426.3663 | 1426.3663 | 0 | 74.171
0 | 29.2321 | 0 | 0 | 0 | 0 | 5.6843e-14 | 29.2321 | 1500 | 1670.408 | 1.0157e-13 | 1670.408 | 1670.408 | 0 | 83.1362
0 | 28.2424 | 0 | 0 | 0 | 0 | -9.2371e-14 | 28.2424 | 1500 | 1613.8514 | 0 | 1613.8514 | 1613.8514 | 0 | 75.851
0 | 23.2191 | 0 | 0 | 0 | 0 | 4.6185e-14 | 23.2191 | 1500 | 1326.8077 | 8.2527e-14 | 1326.8077 | 1326.8077 | 0 | 63.1826
0 | 39.1023 | 0 | 0 | 0 | 0 | 0 | 39.1023 | 1500 | 2234.4192 | 0 | 2234.4192 | 2234.4192 | 0 | 75.2329
0 | 41.3942 | 0 | 0 | 0 | 0 | 5.6843e-14 | 41.3942 | 1500 | 2365.384 | 1.0157e-13 | 2365.384 | 2365.384 | 0 | 92.25
0 | 29.3625 | 0 | 0 | 0 | 0 | -9.9476e-14 | 29.3625 | 1500 | 1677.8543 | 0 | 1677.8543 | 1677.8543 | 0 | 76.8625
0 | 32.2566 | 0 | 0 | 0 | 0 | 0 | 32.2566 | 1500 | 1843.2323 | 0 | 1843.2323 | 1843.2323 | 0 | 82.9455
0 | 35.0146 | 0 | 0 | 0 | 0 | 0 | 35.0146 | 1500 | 2000.8318 | 7.6179e-14 | 2000.8318 | 2000.8318 | 0 | 90.3576
0 | 28.9906 | 0 | 0 | 0 | 0 | -6.7502e-14 | 28.9906 | 1500 | 1656.605 | 0 | 1656.605 | 1656.605 | 0 | 66.2642
0 | 31.9485 | 0 | 0 | 0 | 0 | 6.7502e-14 | 31.9485 | 1500 | 1825.6268 | 1.2062e-13 | 1825.6268 | 1825.6268 | 0 | 32.1128
0 | 25.4984 | 0 | 0 | 0 | 0 | 0 | 25.4984 | 1500 | 1457.0509 | 1.2696e-14 | 1457.0509 | 1457.0509 | 0 | 57.5535
0 | 48.2724 | 0 | 0 | 0 | 0 | -9.9476e-14 | 48.2724 | 1500 | 2758.4232 | 0 | 2758.4232 | 2758.4232 | 0 | 125.7841
0 | 241.7839 | 0 | 0 | 0 | 0 | -189.2839 | 52.5 | 1310.7161 | 3000 | 0 | 3000 | 2962.148 | 0 | 155.7497
0 | 49.8417 | 0 | 0 | 0 | 0 | 2.6583 | 52.5 | 1313.3744 | 3000 | 4.75 | 3004.75 | 2880.3792 | 0 | 151.3927
0 | 42.173 | 0 | 0 | 0 | 0 | 10.327 | 52.5 | 1323.7014 | 3000 | 18.4529 | 3018.4529 | 2861.6376 | 0 | 149.9498
0 | 34.1835 | 0 | 0 | 0 | 0 | 18.3165 | 52.5 | 1342.0179 | 3000 | 32.7292 | 3032.7292 | 2713.6911 | 0 | 141.926
0 | 50.3572 | 0 | 0 | 0 | 0 | 2.1428 | 52.5 | 1344.1607 | 3000 | 3.8289 | 3003.8289 | 2744.2725 | 0 | 139.7932
0 | 29.2151 | 0 | 0 | 0 | 0 | 23.2849 | 52.5 | 1367.4456 | 3000 | 41.607 | 3041.607 | 2971.3105 | 0 | 148.2684
0 | 44.9509 | 0 | 0 | 0 | 0 | 7.5491 | 52.5 | 1374.9947 | 3000 | 13.4892 | 3013.4892 | 2954.0075 | 0 | 150.359
0 | 36.2958 | 0 | 0 | 0 | 0 | 16.2042 | 52.5 | 1391.1989 | 3000 | 28.9547 | 3028.9547 | 3018.1399 | 0 | 158.2109
0 | 52.6594 | 0 | 0 | 0 | 0 | -0.15941 | 52.5 | 1391.0395 | 3000 | 0 | 3000 | 3000 | 0 | 156.54
0 | 29.0572 | 0 | 0 | 0 | 0 | 23.4428 | 52.5 | 1414.4823 | 3000 | 41.8892 | 3041.8892 | 3041.8892 | 0 | 167.3039
0 | 38.6096 | 0 | 0 | 0 | 0 | 13.8904 | 52.5 | 1428.3727 | 3000 | 24.8204 | 3024.8204 | 3024.8204 | 0 | 169.1782
0 | 25.8059 | 0 | 0 | 0 | 0 | 26.6941 | 52.5 | 1455.0669 | 3000 | 47.6989 | 3047.6989 | 3047.6989 | 0 | 165.2462
0 | 32.2146 | 0 | 0 | 0 | 0 | 20.2854 | 52.5 | 1475.3523 | 3000 | 36.2473 | 3036.2473 | 3036.2473 | 0 | 154.7879
0 | 26.827 | 0 | 0 | 0 | 0 | 24.6477 | 51.4747 | 1500 | 2941.4124 | 44.0422 | 2985.4546 | 2985.4546 | 0 | 148.1681
0 | 28.7483 | 0 | 0 | 0 | 0 | -6.7502e-14 | 28.7483 | 1500 | 1642.7605 | 0 | 1642.7605 | 1642.7605 | 0 | 79.0825
0 | 32.1541 | 0 | 0 | 0 | 0 | -9.2371e-14 | 32.1541 | 1500 | 1837.3755 | 0 | 1837.3755 | 1837.3755 | 0 | 87.0916
0 | 225.5404 | 0 | 0 | 0 | 0 | -173.0404 | 52.5 | 1326.9596 | 3000 | 0 | 3000 | 3000 | 0 | 150.54
0 | 27.5207 | 0 | 0 | 0 | 0 | 24.9793 | 52.5 | 1351.939 | 3000 | 44.6347 | 3044.6347 | 3044.6347 | 0 | 152.384
0 | 22.594 | 0 | 0 | 0 | 0 | 29.906 | 52.5 | 1381.845 | 3000 | 53.4381 | 3053.4381 | 3053.4381 | 0 | 144.4887
0 | 30.6044 | 0 | 0 | 0 | 0 | 21.8956 | 52.5 | 1403.7406 | 3000 | 39.1245 | 3039.1245 | 3039.1245 | 0 | 127.9168
0 | 23.3474 | 0 | 0 | 0 | 0 | 29.1526 | 52.5 | 1432.8932 | 3000 | 52.0918 | 3052.0918 | 3052.0918 | 0 | 78.9576
0 | 25.9066 | 0 | 0 | 0 | 0 | 26.5934 | 52.5 | 1459.4866 | 3000 | 47.5189 | 3047.5189 | 3047.5189 | 0 | 83.8677
0 | 23.1477 | 0 | 0 | 0 | 0 | 29.3523 | 52.5 | 1488.8389 | 3000 | 52.4487 | 3052.4487 | 3052.4487 | 0 | 137.3907
0 | 39.4357 | 0 | 0 | 0 | 0 | 11.1611 | 50.5968 | 1500 | 2891.2469 | 19.9434 | 2911.1902 | 2911.1902 | 0 | 146.2582
0 | 51.011 | 0 | 0 | 0 | 0 | 0 | 51.011 | 1500 | 2914.9117 | 0 | 2914.9117 | 2904.0969 | 0 | 145.8437
0 | 39.8325 | 0 | 0 | 0 | 0 | 1.0658e-13 | 39.8325 | 1500 | 2276.1408 | 1.9045e-13 | 2276.1408 | 2254.5111 | 0 | 117.2346
0 | 46.9201 | 0 | 0 | 0 | 0 | 0 | 46.9201 | 1500 | 2681.1474 | 0 | 2681.1474 | 2627.0731 | 0 | 127.5444
0 | 36.4446 | 0 | 0 | 0 | 0 | 9.2371e-14 | 36.4446 | 1500 | 2082.5489 | 1.6505e-13 | 2082.5489 | 2033.8821 | 0 | 105.7619
0 | 49.6177 | 0 | 0 | 0 | 0 | 8.5265e-14 | 49.6177 | 1500 | 2835.2943 | 1.5236e-13 | 2835.2943 | 2754.1829 | 0 | 140.2705
0 | 40.9403 | 0 | 0 | 0 | 0 | 6.3949e-14 | 40.9403 | 1500 | 2339.4438 | 1.1427e-13 | 2339.4438 | 2236.7027 | 0 | 115.8612
0 | 53.2815 | 0 | 0 | 0 | 0 | -0.78148 | 52.5 | 1499.2185 | 3000 | 0 | 3000 | 2962.148 | 0 | 153.5874
0 | 37.2602 | 0 | 0 | 0 | 0 | 0.78148 | 38.0417 | 1500 | 2173.8112 | 1.3964 | 2175.2076 | 2169.8002 | 0 | 111.3324
0 | 37.1557 | 0 | 0 | 0 | 0 | 8.5265e-14 | 37.1557 | 1500 | 2123.182 | 1.5236e-13 | 2123.182 | 2123.182 | 0 | 115.7771
0 | 53.7084 | 0 | 0 | 0 | 0 | -1.2084 | 52.5 | 1498.7916 | 3000 | 0 | 3000 | 3000 | 0 | 169.89
0 | 30.7933 | 0 | 0 | 0 | 0 | 1.2084 | 32.0017 | 1500 | 1828.6687 | 2.1592 | 1830.8279 | 1830.8279 | 0 | 94.3059
0 | 33.0721 | 0 | 0 | 0 | 0 | 0 | 33.0721 | 1500 | 1889.8329 | 2.5393e-14 | 1889.8329 | 1889.8329 | 0 | 92.6585
0 | 18.7849 | 0 | 0 | 0 | 0 | 1.1013e-13 | 18.7849 | 1500 | 1073.4218 | 1.968e-13 | 1073.4218 | 1073.4218 | 0 | 54.1112
0 | 27.6093 | 0 | 0 | 0 | 0 | -3.1974e-14 | 27.6093 | 1500 | 1577.6722 | 0 | 1577.6722 | 1577.6722 | 0 | 73.3618
0 | 25.6449 | 0 | 0 | 0 | 0 | -4.6185e-14 | 25.6449 | 1500 | 1465.4228 | 0 | 1465.4228 | 1465.4228 | 0 | 73.1246
0 | 27.8111 | 0 | 0 | 0 | 0 | -7.1054e-14 | 27.8111 | 1500 | 1589.2064 | 0 | 1589.2064 | 1589.2064 | 0 | 72.3089
0 | 20.5884 | 0 | 0 | 0 | 0 | 0 | 20.5884 | 1500 | 1176.4779 | 0 | 1176.4779 | 1176.4779 | 0 | 48.2356
0 | 25.4483 | 0 | 0 | 0 | 0 | 7.816e-14 | 25.4483 | 1500 | 1454.189 | 1.3966e-13 | 1454.189 | 1454.189 | 0 | 59.6218
0 | 26.1744 | 0 | 0 | 0 | 0 | -2.8422e-14 | 26.1744 | 1500 | 1495.6816 | 0 | 1495.6816 | 1495.6816 | 0 | 45.379
0 | 24.7669 | 0 | 0 | 0 | 0 | 3.5527e-14 | 24.7669 | 1500 | 1415.2522 | 6.3482e-14 | 1415.2522 | 1415.2522 | 0 | 37.4476
0 | 31.3287 | 0 | 0 | 0 | 0 | 7.4607e-14 | 31.3287 | 1500 | 1790.2133 | 1.3331e-13 | 1790.2133 | 1790.2133 | 0 | 44.0751
0 | 30.7598 | 0 | 0 | 0 | 0 | 1.0303e-13 | 30.7598 | 1500 | 1757.7055 | 1.841e-13 | 1757.7055 | 1757.7055 | 0 | 53.9791
0 | 32.7575 | 0 | 0 | 0 | 0 | 1.1369e-13 | 32.7575 | 1500 | 1871.8597 | 2.0314e-13 | 1871.8597 | 1871.8597 | 0 | 45.9729
0 | 49.9593 | 0 | 0 | 0 | 0 | 0 | 49.9593 | 1500 | 2854.8152 | 0 | 2854.8152 | 2849.4077 | 0 | 89.8988
0 | 231.5336 | 0 | 0 | 0 | 0 | -179.0336 | 52.5 | 1320.9664 | 3000 | 0 | 3000 | 2940.5183 | 0 | 126.0012
0 | 51.5644 | 0 | 0 | 0 | 0 | 0.93563 | 52.5 | 1321.902 | 3000 | 1.6719 | 3001.6719 | 2785.3748 | 0 | 133.9765
0 | 50.0929 | 0 | 0 | 0 | 0 | 2.4071 | 52.5 | 1324.3091 | 3000 | 4.3012 | 3004.3012 | 2739.3374 | 0 | 135.8711
0 | 35.1169 | 0 | 0 | 0 | 0 | 17.3831 | 52.5 | 1341.6922 | 3000 | 31.0613 | 3031.0613 | 2847.2088 | 0 | 141.8195
0 | 52.7803 | 0 | 0 | 0 | 0 | -0.2803 | 52.5 | 1341.4119 | 3000 | 0 | 3000 | 2848.5921 | 0 | 135.3081
0 | 30.0918 | 0 | 0 | 0 | 0 | 22.4082 | 52.5 | 1363.8201 | 3000 | 40.0404 | 3040.0404 | 2894.04 | 0 | 142.9656
0 | 53.5516 | 0 | 0 | 0 | 0 | -1.0516 | 52.5 | 1362.7685 | 3000 | 0 | 3000 | 2945.9257 | 0 | 147.1785
0 | 32.5194 | 0 | 0 | 0 | 0 | 19.9806 | 52.5 | 1382.7492 | 3000 | 35.7028 | 3035.7028 | 3024.8879 | 0 | 152.0914
0 | 48.276 | 0 | 0 | 0 | 0 | 4.224 | 52.5 | 1386.9732 | 3000 | 7.5477 | 3007.5477 | 3007.5477 | 0 | 160.6632
0 | 42.812 | 0 | 0 | 0 | 0 | 9.688 | 52.5 | 1396.6612 | 3000 | 17.3112 | 3017.3112 | 3017.3112 | 0 | 187.9785
0 | 44.5571 | 0 | 0 | 0 | 0 | 7.9429 | 52.5 | 1404.6041 | 3000 | 14.1929 | 3014.1929 | 3014.1929 | 0 | 173.1955
0 | 31.7671 | 0 | 0 | 0 | 0 | 20.7329 | 52.5 | 1425.337 | 3000 | 37.0469 | 3037.0469 | 3037.0469 | 0 | 162.5731
0 | 31.0298 | 0 | 0 | 0 | 0 | 21.4702 | 52.5 | 1446.8072 | 3000 | 38.3644 | 3038.3644 | 3038.3644 | 0 | 151.4625
0 | 30.604 | 0 | 0 | 0 | 0 | 21.896 | 52.5 | 1468.7031 | 3000 | 39.1252 | 3039.1252 | 3039.1252 | 0 | 150.8318
0 | 24.9789 | 0 | 0 | 0 | 0 | 27.5211 | 52.5 | 1496.2242 | 3000 | 49.1765 | 3049.1765 | 3049.1765 | 0 | 152.2759
0 | 28.7148 | 0 | 0 | 0 | 0 | 3.7758 | 32.4906 | 1500 | 1856.6029 | 6.7468 | 1863.3498 | 1863.3498 | 0 | 87.7451
0 | 28.4794 | 0 | 0 | 0 | 0 | -1.1013e-13 | 28.4794 | 1500 | 1627.3965 | 0 | 1627.3965 | 1627.3965 | 0 | 80.4259
0 | 25.4953 | 0 | 0 | 0 | 0 | 8.5265e-14 | 25.4953 | 1500 | 1456.877 | 1.5236e-13 | 1456.877 | 1456.877 | 0 | 71.4015
0 | 30.4608 | 0 | 0 | 0 | 0 | -9.9476e-14 | 30.4608 | 1500 | 1740.6176 | 0 | 1740.6176 | 1740.6176 | 0 | 81.5827
0 | 22.3577 | 0 | 0 | 0 | 0 | -1.0658e-13 | 22.3577 | 1500 | 1277.582 | 0 | 1277.582 | 1277.582 | 0 | 59.4842
0 | 30.5587 | 0 | 0 | 0 | 0 | 6.0396e-14 | 30.5587 | 1500 | 1746.2104 | 1.0792e-13 | 1746.2104 | 1746.2104 | 0 | 82.0893
0 | 33.2031 | 0 | 0 | 0 | 0 | -9.9476e-14 | 33.2031 | 1500 | 1897.3202 | 0 | 1897.3202 | 1897.3202 | 0 | 78.0937
0 | 26.4644 | 0 | 0 | 0 | 0 | 3.5527e-14 | 26.4644 | 1500 | 1512.2519 | 6.3482e-14 | 1512.2519 | 1512.2519 | 0 | 62.1687
0 | 29.0861 | 0 | 0 | 0 | 0 | 0 | 29.0861 | 1500 | 1662.0605 | 1.9045e-14 | 1662.0605 | 1656.6531 | 0 | 68.4198
0 | 40.4249 | 0 | 0 | 0 | 0 | 0 | 40.4249 | 1500 | 2309.9941 | 0 | 2309.9941 | 2282.957 | 0 | 102.1623
0 | 50.6101 | 0 | 0 | 0 | 0 | -5.6843e-14 | 50.6101 | 1500 | 2892.0055 | 0 | 2892.0055 | 2778.4496 | 0 | 137.0053
0 | 46.0935 | 0 | 0 | 0 | 0 | 7.1054e-14 | 46.0935 | 1500 | 2633.9133 | 1.2696e-13 | 2633.9133 | 2460.8757 | 0 | 122.9207
0 | 46.6295 | 0 | 0 | 0 | 0 | -7.1054e-14 | 46.6295 | 1500 | 2664.5449 | 0 | 2664.5449 | 2475.2851 | 0 | 125.5217
0 | 38.7559 | 0 | 0 | 0 | 0 | 0 | 38.7559 | 1500 | 2214.6254 | 8.8875e-14 | 2214.6254 | 2046.9952 | 0 | 103.3733
0 | 37.3425 | 0 | 0 | 0 | 0 | 9.9476e-14 | 37.3425 | 1500 | 2133.8583 | 1.7775e-13 | 2133.8583 | 2025.7098 | 0 | 101.2045
0 | 46.0966 | 0 | 0 | 0 | 0 | 0 | 46.0966 | 1500 | 2634.0931 | 1.2696e-14 | 2634.0931 | 2585.4262 | 0 | 132.1411
0 | 230.5542 | 0 | 0 | 0 | 0 | -178.0542 | 52.5 | 1321.9458 | 3000 | 0 | 3000 | 2994.5926 | 0 | 157.1862
0 | 33.5357 | 0 | 0 | 0 | 0 | 18.9643 | 52.5 | 1340.9101 | 3000 | 33.8866 | 3033.8866 | 3033.8866 | 0 | 164.0119
0 | 248.1083 | 0 | 0 | 0 | 0 | -195.6083 | 52.5 | 1145.3018 | 3000 | 0 | 3000 | 3000 | 0 | 172.65
0 | 39.267 | 0 | 0 | 0 | 0 | 13.233 | 52.5 | 1158.5348 | 3000 | 23.6457 | 3023.6457 | 3023.6457 | 0 | 174.2829
0 | 30.535 | 0 | 0 | 0 | 0 | 21.965 | 52.5 | 1180.4998 | 3000 | 39.2485 | 3039.2485 | 3039.2485 | 0 | 169.9548
0 | 20.609 | 0 | 0 | 0 | 0 | 31.891 | 52.5 | 1212.3908 | 3000 | 56.9849 | 3056.9849 | 3056.9849 | 0 | 159.6969
0 | 29.7363 | 0 | 0 | 0 | 0 | 22.7637 | 52.5 | 1235.1545 | 3000 | 40.6758 | 3040.6758 | 3040.6758 | 0 | 156.3515
0 | 27.6914 | 0 | 0 | 0 | 0 | 24.8086 | 52.5 | 1259.9631 | 3000 | 44.3297 | 3044.3297 | 3044.3297 | 0 | 155.139
0 | 24.8046 | 0 | 0 | 0 | 0 | 27.6954 | 52.5 | 1287.6584 | 3000 | 49.4879 | 3049.4879 | 3049.4879 | 0 | 150.1873
0 | 34.4501 | 0 | 0 | 0 | 0 | 18.0499 | 52.5 | 1305.7084 | 3000 | 32.2528 | 3032.2528 | 3032.2528 | 0 | 138.9075
0 | 32.4558 | 0 | 0 | 0 | 0 | 20.0442 | 52.5 | 1325.7525 | 3000 | 35.8163 | 3035.8163 | 3035.8163 | 0 | 135.1242
0 | 31.4839 | 0 | 0 | 0 | 0 | 21.0161 | 52.5 | 1346.7686 | 3000 | 37.553 | 3037.553 | 3037.553 | 0 | 130.0073
0 | 32.5246 | 0 | 0 | 0 | 0 | 19.9754 | 52.5 | 1366.744 | 3000 | 35.6933 | 3035.6933 | 3035.6933 | 0 | 129.9277
0 | 23.0222 | 0 | 0 | 0 | 0 | 29.4778 | 52.5 | 1396.2218 | 3000 | 52.6729 | 3052.6729 | 3052.6729 | 0 | 131.0207
0 | 25.2573 | 0 | 0 | 0 | 0 | 27.2427 | 52.5 | 1423.4645 | 3000 | 48.679 | 3048.679 | 3048.679 | 0 | 136.4589
0 | 37.344 | 0 | 0 | 0 | 0 | 15.156 | 52.5 | 1438.6204 | 3000 | 27.0817 | 3027.0817 | 3027.0817 | 0 | 142.2123
0 | 45.6916 | 0 | 0 | 0 | 0 | 6.8084 | 52.5 | 1445.4289 | 3000 | 12.1658 | 3012.1658 | 3006.7583 | 0 | 157.7947
0 | 47.6431 | 0 | 0 | 0 | 0 | 4.8569 | 52.5 | 1450.2858 | 3000 | 8.6786 | 3008.6786 | 2927.5672 | 0 | 155.1611
0 | 41.3124 | 0 | 0 | 0 | 0 | 11.1876 | 52.5 | 1461.4734 | 3000 | 19.9908 | 3019.9908 | 2738.8047 | 0 | 150.0043
0 | 37.6975 | 0 | 0 | 0 | 0 | 14.8025 | 52.5 | 1476.2759 | 3000 | 26.4501 | 3026.4501 | 2599.2635 | 0 | 142.5176
0 | 37.8299 | 0 | 0 | 0 | 0 | 14.6701 | 52.5 | 1490.946 | 3000 | 26.2136 | 3026.2136 | 2555.7676 | 0 | 141.0017
0 | 32.1998 | 0 | 0 | 0 | 0 | 9.054 | 41.2538 | 1500 | 2357.3596 | 16.1783 | 2373.5379 | 1935.5364 | 0 | 106.4545
0 | 45.6294 | 0 | 0 | 0 | 0 | 0 | 45.6294 | 1500 | 2607.3941 | 1.2696e-14 | 2607.3941 | 2288.356 | 0 | 125.9511
0 | 49.3057 | 0 | 0 | 0 | 0 | -1.0658e-13 | 49.3057 | 1500 | 2817.47 | 0 | 2817.47 | 2720.1364 | 0 | 153.0621
0 | 40.1594 | 0 | 0 | 0 | 0 | -7.1054e-14 | 40.1594 | 1500 | 2294.8252 | 0 | 2294.8252 | 2289.4178 | 0 | 133.9767
0 | 242.956 | 0 | 0 | 0 | 0 | -190.456 | 52.5 | 1309.544 | 3000 | 0 | 3000 | 3000 | 0 | 180.18
0 | 39.2208 | 0 | 0 | 0 | 0 | 13.2792 | 52.5 | 1322.8232 | 3000 | 23.7281 | 3023.7281 | 3023.7281 | 0 | 191.0694
0 | 47.6326 | 0 | 0 | 0 | 0 | 4.8674 | 52.5 | 1327.6906 | 3000 | 8.6974 | 3008.6974 | 3008.6974 | 0 | 180.1608
0 | 25.6242 | 0 | 0 | 0 | 0 | 26.8758 | 52.5 | 1354.5663 | 3000 | 48.0234 | 3048.0234 | 3048.0234 | 0 | 179.8029
0 | 24.2632 | 0 | 0 | 0 | 0 | 28.2368 | 52.5 | 1382.8031 | 3000 | 50.4554 | 3050.4554 | 3050.4554 | 0 | 166.3108
0 | 31.9416 | 0 | 0 | 0 | 0 | 20.5584 | 52.5 | 1403.3615 | 3000 | 36.7352 | 3036.7352 | 3036.7352 | 0 | 156.9081
0 | 27.5865 | 0 | 0 | 0 | 0 | 24.9135 | 52.5 | 1428.2751 | 3000 | 44.5172 | 3044.5172 | 3044.5172 | 0 | 153.3828
0 | 33.0859 | 0 | 0 | 0 | 0 | 19.4141 | 52.5 | 1447.6892 | 3000 | 34.6905 | 3034.6905 | 3034.6905 | 0 | 147.3949
0 | 29.74 | 0 | 0 | 0 | 0 | 22.76 | 52.5 | 1470.4492 | 3000 | 40.6691 | 3040.6691 | 3040.6691 | 0 | 137.347
0 | 23.0083 | 0 | 0 | 0 | 0 | 29.4917 | 52.5 | 1499.9409 | 3000 | 52.6977 | 3052.6977 | 3052.6977 | 0 | 135.845
0 | 33.7736 | 0 | 0 | 0 | 0 | 0.059088 | 33.8326 | 1500 | 1933.2939 | 0.10558 | 1933.3995 | 1933.3995 | 0 | 85.3209
0 | 34.8254 | 0 | 0 | 0 | 0 | 1.1369e-13 | 34.8254 | 1500 | 1990.0239 | 2.0314e-13 | 1990.0239 | 1990.0239 | 0 | 85.4118
0 | 32.4075 | 0 | 0 | 0 | 0 | 7.816e-14 | 32.4075 | 1500 | 1851.8546 | 1.3966e-13 | 1851.8546 | 1851.8546 | 0 | 79.4446
0 | 22.4871 | 0 | 0 | 0 | 0 | 8.5265e-14 | 22.4871 | 1500 | 1284.9775 | 1.5236e-13 | 1284.9775 | 1284.9775 | 0 | 54.0333
0 | 31.6149 | 0 | 0 | 0 | 0 | 5.6843e-14 | 31.6149 | 1500 | 1806.5673 | 1.0157e-13 | 1806.5673 | 1806.5673 | 0 | 78.7121
0 | 48.8657 | 0 | 0 | 0 | 0 | 5.6843e-14 | 48.8657 | 1500 | 2792.3274 | 1.0157e-13 | 2792.3274 | 2786.92 | 0 | 127.8081
0 | 45.7068 | 0 | 0 | 0 | 0 | 0 | 45.7068 | 1500 | 2611.8151 | 0 | 2611.8151 | 2568.5557 | 0 | 125.6794
0 | 47.0028 | 0 | 0 | 0 | 0 | 0 | 47.0028 | 1500 | 2685.8718 | 0 | 2685.8718 | 2534.4639 | 0 | 130.7783
0 | 60.5665 | 0 | 0 | 0 | 0 | -8.0665 | 52.5 | 1491.9335 | 3000 | 0 | 3000 | 2648.5174 | 0 | 134.0415
0 | 38.982 | 0 | 0 | 0 | 0 | 8.0665 | 47.0484 | 1500 | 2688.4823 | 14.4137 | 2702.8959 | 2410.895 | 0 | 120.6653
0 | 45.0252 | 0 | 0 | 0 | 0 | 0 | 45.0252 | 1500 | 2572.8672 | 0 | 2572.8672 | 2394.4221 | 0 | 119.0028
0 | 40.8714 | 0 | 0 | 0 | 0 | 0 | 40.8714 | 1500 | 2335.5081 | 0 | 2335.5081 | 2135.4334 | 0 | 103.8888
0 | 38.5422 | 0 | 0 | 0 | 0 | -8.5265e-14 | 38.5422 | 1500 | 2202.4091 | 0 | 2202.4091 | 2132.1126 | 0 | 107.0321
0 | 43.5233 | 0 | 0 | 0 | 0 | -9.2371e-14 | 43.5233 | 1500 | 2487.0485 | 0 | 2487.0485 | 2481.6411 | 0 | 127.7549
0 | 34.7729 | 0 | 0 | 0 | 0 | 0 | 34.7729 | 1500 | 1987.0251 | 5.0786e-14 | 1987.0251 | 1987.0251 | 0 | 107.6769
0 | 41.3215 | 0 | 0 | 0 | 0 | 0 | 41.3215 | 1500 | 2361.2295 | 0 | 2361.2295 | 2361.2295 | 0 | 131.733
0 | 241.6028 | 0 | 0 | 0 | 0 | -189.1028 | 52.5 | 1310.8972 | 3000 | 0 | 3000 | 3000 | 0 | 176.25
0 | 31.5194 | 0 | 0 | 0 | 0 | 20.9806 | 52.5 | 1331.8777 | 3000 | 37.4895 | 3037.4895 | 3037.4895 | 0 | 177.0553
0 | 24.3489 | 0 | 0 | 0 | 0 | 28.1511 | 52.5 | 1360.0289 | 3000 | 50.3023 | 3050.3023 | 3050.3023 | 0 | 166.6075
0 | 25.1146 | 0 | 0 | 0 | 0 | 27.3854 | 52.5 | 1387.4142 | 3000 | 48.934 | 3048.934 | 3048.934 | 0 | 153.6358
0 | 21.4543 | 0 | 0 | 0 | 0 | 31.0457 | 52.5 | 1418.46 | 3000 | 55.4746 | 3055.4746 | 3055.4746 | 0 | 152.0099
0 | 25.3157 | 0 | 0 | 0 | 0 | 27.1843 | 52.5 | 1445.6443 | 3000 | 48.5747 | 3048.5747 | 3048.5747 | 0 | 137.7041
0 | 31.854 | 0 | 0 | 0 | 0 | 20.646 | 52.5 | 1466.2903 | 3000 | 36.8917 | 3036.8917 | 3036.8917 | 0 | 138.4823
0 | 35.0358 | 0 | 0 | 0 | 0 | 17.4642 | 52.5 | 1483.7544 | 3000 | 31.2062 | 3031.2062 | 3031.2062 | 0 | 130.645
0 | 34.1222 | 0 | 0 | 0 | 0 | 16.2456 | 50.3677 | 1500 | 2878.1553 | 29.0287 | 2907.184 | 2907.184 | 0 | 121.8692
0 | 28.3253 | 0 | 0 | 0 | 0 | 0 | 28.3253 | 1500 | 1618.5894 | 1.2696e-14 | 1618.5894 | 1618.5894 | 0 | 61.2636
0 | 37.0006 | 0 | 0 | 0 | 0 | 0 | 37.0006 | 1500 | 2114.3181 | 0 | 2114.3181 | 2114.3181 | 0 | 76.052
0 | 27.1322 | 0 | 0 | 0 | 0 | 3.1974e-14 | 27.1322 | 1500 | 1550.4128 | 5.7134e-14 | 1550.4128 | 1550.4128 | 0 | 56.2955
0 | 37.2157 | 0 | 0 | 0 | 0 | 0 | 37.2157 | 1500 | 2126.6096 | 6.3482e-14 | 2126.6096 | 2126.6096 | 0 | 80.2157
0 | 41.19 | 0 | 0 | 0 | 0 | 0 | 41.19 | 1500 | 2353.7157 | 0 | 2353.7157 | 2348.3082 | 0 | 94.1672
0 | 36.754 | 0 | 0 | 0 | 0 | -9.9476e-14 | 36.754 | 1500 | 2100.2274 | 0 | 2100.2274 | 2062.3755 | 0 | 87.6922
0 | 47.7355 | 0 | 0 | 0 | 0 | 7.1054e-14 | 47.7355 | 1500 | 2727.7431 | 1.2696e-13 | 2727.7431 | 2570.9277 | 0 | 115.7946
0 | 37.778 | 0 | 0 | 0 | 0 | 0 | 37.778 | 1500 | 2158.7405 | 0 | 2158.7405 | 1964.0732 | 0 | 100.2659
0 | 32.4288 | 0 | 0 | 0 | 0 | 0 | 32.4288 | 1500 | 1853.0741 | 1.2696e-14 | 1853.0741 | 1512.4063 | 0 | 76.3009
0 | 52.2685 | 0 | 0 | 0 | 0 | 0 | 52.2685 | 1500 | 2986.7739 | 0 | 2986.7739 | 2813.7363 | 0 | 132.33
0 | 33.0305 | 0 | 0 | 0 | 0 | 0 | 33.0305 | 1500 | 1887.4599 | 0 | 1887.4599 | 1719.8297 | 0 | 78.4414
0 | 42.3914 | 0 | 0 | 0 | 0 | 7.1054e-14 | 42.3914 | 1500 | 2422.363 | 1.2696e-13 | 2422.363 | 2362.8813 | 0 | 108.22
0 | 36.4591 | 0 | 0 | 0 | 0 | 7.816e-14 | 36.4591 | 1500 | 2083.3786 | 1.3966e-13 | 2083.3786 | 2077.9712 | 0 | 99.514
0 | 31.4629 | 0 | 0 | 0 | 0 | 0 | 31.4629 | 1500 | 1797.8788 | 0 | 1797.8788 | 1797.8788 | 0 | 88.0421
0 | 39.4057 | 0 | 0 | 0 | 0 | -5.6843e-14 | 39.4057 | 1500 | 2251.7527 | 0 | 2251.7527 | 2251.7527 | 0 | 132.6733
0 | 42.7176 | 0 | 0 | 0 | 0 | 7.1054e-14 | 42.7176 | 1500 | 2441.0044 | 1.2696e-13 | 2441.0044 | 2441.0044 | 0 | 149.121
0 | 29.5816 | 0 | 0 | 0 | 0 | -4.6185e-14 | 29.5816 | 1500 | 1690.3787 | 0 | 1690.3787 | 1690.3787 | 0 | 103.5188
0 | 24.9764 | 0 | 0 | 0 | 0 | 9.5923e-14 | 24.9764 | 1500 | 1427.2207 | 1.714e-13 | 1427.2207 | 1427.2207 | 0 | 86.1042
0 | 25.945 | 0 | 0 | 0 | 0 | 7.1054e-14 | 25.945 | 1500 | 1482.5696 | 1.2696e-13 | 1482.5696 | 1482.5696 | 0 | 82.5495
0 | 27.6922 | 0 | 0 | 0 | 0 | 0 | 27.6922 | 1500 | 1582.4094 | 4.4438e-14 | 1582.4094 | 1582.4094 | 0 | 82.0005
0 | 223.9111 | 0 | 0 | 0 | 0 | -171.4111 | 52.5 | 1328.5889 | 3000 | 0 | 3000 | 3000 | 0 | 136.2
0 | 25.2247 | 0 | 0 | 0 | 0 | 27.2753 | 52.5 | 1355.8643 | 3000 | 48.7374 | 3048.7374 | 3048.7374 | 0 | 137.559
0 | 22.5521 | 0 | 0 | 0 | 0 | 29.9479 | 52.5 | 1385.8122 | 3000 | 53.513 | 3053.513 | 3053.513 | 0 | 137.4997
0 | 29.4063 | 0 | 0 | 0 | 0 | 23.0937 | 52.5 | 1408.9059 | 3000 | 41.2653 | 3041.2653 | 3041.2653 | 0 | 129.8316
0 | 30.213 | 0 | 0 | 0 | 0 | 22.287 | 52.5 | 1431.1929 | 3000 | 39.824 | 3039.824 | 3039.824 | 0 | 118.2188
0 | 39.4439 | 0 | 0 | 0 | 0 | 13.0561 | 52.5 | 1444.249 | 3000 | 23.3295 | 3023.3295 | 3023.3295 | 0 | 114.7354
0 | 18.7759 | 0 | 0 | 0 | 0 | 33.7241 | 52.5 | 1477.9731 | 3000 | 60.2605 | 3060.2605 | 3060.2605 | 0 | 122.1044
0 | 29.6025 | 0 | 0 | 0 | 0 | 22.0269 | 51.6294 | 1500 | 2950.2523 | 39.3591 | 2989.6113 | 2989.6113 | 0 | 136.0273
0 | 36.0572 | 0 | 0 | 0 | 0 | -5.6843e-14 | 36.0572 | 1500 | 2060.4115 | 0 | 2060.4115 | 2055.0041 | 0 | 113.2307
0 | 40.5216 | 0 | 0 | 0 | 0 | 0 | 40.5216 | 1500 | 2315.5201 | 0 | 2315.5201 | 2234.4087 | 0 | 130.8023
0 | 49.9062 | 0 | 0 | 0 | 0 | 0 | 49.9062 | 1500 | 2851.7803 | 0 | 2851.7803 | 2640.8907 | 0 | 151.6399
0 | 48.6534 | 0 | 0 | 0 | 0 | 0 | 48.6534 | 1500 | 2780.1931 | 5.0786e-14 | 2780.1931 | 2401.6734 | 0 | 137.9041
0 | 40.1889 | 0 | 0 | 0 | 0 | 8.5265e-14 | 40.1889 | 1500 | 2296.5072 | 1.5236e-13 | 2296.5072 | 1853.0984 | 0 | 107.7206
0 | 51.1625 | 0 | 0 | 0 | 0 | 8.5265e-14 | 51.1625 | 1500 | 2923.5689 | 1.5236e-13 | 2923.5689 | 2480.16 | 0 | 134.0526
0 | 41.2959 | 0 | 0 | 0 | 0 | -8.5265e-14 | 41.2959 | 1500 | 2359.7678 | 0 | 2359.7678 | 2029.9149 | 0 | 111.0769
0 | 43.9809 | 0 | 0 | 0 | 0 | -8.5265e-14 | 43.9809 | 1500 | 2513.1926 | 0 | 2513.1926 | 2410.4516 | 0 | 125.223
0 | 39.7524 | 0 | 0 | 0 | 0 | 5.6843e-14 | 39.7524 | 1500 | 2271.5655 | 1.0157e-13 | 2271.5655 | 2260.7507 | 0 | 120.7241
0 | 40.9476 | 0 | 0 | 0 | 0 | -9.9476e-14 | 40.9476 | 1500 | 2339.8605 | 0 | 2339.8605 | 2339.8605 | 0 | 126.7502
0 | 36.3843 | 0 | 0 | 0 | 0 | -36.3843 | 0 | 1463.6157 | 0 | 0 | 0 | 0 | 0 | 0
0 | 52.2395 | 0 | 0 | 0 | 0 | 0.26053 | 52.5 | 1463.8762 | 3000 | 0.46553 | 3000.4655 | 3000.4655 | 0 | 191.3697
0 | 34.0235 | 0 | 0 | 0 | 0 | 18.4765 | 52.5 | 1482.3527 | 3000 | 33.0151 | 3033.0151 | 3033.0151 | 0 | 207.0639
0 | 25.2958 | 0 | 0 | 0 | 0 | 17.6473 | 42.9431 | 1500 | 2453.8909 | 31.5333 | 2485.4242 | 2485.4242 | 0 | 134.2129
0 | 29.7686 | 0 | 0 | 0 | 0 | -1.0658e-13 | 29.7686 | 1500 | 1701.0651 | 0 | 1701.0651 | 1701.0651 | 0 | 84.7301
0 | 24.3498 | 0 | 0 | 0 | 0 | -3.1974e-14 | 24.3498 | 1500 | 1391.417 | 0 | 1391.417 | 1391.417 | 0 | 66.635
0 | 30.777 | 0 | 0 | 0 | 0 | 0 | 30.777 | 1500 | 1758.6838 | 3.8089e-14 | 1758.6838 | 1758.6838 | 0 | 83.0099
0 | 30.6664 | 0 | 0 | 0 | 0 | 7.4607e-14 | 30.6664 | 1500 | 1752.3665 | 1.3331e-13 | 1752.3665 | 1752.3665 | 0 | 77.8051
0 | 35.3252 | 0 | 0 | 0 | 0 | 9.2371e-14 | 35.3252 | 1500 | 2018.5827 | 1.6505e-13 | 2018.5827 | 2018.5827 | 0 | 90.8362
0 | 35.1235 | 0 | 0 | 0 | 0 | 9.2371e-14 | 35.1235 | 1500 | 2007.0553 | 1.6505e-13 | 2007.0553 | 2007.0553 | 0 | 90.9397
0 | 29.872 | 0 | 0 | 0 | 0 | -7.816e-14 | 29.872 | 1500 | 1706.9723 | 0 | 1706.9723 | 1706.9723 | 0 | 81.7128
0 | 229.9948 | 0 | 0 | 0 | 0 | -177.4948 | 52.5 | 1322.5052 | 3000 | 0 | 3000 | 3000 | 0 | 144
0 | 25.1175 | 0 | 0 | 0 | 0 | 27.3825 | 52.5 | 1349.8878 | 3000 | 48.929 | 3048.929 | 3048.929 | 0 | 145.9522
0 | 24.5004 | 0 | 0 | 0 | 0 | 27.9996 | 52.5 | 1377.8874 | 3000 | 50.0316 | 3050.0316 | 3050.0316 | 0 | 147.286
0 | 40.9353 | 0 | 0 | 0 | 0 | 11.5647 | 52.5 | 1389.4521 | 3000 | 20.6645 | 3020.6645 | 3020.6645 | 0 | 144.8711
0 | 51.1845 | 0 | 0 | 0 | 0 | 1.3155 | 52.5 | 1390.7675 | 3000 | 2.3506 | 3002.3506 | 2932.0541 | 0 | 151.1767
0 | 27.4644 | 0 | 0 | 0 | 0 | 25.0356 | 52.5 | 1415.8031 | 3000 | 44.7353 | 3044.7353 | 2855.4754 | 0 | 162.3338
0 | 41.1982 | 0 | 0 | 0 | 0 | 11.3018 | 52.5 | 1427.1049 | 3000 | 20.1948 | 3020.1948 | 2782.2681 | 0 | 174.6151
0 | 47.442 | 0 | 0 | 0 | 0 | 5.058 | 52.5 | 1432.1629 | 3000 | 9.0379 | 3009.0379 | 2657.5553 | 0 | 143.4548
0 | 43.5471 | 0 | 0 | 0 | 0 | 8.9529 | 52.5 | 1441.1157 | 3000 | 15.9976 | 3015.9976 | 2626.663 | 0 | 140.7891
0 | 53.3145 | 0 | 0 | 0 | 0 | -0.81453 | 52.5 | 1440.3012 | 3000 | 0 | 3000 | 2691.7768 | 0 | 142.395
0 | 32.3741 | 0 | 0 | 0 | 0 | 20.1259 | 52.5 | 1460.4271 | 3000 | 35.9623 | 3035.9623 | 2938.6286 | 0 | 155.7473
0 | 42.1164 | 0 | 0 | 0 | 0 | 10.3836 | 52.5 | 1470.8107 | 3000 | 18.5541 | 3018.5541 | 3007.7392 | 0 | 164.1624
0 | 56.08 | 0 | 0 | 0 | 0 | -3.58 | 52.5 | 1467.2306 | 3000 | 0 | 3000 | 3000 | 0 | 171.84
0 | 29.5645 | 0 | 0 | 0 | 0 | 22.9355 | 52.5 | 1490.1661 | 3000 | 40.9827 | 3040.9827 | 3040.9827 | 0 | 185.6824
0 | 46.1755 | 0 | 0 | 0 | 0 | 6.3245 | 52.5 | 1496.4907 | 3000 | 11.3011 | 3011.3011 | 3011.3011 | 0 | 188.8989
0 | 36.7694 | 0 | 0 | 0 | 0 | 3.5093 | 40.2788 | 1500 | 2301.6439 | 6.2707 | 2307.9146 | 2307.9146 | 0 | 140.7828
0 | 31.655 | 0 | 0 | 0 | 0 | 9.9476e-14 | 31.655 | 1500 | 1808.8587 | 1.7775e-13 | 1808.8587 | 1808.8587 | 0 | 103.4667
0 | 30.5553 | 0 | 0 | 0 | 0 | -9.5923e-14 | 30.5553 | 1500 | 1746.0153 | 0 | 1746.0153 | 1746.0153 | 0 | 95.5769
0 | 27.3242 | 0 | 0 | 0 | 0 | 0 | 27.3242 | 1500 | 1561.3825 | 0 | 1561.3825 | 1561.3825 | 0 | 84.1273
0 | 26.9002 | 0 | 0 | 0 | 0 | -3.908e-14 | 26.9002 | 1500 | 1537.1541 | 0 | 1537.1541 | 1537.1541 | 0 | 80.2548

## Properties
hydrogen properties at 25C and 1 atm
Molecular Weight | 2016
Specific Gravity, air = 1 | 0.070
Specific Volume (ft3/lb, m3/kg) | 194, 12.1
Density of liquid at atmospheric pressure (lb/ft3, kg/m3) | 4.43, 71.0
Absolute Viscosity (lbm/ft s, centipoises) | 6.05 10-6, 0.009
Sound velocity in gas (m/s) | 1315
Specific Heat - cp - (Btu/lboF or cal/goC, J/kgK) | 3.42, 14310
Specific Heat Ratio - cp/cv | 1405
Gas constant - R - (ft lb/lboR, J/kgoC) | 767, 4126
Thermal Conductivity (Btu/hr ft oF, W/moC) | 0.105, 0.182
Boiling Point - saturation pressure 14.7 psia and 760 mm Hg - (oF, oK) | -423, 20.4
Latent Heat of Evaporation at boiling point (Btu/lb, J/kg) | 192, 447000
Freezing or Melting Point at 1 atm (oF, oC) | -434.6, -259.1
Latent Heat of Fusion (Btu/lb, J/kg) | 25.0, 58000
Critical Temperature (oF, oC) | -399.8, -240.0
Critical Pressure (psia, MN/m2) | 189, 1.30
Critical Volume (ft3/lb, m3/kg) | 0.53, 0.033
Flammable | yes
Heat of combustion (Btu/ft3, Btu/lb, kJ/kg) | 320, 62050, 144000
specific energy (kJ/kg) | 144000
beveiligingswachtwoord | @Integration

## Gen GROHW demand
| distribution by pipeline | [5 empty] | Distr by tube trailer
[7 empty] | 200 kg |  | in kg H2 !!
| client 1 | client 2 | client 3 | client 4 | client 5 |  | client 2 | client 3
Time (hrs) | Ind strong peak demnand | Ind cont demand | Office building | Ind cont demand | Fuel station | Total Demand via pipeline | Ind cont demand, distr by road | Office building, distr by road | Total demand 1,4,5 pipe 2,3 road
1 | 0 | 3.5857 | 3.5738 | 28.9376 | 0 | 36.0971 | 0 | 0 | 28.9376
2 | 0 | 3.1131 | 2.1636 | 29.1815 | 0 | 34.4583 | 0 | 0 | 29.1815
3 | 0 | 3.4953 | 1.767 | 35.9061 | 0 | 41.1684 | 0 | 0 | 35.9061
4 | 0 | 2.9847 | 3.2797 | 30.1971 | 0 | 36.4615 | 0 | 0 | 30.1971
5 | 0 | 2.9181 | 6.6416 | 39.6806 | 0 | 49.2403 | 0 | 0 | 39.6806
6 | 0 | 3.714 | 6.6966 | 28.9379 | 0 | 39.3485 | 0 | 0 | 28.9379
7 | 0 | 3.2392 | 6.9432 | 34.4637 | 0 | 44.646 | 0 | 0 | 34.4637
8 | 0 | 3.2138 | 6.6802 | 31.5403 | 18.1746 | 59.6089 | 0 | 0 | 49.7149
9 | 0 | 3.0121 | 6.7845 | 42.2471 | 9.7888 | 61.8326 | 0 | 0 | 52.0359
10 | 0 | 3.1715 | 6.3062 | 31.6994 | 7.4981 | 48.6751 | 0 | 0 | 39.1974
11 | 0 | 3.4585 | 5.8715 | 25.6347 | 16.7703 | 51.7349 | 0 | 0 | 42.405
12 | 0 | 3.251 | 5.5969 | 33.2618 | 19.3878 | 61.4976 | 0 | 0 | 52.6496
13 | 0 | 3.4862 | 5.7129 | 29.9351 | 14.3047 | 53.4389 | 0 | 0 | 44.2398
14 | 0 | 3.4214 | 5.1654 | 29.7209 | 19.3124 | 57.6202 | 0 | 0 | 49.0333
15 | 0 | 3.3301 | 5.5131 | 32.4507 | 14.2697 | 55.5637 | 0 | 0 | 46.7205
16 | 0 | 3.2832 | 5.2591 | 30.2932 | 24.8164 | 63.652 | 0 | 0 | 55.1097
17 | 0 | 3.0253 | 4.8285 | 29.7707 | 13.3425 | 50.9669 | 0 | 0 | 43.1132
18 | 0 | 3.1036 | 3.1881 | 29.1297 | 12.5127 | 47.9341 | 0 | 0 | 41.6424
19 | 0 | 3.8409 | 3.2572 | 32.5944 | 18.87 | 58.5625 | 0 | 0 | 51.4645
20 | 0 | 3.2044 | 3.6609 | 23.9224 | 0 | 30.7877 | 0 | 0 | 23.9224
21 | 0 | 3.5714 | 3.7744 | 27.3412 | 0 | 34.687 | 0 | 0 | 27.3412
22 | 0 | 2.6321 | 4.1084 | 35.8974 | 0 | 42.6378 | 0 | 0 | 35.8974
23 | 0 | 3.304 | 4.1272 | 22.2632 | 0 | 29.6944 | 0 | 0 | 22.2632
24 | 0 | 3.1568 | 5.5069 | 31.9763 | 0 | 40.64 | 0 | 0 | 31.9763
25 | 0 | 3.2633 | 6.9872 | 24.3883 | 0 | 34.6387 | 0 | 0 | 24.3883
26 | 0 | 3.0862 | 9.3024 | 32.4641 | 0 | 44.8527 | 0 | 0 | 32.4641
27 | 0 | 2.5718 | 8.3763 | 24.5208 | 0 | 35.4689 | 0 | 0 | 24.5208
28 | 0 | 2.9276 | 8.2894 | 25.5111 | 0 | 36.7281 | 0 | 0 | 25.5111
29 | 0 | 3.5488 | 8.7742 | 33.3961 | 0 | 45.7191 | 0 | 0 | 33.3961
30 | 0 | 3.3471 | 8.4711 | 24.9132 | 0 | 36.7314 | 0 | 0 | 24.9132
31 | 0 | 3.5618 | 8.1428 | 29.3418 | 0 | 41.0464 | 0 | 0 | 29.3418
32 | 0 | 3.0402 | 8.2516 | 27.5484 | 11.9609 | 50.8011 | 0 | 0 | 39.5093
33 | 0 | 3.808 | 8.0587 | 40.1604 | 7.8074 | 59.8345 | 0 | 0 | 47.9677
34 | 0 | 2.9987 | 7.4196 | 36.2927 | 12.2494 | 58.9604 | 0 | 200 | 248.5421
35 | 0 | 4.0283 | 6.5055 | 30.9465 | 14.9619 | 56.4423 | 0 | 0 | 45.9085
36 | 0 | 3.3289 | 5.891 | 38.1127 | 10.3968 | 57.7294 | 0 | 0 | 48.5094
37 | 0 | 3.2584 | 4.9367 | 25.8575 | 16.3315 | 50.384 | 0 | 0 | 42.1889
38 | 0 | 2.8824 | 4.6065 | 32.486 | 15.9619 | 55.9368 | 0 | 0 | 48.4479
39 | 0 | 3.0826 | 5.2633 | 37.4093 | 16.5915 | 62.3467 | 0 | 0 | 54.0008
40 | 0 | 3.2895 | 5.0827 | 29.2402 | 14.6869 | 52.2993 | 0 | 0 | 43.9271
41 | 0 | 3.2412 | 3.9755 | 29.7658 | 16.8927 | 53.8752 | 0 | 0 | 46.6585
42 | 0 | 3.2551 | 2.3604 | 24.2644 | 19.288 | 49.168 | 0 | 0 | 43.5524
43 | 0 | 3.5543 | 1.5861 | 29.7622 | 14.1966 | 49.0992 | 0 | 0 | 43.9588
44 | 0 | 3.2687 | 1.239 | 31.2894 | 0 | 35.7971 | 0 | 0 | 31.2894
45 | 0 | 3.3707 | 1.0185 | 30.5482 | 0 | 34.9374 | 0 | 0 | 30.5482
46 | 0 | 3.1718 | 1.0722 | 30.2655 | 0 | 34.5095 | 0 | 0 | 30.2655
47 | 0 | 3.3347 | 1.1947 | 24.8339 | 0 | 29.3633 | 0 | 0 | 24.8339
48 | 0 | 2.5924 | 1.2542 | 28.2249 | 0 | 32.0715 | 0 | 0 | 28.2249
49 | 0 | 3.838 | 2.7569 | 23.9772 | 0 | 30.5721 | 0 | 0 | 23.9772
50 | 0 | 3.4096 | 8.6204 | 27.9619 | 0 | 39.9919 | 0 | 0 | 27.9619
51 | 0 | 3.2086 | 7.9665 | 25.8889 | 0 | 37.064 | 0 | 0 | 25.8889
52 | 0 | 3.0784 | 7.1927 | 23.8979 | 0 | 34.1689 | 0 | 0 | 23.8979
53 | 0 | 3.5599 | 8.4946 | 28.6893 | 0 | 40.7438 | 0 | 0 | 28.6893
54 | 0 | 3.6625 | 8.1083 | 30.9944 | 0 | 42.7652 | 0 | 0 | 30.9944
55 | 0 | 3.0314 | 8.0691 | 36.1961 | 0 | 47.2967 | 0 | 0 | 36.1961
56 | 0 | 3.0256 | 7.8403 | 27.9729 | 14.2084 | 53.0472 | 0 | 0 | 42.1813
57 | 0 | 3.348 | 7.1081 | 27.0591 | 16.8657 | 54.381 | 0 | 0 | 43.9248
58 | 0 | 2.9455 | 6.2016 | 30.0733 | 19.5494 | 58.7698 | 0 | 0 | 49.6227
59 | 0 | 3.202 | 5.6547 | 30.3718 | 7.4813 | 46.7097 | 0 | 0 | 37.8531
60 | 0 | 4.523 | 4.6777 | 22.1178 | 9.5137 | 40.8322 | 200 | 0 | 231.6315
61 | 0 | 3.7621 | 3.2509 | 22.0812 | 19.8473 | 48.9415 | 0 | 0 | 41.9285
62 | 0 | 3.0951 | 2.5531 | 24.8909 | 3.6798 | 34.2188 | 0 | 0 | 28.5706
63 | 0 | 3.31 | 3.2024 | 39.2701 | 18.5057 | 64.2882 | 0 | 0 | 57.7758
64 | 0 | 3.2969 | 2.9998 | 26.2349 | -0.94859 | 31.583 | 0 | 0 | 25.2863
65 | 0 | 3.7978 | 3.4053 | 31.8282 | 15.0121 | 54.0434 | 0 | 0 | 46.8403
66 | 0 | 3.4603 | 2.4718 | 31.7863 | 16.9822 | 54.7006 | 0 | 0 | 48.7685
67 | 0 | 3.7124 | 1.7784 | 29.062 | 15.721 | 50.2737 | 0 | 0 | 44.783
68 | 0 | 3.4144 | 1.5791 | 29.8794 | 0 | 34.8729 | 0 | 0 | 29.8794
69 | 0 | 3.2963 | 1.2698 | 30.9745 | 0 | 35.5406 | 0 | 0 | 30.9745
70 | 0 | 3.663 | 1.536 | 29.0631 | 0 | 34.2621 | 0 | 0 | 29.0631
71 | 0 | 3.2573 | 1.6929 | 22.0088 | 0 | 26.959 | 0 | 0 | 22.0088
72 | 0 | 2.6682 | 2.4433 | 28.3787 | 0 | 33.4902 | 0 | 0 | 28.3787
73 | 0 | 3.3227 | 3.9438 | 35.2363 | 0 | 42.5028 | 0 | 0 | 35.2363
74 | 0 | 3.2118 | 7.2566 | 22.4102 | 0 | 32.8785 | 0 | 0 | 22.4102
75 | 0 | 3.6548 | 7.0649 | 31.9103 | 0 | 42.63 | 0 | 0 | 31.9103
76 | 0 | 3.5469 | 7.3983 | 24.9303 | 0 | 35.8755 | 0 | 0 | 24.9303
77 | 0 | 3.0663 | 8.0054 | 35.8227 | 0 | 46.8944 | 0 | 0 | 35.8227
78 | 0 | 3.4948 | 7.6003 | 35.6684 | 0 | 46.7634 | 0 | 200 | 235.6684
79 | 0 | 3.3352 | 7.7008 | 25.5531 | 0 | 36.589 | 0 | 0 | 25.5531
80 | 0 | 3.6811 | 7.4291 | 26.914 | 6.5131 | 44.5373 | 0 | 0 | 33.4271
81 | 0 | 3.4551 | 7.4476 | 21.3076 | 6.968 | 39.1783 | 0 | 0 | 28.2756
82 | 0 | 3.2282 | 6.9459 | 24.5275 | 9.1694 | 43.871 | 0 | 0 | 33.6969
83 | 0 | 3.2839 | 5.5892 | 30.4504 | 15.079 | 54.4025 | 0 | 0 | 45.5294
84 | 0 | 3.5711 | 3.7676 | 24.0651 | 10.3896 | 41.7935 | 0 | 0 | 34.4547
85 | 0 | 3.3114 | 2.3299 | 25.1003 | 8.5954 | 39.337 | 0 | 0 | 33.6957
86 | 0 | 3.4838 | 2.3888 | 31.0112 | 21.7389 | 58.6226 | 0 | 0 | 52.75
87 | 0 | 2.9153 | 2.2579 | 29.8662 | 6.2293 | 41.2687 | 0 | 0 | 36.0955
88 | 0 | 2.999 | 2.5264 | 23.0397 | 14.5028 | 43.0679 | 0 | 0 | 37.5425
89 | 0 | 3.4705 | 2.3789 | 22.5789 | 11.2876 | 39.7159 | 0 | 0 | 33.8665
90 | 0 | 2.7219 | 2.1199 | 30.6477 | 16.7735 | 52.263 | 0 | 0 | 47.4211
91 | 0 | 2.9436 | 1.5861 | 33.6217 | 19.9066 | 58.058 | 0 | 0 | 53.5283
92 | 0 | 3.4553 | 1.239 | 25.7104 | 0 | 30.4048 | 0 | 0 | 25.7104
93 | 0 | 3.4446 | 1.189 | 35.1875 | 0 | 39.8211 | 0 | 0 | 35.1875
94 | 0 | 3.4763 | 1.8576 | 23.4989 | 0 | 28.8328 | 0 | 0 | 23.4989
95 | 0 | 2.9143 | 2.1798 | 29.8849 | 0 | 34.979 | 0 | 0 | 29.8849
96 | 0 | 3.4793 | 4.0557 | 27.9688 | 0 | 35.5039 | 0 | 0 | 27.9688
97 | 0 | 3.0525 | 5.9727 | 31.2013 | 0 | 40.2265 | 0 | 0 | 31.2013
98 | 0 | 3.2005 | 9.3998 | 22.9091 | 0 | 35.5094 | 0 | 0 | 22.9091
99 | 0 | 3.548 | 8.7042 | 32.0143 | 0 | 44.2665 | 0 | 0 | 32.0143
100 | 0 | 3.8957 | 8.7692 | 22.1166 | 0 | 34.7815 | 0 | 0 | 22.1166
101 | 0 | 3.5944 | 9.0537 | 35.5603 | 0 | 48.2085 | 0 | 0 | 35.5603
102 | 0 | 2.9144 | 8.834 | 22.1261 | 0 | 33.8744 | 0 | 0 | 22.1261
103 | 0 | 4.2616 | 8.5112 | 23.3406 | 0 | 36.1134 | 0 | 0 | 23.3406
104 | 0 | 3.2988 | 8.1145 | 19.3504 | 17.935 | 48.6987 | 0 | 0 | 37.2854
105 | 0 | 3.4819 | 7.5155 | 24.1525 | 16.5809 | 51.7309 | 0 | 0 | 40.7334
106 | 0 | 3.7447 | 6.6752 | 22.7785 | 10.1172 | 43.3156 | 0 | 0 | 32.8957
107 | 0 | 3.2057 | 5.6547 | 29.9647 | 15.4948 | 54.3199 | 0 | 0 | 45.4595
108 | 0 | 3.2648 | 4.526 | 24.9272 | 12.6643 | 45.3822 | 0 | 0 | 37.5915
109 | 0 | 3.7314 | 4.4931 | 21.8332 | 20.0596 | 50.1173 | 0 | 0 | 41.8928
110 | 0 | 3.5438 | 4.2779 | 32.1411 | 16.5621 | 56.525 | 0 | 0 | 48.7033
111 | 0 | 3.5182 | 5.2633 | 26.3536 | 23.3518 | 58.4868 | 0 | 0 | 49.7054
112 | 0 | 3.0907 | 5.3667 | 25.1142 | 8.5165 | 42.0881 | 0 | 0 | 33.6307
113 | 0 | 3.0035 | 5.0019 | 24.3178 | 8.504 | 40.8273 | 0 | 0 | 32.8219
114 | 0 | 3.3843 | 4.2536 | 31.725 | 11.6879 | 51.0508 | 0 | 0 | 43.4129
115 | 0 | 3.0092 | 2.3354 | 24.1276 | 12.7137 | 42.1858 | 0 | 0 | 36.8413
116 | 0 | 3.2254 | 1.5255 | 32.8393 | 0 | 37.5901 | 0 | 0 | 32.8393
117 | 0 | 3.4342 | 2.4969 | 24.7761 | 0 | 30.7072 | 0 | 0 | 24.7761
118 | 0 | 2.7594 | 2.4261 | 23.1862 | 0 | 28.3717 | 0 | 0 | 23.1862
119 | 0 | 3.3248 | 3.4495 | 31.7762 | 0 | 38.5505 | 0 | 0 | 31.7762
120 | 0 | 2.8044 | 4.001 | 31.6943 | 0 | 38.4997 | 200 | 200 | 431.6943
121 | 0 | 3.3273 | 4.1976 | 33.0922 | 0 | 40.617 | 0 | 0 | 33.0922
122 | 0 | 3.2509 | 2.1992 | 18.9229 | 0 | 24.3731 | 0 | 0 | 18.9229
123 | 0 | 3.5989 | 2.9795 | 28.2923 | 0 | 34.8707 | 0 | 0 | 28.2923
124 | 0 | 4.2194 | 6.0113 | 27.6968 | 0 | 37.9274 | 0 | 0 | 27.6968
125 | 0 | 3.2662 | 9.1089 | 29.9238 | 0 | 42.2989 | 0 | 0 | 29.9238
126 | 0 | 3.4217 | 8.6426 | 26.377 | 0 | 38.4413 | 0 | 0 | 26.377
127 | 0 | 3.2367 | 8.2156 | 37.3332 | 0 | 48.7855 | 0 | 0 | 37.3332
128 | 0 | 3.0099 | 8.0193 | 31.964 | 11.1361 | 54.1293 | 0 | 0 | 43.1001
129 | 0 | 3.9515 | 7.6773 | 35.1466 | 17.4121 | 64.1875 | 0 | 0 | 52.5587
130 | 0 | 2.9438 | 7.2568 | 23.5496 | 19.2556 | 53.0059 | 0 | 0 | 42.8053
131 | 0 | 2.7584 | 5.6628 | 27.7441 | 17.4561 | 53.6213 | 0 | 0 | 45.2001
132 | 0 | 3.7038 | 3.7194 | 32.561 | 15.7645 | 55.7487 | 0 | 0 | 48.3255
133 | 0 | 3.3538 | 4.5218 | 26.2794 | 6.7101 | 40.8652 | 0 | 0 | 32.9895
134 | 0 | 3.4737 | 4.9255 | 24.751 | 14.0277 | 47.1778 | 0 | 0 | 38.7787
135 | 0 | 3.5153 | 6.1024 | 29.2294 | 15.5682 | 54.4153 | 0 | 0 | 44.7976
136 | 0 | 3.3991 | 7.0179 | 30.4014 | 9.8841 | 50.7025 | 0 | 0 | 40.2855
137 | 0 | 2.963 | 8.4354 | 35.9458 | 17.5801 | 64.9243 | 0 | 0 | 53.5259
138 | 0 | 3.6494 | 7.1338 | 29.4642 | 10.9442 | 51.1916 | 0 | 0 | 40.4084
139 | 0 | 3.5637 | 5.5098 | 28.9622 | 13.7988 | 51.8344 | 0 | 0 | 42.761
140 | 0 | 3.5956 | 5.021 | 30.1487 | 0 | 38.7653 | 0 | 0 | 30.1487
141 | 0 | 2.8083 | 5.0344 | 36.1485 | 0 | 43.9913 | 0 | 0 | 36.1485
142 | 0 | 4.0511 | 5.1512 | 31.3935 | 0 | 40.5958 | 0 | 0 | 31.3935
143 | 0 | 3.5212 | 5.8319 | 23.0256 | 0 | 32.3788 | 0 | 0 | 23.0256
144 | 0 | 3.9338 | 6.7168 | 30.977 | 0 | 41.6276 | 0 | 0 | 30.977
145 | 0 | 3.7468 | 6.8569 | 30.4247 | 0 | 41.0285 | 0 | 0 | 30.4247
146 | 0 | 3.3908 | 5.2533 | 28.4062 | 0 | 37.0502 | 0 | 0 | 28.4062
147 | 0 | 3.5457 | 6.3363 | 24.3526 | 0 | 34.2347 | 0 | 0 | 24.3526
148 | 0 | 3.1611 | 7.9361 | 31.3259 | 0 | 42.4231 | 0 | 0 | 31.3259
149 | 0 | 2.6544 | 9.6027 | 22.6671 | 0 | 34.9241 | 0 | 0 | 22.6671
150 | 0 | 3.6733 | 9.4764 | 22.858 | 0 | 36.0077 | 0 | 0 | 22.858
151 | 0 | 3.475 | 9.9977 | 26.0971 | 0 | 39.5698 | 0 | 200 | 226.0971
152 | 0 | 3.3694 | 9.7792 | 23.2984 | 16.458 | 52.905 | 0 | 0 | 39.7564
153 | 0 | 3.5446 | 9.7888 | 22.5986 | 21.4876 | 57.4196 | 0 | 0 | 44.0862
154 | 0 | 3.1267 | 9.754 | 23.1744 | 15.7569 | 51.8119 | 0 | 0 | 38.9313
155 | 0 | 3.5002 | 9.598 | 23.942 | 22.1695 | 59.2096 | 0 | 0 | 46.1114
156 | 0 | 3.1106 | 9.5917 | 31.772 | 22.3424 | 66.8167 | 0 | 0 | 54.1144
157 | 0 | 2.463 | 10.1184 | 22.8776 | 11.2547 | 46.7136 | 0 | 0 | 34.1323
158 | 0 | 3.4383 | 10.5101 | 25.7623 | 16.1958 | 55.9064 | 0 | 0 | 41.958
159 | 0 | 3.0759 | 11.0854 | 25.1524 | 15.6167 | 54.9304 | 0 | 0 | 40.7691
160 | 0 | 3.1323 | 12.1084 | 25.5996 | 21.0287 | 61.869 | 0 | 0 | 46.6282
161 | 0 | 2.9176 | 12.927 | 31.6377 | 11.1175 | 58.6 | 0 | 0 | 42.7553
162 | 0 | 3.522 | 12.5297 | 23.8792 | 17.3682 | 57.299 | 0 | 0 | 41.2473
163 | 0 | 2.9079 | 10.0596 | 30.1419 | 21.6496 | 64.759 | 0 | 0 | 51.7915
164 | 0 | 2.9471 | 9.2126 | 31.3043 | 0 | 43.464 | 0 | 0 | 31.3043
165 | 0 | 3.5282 | 8.9452 | 34.7601 | 0 | 47.2336 | 0 | 0 | 34.7601
166 | 0 | 3.2788 | 9.0923 | 21.5202 | 0 | 33.8913 | 0 | 0 | 21.5202
167 | 0 | 3.7433 | 9.4828 | 23.6005 | 0 | 36.8266 | 0 | 0 | 23.6005
168 | 0 | 2.8159 | 10.1828 | 33.523 | 0 | 46.5217 | 0 | 0 | 33.523
169 | 0 | 3.0638 | 12.7695 | 28.8656 | 0 | 44.6989 | 0 | 200 | 228.8656
170 | 0 | 3.2639 | 15.7321 | 25.3045 | 0 | 44.3005 | 0 | 0 | 25.3045
171 | 0 | 3.7297 | 14.1136 | 35.6126 | 0 | 53.4558 | 0 | 0 | 35.6126
172 | 0 | 3.0451 | 12.8133 | 23.8576 | 0 | 39.7159 | 0 | 0 | 23.8576
173 | 0 | 3.0917 | 12.9673 | 23.7407 | 0 | 39.7997 | 0 | 0 | 23.7407
174 | 0 | 3.2738 | 12.2447 | 26.0575 | 0 | 41.576 | 0 | 0 | 26.0575
175 | 0 | 4.0525 | 11.6056 | 27.2866 | 0 | 42.9447 | 0 | 0 | 27.2866
176 | 0 | 3.0606 | 10.8563 | 36.1858 | 16.4436 | 66.5462 | 0 | 0 | 52.6294
177 | 0 | 3.7496 | 10.5711 | 28.1759 | 14.9629 | 57.4596 | 0 | 0 | 43.1389
178 | 0 | 2.7177 | 10.2617 | 37.814 | 12.7402 | 63.5336 | 0 | 0 | 50.5542
179 | 0 | 2.9283 | 9.4509 | 33.816 | 17.9722 | 64.1674 | 0 | 0 | 51.7882
180 | 0 | 3.1163 | 9.3795 | 28.9245 | 12.1135 | 53.5337 | 200 | 0 | 241.0379
181 | 0 | 3.6133 | 9.3731 | 33.579 | 9.8957 | 56.4612 | 0 | 0 | 43.4748
182 | 0 | 2.9106 | 8.8775 | 31.2501 | 9.0276 | 52.0658 | 0 | 0 | 40.2777
183 | 0 | 2.8782 | 9.6426 | 32.0397 | 9.0119 | 53.5725 | 0 | 0 | 41.0516
184 | 0 | 3.1124 | 9.9113 | 26.7799 | 17.2473 | 57.0509 | 0 | 0 | 44.0272
185 | 0 | 3.2638 | 10.5902 | 33.6751 | 8.2459 | 55.775 | 0 | 0 | 41.921
186 | 0 | 3.3067 | 9.4876 | 24.5372 | 18.3634 | 55.695 | 0 | 0 | 42.9007
187 | 0 | 2.9566 | 8.3837 | 34.1174 | 9.7923 | 55.2499 | 0 | 0 | 43.9097
188 | 0 | 3.3158 | 7.6512 | 25.4261 | 0 | 36.393 | 0 | 0 | 25.4261
189 | 0 | 3.2022 | 7.5717 | 29.0005 | 0 | 39.7744 | 0 | 200 | 229.0005
190 | 0 | 3.3434 | 7.6453 | 34.6662 | 0 | 45.6549 | 0 | 0 | 34.6662
191 | 0 | 3.3523 | 8.4279 | 32.2576 | 0 | 44.0378 | 0 | 0 | 32.2576
192 | 0 | 3.3925 | 9.1347 | 32.0297 | 0 | 44.5569 | 0 | 0 | 32.0297
193 | 0 | 3.3878 | 11.9579 | 33.0117 | 0 | 48.3575 | 0 | 0 | 33.0117
194 | 0 | 3.2982 | 15.3424 | 24.3904 | 0 | 43.031 | 0 | 0 | 24.3904
195 | 0 | 3.2527 | 13.6218 | 24.2588 | 0 | 41.1333 | 0 | 0 | 24.2588
196 | 0 | 3.2737 | 12.5391 | 30.496 | 0 | 46.3088 | 0 | 0 | 30.496
197 | 0 | 3.1613 | 12.6179 | 27.5075 | 0 | 43.2866 | 0 | 0 | 27.5075
198 | 0 | 2.6065 | 12.2447 | 22.0403 | 0 | 36.8915 | 0 | 0 | 22.0403
199 | 0 | 3.4368 | 11.4583 | 34.1844 | 0 | 49.0795 | 0 | 0 | 34.1844
200 | 0 | 3.131 | 11.2675 | 31.2504 | 13.9935 | 59.6424 | 0 | 0 | 45.2439
201 | 0 | 3.3342 | 10.7069 | 28.104 | 20.0039 | 62.1491 | 0 | 0 | 48.1079
202 | 0 | 3.56 | 10.4647 | 33.8368 | 4.8068 | 52.6683 | 0 | 0 | 38.6436
203 | 0 | 3.4053 | 9.5818 | 31.7929 | 17.2716 | 62.0517 | 0 | 0 | 49.0646
204 | 0 | 3.2273 | 9.5311 | 32.0364 | 18.201 | 62.9959 | 0 | 0 | 50.2374
205 | 0 | 3.3755 | 7.776 | 22.5663 | 18.9638 | 52.6816 | 0 | 0 | 41.5301
206 | 0 | 3.0926 | 6.4135 | 38.1076 | 16.883 | 64.4966 | 0 | 0 | 54.9905
207 | 0 | 2.9658 | 6.0361 | 28.0695 | 19.0015 | 56.073 | 0 | 0 | 47.071
208 | 0 | 3.3537 | 5.7455 | 29.5295 | 10.8137 | 49.4424 | 0 | 0 | 40.3432
209 | 0 | 3.1357 | 5.3441 | 22.0001 | 3.8587 | 34.3386 | 0 | 0 | 25.8587
210 | 0 | 3.9174 | 3.8081 | 29.9673 | 10.613 | 48.3058 | 0 | 200 | 240.5802
211 | 0 | 3.8267 | 2.9614 | 35.7361 | 15.6489 | 58.1731 | 0 | 0 | 51.385
212 | 0 | 3.1677 | 2.7067 | 27.6282 | 0 | 33.5026 | 0 | 0 | 27.6282
213 | 0 | 3.2486 | 2.8049 | 19.5394 | 0 | 25.5929 | 0 | 0 | 19.5394
214 | 0 | 3.2518 | 2.8222 | 31.887 | 0 | 37.961 | 0 | 0 | 31.887
215 | 0 | 2.8794 | 3.3158 | 33.5202 | 0 | 39.7154 | 0 | 0 | 33.5202
216 | 0 | 3.3103 | 3.8139 | 36.0171 | 0 | 43.1412 | 0 | 0 | 36.0171
217 | 0 | 3.5037 | 5.1612 | 28.021 | 0 | 36.6858 | 0 | 0 | 28.021
218 | 0 | 3.2921 | 8.0359 | 41.0792 | 0 | 52.4071 | 0 | 0 | 41.0792
219 | 0 | 3.5023 | 7.7206 | 30.1636 | 0 | 41.3865 | 0 | 0 | 30.1636
220 | 0 | 3.7007 | 7.6039 | 28.0007 | 0 | 39.3053 | 0 | 0 | 28.0007
221 | 0 | 2.6729 | 8.0753 | 27.146 | 0 | 37.8943 | 0 | 0 | 27.146
222 | 0 | 3.0298 | 7.8906 | 30.2858 | 0 | 41.2061 | 0 | 0 | 30.2858
223 | 0 | 3.2357 | 7.7744 | 30.6458 | 0 | 41.6559 | 0 | 0 | 30.6458
224 | 0 | 3.3436 | 7.7032 | 32.1321 | 10.5281 | 53.707 | 0 | 0 | 42.6602
225 | 0 | 3.5547 | 7.3118 | 33.4909 | 19.362 | 63.7194 | 0 | 0 | 52.8529
226 | 0 | 3.0896 | 6.7429 | 31.7446 | 22.815 | 64.3921 | 0 | 0 | 54.5596
227 | 0 | 3.9343 | 5.9819 | 26.3273 | 8.1368 | 44.3803 | 0 | 0 | 34.4641
228 | 0 | 3.6737 | 5.1327 | 30.6984 | 10.9005 | 50.4053 | 0 | 0 | 41.5989
229 | 0 | 3.335 | 4.1382 | 35.554 | 7.8565 | 50.8836 | 0 | 0 | 43.4105
230 | 0 | 3.0142 | 4.0315 | 25.5015 | 20.4551 | 53.0023 | 0 | 0 | 45.9566
231 | 0 | 3.1798 | 4.3187 | 30.1864 | 4.004 | 41.6889 | 0 | 0 | 34.1904
232 | 0 | 3.3576 | 4.704 | 32.0777 | 15.6702 | 55.8095 | 0 | 0 | 47.7479
233 | 0 | 3.1866 | 3.9755 | 32.8334 | 22.8187 | 62.8143 | 0 | 0 | 55.6522
234 | 0 | 3.2179 | 4.0309 | 26.9843 | 15.5661 | 49.7992 | 0 | 0 | 42.5504
235 | 0 | 3.0475 | 3.1586 | 36.7127 | 9.8438 | 52.7626 | 0 | 0 | 46.5565
236 | 0 | 2.8169 | 3.5742 | 21.2737 | 0 | 27.6648 | 0 | 0 | 21.2737
237 | 0 | 3.6345 | 3.7744 | 29.7703 | 0 | 37.1792 | 0 | 0 | 29.7703
238 | 0 | 3.4157 | 4.2691 | 33.3671 | 0 | 41.052 | 0 | 0 | 33.3671
239 | 0 | 3.162 | 5.0198 | 24.0949 | 0 | 32.2767 | 0 | 0 | 24.0949
240 | 0 | 2.8365 | 6.1518 | 25.7918 | 0 | 34.7801 | 0 | 0 | 25.7918
241 | 0 | 3.105 | 7.4944 | 29.9687 | 0 | 40.568 | 0 | 0 | 29.9687
242 | 0 | 3.5743 | 10.6662 | 29.5169 | 0 | 43.7575 | 200 | 0 | 229.5169
243 | 0 | 3.8486 | 9.1959 | 29.1475 | 0 | 42.192 | 0 | 0 | 29.1475
244 | 0 | 3.3909 | 8.9748 | 31.0844 | 0 | 43.4502 | 0 | 0 | 31.0844
245 | 0 | 3.3431 | 8.9838 | 29.9448 | 0 | 42.2716 | 0 | 200 | 229.9448
246 | 0 | 3.2108 | 8.1808 | 27.6725 | 0 | 39.0642 | 0 | 0 | 27.6725
247 | 0 | 3.4151 | 7.7008 | 33.4882 | 0 | 44.6042 | 0 | 0 | 33.4882
248 | 0 | 2.8026 | 7.2234 | 27.3971 | 21.972 | 59.3952 | 0 | 0 | 49.3691
249 | 0 | 3.1427 | 7.2439 | 24.5691 | 6.2986 | 41.2543 | 0 | 0 | 30.8677
250 | 0 | 3.5693 | 7.8933 | 21.0139 | 14.6302 | 47.1067 | 0 | 0 | 35.6441
251 | 0 | 3.0997 | 8.0764 | 27.7109 | 27.2332 | 66.1203 | 0 | 0 | 54.9441
252 | 0 | 3.2273 | 8.1661 | 29.3944 | 16.012 | 56.7998 | 0 | 0 | 45.4064
253 | 0 | 3.0553 | 9.4618 | 27.0886 | 1.2091 | 40.8148 | 0 | 0 | 28.2977
254 | 0 | 2.8939 | 9.6168 | 27.1083 | 11.4645 | 51.0836 | 0 | 0 | 38.5729
255 | 0 | 3.3971 | 10.1579 | 29.4095 | 6.0422 | 49.0066 | 0 | 0 | 35.4517
256 | 0 | 2.9836 | 10.4793 | 21.763 | 18.2975 | 53.5235 | 0 | 0 | 40.0605
257 | 0 | 3.1031 | 10.4761 | 25.7785 | 9.0753 | 48.433 | 0 | 0 | 34.8538
258 | 0 | 3.5589 | 7.9285 | 26.6688 | 11.3685 | 49.5247 | 0 | 0 | 38.0373
259 | 0 | 3.6693 | 6.1162 | 30.5147 | 12.0127 | 52.3129 | 0 | 0 | 42.5274
260 | 0 | 3.8159 | 5.0488 | 25.3995 | 0 | 34.2642 | 0 | 0 | 25.3995
261 | 0 | 2.6523 | 4.7439 | 28.6898 | 0 | 36.086 | 0 | 0 | 28.6898
262 | 0 | 2.732 | 4.8318 | 26.68 | 0 | 34.2439 | 0 | 0 | 26.68
263 | 0 | 3.099 | 5.2633 | 32.5721 | 0 | 40.9343 | 0 | 0 | 32.5721
264 | 0 | 3.4058 | 5.8293 | 27.2078 | 0 | 36.4429 | 0 | 0 | 27.2078
265 | 0 | 3.3656 | 7.6973 | 36.9587 | 0 | 48.0215 | 0 | 0 | 36.9587
266 | 0 | 2.9779 | 10.6662 | 27.7303 | 0 | 41.3744 | 0 | 0 | 27.7303
267 | 0 | 3.7971 | 9.8516 | 29.9659 | 0 | 43.6146 | 0 | 0 | 29.9659
268 | 0 | 3.7036 | 9.6603 | 31.0686 | 0 | 44.4324 | 0 | 0 | 31.0686
269 | 0 | 2.7227 | 10.3815 | 30.4364 | 0 | 43.5407 | 0 | 200 | 230.4364
270 | 0 | 2.8548 | 10.2853 | 29.7964 | 0 | 42.9365 | 0 | 0 | 29.7964
271 | 0 | 3.2429 | 10.2795 | 29.0842 | 0 | 42.6066 | 0 | 0 | 29.0842
272 | 0 | 3.2641 | 9.8966 | 29.5685 | 20.0031 | 62.7323 | 0 | 0 | 49.5716
273 | 0 | 3.3792 | 9.4847 | 39.2097 | 15.1214 | 67.195 | 0 | 0 | 54.3311
274 | 0 | 3.2437 | 8.8406 | 26.2617 | 12.2048 | 50.5508 | 0 | 0 | 38.4665
275 | 0 | 3.3226 | 7.9455 | 29.5274 | 6.6028 | 47.3983 | 0 | 0 | 36.1302
276 | 0 | 3.2932 | 7.4077 | 27.5486 | 20.079 | 58.3286 | 0 | 0 | 47.6277
277 | 0 | 3.2033 | 6.8887 | 16.2774 | 10.3471 | 36.7165 | 0 | 0 | 26.6245
278 | 0 | 3.4554 | 6.4135 | 27.3205 | 12.2067 | 49.3961 | 0 | 0 | 39.5272
279 | 0 | 3.4604 | 6.8948 | 22.4589 | 21.4381 | 54.2523 | 0 | 0 | 43.897
280 | 0 | 3.2575 | 6.9763 | 29.8914 | 17.9163 | 58.0414 | 0 | 0 | 47.8077
281 | 0 | 3.1296 | 7.0548 | 28.1819 | 16.5631 | 54.9293 | 0 | 0 | 44.7449
282 | 0 | 3.2697 | 6.4808 | 28.3832 | 17.9099 | 56.0436 | 0 | 0 | 46.293
283 | 0 | 3.6844 | 4.189 | 27.0718 | 17.7521 | 52.6973 | 0 | 0 | 44.8239
284 | 0 | 3.5068 | 3.1632 | 24.8297 | 0 | 31.4997 | 0 | 0 | 24.8297
285 | 0 | 3.1883 | 3.4556 | 26.8345 | 0 | 33.4783 | 0 | 0 | 26.8345
286 | 0 | 2.9384 | 3.4537 | 32.4557 | 0 | 38.8479 | 0 | 0 | 32.4557
287 | 0 | 3.2024 | 3.8179 | 25.1488 | 0 | 32.1691 | 0 | 0 | 25.1488
288 | 0 | 3.374 | 4.001 | 28.9378 | 0 | 36.3128 | 0 | 0 | 28.9378
289 | 0 | 3.5898 | 3.8797 | 28.351 | 0 | 35.8205 | 0 | 0 | 28.351
290 | 0 | 3.5468 | 2.1992 | 24.858 | 0 | 30.604 | 0 | 0 | 24.858
291 | 0 | 3.7231 | 1.9945 | 34.4758 | 0 | 40.1934 | 0 | 0 | 34.4758
292 | 0 | 3.0644 | 5.4944 | 29.2364 | 0 | 37.7952 | 0 | 0 | 29.2364
293 | 0 | 2.6569 | 9.1089 | 26.0787 | 0 | 37.8445 | 0 | 0 | 26.0787
294 | 0 | 3.1308 | 8.9986 | 25.1098 | 0 | 37.2391 | 0 | 0 | 25.1098
295 | 0 | 3.7336 | 8.6611 | 32.6647 | 0 | 45.0593 | 0 | 0 | 32.6647
296 | 0 | 3.3147 | 8.4972 | 30.1389 | 9.6653 | 51.616 | 0 | 0 | 39.8042
297 | 0 | 3.2231 | 7.8719 | 32.0506 | 22.5219 | 65.6675 | 0 | 0 | 54.5725
298 | 0 | 3.2269 | 7.0761 | 27.207 | 24.8641 | 62.3741 | 0 | 0 | 52.0711
299 | 0 | 3.6114 | 5.4061 | 24.6605 | 10.3096 | 43.9877 | 0 | 0 | 34.9701
300 | 0 | 3.2378 | 3.0301 | 30.9725 | 23.6398 | 60.8802 | 0 | 0 | 54.6123
301 | 0 | 3.5934 | 3.0028 | 29.0561 | 14.6173 | 50.2696 | 0 | 0 | 43.6734
302 | 0 | 3.542 | 4.1228 | 34.6817 | 18.1259 | 60.4724 | 200 | 200 | 452.8076
303 | 0 | 2.9559 | 5.3131 | 31.6688 | 11.3553 | 51.2931 | 0 | 0 | 43.0241
304 | 0 | 3.3252 | 5.3344 | 31.5685 | 7.9775 | 48.2056 | 0 | 0 | 39.5461
305 | 0 | 3.8158 | 6.4019 | 33.8298 | 15.9193 | 59.9667 | 0 | 0 | 49.749
306 | 0 | 3.4157 | 5.9621 | 22.5525 | 9.7724 | 41.7027 | 0 | 0 | 32.325
307 | 0 | 3.2508 | 5.3197 | 29.1613 | 10.9799 | 48.7117 | 0 | 0 | 40.1412
308 | 0 | 3.6736 | 5.021 | 33.0661 | 0 | 41.7607 | 0 | 0 | 33.0661
309 | 0 | 3.5141 | 5.3279 | 30.2421 | 0 | 39.0841 | 0 | 0 | 30.2421
310 | 0 | 3.6137 | 5.1512 | 22.2817 | 0 | 31.0466 | 0 | 0 | 22.2817
311 | 0 | 3.7215 | 5.4804 | 28.1395 | 0 | 37.3415 | 0 | 0 | 28.1395
312 | 0 | 2.9112 | 6.1386 | 26.3932 | 0 | 35.443 | 0 | 0 | 26.3932
313 | 0 | 3.3096 | 6.255 | 38.3196 | 0 | 47.8842 | 0 | 0 | 38.3196
314 | 0 | 3.0428 | 3.6404 | 29.669 | 0 | 36.3522 | 0 | 0 | 29.669
315 | 0 | 2.769 | 5.065 | 27.646 | 0 | 35.48 | 0 | 0 | 27.646
316 | 0 | 3.4511 | 6.9013 | 33.1385 | 0 | 43.491 | 0 | 0 | 33.1385
317 | 0 | 3.6561 | 9.0598 | 23.683 | 0 | 36.3989 | 0 | 0 | 23.683
318 | 0 | 2.9126 | 8.9887 | 25.2497 | 0 | 37.151 | 0 | 0 | 25.2497
319 | 0 | 3.2414 | 9.3431 | 31.1686 | 0 | 43.7532 | 0 | 0 | 31.1686
320 | 0 | 3.0701 | 8.855 | 25.7069 | 17.6652 | 55.2972 | 0 | 0 | 43.3721
321 | 0 | 3.8088 | 8.9476 | 27.2875 | 23.0328 | 63.0767 | 0 | 0 | 50.3204
322 | 0 | 3.0902 | 8.6245 | 29.4009 | 16.4113 | 57.5269 | 0 | 0 | 45.8122
323 | 0 | 3.343 | 9.2431 | 26.2223 | 20.5611 | 59.3696 | 0 | 0 | 46.7834
324 | 0 | 3.5968 | 9.5283 | 29.1888 | 13.3585 | 55.6724 | 0 | 0 | 42.5473
325 | 0 | 3.2892 | 9.745 | 32.3177 | 18.488 | 63.8399 | 0 | 0 | 50.8058
326 | 0 | 3.4752 | 9.6193 | 34.7675 | 15.2626 | 63.1246 | 0 | 0 | 50.03
327 | 0 | 3.223 | 10.2354 | 26.5552 | 14.1819 | 54.1955 | 0 | 0 | 40.7372
328 | 0 | 3.5329 | 10.448 | 29.7743 | 22.0308 | 65.786 | 0 | 0 | 51.8051
329 | 0 | 3.38 | 10.9318 | 24.9834 | 19.6215 | 58.9166 | 0 | 200 | 244.6048
330 | 0 | 2.9707 | 10.3836 | 24.4935 | 15.6117 | 53.4596 | 0 | 0 | 40.1052
331 | 0 | 3.7187 | 8.2851 | 32.9432 | 13.7216 | 58.6685 | 0 | 0 | 46.6648
332 | 0 | 3.7989 | 7.2174 | 28.7799 | 0 | 39.7963 | 0 | 0 | 28.7799
333 | 0 | 3.4061 | 6.279 | 27.929 | 0 | 37.6141 | 0 | 0 | 27.929
334 | 0 | 3.8204 | 6.118 | 25.9792 | 0 | 35.9176 | 0 | 0 | 25.9792
335 | 0 | 3.2167 | 6.0747 | 25.5159 | 0 | 34.8073 | 0 | 0 | 25.5159
336 | 0 | 3.2222 | 6.8774 | 27.8932 | 0 | 37.9928 | 0 | 0 | 27.8932
337 | 0 | 2.9202 | 8.6103 | 26.0457 | 0 | 37.5763 | 0 | 0 | 26.0457
338 | 0 | 2.841 | 10.9585 | 23.4963 | 0 | 37.2958 | 0 | 0 | 23.4963
339 | 0 | 3.6902 | 9.2779 | 23.1824 | 0 | 36.1505 | 0 | 0 | 23.1824
340 | 0 | 3.2905 | 8.8377 | 32.0736 | 0 | 44.2018 | 0 | 0 | 32.0736
341 | 0 | 3.1658 | 9.473 | 24.4647 | 0 | 37.1034 | 0 | 0 | 24.4647
342 | 0 | 3.3157 | 9.2694 | 38.4082 | 0 | 50.9933 | 0 | 0 | 38.4082
343 | 0 | 2.9735 | 8.5112 | 30.9335 | 0 | 42.4182 | 0 | 0 | 30.9335
344 | 0 | 3.4285 | 8.7999 | 30.0622 | 12.7307 | 55.0213 | 0 | 0 | 42.7928
345 | 0 | 3.4345 | 8.2625 | 32.0046 | 22.5531 | 66.2547 | 0 | 0 | 54.5577
346 | 0 | 3.887 | 7.8256 | 29.0345 | 13.1682 | 53.9152 | 0 | 0 | 42.2026
347 | 0 | 2.7654 | 6.8328 | 34.417 | 6.9742 | 50.9894 | 0 | 0 | 41.3912
348 | 0 | 3.2749 | 5.891 | 23.8279 | 17.8886 | 50.8825 | 0 | 0 | 41.7165
349 | 0 | 3.9875 | 5.4691 | 30.8754 | 17.0381 | 57.3701 | 0 | 0 | 47.9135
350 | 0 | 3.4957 | 5.0993 | 26.8008 | 2.4906 | 37.8864 | 0 | 0 | 29.2914
351 | 0 | 3.1954 | 4.834 | 28.6021 | 17.7196 | 54.351 | 0 | 0 | 46.3217
352 | 0 | 3.1757 | 4.2306 | 34.1907 | 17.037 | 58.6341 | 0 | 0 | 51.2278
353 | 0 | 3.493 | 3.0632 | 25.0215 | 3.1283 | 34.706 | 0 | 0 | 28.1498
354 | 0 | 3.5096 | 2.4718 | 21.2097 | 9.5894 | 36.7805 | 0 | 0 | 30.7991
355 | 0 | 3.4075 | 1.9755 | 26.1109 | 11.8835 | 43.3774 | 0 | 0 | 37.9944
356 | 0 | 3.5072 | 2.62 | 29.6628 | 0 | 35.79 | 0 | 0 | 29.6628
357 | 0 | 3.5339 | 2.8049 | 26.6537 | 0 | 32.9925 | 0 | 0 | 26.6537
358 | 0 | 3.3792 | 3.3849 | 27.4278 | 0 | 34.1919 | 0 | 0 | 27.4278
359 | 0 | 2.6846 | 4.1272 | 29.1334 | 0 | 35.9452 | 0 | 0 | 29.1334
360 | 0 | 3.3356 | 4.7007 | 24.1588 | 0 | 32.1951 | 0 | 200 | 224.1588
361 | 0 | 3.4456 | 6.0742 | 28.7125 | 0 | 38.2322 | 0 | 0 | 28.7125
362 | 0 | 4.1934 | 9.9843 | 22.6216 | 0 | 36.7993 | 200 | 0 | 222.6216
363 | 0 | 3.3598 | 10.7532 | 20.8378 | 0 | 34.9508 | 0 | 0 | 20.8378
364 | 0 | 3.5214 | 9.1804 | 26.5316 | 0 | 39.2334 | 0 | 0 | 26.5316
365 | 0 | 3.1939 | 10.3815 | 28.2154 | 0 | 41.7908 | 0 | 0 | 28.2154
366 | 0 | 2.7924 | 9.2694 | 29.3027 | 0 | 41.3645 | 0 | 0 | 29.3027
367 | 0 | 2.8935 | 9.248 | 32.4015 | 0 | 44.543 | 0 | 0 | 32.4015
368 | 0 | 3.4237 | 9.1427 | 22.9003 | 22.0521 | 57.5188 | 0 | 0 | 44.9524
369 | 0 | 3.5689 | 9.3489 | 29.9842 | 8.9254 | 51.8274 | 0 | 0 | 38.9096
370 | 0 | 3.0522 | 8.4346 | 29.1659 | 15.9405 | 56.5932 | 0 | 0 | 45.1064
371 | 0 | 3.9762 | 8.1418 | 29.0954 | 9.0962 | 50.3097 | 0 | 0 | 38.1916
372 | 0 | 2.6821 | 7.2561 | 22.2653 | 4.2008 | 36.4043 | 0 | 0 | 26.4661
373 | 0 | 3.3467 | 7.2436 | 38.7677 | 21.4758 | 70.8338 | 0 | 0 | 60.2435
374 | 0 | 3.4239 | 7.0706 | 20.7585 | 13.2799 | 44.5328 | 0 | 0 | 34.0384
375 | 0 | 2.8046 | 7.7535 | 28.9374 | 7.8672 | 47.3628 | 0 | 0 | 36.8046
376 | 0 | 3.0893 | 7.639 | 36.8432 | 10.4681 | 58.0397 | 0 | 0 | 47.3114
377 | 0 | 3.7284 | 8.6514 | 38.5165 | 6.0063 | 56.9026 | 0 | 0 | 44.5228
378 | 0 | 3.1336 | 7.149 | 34.7732 | 22.9802 | 68.036 | 0 | 0 | 57.7534
379 | 0 | 3.3528 | 6.4119 | 27.7908 | 13.7103 | 51.2659 | 0 | 0 | 41.5012
380 | 0 | 3.2471 | 6.2633 | 31.717 | 0 | 41.2274 | 0 | 0 | 31.717
381 | 0 | 2.8867 | 6.5214 | 27.5847 | 0 | 36.9929 | 0 | 0 | 27.5847
382 | 0 | 3.2584 | 6.6003 | 26.3845 | 0 | 36.2432 | 0 | 0 | 26.3845
383 | 0 | 3.1184 | 6.8861 | 23.1147 | 0 | 33.1192 | 0 | 0 | 23.1147
384 | 0 | 3.8166 | 7.7642 | 25.928 | 0 | 37.5088 | 0 | 200 | 225.928
385 | 0 | 3.3331 | 10.5377 | 18.0538 | 0 | 31.9246 | 0 | 0 | 18.0538
386 | 0 | 3.5046 | 13.2966 | 28.6275 | 0 | 45.4287 | 0 | 0 | 28.6275
387 | 0 | 3.3112 | 11.4908 | 28.882 | 0 | 43.684 | 0 | 0 | 28.882
388 | 0 | 3.6466 | 10.9626 | 26.4434 | 0 | 41.0526 | 0 | 0 | 26.4434
389 | 0 | 3.4808 | 10.8707 | 27.9837 | 0 | 42.3353 | 0 | 0 | 27.9837
390 | 0 | 3.8823 | 11.0836 | 37.1355 | 0 | 52.1013 | 0 | 0 | 37.1355
391 | 0 | 3.5898 | 12.8582 | 28.4755 | 0 | 44.9234 | 0 | 0 | 28.4755
392 | 0 | 3.7903 | 11.953 | 26.9014 | 12.8161 | 55.4607 | 0 | 0 | 39.7175
393 | 0 | 2.8605 | 9.6884 | 30.8854 | 13.1061 | 56.5404 | 0 | 0 | 43.9915
394 | 0 | 3.9965 | 8.2993 | 26.5362 | 11.9201 | 50.752 | 0 | 0 | 38.4562
395 | 0 | 3.1348 | 7.9455 | 32.9891 | 5.6259 | 49.6953 | 0 | 0 | 38.615
396 | 0 | 3.5867 | 7.4077 | 27.7744 | 15.1252 | 53.894 | 0 | 0 | 42.8996
397 | 0 | 3.4662 | 6.4451 | 25.1165 | 2.7819 | 37.8097 | 0 | 0 | 27.8984
398 | 0 | 3.2618 | 5.51 | 17.635 | 16.2405 | 42.6473 | 0 | 0 | 33.8755
399 | 0 | 3.1004 | 6.2937 | 28.6432 | 16.7638 | 54.8011 | 0 | 0 | 45.4069
400 | 0 | 3.4389 | 6.4082 | 29.3046 | 18.5599 | 57.7115 | 0 | 0 | 47.8644
401 | 0 | 3.0791 | 6.2564 | 18.9086 | 11.6433 | 39.8875 | 0 | 0 | 30.5519
402 | 0 | 3.8884 | 5.3672 | 23.7625 | 22.6212 | 55.6393 | 0 | 0 | 46.3837
403 | 0 | 3.2558 | 4.736 | 29.8037 | 11.0698 | 48.8653 | 0 | 0 | 40.8735
404 | 0 | 3.0886 | 4.0947 | 19.4599 | 0 | 26.6431 | 0 | 0 | 19.4599
405 | 0 | 3.1702 | 3.6936 | 25.8481 | 0 | 32.712 | 0 | 0 | 25.8481
406 | 0 | 3.4919 | 4.028 | 25.161 | 0 | 32.6809 | 0 | 0 | 25.161
407 | 0 | 3.963 | 5.5067 | 25.1178 | 0 | 34.5875 | 0 | 0 | 25.1178
408 | 0 | 3.1936 | 6.313 | 29.8766 | 0 | 39.3833 | 0 | 0 | 29.8766
409 | 0 | 3.4734 | 7.6973 | 32.6216 | 0 | 43.7923 | 0 | 0 | 32.6216
410 | 0 | 3.209 | 6.8669 | 28.5986 | 0 | 38.6746 | 0 | 200 | 228.5986
411 | 0 | 3.6736 | 5.4257 | 24.9925 | 0 | 34.0918 | 0 | 0 | 24.9925
412 | 0 | 3.4579 | 7.0556 | 30.1636 | 0 | 40.6771 | 0 | 0 | 30.1636
413 | 0 | 3.0416 | 9.473 | 26.6804 | 0 | 39.1951 | 0 | 0 | 26.6804
414 | 0 | 3.1937 | 9.7773 | 35.4311 | 0 | 48.4022 | 0 | 0 | 35.4311
415 | 0 | 2.7239 | 9.6164 | 27.2988 | 0 | 39.639 | 0 | 0 | 27.2988
416 | 0 | 3.0248 | 9.2798 | 28.1607 | 18.53 | 58.9953 | 0 | 0 | 46.6907
417 | 0 | 2.621 | 8.7378 | 28.5549 | 7.0203 | 46.9339 | 0 | 0 | 35.5752
418 | 0 | 3.6723 | 8.7053 | 35.1788 | 10.0108 | 57.5672 | 0 | 0 | 45.1896
419 | 0 | 2.9224 | 8.2073 | 31.7459 | 7.9238 | 50.7994 | 0 | 0 | 39.6697
420 | 0 | 3.3122 | 7.7111 | 29.0604 | 13.6328 | 53.7165 | 0 | 0 | 42.6932
421 | 0 | 3.0602 | 7.4211 | 27.2943 | 8.2387 | 46.0143 | 0 | 0 | 35.533
422 | 0 | 3.4391 | 7.8098 | 33.3574 | 10.1928 | 54.7991 | 200 | 0 | 243.5502
423 | 0 | 3.3522 | 9.2133 | 34.358 | 4.3259 | 51.2494 | 0 | 0 | 38.6839
424 | 0 | 3.3035 | 9.1539 | 25.6164 | 9.9634 | 48.0371 | 0 | 0 | 35.5798
425 | 0 | 3.3407 | 9.6778 | 23.4511 | 12.6484 | 49.118 | 0 | 0 | 36.0995
426 | 0 | 2.9931 | 9.3762 | 34.3868 | 20.4981 | 67.2542 | 0 | 0 | 54.8848
427 | 0 | 3.0957 | 7.4964 | 25.6227 | 14.9641 | 51.1788 | 0 | 0 | 40.5868
428 | 0 | 3.5807 | 6.697 | 28.6639 | 0 | 38.9415 | 0 | 0 | 28.6639
429 | 0 | 3.4047 | 6.3598 | 31.2309 | 0 | 40.9954 | 0 | 0 | 31.2309
430 | 0 | 3.1705 | 6.2788 | 21.9569 | 0 | 31.4062 | 0 | 0 | 21.9569
431 | 0 | 3.2314 | 6.7239 | 25.6488 | 0 | 35.604 | 0 | 0 | 25.6488
432 | 0 | 2.9092 | 7.5223 | 27.8855 | 0 | 38.317 | 0 | 0 | 27.8855
433 | 0 | 2.9677 | 9.6247 | 31.0568 | 0 | 43.6492 | 0 | 0 | 31.0568
434 | 0 | 2.9831 | 12.3224 | 23.5638 | 0 | 38.8693 | 0 | 200 | 223.5638
435 | 0 | 3.2796 | 10.9171 | 29.576 | 0 | 43.7727 | 0 | 0 | 29.576
436 | 0 | 3.6569 | 10.2086 | 22.1916 | 0 | 36.057 | 0 | 0 | 22.1916
437 | 0 | 2.5607 | 9.8923 | 28.8184 | 0 | 41.2714 | 0 | 0 | 28.8184
438 | 0 | 3.2325 | 9.6322 | 31.8114 | 0 | 44.6761 | 0 | 0 | 31.8114
439 | 0 | 3.542 | 9.1006 | 26.8685 | 0 | 39.5111 | 0 | 0 | 26.8685
440 | 0 | 3.3017 | 9.7596 | 19.5882 | 10.0788 | 42.7283 | 0 | 0 | 29.667
441 | 0 | 3.6743 | 8.8736 | 32.4562 | 19.5522 | 64.5564 | 0 | 0 | 52.0084
442 | 0 | 3.3638 | 8.2316 | 28.2258 | 15.9226 | 55.7438 | 0 | 0 | 44.1484
443 | 0 | 3.5504 | 7.9455 | 29.0512 | 8.0996 | 48.6467 | 0 | 0 | 37.1508
444 | 0 | 3.9158 | 8.0144 | 29.5155 | 18.2212 | 59.6669 | 0 | 0 | 47.7366
445 | 0 | 3.9853 | 8.0422 | 31.3436 | 13.3074 | 56.6784 | 0 | 0 | 44.651
446 | 0 | 3.4908 | 7.8919 | 30.9994 | 12.4526 | 54.8347 | 0 | 0 | 43.4521
447 | 0 | 3.3077 | 8.6981 | 28.946 | 11.4339 | 52.3857 | 0 | 0 | 40.3799
448 | 0 | 3.296 | 8.6805 | 30.6492 | 11.077 | 53.7026 | 0 | 0 | 41.7261
449 | 0 | 3.1598 | 8.9935 | 22.1808 | 9.7896 | 44.1236 | 0 | 0 | 31.9703
450 | 0 | 3.3708 | 8.374 | 31.4083 | 12.3088 | 55.4618 | 0 | 0 | 43.717
451 | 0 | 2.9126 | 6.3902 | 30.7365 | 16.5489 | 56.5882 | 0 | 0 | 47.2854
452 | 0 | 3.9961 | 5.6628 | 33.1457 | 0 | 42.8047 | 0 | 0 | 33.1457
453 | 0 | 3.4305 | 5.8087 | 24.3136 | 0 | 33.5527 | 0 | 0 | 24.3136
454 | 0 | 3.144 | 5.4298 | 34.9431 | 0 | 43.5169 | 0 | 0 | 34.9431
455 | 0 | 3.7091 | 5.8072 | 27.0448 | 0 | 36.5611 | 0 | 0 | 27.0448
456 | 0 | 3.0568 | 6.3548 | 32.6608 | 0 | 42.0723 | 0 | 0 | 32.6608
457 | 0 | 3.6435 | 6.5811 | 32.6593 | 0 | 42.884 | 0 | 0 | 32.6593
458 | 0 | 3.3484 | 3.7288 | 22.2466 | 0 | 29.3238 | 0 | 0 | 22.2466
459 | 0 | 3.2501 | 6.1377 | 27.7585 | 0 | 37.1463 | 0 | 0 | 27.7585
460 | 0 | 2.9799 | 8.182 | 19.481 | 0 | 30.6429 | 0 | 200 | 219.481
461 | 0 | 3.7189 | 10.6167 | 33.4539 | 0 | 47.7895 | 0 | 0 | 33.4539
462 | 0 | 3.3309 | 10.4817 | 25.7861 | 0 | 39.5987 | 0 | 0 | 25.7861
463 | 0 | 2.3629 | 10.1885 | 27.1068 | 0 | 39.6582 | 0 | 0 | 27.1068
464 | 0 | 3.3608 | 9.9906 | 22.0963 | 18.7759 | 54.2236 | 0 | 0 | 40.8722
465 | 0 | 3.3318 | 9.5585 | 24.3381 | 14.5617 | 51.79 | 0 | 0 | 38.8998
466 | 0 | 3.4958 | 8.6428 | 32.568 | 14.4029 | 59.1095 | 0 | 0 | 46.9709
467 | 0 | 3.1883 | 7.0745 | 31.6172 | 18.9723 | 60.8522 | 0 | 0 | 50.5895
468 | 0 | 3.0291 | 5.5904 | 30.5473 | 15.9143 | 55.0811 | 0 | 0 | 46.4616
469 | 0 | 3.507 | 5.8383 | 29.8436 | 8.4204 | 47.6093 | 0 | 0 | 38.264
470 | 0 | 3.3908 | 6.2298 | 34.1328 | 12.8288 | 56.5823 | 0 | 0 | 46.9616
471 | 0 | 3.3162 | 6.1024 | 25.7638 | 19.5545 | 54.7369 | 0 | 0 | 45.3184
472 | 0 | 3.7657 | 6.2322 | 38.937 | 7.5643 | 56.4994 | 0 | 0 | 46.5014
473 | 0 | 2.6594 | 6.8861 | 29.9988 | 13.8672 | 53.4115 | 0 | 0 | 43.866
474 | 0 | 2.9782 | 7.7729 | 29.4498 | 15.6654 | 55.8664 | 0 | 0 | 45.1152
475 | 0 | 4.1626 | 7.2203 | 21.7011 | 10.1656 | 43.2496 | 0 | 0 | 31.8667
476 | 0 | 3.4996 | 7.667 | 29.4772 | 0 | 40.6438 | 0 | 0 | 29.4772
477 | 0 | 3.4265 | 6.2819 | 28.5616 | 0 | 38.27 | 0 | 0 | 28.5616
478 | 0 | 3.461 | 6.0227 | 25.0183 | 0 | 34.502 | 0 | 0 | 25.0183
479 | 0 | 3.0874 | 6.1834 | 27.6388 | 0 | 36.9096 | 0 | 0 | 27.6388
480 | 0 | 3.0017 | 6.6445 | 33.5992 | 0 | 43.2455 | 0 | 0 | 33.5992
481 | 0 | 3.2863 | 6.255 | 25.0849 | 0 | 34.6263 | 0 | 0 | 25.0849
482 | 0 | 3.4352 | 3.842 | 28.2249 | 0 | 35.5022 | 200 | 0 | 228.2249
483 | 0 | 2.8382 | 5.6212 | 26.7338 | 0 | 35.1931 | 0 | 0 | 26.7338
484 | 0 | 4.0857 | 6.4578 | 37.3053 | 0 | 47.8489 | 0 | 0 | 37.3053
485 | 0 | 3.1661 | 8.1221 | 35.9388 | 0 | 47.227 | 0 | 0 | 35.9388
486 | 0 | 3.3468 | 7.7695 | 35.081 | 0 | 46.1973 | 0 | 0 | 35.081
487 | 0 | 3.3879 | 7.9795 | 29.5625 | 0 | 40.9299 | 0 | 200 | 229.5625
488 | 0 | 3.5335 | 7.7676 | 36.8225 | 21.9687 | 70.0923 | 0 | 0 | 58.7912
489 | 0 | 3.3934 | 7.9862 | 24.543 | 11.0817 | 47.0043 | 0 | 0 | 35.6246
490 | 0 | 3.3769 | 7.7923 | 32.5349 | 15.3945 | 59.0987 | 0 | 0 | 47.9294
491 | 0 | 3.4417 | 8.1192 | 25.8164 | 15.1511 | 52.5284 | 0 | 0 | 40.9674
492 | 0 | 2.8406 | 9.021 | 34.4578 | 13.7391 | 60.0584 | 0 | 0 | 48.1968
493 | 0 | 3.066 | 8.9983 | 20.8415 | 13.6251 | 46.5309 | 0 | 0 | 34.4666
494 | 0 | 2.6928 | 8.8176 | 32.3668 | 18.6957 | 62.573 | 0 | 0 | 51.0626
495 | 0 | 3.5291 | 8.0632 | 28.2306 | 13.5979 | 53.4207 | 0 | 0 | 41.8285
496 | 0 | 3.1109 | 8.4762 | 25.7343 | 23.8597 | 61.1811 | 0 | 0 | 49.594
497 | 0 | 3.4433 | 8.5844 | 24.9248 | 22.864 | 59.8165 | 0 | 0 | 47.7888
498 | 0 | 3.3507 | 7.1015 | 26.9363 | 15.4951 | 52.8837 | 0 | 0 | 42.4315
499 | 0 | 3.0832 | 6.3133 | 30.4298 | 11.7372 | 51.5635 | 0 | 0 | 42.167
500 | 0 | 3.0129 | 5.6561 | 31.6926 | 0 | 40.3616 | 0 | 0 | 31.6926
501 | 0 | 3.3963 | 5.6327 | 32.3568 | 0 | 41.3858 | 0 | 0 | 32.3568
502 | 0 | 3.6036 | 5.7161 | 28.9903 | 0 | 38.3099 | 0 | 0 | 28.9903
503 | 0 | 3.5115 | 6.1558 | 35.4996 | 0 | 45.1669 | 0 | 0 | 35.4996
504 | 0 | 3.1121 | 6.7161 | 37.1881 | 0 | 47.0163 | 0 | 0 | 37.1881
505 | 0 | 3.2541 | 8.6103 | 32.0932 | 0 | 43.9576 | 0 | 0 | 32.0932
506 | 0 | 3.2651 | 11.1533 | 23.4575 | 0 | 37.8759 | 0 | 0 | 23.4575
507 | 0 | 2.9808 | 9.6057 | 34.6788 | 0 | 47.2654 | 0 | 0 | 34.6788
508 | 0 | 3.3633 | 8.5636 | 26.4522 | 0 | 38.3791 | 0 | 0 | 26.4522
509 | 0 | 3.2649 | 8.4946 | 27.7879 | 0 | 39.5474 | 0 | 0 | 27.7879
510 | 0 | 3.4727 | 8.1808 | 37.4635 | 0 | 49.117 | 0 | 0 | 37.4635
511 | 0 | 3.6498 | 7.8481 | 28.4818 | 0 | 39.9797 | 0 | 0 | 28.4818
512 | 0 | 2.9836 | 7.7718 | 33.504 | 19.056 | 63.3153 | 0 | 200 | 252.56
513 | 0 | 4.1099 | 7.3118 | 29.6726 | 21.2909 | 62.3852 | 0 | 0 | 50.9635
514 | 0 | 3.8598 | 6.7429 | 30.613 | 9.1887 | 50.4044 | 0 | 0 | 39.8017
515 | 0 | 3.1349 | 6.1128 | 23.6629 | 1.9438 | 34.8544 | 0 | 0 | 25.6067
516 | 0 | 2.9501 | 5.3602 | 28.4294 | 20.4276 | 57.1673 | 0 | 0 | 48.857
517 | 0 | 3.45 | 4.4931 | 31.5997 | 11.2962 | 50.839 | 0 | 0 | 42.8959
518 | 0 | 3.0837 | 4.4422 | 32.8697 | 17.9914 | 58.3871 | 0 | 0 | 50.8611
519 | 0 | 3.2958 | 5.0057 | 24.1338 | 7.4199 | 39.8552 | 0 | 0 | 31.5537
520 | 0 | 3.6102 | 4.704 | 32.2277 | 13.604 | 54.1459 | 0 | 0 | 45.8317
521 | 0 | 3.2172 | 3.9755 | 29.5831 | 4.3976 | 41.1735 | 0 | 0 | 33.9808
522 | 0 | 3.5977 | 2.9172 | 24.6606 | 26.3816 | 57.5571 | 0 | 0 | 51.0422
523 | 0 | 3.8518 | 2.2713 | 26.1442 | 22.9175 | 55.1848 | 0 | 0 | 49.0618
524 | 0 | 3.3493 | 2.273 | 28.4429 | 0 | 34.0652 | 0 | 0 | 28.4429
525 | 0 | 3.749 | 2.3201 | 28.7806 | 0 | 34.8497 | 0 | 0 | 28.7806
526 | 0 | 3.4076 | 2.8222 | 35.0889 | 0 | 41.3187 | 0 | 0 | 35.0889
527 | 0 | 2.8702 | 3.3158 | 27.3671 | 0 | 33.5531 | 0 | 0 | 27.3671
528 | 0 | 3.5751 | 3.8139 | 38.4743 | 0 | 45.8633 | 0 | 0 | 38.4743
529 | 0 | 3.5172 | 5.4655 | 22.8722 | 0 | 31.8549 | 0 | 0 | 22.8722
530 | 0 | 3.5739 | 8.4256 | 26.6235 | 0 | 38.623 | 0 | 0 | 26.6235
531 | 0 | 2.8809 | 7.6387 | 19.6632 | 0 | 30.1827 | 0 | 0 | 19.6632
532 | 0 | 3.6539 | 7.8096 | 29.835 | 0 | 41.2985 | 0 | 0 | 29.835
533 | 0 | 3.6202 | 8.0054 | 24.3884 | 0 | 36.014 | 0 | 0 | 24.3884
534 | 0 | 3.3231 | 7.6729 | 22.2841 | 0 | 33.28 | 0 | 0 | 22.2841
535 | 0 | 3.4165 | 7.1113 | 30.2185 | 0 | 40.7463 | 0 | 0 | 30.2185
536 | 0 | 3.3854 | 6.8807 | 34.3226 | 9.9098 | 54.4985 | 0 | 0 | 44.2324
537 | 0 | 2.8508 | 6.2933 | 28.0526 | 11.1884 | 48.3852 | 0 | 0 | 39.2411
538 | 0 | 3.3764 | 6.0662 | 28.7199 | 19.3979 | 57.5605 | 0 | 0 | 48.1178
539 | 0 | 2.765 | 5.3274 | 24.7998 | 20.2175 | 53.1096 | 0 | 0 | 45.0172
540 | 0 | 3.283 | 4.071 | 36.5247 | 11.661 | 55.5396 | 0 | 0 | 48.1857
541 | 0 | 3.2522 | 2.3299 | 29.4316 | 9.9919 | 45.0056 | 0 | 0 | 39.4235
542 | 0 | 3.0917 | 2.3888 | 31.4492 | 4.9815 | 41.9111 | 200 | 0 | 236.4306
543 | 0 | 2.944 | 2.0862 | 33.4726 | 14.7353 | 53.238 | 0 | 0 | 48.2079
544 | 0 | 3.8968 | 1.9886 | 33.6831 | 5.7053 | 45.2738 | 0 | 0 | 39.3884
545 | 0 | 3.3813 | 2.2272 | 23.9156 | 22.0718 | 51.596 | 0 | 0 | 45.9874
546 | 0 | 3.3367 | 2.1199 | 38.1041 | 16.8335 | 60.3942 | 0 | 0 | 54.9375
547 | 0 | 3.2037 | 1.5861 | 26.4877 | 9.6471 | 40.9245 | 0 | 0 | 36.1348
548 | 0 | 2.8634 | 1.239 | 26.3085 | 0 | 30.411 | 0 | 0 | 26.3085
549 | 0 | 3.056 | 1.0185 | 26.6251 | 0 | 30.6996 | 0 | 0 | 26.6251
550 | 0 | 3.4954 | 1.0722 | 34.3396 | 0 | 38.9072 | 0 | 0 | 34.3396
551 | 0 | 2.9849 | 1.1947 | 31.6426 | 0 | 35.8221 | 0 | 0 | 31.6426
552 | 0 | 3.5521 | 1.2542 | 33.4594 | 0 | 38.2657 | 0 | 0 | 33.4594
553 | 0 | 3.1225 | 2.7569 | 30.141 | 0 | 36.0204 | 0 | 0 | 30.141
554 | 0 | 3.287 | 4.3028 | 29.2071 | 0 | 36.7969 | 0 | 0 | 29.2071
555 | 0 | 2.9454 | 3.0702 | 31.9416 | 0 | 37.9571 | 0 | 0 | 31.9416
556 | 0 | 3.5678 | 3.834 | 30.5551 | 0 | 37.9569 | 0 | 0 | 30.5551
557 | 0 | 2.9978 | 4.3714 | 29.2203 | 0 | 36.5894 | 0 | 0 | 29.2203
558 | 0 | 3.9417 | 3.609 | 35.2845 | 0 | 42.8352 | 0 | 0 | 35.2845
559 | 0 | 3.8941 | 3.5748 | 30.8354 | 0 | 38.3043 | 0 | 0 | 30.8354
560 | 0 | 3.0043 | 3.385 | 34.8805 | 17.3943 | 58.6641 | 0 | 0 | 52.2748
561 | 0 | 3.4014 | 2.8303 | 19.901 | 14.5563 | 40.689 | 0 | 0 | 34.4573
562 | 0 | 3.416 | 2.2768 | 29.4807 | 18.3795 | 53.5529 | 0 | 0 | 47.8602
563 | 0 | 3.096 | 1.9239 | 33.11 | 22.6396 | 60.7694 | 0 | 200 | 255.7495
564 | 0 | 3.3349 | 1.3773 | 23.9715 | 20.6178 | 49.3015 | 0 | 0 | 44.5893
565 | 0 | 3.7297 | 2.3299 | 26.6655 | 12.6362 | 45.3612 | 0 | 0 | 39.3016
566 | 0 | 3.7616 | 2.3888 | 34.326 | 16.2824 | 56.7588 | 0 | 0 | 50.6084
567 | 0 | 3.0694 | 2.0295 | 34.6411 | 26.2584 | 65.9984 | 0 | 0 | 60.8995
568 | 0 | 3.2735 | 3.2838 | 35.8713 | 16.4324 | 58.861 | 0 | 0 | 52.3037
569 | 0 | 3.6661 | 2.607 | 24.4493 | 11.9854 | 42.7078 | 0 | 0 | 36.4347
570 | 0 | 2.8689 | 2.1199 | 28.4211 | 27.5754 | 60.9852 | 0 | 0 | 55.9964
571 | 0 | 3.2992 | 1.5861 | 32.4206 | 14.3872 | 51.6931 | 0 | 0 | 46.8078
572 | 0 | 3.377 | 1.239 | 30.2214 | 0 | 34.8374 | 0 | 0 | 30.2214
573 | 0 | 3.1156 | 1.3506 | 30.6821 | 0 | 35.1483 | 0 | 0 | 30.6821
574 | 0 | 2.9388 | 1.4556 | 19.7733 | 0 | 24.1677 | 0 | 0 | 19.7733
575 | 0 | 3.4771 | 1.9364 | 29.8276 | 0 | 35.2411 | 0 | 0 | 29.8276
576 | 0 | 3.9517 | 2.6046 | 29.3929 | 0 | 35.9491 | 0 | 0 | 29.3929
577 | 0 | 3.3243 | 3.6395 | 27.8476 | 0 | 34.8114 | 0 | 0 | 27.8476
578 | 0 | 3.1697 | 7.354 | 26.4636 | 0 | 36.9872 | 0 | 0 | 26.4636
579 | 0 | 3.0239 | 7.0649 | 23.5852 | 0 | 33.674 | 0 | 0 | 23.5852
580 | 0 | 4.394 | 7.0556 | 22.7515 | 0 | 34.2011 | 0 | 0 | 22.7515
581 | 0 | 2.3563 | 7.4463 | 29.1842 | 0 | 38.9869 | 0 | 0 | 29.1842
582 | 0 | 3.4028 | 6.8746 | 26.3707 | 0 | 36.6481 | 0 | 0 | 26.3707
583 | 0 | 3.3798 | 6.8166 | 25.1949 | 0 | 35.3914 | 0 | 0 | 25.1949
584 | 0 | 3.3783 | 6.8122 | 24.3991 | 17.155 | 51.7446 | 0 | 0 | 41.5541
585 | 0 | 3.257 | 6.4291 | 26.0382 | 20.4127 | 56.137 | 0 | 0 | 46.4509
586 | 0 | 3.7003 | 5.8632 | 28.3126 | 4.4786 | 42.3548 | 0 | 0 | 32.7913
587 | 0 | 2.9544 | 5.262 | 25.4286 | 9.1574 | 42.8024 | 0 | 0 | 34.586
588 | 0 | 3.3926 | 4.3743 | 31.04 | 16.5987 | 55.4056 | 0 | 0 | 47.6387
589 | 0 | 3.1618 | 3.4283 | 27.1994 | 19.0212 | 52.8108 | 0 | 0 | 46.2206
590 | 0 | 3.3452 | 3.3744 | 31.2111 | 12.6925 | 50.6233 | 0 | 0 | 43.9036
591 | 0 | 2.6694 | 4.0611 | 30.835 | 12.7511 | 50.3166 | 0 | 0 | 43.586
592 | 0 | 3.3758 | 3.7572 | 33.5129 | 16.9544 | 57.6004 | 0 | 0 | 50.4673
593 | 0 | 3.3904 | 3.2913 | 28.993 | 17.9088 | 53.5835 | 0 | 0 | 46.9018
594 | 0 | 3.6928 | 3.14 | 25.245 | 6.5764 | 38.6543 | 0 | 0 | 31.8215
595 | 0 | 3.0361 | 2.4685 | 26.0894 | 9.912 | 41.506 | 0 | 0 | 36.0014
596 | 0 | 2.8626 | 2.7067 | 32.1708 | 0 | 37.7401 | 0 | 0 | 32.1708
597 | 0 | 2.5115 | 3.3704 | 26.9408 | 0 | 32.8227 | 0 | 0 | 26.9408
598 | 0 | 3.6659 | 3.7064 | 23.3208 | 0 | 30.6931 | 0 | 0 | 23.3208
599 | 0 | 2.9799 | 4.1272 | 23.849 | 0 | 30.9561 | 0 | 0 | 23.849
600 | 0 | 3.53 | 4.7007 | 26.3956 | 0 | 34.6262 | 0 | 0 | 26.3956
601 | 0 | 2.8615 | 6.3785 | 24.1461 | 0 | 33.3861 | 0 | 0 | 24.1461
602 | 0 | 3.1031 | 9.1075 | 29.7635 | 0 | 41.9741 | 0 | 0 | 29.7635
603 | 0 | 3.2231 | 8.3763 | 30.1806 | 0 | 41.78 | 200 | 0 | 230.1806
604 | 0 | 3.3141 | 8.3579 | 34.3061 | 0 | 45.9781 | 0 | 0 | 34.3061
605 | 0 | 2.9926 | 9.0537 | 35.7783 | 0 | 47.8246 | 0 | 0 | 35.7783
606 | 0 | 3.2138 | 8.9791 | 25.6449 | 0 | 37.8377 | 0 | 200 | 225.6449
607 | 0 | 3.0842 | 8.8059 | 20.5303 | 0 | 32.4204 | 0 | 0 | 20.5303
608 | 0 | 3.1412 | 8.4572 | 27.5006 | 15.5215 | 54.6205 | 0 | 0 | 43.0221
609 | 0 | 3.4197 | 7.9229 | 31.0826 | 26.1186 | 68.5439 | 0 | 0 | 57.2012
610 | 0 | 3.4722 | 7.0812 | 21.6724 | 9.5092 | 41.735 | 0 | 0 | 31.1815
611 | 0 | 3.8746 | 6.3092 | 30.0426 | 24.9731 | 65.1994 | 0 | 0 | 55.0157
612 | 0 | 3.9939 | 6.0427 | 19.603 | 19.1564 | 48.7959 | 0 | 0 | 38.7594
613 | 0 | 3.066 | 5.3804 | 31.4348 | 14.7766 | 54.6578 | 0 | 0 | 46.2114
614 | 0 | 3.134 | 4.8529 | 25.5772 | 16.3513 | 49.9154 | 0 | 0 | 41.9285
615 | 0 | 3.0003 | 5.3492 | 19.6986 | 12.6551 | 40.7031 | 0 | 0 | 32.3537
616 | 0 | 3.2198 | 5.0827 | 29.6578 | 9.6227 | 47.583 | 0 | 0 | 39.2805
617 | 0 | 3.9627 | 4.6598 | 29.0311 | 18.9409 | 56.5945 | 0 | 0 | 47.972
618 | 0 | 3.8528 | 3.6968 | 31.6594 | 3.4322 | 42.6411 | 0 | 0 | 35.0916
619 | 0 | 3.1974 | 1.9531 | 29.0595 | 22.1711 | 56.3811 | 0 | 0 | 51.2306
620 | 0 | 3.4289 | 1.5255 | 31.4108 | 0 | 36.3651 | 0 | 0 | 31.4108
621 | 0 | 3.1073 | 3.1941 | 30.1674 | 0 | 36.4688 | 0 | 0 | 30.1674
622 | 0 | 3.5396 | 3.8489 | 27.2466 | 0 | 34.6351 | 0 | 0 | 27.2466
623 | 0 | 3.4294 | 3.5232 | 31.0404 | 0 | 37.993 | 0 | 0 | 31.0404
624 | 0 | 3.7568 | 3.6648 | 27.1061 | 0 | 34.5277 | 0 | 0 | 27.1061
625 | 0 | 3.1068 | 3.5619 | 25.322 | 0 | 31.9907 | 0 | 0 | 25.322
626 | 0 | 3.2567 | 2.1992 | 34.7981 | 0 | 40.254 | 0 | 0 | 34.7981
627 | 0 | 3.6322 | 1.9945 | 23.1989 | 0 | 28.8256 | 0 | 0 | 23.1989
628 | 0 | 2.7743 | 4.254 | 27.2568 | 0 | 34.2851 | 0 | 0 | 27.2568
629 | 0 | 3.5038 | 8.355 | 30.4834 | 0 | 42.3421 | 0 | 0 | 30.4834
630 | 0 | 3.4256 | 8.4053 | 29.3472 | 0 | 41.178 | 0 | 0 | 29.3472
631 | 0 | 3.1866 | 8.0883 | 31.6479 | 0 | 42.9228 | 0 | 0 | 31.6479
632 | 0 | 3.4181 | 8.0193 | 36.5064 | 11.7133 | 59.6571 | 0 | 0 | 48.2197
633 | 0 | 3.0737 | 7.1583 | 30.421 | 10.245 | 50.8981 | 0 | 0 | 40.666
634 | 0 | 3.3075 | 6.8953 | 25.8721 | 5.1133 | 41.1883 | 0 | 0 | 30.9855
635 | 0 | 3.1157 | 5.4061 | 27.7901 | 20.6407 | 56.9527 | 0 | 0 | 48.4308
636 | 0 | 3.2261 | 2.4393 | 27.0353 | 5.3258 | 38.0266 | 0 | 0 | 32.3611
637 | 0 | 2.8496 | 2.4752 | 26.4421 | 28.4889 | 60.2558 | 0 | 0 | 54.931
638 | 0 | 3.4998 | 2.0157 | 38.8958 | 20.2829 | 64.6942 | 0 | 0 | 59.1787
639 | 0 | 3.1698 | 2.2301 | 17.1409 | 12.7023 | 35.2432 | 0 | 0 | 29.8432
640 | 0 | 3.2013 | 2.9774 | 31.8453 | 22.087 | 60.111 | 0 | 0 | 53.9323
641 | 0 | 3.3334 | 4.4652 | 30.3855 | 9.3277 | 47.5117 | 0 | 0 | 39.7132
642 | 0 | 2.8131 | 3.2991 | 35.7947 | 8.4649 | 50.3718 | 0 | 0 | 44.2596
643 | 0 | 3.3522 | 2.0888 | 29.6905 | 13.3502 | 48.4816 | 0 | 0 | 43.0407
644 | 0 | 2.5618 | 1.4117 | 26.3463 | 0 | 30.3198 | 0 | 0 | 26.3463
645 | 0 | 3.1909 | 1.3651 | 28.7287 | 0 | 33.2847 | 0 | 0 | 28.7287
646 | 0 | 3.2291 | 1.2344 | 31.9707 | 0 | 36.4341 | 0 | 0 | 31.9707
647 | 0 | 2.8243 | 1.1264 | 26.4573 | 0 | 30.4081 | 0 | 0 | 26.4573
648 | 0 | 3.6136 | 1.1609 | 38.6188 | 0 | 43.3932 | 0 | 0 | 38.6188
649 | 0 | 3.1124 | 1.987 | 31.0334 | 0 | 36.1328 | 0 | 0 | 31.0334
650 | 0 | 3.29 | 2.1636 | 35.2486 | 0 | 40.7023 | 0 | 0 | 35.2486
651 | 0 | 3.5541 | 1.767 | 27.121 | 0 | 32.4421 | 0 | 0 | 27.121
652 | 0 | 2.8861 | 2.6204 | 29.3082 | 0 | 34.8147 | 0 | 0 | 29.3082
653 | 0 | 2.8984 | 5.3091 | 28.6285 | 0 | 36.836 | 0 | 0 | 28.6285
654 | 0 | 3.6936 | 5.3311 | 25.7937 | 0 | 34.8184 | 0 | 200 | 225.7937
655 | 0 | 3.3015 | 5.2524 | 24.7345 | 0 | 33.2884 | 0 | 0 | 24.7345
656 | 0 | 3.3585 | 4.7774 | 28.0652 | 16.1282 | 52.3292 | 0 | 0 | 44.1933
657 | 0 | 3.012 | 4.321 | 30.676 | 7.5921 | 45.6012 | 0 | 0 | 38.2682
658 | 0 | 3.458 | 4.2257 | 28.8031 | 12.5843 | 49.0712 | 0 | 0 | 41.3874
659 | 0 | 2.8788 | 3.742 | 34.3006 | 7.3469 | 48.2683 | 0 | 0 | 41.6475
660 | 0 | 3.7053 | 2.997 | 28.0485 | 18.677 | 53.4279 | 0 | 0 | 46.7255
661 | 0 | 3.2512 | 2.2781 | 25.0739 | 12.751 | 43.3542 | 0 | 0 | 37.8249
662 | 0 | 2.526 | 2.2196 | 28.5836 | 23.6774 | 57.0067 | 0 | 0 | 52.261
663 | 0 | 3.4368 | 2.2605 | 26.999 | 10.5811 | 43.2773 | 0 | 0 | 37.5801
664 | 0 | 2.9229 | 2.1706 | 29.6653 | 7.4599 | 42.2187 | 200 | 0 | 237.1252
665 | 0 | 3.438 | 2.1677 | 22.1692 | 3.3442 | 31.1192 | 0 | 0 | 25.5135
666 | 0 | 3.6247 | 2.1706 | 28.5402 | 6.5367 | 40.8722 | 0 | 0 | 35.0769
667 | 0 | 2.8407 | 1.5861 | 24.958 | 10.1734 | 39.5582 | 0 | 0 | 35.1314
668 | 0 | 3.2598 | 1.239 | 36.1082 | 0 | 40.607 | 0 | 0 | 36.1082
669 | 0 | 2.8732 | 1.0185 | 34.3977 | 0 | 38.2894 | 0 | 0 | 34.3977
670 | 0 | 3.1676 | 1.0722 | 29.1056 | 0 | 33.3454 | 0 | 0 | 29.1056
671 | 0 | 3.1039 | 1.1947 | 28.4642 | 0 | 32.7629 | 0 | 0 | 28.4642
672 | 0 | 2.8522 | 1.2542 | 34.7335 | 0 | 38.8399 | 0 | 0 | 34.7335
673 | 0 | 3.8218 | 2.7569 | 26.9206 | 0 | 33.4993 | 0 | 0 | 26.9206
674 | 0 | 3.4186 | 4.334 | 30.4782 | 0 | 38.2308 | 0 | 0 | 30.4782
675 | 0 | 3.2462 | 4.5242 | 28.3494 | 0 | 36.1197 | 0 | 0 | 28.3494
676 | 0 | 2.8983 | 5.2735 | 30.1916 | 0 | 38.3633 | 0 | 0 | 30.1916
677 | 0 | 2.8245 | 5.6293 | 28.6293 | 0 | 37.0832 | 0 | 0 | 28.6293
678 | 0 | 3.2895 | 5.7135 | 32.9765 | 0 | 41.9795 | 0 | 0 | 32.9765
679 | 0 | 3.6777 | 6.1535 | 24.2772 | 0 | 34.1085 | 0 | 0 | 24.2772
680 | 0 | 3.9295 | 6.538 | 27.635 | 8.5119 | 46.6143 | 0 | 0 | 36.1468
681 | 0 | 3.6319 | 6.4291 | 28.3218 | 5.6888 | 44.0716 | 0 | 0 | 34.0107
682 | 0 | 3.3129 | 5.8632 | 34.3417 | 8.496 | 52.0138 | 0 | 0 | 42.8377
683 | 0 | 2.9342 | 4.6729 | 41.3628 | 28.5071 | 77.477 | 0 | 0 | 69.8699
684 | 0 | 3.2664 | 4.071 | 20.038 | 12.3756 | 39.7509 | 0 | 0 | 32.4136
685 | 0 | 3.1961 | 3.7833 | 36.1419 | 13.6159 | 56.7372 | 0 | 0 | 49.7578
686 | 0 | 3.5858 | 3.7851 | 28.9789 | 5.1954 | 41.5452 | 0 | 0 | 34.1743
687 | 0 | 3.3402 | 4.3187 | 25.3871 | 20.7508 | 53.7969 | 0 | 0 | 46.1379
688 | 0 | 3.5815 | 5.1774 | 25.7195 | 23.1088 | 57.5871 | 0 | 0 | 48.8282
689 | 0 | 3.8632 | 5.4581 | 29.2247 | 24.4155 | 62.9615 | 0 | 0 | 53.6402
690 | 0 | 3.188 | 5.1445 | 23.0231 | 10.007 | 41.3626 | 0 | 0 | 33.0301
691 | 0 | 3.5422 | 5.4261 | 30.2826 | 6.9042 | 46.1551 | 0 | 0 | 37.1868
692 | 0 | 3.4268 | 4.6151 | 24.4988 | 0 | 32.5407 | 0 | 0 | 24.4988
693 | 0 | 2.8229 | 5.2287 | 30.8055 | 0 | 38.8571 | 0 | 0 | 30.8055
694 | 0 | 3.3503 | 5.1534 | 27.6854 | 0 | 36.189 | 0 | 0 | 27.6854
695 | 0 | 3.5741 | 5.9936 | 27.3404 | 0 | 36.908 | 0 | 0 | 27.3404
696 | 0 | 3.1769 | 6.313 | 34.6376 | 0 | 44.1276 | 0 | 0 | 34.6376
697 | 0 | 3.0006 | 9.7262 | 25.831 | 0 | 38.5578 | 0 | 0 | 25.831
698 | 0 | 3.23 | 12.2249 | 26.8909 | 0 | 42.3458 | 0 | 0 | 26.8909
699 | 0 | 3.7697 | 11.2449 | 28.3825 | 0 | 43.3972 | 0 | 200 | 228.3825
700 | 0 | 3.6806 | 10.1401 | 33.6378 | 0 | 47.4585 | 0 | 0 | 33.6378
701 | 0 | 3.5848 | 9.5429 | 22.4672 | 0 | 35.5949 | 0 | 0 | 22.4672
702 | 0 | 3.1006 | 8.6888 | 35.39 | 0 | 47.1794 | 0 | 0 | 35.39
703 | 0 | 3.2482 | 8.2165 | 40.2739 | 0 | 51.7386 | 0 | 0 | 40.2739
704 | 0 | 2.404 | 7.8403 | 30.2176 | 10.0935 | 50.5555 | 0 | 0 | 40.3111
705 | 0 | 3.0832 | 7.3797 | 30.3321 | 13.3593 | 54.1544 | 0 | 0 | 43.6914
706 | 0 | 3.0831 | 6.8782 | 29.5452 | 21.001 | 60.5075 | 0 | 0 | 50.5462
707 | 0 | 3.7919 | 6.6364 | 30.3853 | 16.2611 | 57.0748 | 0 | 0 | 46.6464
708 | 0 | 2.6375 | 6.8769 | 34.4828 | 11.4737 | 55.4709 | 0 | 0 | 45.9565
709 | 0 | 3.7996 | 6.8 | 33.1246 | 19.6999 | 63.4242 | 0 | 0 | 52.8245
710 | 0 | 3.3257 | 6.4956 | 23.8253 | 18.6858 | 52.3324 | 0 | 0 | 42.5111
711 | 0 | 3.0473 | 7.4959 | 25.6717 | 12.1074 | 48.3223 | 0 | 0 | 37.7791
712 | 0 | 3.3449 | 8.3018 | 34.9317 | 11.8283 | 58.4067 | 0 | 0 | 46.76
713 | 0 | 2.8017 | 8.4233 | 30.0768 | 9.0143 | 50.3161 | 0 | 0 | 39.0911
714 | 0 | 3.3479 | 7.5944 | 26.1801 | 15.7623 | 52.8847 | 0 | 0 | 41.9424
715 | 0 | 3.4557 | 5.919 | 34.9891 | 16.6576 | 61.0214 | 0 | 0 | 51.6467
716 | 0 | 3.3558 | 3.9212 | 28.7625 | 0 | 36.0394 | 0 | 0 | 28.7625
717 | 0 | 3.0292 | 3.3704 | 27.6442 | 0 | 34.0439 | 0 | 0 | 27.6442
718 | 0 | 3.2959 | 2.9026 | 24.1373 | 0 | 30.3357 | 0 | 0 | 24.1373
719 | 0 | 3.2063 | 2.2609 | 23.9933 | 0 | 29.4605 | 0 | 0 | 23.9933
720 | 0 | 3.5595 | 1.9596 | 34.2359 | 0 | 39.755 | 0 | 0 | 34.2359
721 | 0 | 3.5189 | 2.7569 | 25.8696 | 0 | 32.1454 | 0 | 0 | 25.8696
722 | 0 | 4.1086 | 5.2107 | 27.0007 | 0 | 36.32 | 0 | 0 | 27.0007
723 | 0 | 2.8594 | 5.2618 | 29.368 | 0 | 37.4892 | 0 | 0 | 29.368
724 | 0 | 3.1886 | 5.7533 | 26.95 | 0 | 35.8919 | 0 | 0 | 26.95
725 | 0 | 3.5257 | 6.5378 | 23.8102 | 0 | 33.8737 | 200 | 0 | 223.8102
726 | 0 | 3.4409 | 7.2374 | 23.2456 | 0 | 33.9239 | 0 | 0 | 23.2456
727 | 0 | 2.7675 | 7.5534 | 19.5995 | 0 | 29.9204 | 0 | 0 | 19.5995
728 | 0 | 3.132 | 7.8403 | 27.6908 | 15.6534 | 54.3166 | 0 | 0 | 43.3442
729 | 0 | 3.3427 | 7.3118 | 23.8027 | 8.7499 | 43.2071 | 0 | 0 | 32.5526
730 | 0 | 3.3223 | 9.1113 | 25.9221 | 10.8707 | 49.2264 | 0 | 200 | 236.7928
731 | 0 | 3.5505 | 7.9455 | 30.0677 | 6.9167 | 48.4804 | 0 | 0 | 36.9844
732 | 0 | 3.007 | 7.1802 | 33.1705 | 13.3996 | 56.7573 | 0 | 0 | 46.57
733 | 0 | 3.3351 | 6.4451 | 34.8696 | 11.3372 | 55.987 | 0 | 0 | 46.2068
734 | 0 | 3.3078 | 7.3991 | 24.2014 | 4.1908 | 39.0991 | 0 | 0 | 28.3922
735 | 0 | 3.6538 | 9.2992 | 24.5322 | 14.236 | 51.7212 | 0 | 0 | 38.7682
736 | 0 | 2.9235 | 9.5326 | 22.2916 | 16.6154 | 51.3632 | 0 | 0 | 38.9071
737 | 0 | 2.9144 | 9.9059 | 27.5797 | 8.2279 | 48.6279 | 0 | 0 | 35.8076
738 | 0 | 3.7685 | 8.1512 | 31.2721 | 6.0932 | 49.285 | 0 | 0 | 37.3653
739 | 0 | 2.7725 | 7.102 | 34.8301 | 15.9691 | 60.6737 | 0 | 0 | 50.7992
740 | 0 | 3.3487 | 6.0898 | 31.9679 | 0 | 41.4064 | 0 | 0 | 31.9679
741 | 0 | 3.2403 | 5.8751 | 26.9057 | 0 | 36.0211 | 0 | 0 | 26.9057
742 | 0 | 3.695 | 5.7965 | 18.6215 | 0 | 28.113 | 0 | 0 | 18.6215
743 | 0 | 3.6023 | 6.3181 | 37.4248 | 0 | 47.3453 | 0 | 0 | 37.4248
744 | 0 | 3.5379 | 6.7968 | 31.8545 | 0 | 42.1892 | 0 | 0 | 31.8545
745 | 0 | 3.0878 | 9.7262 | 27.7504 | 0 | 40.5643 | 0 | 0 | 27.7504
746 | 0 | 3.7529 | 12.9069 | 29.4674 | 0 | 46.1272 | 0 | 0 | 29.4674
747 | 0 | 3.3451 | 11.5728 | 21.0133 | 0 | 35.9311 | 0 | 0 | 21.0133
748 | 0 | 2.6914 | 10.757 | 26.8104 | 0 | 40.2587 | 0 | 0 | 26.8104
749 | 0 | 2.8008 | 11.3599 | 19.0031 | 0 | 33.1638 | 0 | 0 | 19.0031
750 | 0 | 3.0064 | 10.7207 | 30.8492 | 0 | 44.5763 | 0 | 0 | 30.8492
751 | 0 | 3.5373 | 10.6478 | 29.3011 | 0 | 43.4862 | 0 | 0 | 29.3011
752 | 0 | 3.2303 | 10.8563 | 24.548 | 12.2353 | 50.8699 | 0 | 200 | 236.7833
753 | 0 | 3.0855 | 10.3674 | 31.3489 | 22.7035 | 67.5054 | 0 | 0 | 54.0525
754 | 0 | 3.407 | 9.382 | 30.9632 | 18.5685 | 62.3207 | 0 | 0 | 49.5317
755 | 0 | 3.5406 | 8.6655 | 24.7851 | 11.7336 | 48.7248 | 0 | 0 | 36.5187
756 | 0 | 2.9958 | 8.3936 | 32.1706 | 5.2255 | 48.7855 | 0 | 0 | 37.3961
757 | 0 | 3.4813 | 7.776 | 27.0157 | 15.5631 | 53.8362 | 0 | 0 | 42.5789
758 | 0 | 2.8632 | 7.8098 | 23.6659 | 14.783 | 49.1219 | 0 | 0 | 38.4489
759 | 0 | 3.3298 | 8.2687 | 28.9975 | 19.9258 | 60.5218 | 0 | 0 | 48.9233
760 | 0 | 3.2695 | 8.3964 | 29.1449 | 12.9298 | 53.7407 | 0 | 0 | 42.0748
761 | 0 | 3.1846 | 8.5373 | 31.7845 | 19.4975 | 63.0038 | 0 | 0 | 51.2819
762 | 0 | 3.3662 | 6.5922 | 36.1459 | 18.1296 | 64.2339 | 0 | 0 | 54.2755
763 | 0 | 3.6147 | 5.2289 | 25.0912 | 12.6806 | 46.6155 | 0 | 0 | 37.7718
764 | 0 | 3.2208 | 5.1356 | 29.0436 | 0 | 37.3999 | 0 | 0 | 29.0436
765 | 0 | 2.5705 | 4.8247 | 29.1626 | 0 | 36.5579 | 0 | 0 | 29.1626
766 | 0 | 2.9419 | 4.5907 | 23.8339 | 0 | 31.3665 | 0 | 0 | 23.8339
767 | 0 | 3.6758 | 5.5067 | 27.2169 | 0 | 36.3994 | 0 | 0 | 27.2169
768 | 0 | 2.8483 | 6.6355 | 24.0932 | 0 | 33.577 | 0 | 0 | 24.0932
769 | 0 | 3.4622 | 8.4074 | 37.6227 | 0 | 49.4923 | 0 | 0 | 37.6227
770 | 0 | 3.2222 | 10.8611 | 22.4747 | 0 | 36.5579 | 0 | 0 | 22.4747
771 | 0 | 3.1077 | 9.114 | 25.3056 | 0 | 37.5273 | 0 | 0 | 25.3056
772 | 0 | 3.378 | 9.4546 | 30.016 | 0 | 42.8486 | 0 | 0 | 30.016
773 | 0 | 3.5437 | 9.5429 | 25.4587 | 0 | 38.5453 | 0 | 0 | 25.4587
774 | 0 | 3.0847 | 8.7614 | 25.1725 | 0 | 37.0185 | 0 | 0 | 25.1725
775 | 0 | 3.001 | 8.8059 | 20.1159 | 0 | 31.9227 | 0 | 0 | 20.1159
776 | 0 | 2.8663 | 8.2516 | 29.1097 | 19.9516 | 60.1791 | 0 | 0 | 49.0612
777 | 0 | 3.1037 | 8.1946 | 28.243 | 10.8509 | 50.3922 | 0 | 0 | 39.0939
778 | 0 | 2.9546 | 7.6903 | 27.9807 | 13.1178 | 51.7433 | 0 | 200 | 241.0984
779 | 0 | 3.0867 | 7.4219 | 27.8636 | 10.5395 | 48.9117 | 0 | 0 | 38.4031
780 | 0 | 3.4213 | 7.2561 | 28.0145 | 32.9157 | 71.6076 | 0 | 0 | 60.9302
781 | 0 | 3.4915 | 7.0662 | 22.6313 | 13.4419 | 46.6309 | 0 | 0 | 36.0732
782 | 0 | 2.8875 | 6.742 | 16.6219 | 27.0632 | 53.3147 | 0 | 0 | 43.6851
783 | 0 | 3.2348 | 7.4959 | 21.8505 | 3.5194 | 36.1006 | 0 | 0 | 25.37
784 | 0 | 3.4235 | 7.5443 | 26.9968 | 12.0577 | 50.0223 | 0 | 0 | 39.0545
785 | 0 | 3.4983 | 7.8531 | 28.3367 | 19.1658 | 58.8539 | 0 | 0 | 47.5025
786 | 0 | 2.5956 | 8.2626 | 29.012 | 16.0597 | 55.9298 | 0 | 0 | 45.0717
787 | 0 | 3.5376 | 5.9268 | 31.01 | 13.1467 | 53.6211 | 200 | 0 | 244.1567
788 | 0 | 2.7439 | 5.2281 | 27.0043 | 0 | 34.9763 | 0 | 0 | 27.0043
789 | 0 | 2.9874 | 4.9371 | 23.9091 | 0 | 31.8336 | 0 | 0 | 23.9091
790 | 0 | 3.4503 | 4.7975 | 26.7609 | 0 | 35.0086 | 0 | 0 | 26.7609
791 | 0 | 2.9432 | 5.0704 | 31.1597 | 0 | 39.1733 | 0 | 0 | 31.1597
792 | 0 | 3.2668 | 5.7663 | 23.9608 | 0 | 32.994 | 0 | 0 | 23.9608
793 | 0 | 3.5247 | 5.7072 | 27.5059 | 0 | 36.7378 | 0 | 0 | 27.5059
794 | 0 | 2.9941 | 2.4002 | 26.1358 | 0 | 31.5301 | 0 | 0 | 26.1358
795 | 0 | 2.8435 | 5.8369 | 31.3816 | 0 | 40.062 | 0 | 0 | 31.3816
796 | 0 | 3.4978 | 6.4247 | 20.1976 | 0 | 30.1202 | 0 | 0 | 20.1976
797 | 0 | 3.0255 | 9.8 | 22.75 | 0 | 35.5755 | 0 | 0 | 22.75
798 | 0 | 2.4597 | 9.6512 | 28.7945 | 0 | 40.9054 | 0 | 0 | 28.7945
799 | 0 | 3.5021 | 9.6157 | 29.0732 | 0 | 42.191 | 0 | 0 | 29.0732
800 | 0 | 3.3156 | 9.453 | 27.2968 | 14.3971 | 54.4624 | 0 | 0 | 41.6938
801 | 0 | 2.9374 | 8.7152 | 33.7678 | 1.7597 | 47.1801 | 0 | 0 | 35.5276
802 | 0 | 3.4211 | 9.0646 | 29.0779 | 13.9326 | 55.4963 | 0 | 0 | 43.0105
803 | 0 | 2.9324 | 8.8071 | 27.9192 | 8.8934 | 48.5521 | 0 | 0 | 36.8126
804 | 0 | 3.4035 | 8.1506 | 23.8237 | 23.901 | 59.2788 | 0 | 0 | 47.7247
805 | 0 | 3.3458 | 8.0663 | 23.5623 | 17.5237 | 52.4981 | 0 | 0 | 41.086
806 | 0 | 3.5935 | 7.7349 | 30.0458 | 7.5234 | 48.8977 | 0 | 200 | 237.5692
807 | 0 | 3.4783 | 7.7938 | 32.6008 | 14.3669 | 58.2398 | 0 | 0 | 46.9677
808 | 0 | 3.0433 | 8.7014 | 26.9676 | 3.4422 | 42.1546 | 0 | 0 | 30.4098
809 | 0 | 3.2425 | 9.9848 | 27.7847 | 20.9362 | 61.9482 | 0 | 0 | 48.7209
810 | 0 | 3.2151 | 9.7968 | 27.2535 | 20.8114 | 61.0768 | 0 | 0 | 48.0649
811 | 0 | 2.6566 | 8.7407 | 26.0038 | 21.4742 | 58.8753 | 0 | 0 | 47.478
812 | 0 | 2.7856 | 7.8434 | 18.8247 | 0 | 29.4538 | 0 | 0 | 18.8247
813 | 0 | 3.091 | 7.4561 | 23.5602 | 0 | 34.1073 | 0 | 0 | 23.5602
814 | 0 | 2.8491 | 6.8942 | 27.4282 | 0 | 37.1715 | 0 | 0 | 27.4282
815 | 0 | 2.8761 | 7.0269 | 30.2065 | 0 | 40.1095 | 0 | 0 | 30.2065
816 | 0 | 2.5881 | 7.5119 | 34.2735 | 0 | 44.3736 | 0 | 0 | 34.2735
817 | 0 | 2.8087 | 7.2947 | 21.6424 | 0 | 31.7458 | 0 | 0 | 21.6424
818 | 0 | 2.977 | 5.6565 | 24.5274 | 0 | 33.1609 | 0 | 0 | 24.5274
819 | 0 | 3.074 | 5.7007 | 27.9379 | 0 | 36.7126 | 0 | 0 | 27.9379
820 | 0 | 3.9119 | 7.4187 | 29.208 | 0 | 40.5386 | 0 | 0 | 29.208
821 | 0 | 3.2163 | 9.5533 | 25.0777 | 0 | 37.8473 | 0 | 0 | 25.0777
822 | 0 | 3.5356 | 9.6227 | 27.7651 | 0 | 40.9234 | 0 | 0 | 27.7651
823 | 0 | 3.3724 | 9.9977 | 28.5627 | 0 | 41.9327 | 0 | 0 | 28.5627
824 | 0 | 2.7093 | 9.5618 | 33.8307 | 13.3293 | 59.4311 | 0 | 0 | 47.16
825 | 0 | 2.7445 | 9.6085 | 29.6419 | 20.1106 | 62.1055 | 0 | 0 | 49.7525
826 | 0 | 2.5357 | 9.4567 | 28.0165 | 12.6346 | 52.6435 | 0 | 0 | 40.6511
827 | 0 | 3.4042 | 8.9473 | 28.1283 | 17.729 | 58.2088 | 0 | 0 | 45.8572
828 | 0 | 2.7499 | 8.5137 | 31.3705 | 13.0893 | 55.7235 | 0 | 0 | 44.4598
829 | 0 | 2.8193 | 8.5503 | 28.297 | 18.1743 | 57.8409 | 0 | 0 | 46.4712
830 | 0 | 3.358 | 8.5504 | 29.9177 | 14.1559 | 55.982 | 0 | 200 | 244.0736
831 | 0 | 3.0523 | 8.5354 | 24.355 | 12.2599 | 48.2026 | 0 | 0 | 36.6149
832 | 0 | 3.0851 | 8.9951 | 25.1798 | 20.9343 | 58.1943 | 0 | 0 | 46.1141
833 | 0 | 3.4863 | 9.5233 | 31.5137 | 20.4408 | 64.9641 | 0 | 0 | 51.9545
834 | 0 | 3.4184 | 8.3638 | 34.564 | 16.6565 | 63.0028 | 0 | 0 | 51.2205
835 | 0 | 3.0124 | 6.7077 | 31.1639 | 3.6319 | 44.5159 | 0 | 0 | 34.7958
836 | 0 | 3.4087 | 6.0898 | 31.2255 | 0 | 40.724 | 0 | 0 | 31.2255
837 | 0 | 3.2808 | 5.9559 | 26.4321 | 0 | 35.6688 | 0 | 0 | 26.4321
838 | 0 | 3.3715 | 6.118 | 23.7593 | 0 | 33.2488 | 0 | 0 | 23.7593
839 | 0 | 3.3898 | 7.0484 | 31.5968 | 0 | 42.035 | 0 | 0 | 31.5968
840 | 0 | 3.2238 | 8.2479 | 30.4644 | 0 | 41.9362 | 0 | 0 | 30.4644
841 | 0 | 3.8559 | 10.3348 | 22.7136 | 0 | 36.9043 | 0 | 0 | 22.7136
842 | 0 | 3.7627 | 13.9785 | 31.2066 | 0 | 48.9478 | 0 | 0 | 31.2066
843 | 0 | 3.0862 | 12.9661 | 18.8395 | 0 | 34.8918 | 0 | 0 | 18.8395
844 | 0 | 3.571 | 11.7166 | 30.6296 | 0 | 45.9172 | 0 | 0 | 30.6296
845 | 0 | 3.5756 | 11.8491 | 27.7787 | 0 | 43.2035 | 0 | 0 | 27.7787
846 | 0 | 2.8583 | 11.519 | 27.9395 | 0 | 42.3168 | 0 | 0 | 27.9395
847 | 0 | 3.505 | 11.6056 | 29.4204 | 0 | 44.5311 | 0 | 0 | 29.4204
848 | 0 | 3.5035 | 11.4731 | 31.7625 | 5.8062 | 52.5453 | 0 | 0 | 37.5687
849 | 0 | 3.3589 | 11.2501 | 29.7632 | 18.4171 | 62.7894 | 0 | 0 | 48.1803
850 | 0 | 2.7557 | 10.6 | 33.8228 | 21.1667 | 68.3452 | 200 | 200 | 454.9894
851 | 0 | 3.2228 | 9.8436 | 25.8051 | 16.6986 | 55.5701 | 0 | 0 | 42.5037
852 | 0 | 3.7698 | 9.6828 | 30.7143 | 1.6876 | 45.8545 | 0 | 0 | 32.4019
853 | 0 | 2.9196 | 10.3491 | 25.7153 | 15.3556 | 54.3396 | 0 | 0 | 41.071
854 | 0 | 3.2883 | 10.4381 | 23.2342 | 12.4036 | 49.3641 | 0 | 0 | 35.6377
855 | 0 | 2.8922 | 11.7894 | 30.8248 | 12.1232 | 57.6295 | 0 | 0 | 42.9479
856 | 0 | 3.1778 | 12.941 | 24.6084 | 5.3269 | 46.0541 | 0 | 0 | 29.9353
857 | 0 | 2.9652 | 14.3536 | 36.0116 | 14.8008 | 68.1312 | 0 | 0 | 50.8124
858 | 0 | 3.2452 | 13.8307 | 23.7469 | 7.0849 | 47.9077 | 0 | 0 | 30.8318
859 | 0 | 2.6982 | 12.5243 | 28.4601 | 18.0624 | 61.745 | 0 | 0 | 46.5226
860 | 0 | 3.2103 | 11.1209 | 28.1558 | 0 | 42.487 | 0 | 0 | 28.1558
861 | 0 | 3.0752 | 9.834 | 27.7353 | 0 | 40.6445 | 0 | 0 | 27.7353
862 | 0 | 3.8393 | 10.5392 | 23.2862 | 0 | 37.6647 | 0 | 0 | 23.2862
863 | 0 | 3.2402 | 11.1868 | 33.0772 | 0 | 47.5042 | 0 | 0 | 33.0772
864 | 0 | 2.6757 | 12.5207 | 35.2004 | 0 | 50.3969 | 0 | 0 | 35.2004
865 | 0 | 3.3076 | 16.523 | 23.5877 | 0 | 43.4182 | 0 | 0 | 23.5877
866 | 0 | 2.871 | 18.7521 | 41.5089 | 0 | 63.1319 | 0 | 200 | 241.5089
867 | 0 | 3.5392 | 16.1626 | 29.5932 | 0 | 49.295 | 0 | 0 | 29.5932
868 | 0 | 3.3358 | 13.91 | 30.1307 | 0 | 47.3765 | 0 | 0 | 30.1307
869 | 0 | 3.4539 | 13.736 | 24.4375 | 0 | 41.6275 | 0 | 0 | 24.4375
870 | 0 | 3.7828 | 13.1881 | 31.9131 | 0 | 48.884 | 0 | 0 | 31.9131
871 | 0 | 3.5807 | 13.0792 | 24.5555 | 0 | 41.2155 | 0 | 0 | 24.5555
872 | 0 | 3.4448 | 12.2957 | 26.6866 | 12.9594 | 55.3865 | 0 | 0 | 39.646
873 | 0 | 3.4189 | 12.3366 | 28.0785 | 19.8736 | 63.7076 | 0 | 0 | 47.9521
874 | 0 | 2.7354 | 11.8181 | 28.0446 | 12.8911 | 55.4891 | 0 | 0 | 40.9357
875 | 0 | 2.7234 | 11.2181 | 19.3468 | 7.6731 | 40.9613 | 0 | 0 | 27.0199
876 | 0 | 2.6367 | 11.882 | 32.3345 | 11.7375 | 58.5907 | 0 | 0 | 44.072
877 | 0 | 2.9791 | 12.5673 | 32.7457 | 10.0254 | 58.3175 | 0 | 0 | 42.7712
878 | 0 | 3.508 | 12.163 | 25.7041 | 19.6974 | 61.0725 | 0 | 0 | 45.4015
879 | 0 | 2.9291 | 13.0774 | 31.855 | 10.2931 | 58.1546 | 0 | 0 | 42.1481
880 | 0 | 2.9452 | 13.9824 | 27.7497 | 15.0402 | 59.7175 | 0 | 0 | 42.7899
881 | 0 | 3.249 | 15.9503 | 30.0442 | 8.2897 | 57.5331 | 0 | 0 | 38.3339
882 | 0 | 3.1824 | 14.9443 | 27.0708 | 21.8874 | 67.0849 | 0 | 200 | 248.9582
883 | 0 | 3.1633 | 13.1158 | 31.0528 | 11.6256 | 58.9575 | 0 | 0 | 42.6784
884 | 0 | 2.754 | 11.9884 | 31.2446 | 0 | 45.987 | 0 | 0 | 31.2446
885 | 0 | 3.1095 | 11.3691 | 31.8933 | 0 | 46.3719 | 0 | 0 | 31.8933
886 | 0 | 3.1126 | 11.745 | 24.6425 | 0 | 39.5002 | 0 | 0 | 24.6425
887 | 0 | 2.6686 | 12.6474 | 26.0042 | 0 | 41.3202 | 0 | 0 | 26.0042
888 | 0 | 3.5138 | 13.8106 | 23.2878 | 0 | 40.6122 | 0 | 0 | 23.2878
889 | 0 | 3.0293 | 18.5518 | 24.6623 | 0 | 46.2434 | 0 | 0 | 24.6623
890 | 0 | 3.236 | 20.8953 | 37.2879 | 0 | 61.4191 | 0 | 0 | 37.2879
891 | 0 | 3.1334 | 18.2116 | 19.6873 | 0 | 41.0322 | 0 | 0 | 19.6873
892 | 0 | 3.4084 | 14.4583 | 37.0377 | 0 | 54.9045 | 0 | 0 | 37.0377
893 | 0 | 3.1896 | 14.0156 | 26.3852 | 0 | 43.5903 | 0 | 0 | 26.3852
894 | 0 | 3.8934 | 13.3332 | 30.3763 | 0 | 47.603 | 0 | 0 | 30.3763
895 | 0 | 2.7568 | 12.7845 | 27.107 | 0 | 42.6483 | 0 | 0 | 27.107
896 | 0 | 3.0015 | 12.2271 | 31.4228 | 16.8289 | 63.4802 | 0 | 200 | 248.2516
897 | 0 | 3.6134 | 11.5897 | 22.2563 | 12.9651 | 50.4244 | 0 | 0 | 35.2214
898 | 0 | 3.5589 | 11.006 | 28.5198 | 6.4154 | 49.5001 | 0 | 0 | 34.9352
899 | 0 | 2.9751 | 10.4981 | 34.5109 | 16.6918 | 64.676 | 0 | 0 | 51.2028
900 | 0 | 3.0928 | 11.3512 | 29.5205 | 11.9207 | 55.8853 | 0 | 0 | 41.4413
901 | 0 | 3.4247 | 13.3658 | 28.0315 | 7.0366 | 51.8586 | 0 | 0 | 35.068
902 | 0 | 3.4307 | 12.9843 | 32.6067 | 18.4905 | 67.5122 | 0 | 0 | 51.0973
903 | 0 | 3.5163 | 14.3654 | 16.104 | 17.5898 | 51.5755 | 0 | 0 | 33.6938
904 | 0 | 3.4617 | 15.4973 | 21.5595 | 14.4908 | 55.0093 | 0 | 0 | 36.0503
905 | 0 | 2.8086 | 17.5469 | 32.0453 | 9.3695 | 61.7703 | 0 | 0 | 41.4148
906 | 0 | 3.2537 | 16.7261 | 35.3388 | 9.2034 | 64.5219 | 0 | 0 | 44.5421
907 | 0 | 3.387 | 14.8903 | 35.4219 | 26.622 | 80.3213 | 0 | 0 | 62.044
908 | 0 | 3.3289 | 13.6365 | 33.2646 | 0 | 50.23 | 0 | 0 | 33.2646
909 | 0 | 3.2309 | 13.0657 | 31.5205 | 0 | 47.8171 | 0 | 0 | 31.5205
910 | 0 | 2.3104 | 13.3527 | 22.9601 | 0 | 38.6232 | 0 | 200 | 222.9601
911 | 0 | 3.4318 | 14.108 | 35.5537 | 0 | 53.0935 | 0 | 0 | 35.5537
912 | 0 | 3.6539 | 14.9393 | 23.3612 | 0 | 41.9544 | 0 | 0 | 23.3612
913 | 0 | 2.7091 | 19.7692 | 29.1615 | 0 | 51.6398 | 200 | 0 | 229.1615
914 | 0 | 3.2096 | 21.4798 | 40.0163 | 0 | 64.7057 | 0 | 0 | 40.0163
915 | 0 | 3.2156 | 17.392 | 26.3415 | 0 | 46.949 | 0 | 0 | 26.3415
916 | 0 | 3.2292 | 14.1841 | 29.5425 | 0 | 46.9558 | 0 | 0 | 29.5425
917 | 0 | 3.2079 | 13.4565 | 17.8858 | 0 | 34.5502 | 0 | 0 | 17.8858
918 | 0 | 2.9869 | 12.3898 | 30.3243 | 0 | 45.701 | 0 | 0 | 30.3243
919 | 0 | 3.376 | 12.1214 | 19.8122 | 0 | 35.3096 | 0 | 0 | 19.8122
920 | 0 | 2.9692 | 11.0619 | 34.6224 | 7.8288 | 56.4822 | 0 | 0 | 42.4511
921 | 0 | 3.0514 | 10.1637 | 36.0803 | 17.9907 | 67.2861 | 0 | 0 | 54.071
922 | 0 | 3.8466 | 9.6527 | 33.3236 | 10.9515 | 57.7743 | 0 | 0 | 44.275
923 | 0 | 3.168 | 9.1891 | 29.7235 | 23.092 | 65.1725 | 0 | 0 | 52.8155
924 | 0 | 2.9332 | 9.7586 | 21.7904 | 13.8999 | 48.3821 | 0 | 0 | 35.6903
925 | 0 | 3.0265 | 10.2604 | 23.2009 | 21.8091 | 58.2968 | 0 | 0 | 45.01
926 | 0 | 3.4215 | 9.8632 | 29.9213 | 4.3057 | 47.5116 | 0 | 200 | 234.227
927 | 0 | 3.296 | 10.5872 | 18.98 | 20.278 | 53.1411 | 0 | 0 | 39.258
928 | 0 | 2.9414 | 11.4261 | 31.8385 | 6.7136 | 52.9196 | 0 | 0 | 38.5521
929 | 0 | 2.9659 | 12.643 | 24.365 | 15.2411 | 55.215 | 0 | 0 | 39.6061
930 | 0 | 3.3045 | 11.7148 | 29.8913 | 13.84 | 58.7506 | 0 | 0 | 43.7313
931 | 0 | 3.3679 | 10.3554 | 17.5499 | 19.9677 | 51.2409 | 0 | 0 | 37.5176
932 | 0 | 3.2204 | 9.2993 | 28.6655 | 0 | 41.1852 | 0 | 0 | 28.6655
933 | 0 | 3.0977 | 8.6221 | 25.8979 | 0 | 37.6176 | 0 | 0 | 25.8979
934 | 0 | 3.9558 | 9.0119 | 31.4318 | 0 | 44.3995 | 0 | 0 | 31.4318
935 | 0 | 3.386 | 9.8073 | 27.4449 | 0 | 40.6382 | 0 | 0 | 27.4449
936 | 0 | 3.562 | 10.7471 | 26.3503 | 0 | 40.6594 | 0 | 0 | 26.3503
937 | 0 | 3.1773 | 14.1897 | 23.6011 | 0 | 40.9682 | 0 | 0 | 23.6011
938 | 0 | 2.859 | 16.6088 | 25.2462 | 0 | 44.714 | 0 | 0 | 25.2462
939 | 0 | 3.2008 | 14.0316 | 34.6299 | 0 | 51.8622 | 0 | 0 | 34.6299
940 | 0 | 2.7603 | 12.6076 | 28.945 | 0 | 44.3129 | 0 | 0 | 28.945
941 | 0 | 3.4178 | 12.6878 | 27.2492 | 0 | 43.3547 | 0 | 0 | 27.2492
942 | 0 | 3.1199 | 12.027 | 23.6823 | 0 | 38.8292 | 0 | 0 | 23.6823
943 | 0 | 3.2281 | 11.974 | 24.6306 | 0 | 39.8328 | 0 | 200 | 224.6306
944 | 0 | 3.0498 | 11.4046 | 32.3024 | 17.2709 | 64.0276 | 0 | 0 | 49.5732
945 | 0 | 3.4552 | 10.8427 | 23.3421 | 26.9646 | 64.6046 | 0 | 0 | 50.3067
946 | 0 | 3.6741 | 10.3293 | 33.4935 | 17.3671 | 64.8641 | 0 | 0 | 50.8606
947 | 0 | 2.6815 | 9.5163 | 25.2405 | 11.1327 | 48.571 | 0 | 0 | 36.3732
948 | 0 | 3.2372 | 9.152 | 24.7914 | 6.2662 | 43.4467 | 0 | 0 | 31.0576
949 | 0 | 2.4183 | 9.1069 | 30.3119 | 14.8145 | 56.6516 | 0 | 0 | 45.1264
950 | 0 | 2.6772 | 8.6311 | 35.9693 | 10.1334 | 57.411 | 0 | 0 | 46.1026
951 | 0 | 2.9434 | 9.4709 | 32.2552 | 10.1354 | 54.8049 | 0 | 0 | 42.3906
952 | 0 | 3.9209 | 9.8166 | 30.8638 | 16.6542 | 61.2555 | 0 | 0 | 47.518
953 | 0 | 3.2969 | 10.9323 | 24.8485 | 14.7337 | 53.8114 | 0 | 0 | 39.5822
954 | 0 | 3.5539 | 10.2671 | 33.7246 | 21.7977 | 69.3433 | 0 | 0 | 55.5223
955 | 0 | 3.5031 | 8.4756 | 25.876 | 15.7823 | 53.6371 | 0 | 0 | 41.6583
956 | 0 | 3.0347 | 6.7496 | 30.995 | 0 | 40.7793 | 0 | 0 | 30.995
957 | 0 | 3.1367 | 6.5059 | 29.7065 | 0 | 39.3491 | 0 | 0 | 29.7065
958 | 0 | 2.705 | 5.825 | 23.928 | 0 | 32.458 | 0 | 0 | 23.928
959 | 0 | 3.5688 | 6.1756 | 24.9093 | 0 | 34.6537 | 0 | 0 | 24.9093
960 | 0 | 3.241 | 7.1113 | 26.9518 | 0 | 37.3041 | 0 | 0 | 26.9518
961 | 0 | 3.0156 | 7.1373 | 29.4341 | 0 | 39.587 | 0 | 0 | 29.4341
962 | 0 | 2.9592 | 5.0575 | 35.1751 | 0 | 43.1917 | 0 | 0 | 35.1751
963 | 0 | 3.3913 | 7.04 | 28.5457 | 0 | 38.9769 | 0 | 0 | 28.5457
964 | 0 | 3.6103 | 8.9056 | 24.1631 | 0 | 36.679 | 0 | 0 | 24.1631
965 | 0 | 3.4434 | 10.9937 | 24.3309 | 0 | 38.768 | 0 | 0 | 24.3309
966 | 0 | 3.2028 | 10.2444 | 32.5897 | 0 | 46.0369 | 0 | 200 | 232.5897
967 | 0 | 3.4351 | 9.8703 | 27.8458 | 0 | 41.1512 | 0 | 0 | 27.8458
968 | 0 | 3.2264 | 9.6919 | 28.3236 | 15.5447 | 56.7866 | 0 | 0 | 43.8683
969 | 0 | 2.6789 | 9.2341 | 29.9609 | 7.3606 | 49.2345 | 0 | 0 | 37.3215
970 | 0 | 3.0357 | 7.9197 | 21.3971 | 9.6081 | 41.9606 | 0 | 0 | 31.0052
971 | 0 | 3.6722 | 6.6895 | 25.1058 | 15.7459 | 51.2135 | 0 | 0 | 40.8518
972 | 0 | 3.0899 | 6.0827 | 29.8329 | 20.5944 | 59.5999 | 0 | 0 | 50.4274
973 | 0 | 3.0775 | 6.1421 | 31.6828 | 17.9318 | 58.8342 | 0 | 0 | 49.6145
974 | 0 | 3.7249 | 5.2265 | 30.7792 | 14.728 | 54.4586 | 0 | 0 | 45.5072
975 | 0 | 3.2224 | 4.9748 | 28.8511 | 17.2862 | 54.3345 | 200 | 0 | 246.1374
976 | 0 | 3.3315 | 5.5588 | 26.1401 | 7.9172 | 42.9477 | 0 | 0 | 34.0574
977 | 0 | 3.0323 | 6.9829 | 26.2461 | 12.2358 | 48.4971 | 0 | 0 | 38.4819
978 | 0 | 2.8437 | 7.2403 | 32.053 | 14.4018 | 56.5388 | 0 | 0 | 46.4548
979 | 0 | 3.0444 | 6.175 | 28.6847 | 24.8227 | 62.7267 | 0 | 0 | 53.5073
980 | 0 | 3.0022 | 5.903 | 32.3672 | 0 | 41.2724 | 0 | 0 | 32.3672
981 | 0 | 3.1844 | 5.7682 | 25.0118 | 0 | 33.9645 | 0 | 0 | 25.0118
982 | 0 | 3.2647 | 5.1512 | 28.3948 | 0 | 36.8106 | 0 | 0 | 28.3948
983 | 0 | 3.2683 | 5.129 | 28.7864 | 0 | 37.1837 | 0 | 0 | 28.7864
984 | 0 | 2.9894 | 5.4158 | 33.1314 | 0 | 41.5367 | 0 | 0 | 33.1314
985 | 0 | 3.5863 | 5.3795 | 30.5124 | 0 | 39.4783 | 0 | 0 | 30.5124
986 | 0 | 3.0658 | 2.1636 | 23.8835 | 0 | 29.1129 | 0 | 0 | 23.8835
987 | 0 | 2.8309 | 2.4431 | 26.5428 | 0 | 31.8168 | 0 | 0 | 26.5428
988 | 0 | 3.0145 | 4.1666 | 28.4619 | 0 | 35.6431 | 0 | 0 | 28.4619
989 | 0 | 3.5962 | 6.839 | 28.7163 | 0 | 39.1515 | 0 | 0 | 28.7163
990 | 0 | 3.3416 | 6.8917 | 34.3446 | 0 | 44.5779 | 0 | 0 | 34.3446
991 | 0 | 3.2597 | 7.4341 | 27.7669 | 0 | 38.4607 | 0 | 0 | 27.7669
992 | 0 | 2.9915 | 7.5501 | 26.408 | 11.642 | 48.5917 | 0 | 0 | 38.0501
993 | 0 | 3.017 | 7.4455 | 22.1529 | 21.8454 | 54.4608 | 0 | 0 | 43.9983
994 | 0 | 2.5139 | 7.8518 | 25.4198 | 14.3442 | 50.1297 | 0 | 0 | 39.764
995 | 0 | 4.1887 | 8.1784 | 35.6337 | 3.8288 | 51.8295 | 0 | 0 | 39.4625
996 | 0 | 2.8921 | 8.2601 | 30.1773 | 8.9964 | 50.3259 | 0 | 0 | 39.1737
997 | 0 | 2.9866 | 8.6997 | 30.6691 | 12.6518 | 55.0072 | 0 | 200 | 243.3209
998 | 0 | 3.0649 | 8.7286 | 26.6915 | 19.2593 | 57.7443 | 0 | 0 | 45.9509
999 | 0 | 3.1573 | 8.8187 | 35.1706 | 8.6155 | 55.7621 | 0 | 0 | 43.7861
1000 | 0 | 3.241 | 10.2404 | 31.6456 | 14.3088 | 59.4359 | 0 | 0 | 45.9544
1001 | 0 | 2.7333 | 10.4623 | 27.4634 | 0.31713 | 40.9761 | 0 | 0 | 27.7805
1002 | 0 | 3.3176 | 9.3737 | 32.6903 | 18.9239 | 64.3055 | 0 | 0 | 51.6142
1003 | 0 | 3.6844 | 7.595 | 31.8299 | 13.4357 | 56.5449 | 0 | 0 | 45.2656
1004 | 0 | 3.3435 | 6.6102 | 32.769 | 0 | 42.7228 | 0 | 0 | 32.769
1005 | 0 | 3.5437 | 6.683 | 31.5303 | 0 | 41.757 | 0 | 0 | 31.5303
1006 | 0 | 3.1954 | 6.5199 | 30.6981 | 0 | 40.4134 | 0 | 0 | 30.6981
1007 | 0 | 3.8569 | 6.9673 | 33.9295 | 0 | 44.7537 | 0 | 0 | 33.9295
1008 | 0 | 3.8159 | 8.0867 | 29.3875 | 0 | 41.2901 | 0 | 0 | 29.3875
1009 | 0 | 3.4691 | 10.6392 | 23.8371 | 0 | 37.9453 | 0 | 0 | 23.8371
1010 | 0 | 3.4245 | 13.2966 | 24.6604 | 0 | 41.3814 | 0 | 0 | 24.6604
1011 | 0 | 3.1276 | 12.2285 | 28.5887 | 0 | 43.9447 | 0 | 0 | 28.5887
1012 | 0 | 3.2587 | 10.8255 | 28.3262 | 0 | 42.4104 | 0 | 0 | 28.3262
1013 | 0 | 2.9287 | 10.8008 | 27.6011 | 0 | 41.3306 | 0 | 0 | 27.6011
1014 | 0 | 3.3466 | 9.7048 | 24.82 | 0 | 37.8714 | 0 | 0 | 24.82
1015 | 0 | 3.2019 | 10.2058 | 28.984 | 0 | 42.3917 | 0 | 0 | 28.984
1016 | 0 | 3.0941 | 10.5135 | 20.5794 | 12.1889 | 46.3759 | 0 | 0 | 32.7683
1017 | 0 | 3.4527 | 9.4847 | 24.3373 | 8.637 | 45.9116 | 0 | 0 | 32.9742
1018 | 0 | 3.2299 | 9.3143 | 23.8183 | 3.2971 | 39.6597 | 0 | 200 | 227.1155
1019 | 0 | 3.8186 | 9.1236 | 31.9515 | 16.7564 | 61.6501 | 0 | 0 | 48.7079
1020 | 0 | 3.3355 | 8.3936 | 24.0254 | 26.3797 | 62.1343 | 0 | 0 | 50.4051
1021 | 0 | 3.2915 | 8.9295 | 29.6821 | 12.2263 | 54.1293 | 0 | 0 | 41.9084
1022 | 0 | 3.2688 | 8.4669 | 26.4467 | 8.0471 | 46.2295 | 0 | 0 | 34.4938
1023 | 0 | 3.3392 | 9.2133 | 28.6713 | 6.827 | 48.0508 | 0 | 0 | 35.4983
1024 | 0 | 3.1696 | 9.9113 | 31.4845 | 11.2908 | 55.8562 | 0 | 0 | 42.7753
1025 | 0 | 3.1206 | 10.5902 | 22.3741 | 20.4897 | 56.5746 | 0 | 0 | 42.8639
1026 | 0 | 3.5728 | 9.2649 | 33.1914 | 8.0317 | 54.0608 | 0 | 0 | 41.2231
1027 | 0 | 3.3998 | 8.0879 | 27.8241 | 4.4025 | 43.7143 | 0 | 0 | 32.2266
1028 | 0 | 2.8296 | 7.4777 | 23.4302 | 0 | 33.7375 | 0 | 0 | 23.4302
1029 | 0 | 3.3032 | 7.4101 | 26.2641 | 0 | 36.9775 | 0 | 0 | 26.2641
1030 | 0 | 3.4614 | 7.9669 | 32.2023 | 0 | 43.6306 | 0 | 0 | 32.2023
1031 | 0 | 2.9815 | 8.8336 | 25.4473 | 0 | 37.2624 | 0 | 0 | 25.4473
1032 | 0 | 3.5498 | 9.4572 | 26.6711 | 0 | 39.6781 | 0 | 0 | 26.6711
1033 | 0 | 3.2815 | 12.5666 | 29.407 | 0 | 45.2551 | 0 | 0 | 29.407
1034 | 0 | 3.0933 | 15.5372 | 27.5506 | 0 | 46.181 | 0 | 0 | 27.5506
1035 | 0 | 3.0234 | 13.13 | 17.0821 | 0 | 33.2355 | 0 | 0 | 17.0821
1036 | 0 | 3.3371 | 11.4424 | 34.6764 | 0 | 49.4558 | 0 | 0 | 34.6764
1037 | 0 | 3.053 | 11.2202 | 31.695 | 0 | 45.9681 | 200 | 0 | 231.695
1038 | 0 | 3.1489 | 10.2853 | 36.3312 | 0 | 49.7655 | 0 | 200 | 236.3312
1039 | 0 | 3.3656 | 9.3217 | 33.7219 | 0 | 46.4092 | 0 | 0 | 33.7219
1040 | 0 | 3.101 | 8.7314 | 31.1393 | 18.3252 | 61.297 | 0 | 0 | 49.4646
1041 | 0 | 2.986 | 7.9908 | 23.3824 | 23.5162 | 57.8755 | 0 | 0 | 46.8986
1042 | 0 | 3.0609 | 8.2316 | 26.3535 | 15.7134 | 53.3594 | 0 | 0 | 42.0669
1043 | 0 | 3.4438 | 7.8146 | 35.7273 | 9.2032 | 56.189 | 0 | 0 | 44.9306
1044 | 0 | 3.0239 | 7.9386 | 30.7956 | 5.7369 | 47.4949 | 0 | 0 | 36.5325
1045 | 0 | 3.4278 | 8.4858 | 28.3749 | 9.5188 | 49.8074 | 0 | 0 | 37.8937
1046 | 0 | 2.4991 | 9.2061 | 30.6139 | 17.9979 | 60.3169 | 0 | 0 | 48.6118
1047 | 0 | 3.4205 | 9.8144 | 29.262 | 23.6732 | 66.1702 | 0 | 0 | 52.9352
1048 | 0 | 3.0681 | 10.8581 | 21.8333 | 19.7504 | 55.5099 | 0 | 0 | 41.5837
1049 | 0 | 2.3418 | 11.6166 | 34.6067 | 22.2529 | 70.818 | 0 | 0 | 56.8597
1050 | 0 | 3.2971 | 10.4898 | 22.622 | 16.7331 | 53.142 | 0 | 0 | 39.355
1051 | 0 | 3.7402 | 10.0596 | 25.874 | 23.6988 | 63.3727 | 0 | 0 | 49.5728
1052 | 0 | 3.0671 | 9.2126 | 30.7738 | 0 | 43.0534 | 0 | 0 | 30.7738
1053 | 0 | 2.9497 | 9.2684 | 28.5097 | 0 | 40.7277 | 0 | 0 | 28.5097
1054 | 0 | 3.5358 | 9.4138 | 27.2214 | 0 | 40.171 | 0 | 0 | 27.2214
1055 | 0 | 3.3927 | 10.2131 | 25.1594 | 0 | 38.7651 | 0 | 0 | 25.1594
1056 | 0 | 2.897 | 10.7471 | 30.7699 | 0 | 44.4141 | 0 | 0 | 30.7699
1057 | 0 | 3.1465 | 14.2912 | 21.3458 | 0 | 38.7835 | 0 | 0 | 21.3458
1058 | 0 | 3.1037 | 17.0959 | 25.6436 | 0 | 45.8433 | 0 | 200 | 225.6436
1059 | 0 | 3.4709 | 13.9496 | 24.7531 | 0 | 42.1736 | 0 | 0 | 24.7531
1060 | 0 | 3.3676 | 11.9222 | 22.8626 | 0 | 38.1525 | 0 | 0 | 22.8626
1061 | 0 | 3.0041 | 11.9889 | 34.7696 | 0 | 49.7626 | 0 | 0 | 34.7696
1062 | 0 | 2.9165 | 10.9384 | 20.9508 | 0 | 34.8058 | 0 | 0 | 20.9508
1063 | 0 | 4.043 | 10.0584 | 31.1328 | 0 | 45.2342 | 0 | 0 | 31.1328
1064 | 0 | 3.2755 | 9.4168 | 28.4381 | 16.6453 | 57.7757 | 0 | 0 | 45.0834
1065 | 0 | 3.4635 | 8.8736 | 25.8945 | 17.6958 | 55.9274 | 0 | 0 | 43.5904
1066 | 0 | 3.1135 | 8.1639 | 23.5213 | 20.3694 | 55.1681 | 0 | 0 | 43.8907
1067 | 0 | 3.2072 | 7.8146 | 16.2091 | 6.114 | 33.3449 | 0 | 0 | 22.3231
1068 | 0 | 3.3991 | 8.1661 | 32.1105 | 15.232 | 58.9078 | 0 | 0 | 47.3425
1069 | 0 | 3.2194 | 8.3084 | 35.5828 | 9.9176 | 57.0282 | 0 | 0 | 45.5004
1070 | 0 | 3.7989 | 6.9063 | 26.9201 | 10.2489 | 47.8742 | 0 | 0 | 37.169
1071 | 0 | 2.9102 | 7.5818 | 26.1551 | 19.5484 | 56.1955 | 0 | 0 | 45.7035
1072 | 0 | 3.2743 | 7.8284 | 29.5247 | 25.3783 | 66.0057 | 0 | 0 | 54.903
1073 | 0 | 3.0297 | 8.1952 | 37.1246 | 4.3916 | 52.7411 | 0 | 0 | 41.5162
1074 | 0 | 3.2983 | 7.0376 | 26.1588 | 12.2247 | 48.7194 | 0 | 0 | 38.3835
1075 | 0 | 3.6838 | 5.6232 | 31.8654 | 16.2947 | 57.4671 | 0 | 0 | 48.16
1076 | 0 | 3.3761 | 4.7019 | 34.4913 | 0 | 42.5692 | 0 | 0 | 34.4913
1077 | 0 | 3.477 | 4.4208 | 26.8361 | 0 | 34.7338 | 0 | 0 | 26.8361
1078 | 0 | 3.0697 | 5.073 | 26.6508 | 0 | 34.7935 | 0 | 0 | 26.6508
1079 | 0 | 3.3874 | 7.4542 | 29.3156 | 0 | 40.1572 | 0 | 0 | 29.3156
1080 | 0 | 3.4577 | 8.3285 | 24.7294 | 0 | 36.5157 | 0 | 0 | 24.7294
1081 | 0 | 3.5191 | 10.5377 | 32.5214 | 0 | 46.5782 | 0 | 200 | 232.5214
1082 | 0 | 3.665 | 13.1991 | 32.6275 | 0 | 49.4916 | 0 | 0 | 32.6275
1083 | 0 | 3.2402 | 11.7367 | 29.7883 | 0 | 44.7652 | 0 | 0 | 29.7883
1084 | 0 | 3.0095 | 11.0997 | 24.6405 | 0 | 38.7496 | 0 | 0 | 24.6405
1085 | 0 | 3.2051 | 11.7792 | 28.1922 | 0 | 43.1765 | 0 | 0 | 28.1922
1086 | 0 | 3.0245 | 11.4464 | 22.7569 | 0 | 37.2278 | 0 | 0 | 22.7569
1087 | 0 | 3.396 | 11.2373 | 36.4643 | 0 | 51.0976 | 0 | 0 | 36.4643
1088 | 0 | 3.6955 | 10.445 | 27.5538 | 12.8658 | 54.56 | 0 | 0 | 40.4196
1089 | 0 | 3.254 | 9.5526 | 30.2511 | 7.039 | 50.0967 | 0 | 0 | 37.2901
1090 | 0 | 3.2087 | 7.8256 | 29.9381 | 13.8862 | 54.8586 | 0 | 0 | 43.8243
1091 | 0 | 3.2742 | 6.5055 | 24.7838 | 22.9737 | 57.5373 | 0 | 0 | 47.7576
1092 | 0 | 3.1926 | 6.7252 | 32.0882 | 22.2306 | 64.2367 | 0 | 0 | 54.3189
1093 | 0 | 3.4284 | 6.8887 | 30.4569 | 8.3271 | 49.1012 | 0 | 0 | 38.784
1094 | 1.9 | 2.9809 | 7.0706 | 21.6914 | 16.4684 | 50.1112 | 0 | 0 | 40.0597
1095 | 5.5379 | 3.4795 | 7.41 | 28.9684 | 19.4149 | 64.8107 | 0 | 0 | 53.9211
1096 | 0 | 3.0937 | 9.0592 | 35.3151 | 12.0037 | 59.4716 | 0 | 0 | 47.3188
1097 | 0 | 3.075 | 9.6778 | 28.5608 | 22.4061 | 63.7197 | 0 | 0 | 50.9669
1098 | 0 | 3.4139 | 7.8172 | 27.273 | 7.0892 | 45.5933 | 200 | 0 | 234.3623
1099 | 0 | 3.1467 | 6.7077 | 23.4162 | 2.9767 | 36.2473 | 0 | 0 | 26.3929
1100 | 0 | 3.4977 | 6.4368 | 27.0777 | 0 | 37.0122 | 0 | 0 | 27.0777
1101 | 0 | 3.2417 | 6.279 | 27.4702 | 0 | 36.9909 | 0 | 0 | 27.4702
1102 | 0 | 3.5082 | 6.8415 | 26.8576 | 0 | 37.2073 | 0 | 0 | 26.8576
1103 | 0 | 3.9141 | 7.6164 | 22.0869 | 0 | 33.6175 | 0 | 0 | 22.0869
1104 | 0 | 2.8418 | 8.651 | 26.2586 | 0 | 37.7514 | 0 | 200 | 226.2586
1105 | 0 | 3.8772 | 11.5522 | 36.4563 | 0 | 51.8857 | 0 | 0 | 36.4563
1106 | 0 | 2.8954 | 14.2708 | 25.5304 | 0 | 42.6966 | 0 | 0 | 25.5304
1107 | 0 | 2.1784 | 12.2285 | 32.9379 | 0 | 47.3448 | 0 | 0 | 32.9379
1108 | 0 | 2.9708 | 10.1401 | 26.9056 | 0 | 40.0165 | 0 | 0 | 26.9056
1109 | 0 | 3.5742 | 9.3333 | 24.1278 | 0 | 37.0353 | 0 | 0 | 24.1278
1110 | 0 | 3.1942 | 8.6162 | 31.6212 | 0 | 43.4316 | 0 | 0 | 31.6212
1111 | 1.0858 | 3.3137 | 7.9218 | 31.184 | 0 | 43.5053 | 0 | 0 | 32.2698
1112 | 3.8209 | 3.2891 | 7.9774 | 21.646 | 13.6641 | 50.3975 | 0 | 0 | 39.131
1113 | 0.4539 | 3.904 | 7.2439 | 31.7104 | 17.0445 | 60.3567 | 0 | 0 | 49.2088
1114 | 9.0605 | 3.9111 | 6.8782 | 21.4983 | 4.9094 | 46.2574 | 0 | 0 | 35.4681
1115 | 23.6549 | 2.7375 | 6.8983 | 27.8674 | 16.0283 | 77.1864 | 0 | 0 | 67.5506
1116 | 0 | 3.2228 | 8.1661 | 27.0826 | 19.9814 | 58.4529 | 0 | 0 | 47.064
1117 | 0 | 3.0971 | 9.8167 | 21.7724 | 11.1487 | 45.835 | 0 | 0 | 32.9211
1118 | 0 | 2.9889 | 10.6024 | 28.1642 | 15.2591 | 57.0146 | 0 | 0 | 43.4233
1119 | 0 | 3.0857 | 11.7035 | 26.5506 | 7.8493 | 49.1891 | 0 | 0 | 34.3999
1120 | 0 | 2.7776 | 13.1303 | 29.1263 | 14.4484 | 59.4827 | 0 | 0 | 43.5748
1121 | 0 | 3.2925 | 14.3536 | 25.0473 | 18.5863 | 61.2797 | 0 | 0 | 43.6336
1122 | 0 | 3.5634 | 13.942 | 30.6713 | 19.0932 | 67.27 | 0 | 0 | 49.7645
1123 | 0 | 3.4766 | 11.6036 | 31.781 | 8.1521 | 55.0133 | 0 | 0 | 39.933
1124 | 0 | 3.4729 | 10.5534 | 25.2738 | 0 | 39.3 | 0 | 200 | 225.2738
1125 | 0 | 3.4071 | 9.5562 | 27.0908 | 0 | 40.0541 | 0 | 0 | 27.0908
1126 | 0 | 3.2253 | 8.7497 | 32.1955 | 0 | 44.1704 | 0 | 0 | 32.1955
1127 | 0 | 3.5976 | 9.27 | 22.8427 | 0 | 35.7103 | 0 | 0 | 22.8427
1128 | 0 | 2.9892 | 10.3897 | 26.425 | 0 | 39.8039 | 0 | 0 | 26.425
1129 | 0 | 3.5938 | 9.6798 | 29.4357 | 0 | 42.7093 | 0 | 0 | 29.4357
1130 | 0 | 3.8736 | 9.8738 | 23.2053 | 0 | 36.9527 | 0 | 0 | 23.2053
1131 | 0 | 3.5868 | 11.2508 | 31.0175 | 0 | 45.8551 | 0 | 0 | 31.0175
1132 | 0 | 3.3879 | 9.9393 | 27.141 | 0 | 40.4683 | 0 | 0 | 27.141
1133 | 0 | 3.0552 | 10.868 | 26.1936 | 0 | 40.1168 | 0 | 0 | 26.1936
1134 | 0 | 3.5228 | 10.2444 | 28.4477 | 0 | 42.2149 | 0 | 0 | 28.4477
1135 | 0 | 3.0705 | 9.1702 | 21.9522 | 0 | 34.1929 | 0 | 0 | 21.9522
1136 | 0 | 2.9358 | 8.5569 | 24.2134 | 19.9287 | 55.6349 | 0 | 0 | 44.1421
1137 | 0 | 3.413 | 7.6124 | 24.7386 | 13.0016 | 48.7656 | 0 | 0 | 37.7402
1138 | 0 | 2.9944 | 6.9555 | 23.7065 | 20.4826 | 54.139 | 0 | 0 | 44.1891
1139 | 0 | 3.5285 | 6.497 | 23.3389 | 8.169 | 41.5334 | 0 | 0 | 31.5079
1140 | 0 | 3.0266 | 7.5597 | 35.1625 | 22.1425 | 67.8913 | 0 | 0 | 57.305
1141 | 0 | 2.8065 | 9.0789 | 30.626 | 8.1897 | 50.7012 | 0 | 0 | 38.8158
1142 | 0 | 3.1013 | 9.5409 | 29.1105 | 18.1379 | 59.8905 | 0 | 0 | 47.2483
1143 | 0 | 3.4481 | 10.8384 | 28.0452 | 21.2349 | 63.5665 | 0 | 0 | 49.2801
1144 | 0 | 3.145 | 12.1808 | 29.6443 | 11.2809 | 56.2509 | 0 | 0 | 40.9252
1145 | 0 | 3.0053 | 13.5678 | 26.1643 | 4.4874 | 47.2247 | 0 | 200 | 230.6516
1146 | 0 | 3.0184 | 12.6729 | 23.4575 | 6.1229 | 45.2716 | 0 | 0 | 29.5804
1147 | 0 | 2.958 | 10.9264 | 29.9957 | 18.6349 | 62.515 | 0 | 0 | 48.6306
1148 | 0 | 3.2597 | 10.3131 | 24.325 | 0 | 37.8978 | 0 | 0 | 24.325
1149 | 0 | 3.5947 | 7.9698 | 31.7448 | 0 | 43.3094 | 0 | 0 | 31.7448
1150 | 0 | 2.9495 | 7.6931 | 30.443 | 0 | 41.0857 | 0 | 0 | 30.443
1151 | 0 | 3.2545 | 7.9407 | 36.0715 | 0 | 47.2668 | 0 | 0 | 36.0715
1152 | 0 | 3.312 | 8.8128 | 30.4415 | 0 | 42.5663 | 0 | 0 | 30.4415
1153 | 0 | 3.4716 | 8.1155 | 25.9321 | 0 | 37.5192 | 0 | 0 | 25.9321
1154 | 0 | 3.0901 | 7.5717 | 36.6097 | 0 | 47.2715 | 0 | 0 | 36.6097
1155 | 0 | 3.1555 | 6.4952 | 21.7514 | 0 | 31.4021 | 0 | 0 | 21.7514
1156 | 0 | 2.863 | 7.2709 | 30.231 | 0 | 40.3649 | 0 | 0 | 30.231
1157 | 0 | 3.7541 | 8.813 | 27.5763 | 0 | 40.1434 | 0 | 0 | 27.5763
1158 | 0 | 3.1172 | 8.2084 | 34.6538 | 0 | 45.9794 | 0 | 0 | 34.6538
1159 | 0 | 2.7951 | 7.925 | 32.5374 | 0 | 43.2575 | 0 | 0 | 32.5374
1160 | 0 | 3.1571 | 7.4958 | 26.9192 | 13.3573 | 50.9294 | 200 | 0 | 240.2765
1161 | 0 | 3.3233 | 6.9047 | 24.972 | 1.2498 | 36.4498 | 0 | 0 | 26.2217
1162 | 0 | 3.2078 | 6.1279 | 28.1792 | 9.4163 | 46.9312 | 0 | 0 | 37.5956
1163 | 0 | 3.2203 | 6.3447 | 34.666 | 17.3176 | 61.5486 | 0 | 0 | 51.9836
1164 | 0 | 3.2108 | 7.2455 | 31.7346 | 14.758 | 56.9488 | 0 | 0 | 46.4926
1165 | 0 | 2.862 | 8.5503 | 24.0781 | 12.542 | 48.0323 | 0 | 0 | 36.62
1166 | 0 | 3.0176 | 8.0159 | 26.0277 | 25.4445 | 62.5057 | 0 | 0 | 51.4722
1167 | 0 | 3.5544 | 9.2909 | 19.6213 | 13.1181 | 45.5847 | 0 | 0 | 32.7394
1168 | 0 | 3.9251 | 10.0329 | 29.6216 | 16.8662 | 60.4458 | 0 | 200 | 246.4878
1169 | 0 | 2.9532 | 12.1055 | 18.5983 | 17.1151 | 50.7721 | 0 | 0 | 35.7134
1170 | 0 | 2.8675 | 11.8985 | 30.9818 | 3.4967 | 49.2444 | 0 | 0 | 34.4785
1171 | 0 | 3.7355 | 9.7639 | 25.8569 | 11.0315 | 50.3877 | 0 | 0 | 36.8884
1172 | 0 | 3.2185 | 7.9114 | 32.293 | 0 | 43.4229 | 0 | 0 | 32.293
1173 | 0 | 3.2977 | 7.3294 | 32.4077 | 0 | 43.0347 | 0 | 0 | 32.4077
1174 | 0 | 2.4834 | 7.163 | 28.7458 | 0 | 38.3923 | 0 | 0 | 28.7458
1175 | 0 | 3.3717 | 7.7787 | 34.4025 | 0 | 45.553 | 0 | 0 | 34.4025
1176 | 0 | 3.1016 | 8.651 | 25.8467 | 0 | 37.5993 | 0 | 0 | 25.8467
1177 | 0 | 2.879 | 11.1464 | 27.3773 | 0 | 41.4027 | 0 | 0 | 27.3773
1178 | 0 | 3.4617 | 14.0759 | 32.2122 | 0 | 49.7498 | 0 | 0 | 32.2122
1179 | 0 | 3.6105 | 12.3924 | 23.1628 | 0 | 39.1657 | 0 | 0 | 23.1628
1180 | 0 | 2.9432 | 11.4424 | 19.3406 | 0 | 33.7262 | 0 | 0 | 19.3406
1181 | 2.1823 | 3.4638 | 11.7792 | 25.3683 | 0 | 42.7936 | 0 | 0 | 27.5506
1182 | 24.5856 | 2.9913 | 11.011 | 37.685 | 0 | 76.2729 | 0 | 0 | 62.2706
1183 | 71.7585 | 3.0134 | 10.6478 | 30.8822 | 0 | 116.3019 | 0 | 0 | 102.6407
1184 | 22.8535 | 3.5468 | 10.0337 | 27.9267 | 9.7968 | 74.1575 | 0 | 0 | 60.577
1185 | 0 | 3.102 | 9.6205 | 33.1263 | 25.672 | 71.5208 | 0 | 0 | 58.7983
1186 | 0 | 3.2772 | 8.7053 | 38.1228 | 13.1374 | 63.2426 | 0 | 0 | 51.2601
1187 | 0 | 3.0445 | 7.8146 | 33.1707 | 15.6814 | 59.7111 | 0 | 0 | 48.852
1188 | 0 | 3.3199 | 7.7869 | 16.1951 | 1.2106 | 28.5124 | 0 | 0 | 17.4057
1189 | 0 | 3.2214 | 8.3971 | 32.5908 | 13.3646 | 57.5739 | 0 | 200 | 245.9554
1190 | 0 | 3.1845 | 7.8098 | 25.2473 | 5.9582 | 42.1997 | 0 | 0 | 31.2054
1191 | 0 | 2.8125 | 9.5568 | 27.7329 | 22.2649 | 62.3671 | 0 | 0 | 49.9978
1192 | 0 | 2.9867 | 11.5208 | 29.037 | 23.1868 | 66.7313 | 0 | 0 | 52.2237
1193 | 0 | 2.9493 | 12.9851 | 33.4525 | 6.211 | 55.5979 | 0 | 0 | 39.6635
1194 | 0 | 2.8037 | 13.2739 | 25.6618 | 8.6951 | 50.4344 | 0 | 0 | 34.3569
1195 | 0 | 2.678 | 11.4398 | 36.8405 | 7.9727 | 58.931 | 0 | 0 | 44.8131
1196 | 0 | 3.4959 | 10.427 | 27.5067 | 0 | 41.4296 | 0 | 0 | 27.5067
1197 | 0 | 3.004 | 10.4803 | 22.2128 | 0 | 35.6971 | 0 | 0 | 22.2128
1198 | 0 | 3.2297 | 10.8608 | 32.6506 | 0 | 46.7411 | 0 | 0 | 32.6506
1199 | 0 | 3.0996 | 11.6736 | 28.0464 | 0 | 42.8196 | 0 | 0 | 28.0464
1200 | 0 | 3.3792 | 12.9238 | 28.0002 | 0 | 44.3033 | 0 | 0 | 28.0002
1201 | 0 | 3.4995 | 16.8273 | 31.9262 | 0 | 52.253 | 0 | 0 | 31.9262
1202 | 0 | 3.2296 | 19.0443 | 27.9796 | 0 | 50.2535 | 0 | 0 | 27.9796
1203 | 0 | 3.4402 | 14.2775 | 36.7374 | 0 | 54.455 | 0 | 0 | 36.7374
1204 | 0 | 3.2287 | 11.5109 | 32.8994 | 0 | 47.639 | 0 | 0 | 32.8994
1205 | 2.1459 | 3.3755 | 11.2202 | 22.8114 | 0 | 39.5529 | 0 | 200 | 224.9573
1206 | 23.0593 | 3.0117 | 10.6482 | 38.9098 | 0 | 75.629 | 0 | 0 | 61.9691
1207 | 79.4737 | 2.8235 | 10.2058 | 27.878 | 0 | 120.381 | 0 | 0 | 107.3517
1208 | 73.0241 | 2.7687 | 9.5539 | 22.1374 | 11.3833 | 118.8675 | 0 | 0 | 106.5449
1209 | 57.6825 | 3.1325 | 9.0094 | 24.6143 | 17.2576 | 111.6963 | 0 | 0 | 99.5544
1210 | 24.6661 | 3.4784 | 8.57 | 25.8776 | 14.9593 | 77.5514 | 0 | 0 | 65.5031
1211 | 55.4199 | 3.3322 | 8.7964 | 28.2225 | 16.6965 | 112.4675 | 0 | 0 | 100.3389
1212 | 18.5796 | 3.5909 | 9.5311 | 24.9371 | 9.8017 | 66.4405 | 0 | 0 | 53.3184
1213 | 0 | 3.1954 | 9.3731 | 37.5025 | 16.7168 | 66.7878 | 0 | 0 | 54.2194
1214 | 0 | 3.4298 | 9.5346 | 29.3432 | 19.6348 | 61.9424 | 0 | 0 | 48.978
1215 | 0 | 3.1452 | 11.6176 | 22.8659 | 26.9072 | 64.5359 | 0 | 0 | 49.7731
1216 | 0 | 3.5446 | 12.941 | 20.4913 | 16.0386 | 53.0155 | 0 | 0 | 36.5299
1217 | 0 | 3.4383 | 12.1868 | 28.705 | 24.3931 | 68.7232 | 0 | 0 | 53.0981
1218 | 0 | 3.4832 | 10.9353 | 27.9476 | 17.0997 | 59.4657 | 0 | 0 | 45.0473
1219 | 8.03 | 3.9009 | 11.0455 | 35.3364 | 15.2406 | 73.5533 | 0 | 0 | 58.6069
1220 | 32.3718 | 2.8242 | 9.5595 | 36.1065 | 0 | 80.862 | 0 | 0 | 68.4782
1221 | 44.1918 | 3.0917 | 10.0764 | 26.315 | 0 | 83.6749 | 0 | 0 | 70.5068
1222 | 44.2569 | 3.482 | 10.0569 | 37.028 | 0 | 94.8238 | 200 | 0 | 281.2849
1223 | 16.7618 | 3.4495 | 11.0245 | 24.9461 | 0 | 56.1819 | 0 | 0 | 41.7079
1224 | 41.3306 | 2.9266 | 12.2789 | 18.024 | 0 | 74.56 | 0 | 200 | 259.3546
1225 | 29.2484 | 2.6252 | 16.1172 | 27.8117 | 0 | 75.8024 | 0 | 0 | 57.0601
1226 | 1.0175 | 3.0725 | 19.434 | 26.8676 | 0 | 50.3916 | 0 | 0 | 27.8851
1227 | 0 | 3.3881 | 15.8347 | 23.0899 | 0 | 42.3127 | 0 | 0 | 23.0899
1228 | 0 | 3.4733 | 12.8133 | 31.7035 | 0 | 47.99 | 0 | 0 | 31.7035
1229 | 0 | 3.4314 | 12.2684 | 25.3711 | 0 | 41.071 | 0 | 0 | 25.3711
1230 | 0.030627 | 2.9968 | 11.2287 | 35.107 | 0 | 49.3631 | 0 | 0 | 35.1376
1231 | 10.3802 | 3.1705 | 10.5005 | 31.4632 | 0 | 55.5144 | 0 | 0 | 41.8434
1232 | 51.8798 | 3.2188 | 10.1023 | 26.489 | 22.8955 | 114.5853 | 0 | 0 | 101.2642
1233 | 64.9662 | 3.7236 | 9.7563 | 27.5246 | 26.5436 | 132.5143 | 0 | 0 | 119.0344
1234 | 17.1405 | 3.3271 | 9.179 | 26.4697 | 9.1869 | 65.3031 | 0 | 0 | 52.7971
1235 | 15.2187 | 2.6307 | 9.0582 | 27.9183 | 11.2274 | 66.0532 | 0 | 0 | 54.3644
1236 | 64.8722 | 3.3331 | 9.3036 | 34.7525 | 13.6946 | 125.956 | 0 | 0 | 113.3193
1237 | 49.4701 | 3.3014 | 10.4378 | 22.5283 | 12.1754 | 97.9131 | 0 | 0 | 84.1738
1238 | 56.7473 | 3.1849 | 10.5203 | 31.7434 | 16.5998 | 118.7956 | 0 | 0 | 105.0904
1239 | 65.4605 | 2.7498 | 11.36 | 33.0186 | 11.8811 | 124.47 | 0 | 0 | 110.3602
1240 | 33.1047 | 3.2081 | 12.5623 | 34.1523 | 18.9493 | 101.9768 | 0 | 0 | 86.2064
1241 | 0 | 3.574 | 14.2396 | 26.0171 | 11.0967 | 54.9274 | 0 | 200 | 237.1138
1242 | 0 | 3.0519 | 13.1625 | 36.2784 | 9.6375 | 62.1304 | 0 | 0 | 45.916
1243 | 0 | 2.6409 | 10.9469 | 33.0895 | 8.6251 | 55.3024 | 0 | 0 | 41.7146
1244 | 0 | 3.3147 | 10.1668 | 31.1198 | 0 | 44.6013 | 0 | 0 | 31.1198
1245 | 0 | 3.3432 | 9.6724 | 33.4178 | 0 | 46.4333 | 0 | 0 | 33.4178
1246 | 0 | 2.6452 | 9.5746 | 29.2893 | 0 | 41.5091 | 0 | 0 | 29.2893
1247 | 0 | 3.61 | 10.6188 | 25.94 | 0 | 40.1688 | 0 | 0 | 25.94
1248 | 0 | 3.1314 | 11.392 | 26.4008 | 0 | 40.9243 | 0 | 0 | 26.4008
1249 | 0 | 3.2855 | 15.4071 | 25.5502 | 0 | 44.2428 | 0 | 0 | 25.5502
1250 | 0 | 3.3698 | 18.1675 | 25.5442 | 0 | 47.0815 | 0 | 0 | 25.5442
1251 | 0 | 3.5471 | 14.3594 | 31.083 | 0 | 48.9895 | 0 | 0 | 31.083
1252 | 0 | 2.9685 | 12.2649 | 31.1269 | 0 | 46.3603 | 0 | 0 | 31.1269
1253 | 0 | 3.5751 | 11.8491 | 24.4974 | 0 | 39.9215 | 0 | 0 | 24.4974
1254 | 0 | 3.1453 | 10.7207 | 22.6206 | 0 | 36.4866 | 0 | 0 | 22.6206
1255 | 0 | 2.8624 | 10.7952 | 33.8785 | 0 | 47.536 | 0 | 0 | 33.8785
1256 | 0.082754 | 3.1933 | 11.1304 | 27.5873 | 13.6752 | 55.669 | 0 | 0 | 41.3453
1257 | 18.8717 | 3.171 | 10.2995 | 34.3106 | 13.4592 | 80.112 | 0 | 0 | 66.6415
1258 | 75.092 | 3.9056 | 9.788 | 28.6643 | 23.1994 | 140.6494 | 0 | 200 | 326.9558
1259 | 72.269 | 2.5721 | 9.2545 | 19.8713 | 21.6064 | 125.5732 | 0 | 0 | 113.7466
1260 | 68.9358 | 3.6631 | 10.1378 | 24.2173 | 13.0819 | 120.0359 | 0 | 0 | 106.235
1261 | 88.8157 | 2.7737 | 11.0589 | 28.2051 | 16.1002 | 146.9536 | 0 | 0 | 133.121
1262 | 74.8784 | 3.1896 | 10.5203 | 30.9441 | 15.344 | 134.8763 | 0 | 0 | 121.1665
1263 | 18.896 | 3.3325 | 11.7894 | 22.3179 | 17.2583 | 73.594 | 0 | 0 | 58.4722
1264 | 0 | 3.736 | 12.941 | 30.2695 | 16.2342 | 63.1807 | 0 | 0 | 46.5037
1265 | 0 | 2.9151 | 14.4677 | 27.6752 | 17.8576 | 62.9155 | 0 | 0 | 45.5327
1266 | 0 | 3.1591 | 12.6057 | 26.8384 | 16.4361 | 59.0394 | 0 | 0 | 43.2745
1267 | 0 | 3.4602 | 10.9469 | 17.7977 | 23.5539 | 55.7588 | 0 | 0 | 41.3517
1268 | 0 | 2.979 | 10.3402 | 15.3494 | 0 | 28.6686 | 0 | 0 | 15.3494
1269 | 0 | 3.8421 | 10.0764 | 34.1867 | 0 | 48.1052 | 0 | 0 | 34.1867
1270 | 0 | 2.841 | 10.2177 | 25.8198 | 0 | 38.8786 | 0 | 0 | 25.8198
1271 | 0 | 3.4074 | 11.1056 | 34.4782 | 0 | 48.9912 | 0 | 0 | 34.4782
1272 | 0 | 3.7508 | 10.7471 | 21.5272 | 0 | 36.0251 | 0 | 0 | 21.5272
1273 | 0 | 2.7834 | 13.6825 | 29.3284 | 0 | 45.7943 | 0 | 0 | 29.3284
1274 | 0 | 3.1437 | 16.1217 | 28.63 | 0 | 47.8954 | 0 | 0 | 28.63
1275 | 0 | 2.8109 | 13.8677 | 26.2449 | 0 | 42.9234 | 0 | 200 | 226.2449
1276 | 0 | 2.6629 | 12.1278 | 34.7195 | 0 | 49.5103 | 0 | 0 | 34.7195
1277 | 0 | 2.775 | 12.1287 | 22.126 | 0 | 37.0297 | 0 | 0 | 22.126
1278 | 0 | 3.3576 | 12.027 | 29.3256 | 0 | 44.7102 | 0 | 0 | 29.3256
1279 | 0 | 2.9375 | 11.3109 | 34.9674 | 0 | 49.2158 | 0 | 0 | 34.9674
1280 | 0 | 2.689 | 11.1304 | 33.4611 | 14.7153 | 61.9958 | 0 | 0 | 48.1763
1281 | 0 | 3.1184 | 10.639 | 26.7061 | 6.8786 | 47.3421 | 0 | 0 | 33.5846
1282 | 0 | 2.9624 | 10.2617 | 33.245 | 19.2527 | 65.7217 | 0 | 0 | 52.4977
1283 | 0 | 3.0226 | 9.2545 | 28.608 | 10.7597 | 51.6448 | 0 | 0 | 39.3677
1284 | 0 | 3.667 | 10.062 | 24.5177 | 13.8272 | 52.0739 | 200 | 0 | 238.3449
1285 | 0 | 4.0109 | 10.4378 | 25.2849 | 5.1757 | 44.9094 | 0 | 0 | 30.4606
1286 | 0 | 3.2226 | 10.4381 | 26.1009 | 21.9352 | 61.6968 | 0 | 0 | 48.0361
1287 | 0 | 3.4192 | 11.4459 | 29.5958 | 12.7178 | 57.1787 | 0 | 0 | 42.3136
1288 | 0 | 3.367 | 12.0889 | 27.5097 | 13.7615 | 56.7271 | 0 | 0 | 41.2712
1289 | 0 | 3.2768 | 13.6694 | 23.7188 | 7.5029 | 48.1679 | 0 | 0 | 31.2217
1290 | 0 | 3.1561 | 12.7171 | 38.8648 | 11.9139 | 66.6519 | 0 | 0 | 50.7787
1291 | 0 | 3.1386 | 11.3719 | 26.5829 | 11.3456 | 52.4391 | 0 | 0 | 37.9285
1292 | 0 | 3.2583 | 10.5534 | 28.901 | 0 | 42.7127 | 0 | 0 | 28.901
1293 | 0 | 3.0271 | 9.1205 | 30.8973 | 0 | 43.0448 | 0 | 200 | 230.8973
1294 | 0 | 3.4246 | 8.9868 | 24.3479 | 0 | 36.7594 | 0 | 0 | 24.3479
1295 | 0 | 3.4459 | 9.3437 | 27.179 | 0 | 39.9685 | 0 | 0 | 27.179
1296 | 0 | 3.3299 | 10.7259 | 29.7341 | 0 | 43.7899 | 0 | 0 | 29.7341
1297 | 0 | 3.1776 | 10.1565 | 25.7631 | 0 | 39.0972 | 0 | 0 | 25.7631
1298 | 0 | 2.8875 | 11.7007 | 36.7342 | 0 | 51.3224 | 0 | 0 | 36.7342
1299 | 0 | 3.0924 | 11.702 | 26.1432 | 0 | 40.9377 | 0 | 0 | 26.1432
1300 | 0 | 3.3349 | 11.0764 | 31.5286 | 0 | 45.9399 | 0 | 0 | 31.5286
1301 | 0 | 3.5872 | 11.7476 | 22.7249 | 0 | 38.0597 | 0 | 0 | 22.7249
1302 | 0 | 2.8029 | 11.3716 | 28.5585 | 0 | 42.733 | 0 | 0 | 28.5585
1303 | 0 | 3.4003 | 10.9522 | 18.6602 | 0 | 33.0127 | 0 | 0 | 18.6602
1304 | 0 | 3.0475 | 10.4087 | 23.2562 | 7.4143 | 44.1268 | 0 | 0 | 30.6706
1305 | 0 | 3.5574 | 10.0126 | 27.8394 | 10.1499 | 51.5592 | 0 | 0 | 37.9893
1306 | 0 | 3.308 | 9.2454 | 33.1071 | 10.8542 | 56.5147 | 0 | 0 | 43.9613
1307 | 0 | 2.0999 | 8.1012 | 32.4381 | 12.4949 | 55.1342 | 0 | 0 | 44.933
1308 | 0 | 2.9623 | 8.6429 | 25.7497 | 22.5283 | 59.8832 | 0 | 0 | 48.2779
1309 | 0 | 3.296 | 8.5726 | 28.6919 | 11.3006 | 51.8611 | 0 | 0 | 39.9926
1310 | 0 | 2.6164 | 9.0392 | 38.6588 | 7.8799 | 58.1944 | 0 | 0 | 46.5387
1311 | 0 | 3.0832 | 10.049 | 30.8093 | 10.6152 | 54.5567 | 0 | 0 | 41.4245
1312 | 0 | 3.5299 | 10.6095 | 24.8142 | 9.1792 | 48.1328 | 0 | 0 | 33.9934
1313 | 0 | 3.9781 | 11.2437 | 34.7876 | 20.1016 | 70.111 | 0 | 200 | 254.8892
1314 | 0 | 3.2551 | 11.7142 | 36.1413 | 18.2441 | 69.3547 | 0 | 0 | 54.3854
1315 | 0 | 3.2383 | 10.5463 | 28.6727 | 9.582 | 52.0393 | 0 | 0 | 38.2547
1316 | 0 | 2.916 | 10.2249 | 33.2418 | 0 | 46.3827 | 0 | 0 | 33.2418
1317 | 0 | 3.2253 | 9.6577 | 27.6025 | 0 | 40.4854 | 0 | 0 | 27.6025
1318 | 0 | 3.2447 | 9.5814 | 26.8306 | 0 | 39.6567 | 0 | 0 | 26.8306
1319 | 0 | 3.107 | 9.9792 | 29.9744 | 0 | 43.0606 | 0 | 0 | 29.9744
1320 | 0 | 3.1947 | 11.1257 | 25.6796 | 0 | 40 | 0 | 0 | 25.6796
1321 | 0 | 3.2833 | 10.14 | 25.1535 | 0 | 38.5769 | 0 | 0 | 25.1535
1322 | 0 | 3.365 | 10.7974 | 28.1988 | 0 | 42.3612 | 0 | 0 | 28.1988
1323 | 0 | 3.2799 | 9.5144 | 23.7947 | 0 | 36.5889 | 0 | 0 | 23.7947
1324 | 0 | 3.8858 | 10.0795 | 20.2424 | 0 | 34.2077 | 0 | 0 | 20.2424
1325 | 0 | 2.4242 | 10.8858 | 32.6515 | 0 | 45.9615 | 0 | 0 | 32.6515
1326 | 0 | 3.0434 | 10.6468 | 25.8483 | 0 | 39.5385 | 0 | 0 | 25.8483
1327 | 0 | 3.2602 | 11.0885 | 27.2882 | 0 | 41.637 | 0 | 0 | 27.2882
1328 | 0 | 3.5029 | 10.8666 | 30.9982 | 11.7231 | 57.0909 | 0 | 0 | 42.7214
1329 | 0 | 3.2315 | 10.8102 | 31.8218 | 14.2788 | 60.1424 | 0 | 0 | 46.1006
1330 | 0 | 3.6777 | 10.5267 | 34.1277 | 19.298 | 67.6301 | 0 | 0 | 53.4257
1331 | 0 | 2.7793 | 10.367 | 27.259 | -3.9785 | 36.4268 | 0 | 0 | 23.2805
1332 | 0 | 3.1772 | 10.3526 | 23.9092 | 10.3939 | 47.833 | 0 | 200 | 234.3032
1333 | 0 | 3.2817 | 11.6118 | 28.2945 | 17.4589 | 60.6469 | 0 | 0 | 45.7535
1334 | 0 | 3.0507 | 12.737 | 28.0891 | 3.7626 | 47.6394 | 0 | 0 | 31.8517
1335 | 0 | 2.9087 | 13.6354 | 25.7318 | 20.5046 | 62.7805 | 0 | 0 | 46.2365
1336 | 0 | 3.1605 | 14.7029 | 26.9718 | 14.7417 | 59.5768 | 0 | 0 | 41.7134
1337 | 0 | 3.3159 | 15.8613 | 22.9992 | 9.8096 | 51.9859 | 0 | 0 | 32.8088
1338 | 0 | 3.3762 | 14.8019 | 27.2244 | 15.0597 | 60.4622 | 0 | 0 | 42.2842
1339 | 0 | 3.6273 | 12.0313 | 29.9353 | 18.2408 | 63.8347 | 0 | 0 | 48.1761
1340 | 0 | 2.917 | 10.9474 | 28.9345 | 0 | 42.799 | 0 | 0 | 28.9345
1341 | 0 | 3.3354 | 10.9651 | 25.6343 | 0 | 39.9348 | 0 | 0 | 25.6343
1342 | 0 | 3.3774 | 11.9058 | 31.3575 | 0 | 46.6407 | 0 | 0 | 31.3575
1343 | 0 | 2.992 | 12.8908 | 24.5776 | 0 | 40.4605 | 0 | 0 | 24.5776
1344 | 0 | 3.0998 | 13.5688 | 26.0664 | 0 | 42.735 | 0 | 0 | 26.0664
1345 | 0 | 3.3083 | 18.0446 | 32.2527 | 0 | 53.6056 | 0 | 0 | 32.2527
1346 | 0 | 3.2762 | 19.5314 | 29.5003 | 0 | 52.3079 | 0 | 200 | 229.5003
1347 | 0 | 3.8529 | 16.6543 | 38.28 | 0 | 58.7872 | 200 | 0 | 238.28
1348 | 0 | 2.9971 | 15.1437 | 26.1604 | 0 | 44.3013 | 0 | 0 | 26.1604
1349 | 0 | 3.5472 | 14.5048 | 27.8738 | 0 | 45.9258 | 0 | 0 | 27.8738
1350 | 0 | 3.5952 | 14.712 | 23.5772 | 0 | 41.8845 | 0 | 0 | 23.5772
1351 | 0 | 3.0736 | 13.5213 | 33.1877 | 0 | 49.7826 | 0 | 0 | 33.1877
1352 | 0 | 3.3831 | 13.1182 | 22.0973 | 9.7707 | 48.3693 | 0 | 0 | 31.868
1353 | 0 | 2.9 | 13.423 | 25.0054 | -0.86442 | 40.464 | 0 | 0 | 24.141
1354 | 0 | 3.7367 | 12.4947 | 26.4316 | 16.8684 | 59.5314 | 0 | 0 | 43.3
1355 | 0 | 3.5853 | 11.5453 | 30.68 | 1.1994 | 47.01 | 0 | 0 | 31.8794
1356 | 0 | 2.7883 | 12.337 | 26.8395 | 10.2343 | 52.1991 | 0 | 0 | 37.0738
1357 | 0 | 2.4319 | 12.8335 | 24.7191 | 19.1845 | 59.1689 | 0 | 0 | 43.9036
1358 | 0 | 2.445 | 12.0808 | 28.6399 | 3.296 | 46.4618 | 0 | 0 | 31.9359
1359 | 0 | 3.1509 | 13.6785 | 29.3155 | 18.0667 | 64.2115 | 0 | 0 | 47.3822
1360 | 0 | 2.9991 | 14.3611 | 26.3232 | 11.2852 | 54.9687 | 0 | 0 | 37.6085
1361 | 0 | 3.257 | 14.3536 | 30.5961 | 24.4979 | 72.7047 | 0 | 200 | 255.094
1362 | 0 | 3.4175 | 13.1625 | 26.0238 | 14.4372 | 57.041 | 0 | 0 | 40.461
1363 | 0 | 3.7602 | 11.2427 | 30.7975 | 8.3992 | 54.1996 | 0 | 0 | 39.1968
1364 | 0 | 2.6232 | 10.6872 | 23.6679 | 0 | 36.9783 | 0 | 0 | 23.6679
1365 | 0 | 3.3189 | 11.4498 | 29.8453 | 0 | 44.6141 | 0 | 0 | 29.8453
1366 | 0 | 3.2061 | 12.0666 | 32.0434 | 0 | 47.3161 | 0 | 0 | 32.0434
1367 | 0 | 3.3057 | 12.8908 | 23.1248 | 0 | 39.3213 | 0 | 0 | 23.1248
1368 | 0 | 3.2196 | 14.1331 | 28.0898 | 0 | 45.4425 | 0 | 0 | 28.0898
1369 | 0 | 3.23 | 18.5518 | 31.9329 | 0 | 53.7148 | 0 | 0 | 31.9329
1370 | 0 | 2.3848 | 22.3566 | 31.8125 | 0 | 56.554 | 0 | 0 | 31.8125
1371 | 0 | 3.6309 | 17.0642 | 28.4381 | 0 | 49.1332 | 0 | 0 | 28.4381
1372 | 0 | 3.4074 | 14.6639 | 26.8738 | 0 | 44.9452 | 0 | 0 | 26.8738
1373 | 0 | 3.1709 | 14.365 | 30.6236 | 0 | 48.1595 | 0 | 0 | 30.6236
1374 | 0 | 3.196 | 14.6395 | 27.1077 | 0 | 44.9431 | 0 | 0 | 27.1077
1375 | 0 | 3.4762 | 13.7423 | 19.9795 | 0 | 37.198 | 0 | 200 | 219.9795
1376 | 0 | 3.2548 | 13.2553 | 23.9164 | 14.5545 | 54.981 | 0 | 0 | 38.4709
1377 | 0 | 2.9476 | 13.2872 | 26.7403 | 9.8827 | 52.8578 | 0 | 0 | 36.623
1378 | 0 | 2.8753 | 12.5624 | 28.3002 | 18.9716 | 62.7095 | 0 | 0 | 47.2718
1379 | 0 | 3.6019 | 12.069 | 25.9867 | 19.6573 | 61.3149 | 0 | 0 | 45.644
1380 | 0 | 3.0808 | 13.6263 | 29.8327 | 21.438 | 67.9778 | 0 | 0 | 51.2707
1381 | 0 | 2.8466 | 14.608 | 27.3105 | 15.5847 | 60.3498 | 0 | 0 | 42.8951
1382 | 0 | 3.6308 | 15.0377 | 29.9393 | 9.882 | 58.4898 | 0 | 0 | 39.8213
1383 | 0 | 3.1918 | 16.4263 | 23.1355 | 13.839 | 56.5927 | 0 | 0 | 36.9745
1384 | 0 | 3.5353 | 16.9174 | 32.2292 | 22.0567 | 74.7386 | 0 | 0 | 54.2859
1385 | 0 | 3.1903 | 19.5997 | 30.1323 | 5.922 | 58.8443 | 0 | 0 | 36.0543
1386 | 0 | 2.6758 | 18.0624 | 23.0059 | 21.3921 | 65.1361 | 0 | 0 | 44.398
1387 | 0 | 3.5996 | 15.0875 | 21.3588 | 11.5564 | 51.6023 | 0 | 0 | 32.9151
1388 | 0 | 3.5651 | 12.9426 | 30.2701 | 0 | 46.7778 | 0 | 200 | 230.2701
1389 | 0 | 3.6376 | 12.4194 | 22.7522 | 0 | 38.8092 | 0 | 0 | 22.7522
1390 | 0 | 3.6708 | 12.6293 | 29.6175 | 0 | 45.9176 | 0 | 0 | 29.6175
1391 | 0 | 2.3549 | 13.0531 | 20.0647 | 0 | 35.4726 | 0 | 0 | 20.0647
1392 | 0 | 3.2041 | 14.1331 | 33.8752 | 0 | 51.2124 | 0 | 0 | 33.8752
1393 | 0 | 3.5395 | 18.8562 | 28.7071 | 0 | 51.1028 | 0 | 0 | 28.7071
1394 | 0 | 3.5782 | 21.8695 | 30.796 | 0 | 56.2437 | 0 | 0 | 30.796
1395 | 0 | 3.3241 | 18.9492 | 35.1562 | 0 | 57.4296 | 0 | 0 | 35.1562
1396 | 0 | 3.6447 | 17.2001 | 28.5349 | 0 | 49.3797 | 0 | 0 | 28.5349
1397 | 0 | 3.5885 | 17.5797 | 33.4113 | 0 | 54.5796 | 0 | 0 | 33.4113
1398 | 0 | 2.9853 | 17.6148 | 29.1302 | 0 | 49.7302 | 0 | 0 | 29.1302
1399 | 0 | 3.1207 | 18.0156 | 25.2602 | 0 | 46.3966 | 0 | 0 | 25.2602
1400 | 0 | 3.279 | 16.6139 | 27.9629 | 15.7701 | 63.6259 | 0 | 200 | 243.733
1401 | 0 | 3.0055 | 16.8181 | 19.8059 | 24.9453 | 64.5748 | 0 | 0 | 44.7512
1402 | 0 | 3.7276 | 16.4872 | 37.4405 | 25.2909 | 82.9463 | 0 | 0 | 62.7315
1403 | 0 | 3.4335 | 15.3416 | 27.6249 | 14.2902 | 60.6901 | 0 | 0 | 41.9151
1404 | 0 | 3.4579 | 16.508 | 28.2766 | 16.8827 | 65.1252 | 0 | 0 | 45.1593
1405 | 0 | 3.2385 | 17.6248 | 36.5027 | 15.3547 | 72.7207 | 0 | 0 | 51.8574
1406 | 0 | 3.247 | 16.434 | 27.2486 | 13.8796 | 60.8092 | 0 | 0 | 41.1282
1407 | 0 | 3.4879 | 17.5426 | 27.2568 | 8.2577 | 56.545 | 0 | 0 | 35.5145
1408 | 0 | 3.836 | 18.7163 | 33.1887 | 13.6824 | 69.4234 | 200 | 0 | 246.8711
1409 | 0 | 3.3345 | 20.9683 | 28.3496 | 12.5268 | 65.1792 | 0 | 0 | 40.8765
1410 | 0 | 2.9127 | 19.3988 | 25.651 | 13.1543 | 61.1167 | 0 | 0 | 38.8053
1411 | 0 | 3.4919 | 16.7635 | 27.3957 | 8.5497 | 56.2007 | 0 | 0 | 35.9454
1412 | 0 | 3.6125 | 14.6775 | 25.9732 | 0 | 44.2631 | 0 | 200 | 225.9732
1413 | 0 | 2.8444 | 13.7929 | 27.7613 | 0 | 44.3986 | 0 | 0 | 27.7613
1414 | 0 | 3.1818 | 13.835 | 30.7411 | 0 | 47.7579 | 0 | 0 | 30.7411
1415 | 0 | 3.9852 | 14.2703 | 32.5301 | 0 | 50.7855 | 0 | 0 | 32.5301
1416 | 0 | 3.3439 | 14.778 | 30.4671 | 0 | 48.589 | 0 | 0 | 30.4671
1417 | 0 | 2.9063 | 18.9576 | 28.6062 | 0 | 50.4701 | 0 | 0 | 28.6062
1418 | 0 | 2.772 | 21.5772 | 39.244 | 0 | 63.5932 | 0 | 0 | 39.244
1419 | 0 | 3.3971 | 18.2116 | 33.092 | 0 | 54.7007 | 0 | 0 | 33.092
1420 | 0 | 3.1054 | 15.8977 | 27.2554 | 0 | 46.2586 | 0 | 0 | 27.2554
1421 | 0 | 3.2498 | 15.9025 | 31.9511 | 0 | 51.1034 | 0 | 0 | 31.9511
1422 | 0 | 3.1626 | 15.6554 | 30.7816 | 0 | 49.5996 | 0 | 0 | 30.7816
1423 | 0 | 2.4745 | 15.2895 | 23.793 | 0 | 41.557 | 0 | 0 | 23.793
1424 | 0 | 3.0639 | 14.4891 | 25.5645 | 4.0373 | 47.1548 | 0 | 200 | 229.6018
1425 | 0 | 2.9351 | 14.0341 | 37.1451 | 6.1293 | 60.2436 | 0 | 0 | 43.2744
1426 | 0 | 2.8989 | 13.1038 | 33.1523 | 17.9024 | 67.0573 | 0 | 0 | 51.0547
1427 | 0 | 2.7941 | 12.3308 | 27.3678 | 12.9735 | 55.4662 | 0 | 0 | 40.3414
1428 | 0 | 2.7432 | 13.0196 | 39.2694 | 9.1647 | 64.1969 | 0 | 0 | 48.4341
1429 | 0 | 2.9817 | 13.8982 | 39.4379 | 12.863 | 69.1808 | 0 | 0 | 52.3009
1430 | 0 | 2.613 | 13.3129 | 32.1231 | 16.1504 | 64.1994 | 0 | 0 | 48.2735
1431 | 0 | 2.9983 | 14.4513 | 39.2915 | 11.3441 | 68.0852 | 0 | 0 | 50.6356
1432 | 0 | 3.0062 | 15.5919 | 29.3215 | 17.1603 | 65.0799 | 0 | 0 | 46.4818
1433 | 0 | 3.0627 | 17.889 | 38.2687 | 16.3256 | 75.546 | 0 | 0 | 54.5943
1434 | 0 | 3.3596 | 16.6147 | 30.2993 | 1.8285 | 52.1021 | 0 | 0 | 32.1278
1435 | 0 | 2.7707 | 14.7918 | 31.3164 | 8.1877 | 57.0666 | 0 | 0 | 39.5041
1436 | 0 | 3.3159 | 13.463 | 23.1742 | 0 | 39.9532 | 0 | 0 | 23.1742
1437 | 0 | 3.0927 | 12.9849 | 31.8165 | 0 | 47.8941 | 0 | 0 | 31.8165
1438 | 0 | 2.5565 | 13.5135 | 32.3626 | 0 | 48.4325 | 0 | 200 | 232.3626
1439 | 0 | 2.988 | 14.3514 | 37.1524 | 0 | 54.4917 | 0 | 0 | 37.1524
1440 | 0 | 2.7678 | 15.3424 | 24.8183 | 0 | 42.9285 | 0 | 0 | 24.8183
1441 | 0 | 2.8901 | 19.9721 | 26.907 | 0 | 49.7693 | 0 | 0 | 26.907
1442 | 0 | 2.6656 | 22.454 | 30.2771 | 0 | 55.3966 | 0 | 0 | 30.2771
1443 | 0 | 3.2085 | 18.9492 | 32.0587 | 0 | 54.2165 | 0 | 0 | 32.0587
1444 | 0 | 3.1783 | 16.3775 | 35.3944 | 0 | 54.9503 | 0 | 0 | 35.3944
1445 | 0 | 3.0657 | 16.0423 | 30.6516 | 0 | 49.7596 | 0 | 0 | 30.6516
1446 | 0 | 3.0022 | 15.0023 | 36.7951 | 0 | 54.7996 | 0 | 0 | 36.7951
1447 | 0 | 2.0207 | 14.7738 | 35.8599 | 0 | 52.6543 | 0 | 0 | 35.8599
1448 | 0 | 3.5425 | 13.5295 | 30.98 | 7.158 | 55.2099 | 0 | 0 | 38.138
1449 | 0 | 2.7549 | 12.6761 | 28.704 | 4.8428 | 48.9778 | 0 | 0 | 33.5468
1450 | 0 | 2.3947 | 12.4947 | 29.0878 | 18.5624 | 62.5397 | 0 | 0 | 47.6502
1451 | 0 | 3.2943 | 11.8726 | 39.5467 | 16.3342 | 71.0478 | 0 | 200 | 255.8809
1452 | 0 | 2.3831 | 12.0337 | 32.6247 | 6.6309 | 53.6724 | 0 | 0 | 39.2557
1453 | 0 | 3.0873 | 12.9222 | 28.3526 | 17.6846 | 62.0467 | 0 | 0 | 46.0372
1454 | 0 | 2.9624 | 12.5737 | 38.068 | 20.6312 | 74.2353 | 0 | 0 | 58.6992
1455 | 0 | 2.935 | 13.8502 | 32.6698 | 20.0208 | 69.4759 | 0 | 0 | 52.6907
1456 | 0 | 3.2513 | 15.1186 | 23.2023 | 23.751 | 65.3232 | 0 | 0 | 46.9533
1457 | 0 | 2.9794 | 16.9767 | 22.1525 | 9.9757 | 52.0842 | 0 | 0 | 32.1282
1458 | 0 | 2.5938 | 16.1693 | 19.8809 | 17.1273 | 55.7713 | 0 | 0 | 37.0082
1459 | 0 | 3.0889 | 15.1951 | 25.1373 | 8.1093 | 51.5305 | 0 | 0 | 33.2466
1460 | 0 | 2.538 | 14.2484 | 34.0591 | 0 | 50.8455 | 0 | 0 | 34.0591
1461 | 0 | 2.9005 | 12.9552 | 31.9849 | 0 | 47.8406 | 0 | 0 | 31.9849
1462 | 0 | 2.8846 | 12.2276 | 34.2913 | 0 | 49.4035 | 0 | 0 | 34.2913
1463 | 0 | 2.969 | 11.7014 | 29.0835 | 0 | 43.7539 | 0 | 0 | 29.0835
1464 | 0 | 2.9939 | 12.9956 | 35.0135 | 0 | 51.003 | 0 | 0 | 35.0135
1465 | 0 | 3.1728 | 12.3017 | 31.5357 | 0 | 47.0102 | 0 | 0 | 31.5357
1466 | 0 | 2.8332 | 16.517 | 30.642 | 0 | 49.9922 | 0 | 200 | 230.642
1467 | 0 | 2.5975 | 17.5671 | 33.6174 | 0 | 53.782 | 0 | 0 | 33.6174
1468 | 0 | 2.5129 | 14.5909 | 26.5491 | 0 | 43.653 | 0 | 0 | 26.5491
1469 | 0 | 2.9804 | 13.6953 | 36.3983 | 0 | 53.074 | 0 | 0 | 36.3983
1470 | 0 | 3.3543 | 12.8548 | 25.333 | 0 | 41.542 | 0 | 0 | 25.333
1471 | 0 | 2.9 | 12.7343 | 33.1298 | 0 | 48.764 | 0 | 0 | 33.1298
1472 | 0 | 2.8391 | 12.0216 | 31.2042 | 18.3475 | 64.4123 | 0 | 0 | 49.5516
1473 | 0 | 3.1164 | 11.6343 | 25.609 | 12.1719 | 52.5316 | 0 | 0 | 37.7809
1474 | 0 | 2.8326 | 10.3904 | 22.1316 | 17.6291 | 52.9837 | 0 | 0 | 39.7608
1475 | 0 | 2.6005 | 8.8071 | 33.7862 | 9.8628 | 55.0566 | 200 | 0 | 243.649
1476 | 0 | 3.2074 | 8.1506 | 27.8653 | 23.2464 | 62.4697 | 0 | 0 | 51.1117
1477 | 0 | 2.8323 | 8.5726 | 37.5167 | 10.4577 | 59.3793 | 0 | 0 | 47.9744
1478 | 0 | 3.0934 | 8.4372 | 35.7101 | 11.4189 | 58.6597 | 0 | 0 | 47.129
1479 | 0 | 2.8193 | 9.8235 | 33.1042 | 11.4298 | 57.1769 | 0 | 0 | 44.534
1480 | 0 | 2.8009 | 12.6297 | 24.5812 | 4.709 | 44.7208 | 0 | 0 | 29.2902
1481 | 0 | 3.4712 | 14.633 | 32.604 | 12.5839 | 63.2921 | 0 | 0 | 45.1879
1482 | 0 | 3.0583 | 12.0337 | 33.4961 | 20.1706 | 68.7588 | 0 | 0 | 53.6667
1483 | 0 | 2.6591 | 11.8766 | 34.8222 | 12.9747 | 62.3327 | 0 | 200 | 247.7969
1484 | 0 | 2.6602 | 10.3131 | 22.5984 | 0 | 35.5717 | 0 | 0 | 22.5984
1485 | 0 | 3.3881 | 9.3641 | 36.8827 | 0 | 49.6349 | 0 | 0 | 36.8827
1486 | 0 | 2.8134 | 9.8719 | 33.4707 | 0 | 46.156 | 0 | 0 | 33.4707
1487 | 0 | 2.7613 | 9.5575 | 31.5959 | 0 | 43.9146 | 0 | 0 | 31.5959
1488 | 0 | 2.9082 | 9.6079 | 35.662 | 0 | 48.1781 | 0 | 0 | 35.662
1489 | 0 | 2.6054 | 9.1004 | 36.4641 | 0 | 48.1699 | 0 | 0 | 36.4641
1490 | 0 | 2.5616 | 8.479 | 23.5752 | 0 | 34.6158 | 0 | 0 | 23.5752
1491 | 0 | 2.7558 | 7.2102 | 30.2902 | 0 | 40.2562 | 0 | 0 | 30.2902
1492 | 0 | 3.2021 | 7.5665 | 35.8145 | 0 | 46.5831 | 0 | 0 | 35.8145
1493 | 0 | 2.863 | 8.5663 | 37.0185 | 0 | 48.4478 | 0 | 0 | 37.0185
1494 | 0 | 2.5409 | 7.9646 | 30.2612 | 0 | 40.7666 | 0 | 0 | 30.2612
1495 | 0 | 2.3187 | 6.9432 | 29.1414 | 0 | 38.4034 | 0 | 0 | 29.1414
1496 | 0 | 3.2076 | 5.8104 | 29.7233 | 17.9195 | 56.6609 | 0 | 0 | 47.6429
1497 | 0 | 2.7793 | 5.1622 | 28.6539 | 17.7063 | 54.3017 | 0 | 0 | 46.3601
1498 | 0 | 2.8834 | 4.8796 | 28.363 | 11.0354 | 47.1615 | 0 | 0 | 39.3985
1499 | 0 | 3.1835 | 5.2208 | 30.7142 | 12.8555 | 51.9739 | 0 | 0 | 43.5696
1500 | 0 | 3.4446 | 5.5969 | 35.3945 | 8.2408 | 52.6768 | 0 | 0 | 43.6353
1501 | 0 | 2.8843 | 5.5636 | 37.1951 | 8.0227 | 53.6657 | 0 | 0 | 45.2178
1502 | 0 | 3.3515 | 5.1654 | 35.3304 | 19.0301 | 62.8774 | 0 | 0 | 54.3604
1503 | 0 | 2.9575 | 4.852 | 28.5206 | 9.3542 | 45.6843 | 0 | 0 | 37.8748
1504 | 0 | 3.2426 | 5.3629 | 33.4548 | 9.5917 | 51.6519 | 0 | 0 | 43.0465
1505 | 0 | 2.6347 | 5.6501 | 27.7503 | 16.8307 | 52.8657 | 0 | 0 | 44.581
1506 | 0 | 3.4689 | 2.9356 | 30.5179 | 20.7633 | 57.6856 | 0 | 0 | 51.2811
1507 | 0 | 2.3557 | 2.3699 | 34.2066 | 10.6231 | 49.5553 | 0 | 0 | 44.8298
1508 | 0 | 3.5524 | 2.62 | 25.469 | 0 | 31.6414 | 0 | 0 | 25.469
1509 | 0 | 2.7757 | 2.6433 | 34.1754 | 0 | 39.5944 | 0 | 0 | 34.1754
1510 | 0 | 3.1277 | 2.8222 | 37.3744 | 0 | 43.3243 | 0 | 0 | 37.3744
1511 | 0 | 3.1664 | 3.3158 | 29.762 | 0 | 36.2442 | 0 | 0 | 29.762
1512 | 0 | 3.1404 | 4.217 | 32.5639 | 0 | 39.9213 | 0 | 0 | 32.5639
1513 | 0 | 2.5224 | 5.8713 | 22.2649 | 0 | 30.6586 | 0 | 0 | 22.2649
1514 | 0 | 3.0366 | 9.692 | 35.1355 | 0 | 47.8641 | 0 | 200 | 235.1355
1515 | 0 | 2.8211 | 8.6222 | 35.6054 | 0 | 47.0487 | 0 | 0 | 35.6054
1516 | 0 | 2.6041 | 7.3298 | 27.0673 | 0 | 37.0011 | 0 | 0 | 27.0673
1517 | 0 | 2.5411 | 6.8174 | 34.4067 | 0 | 43.7652 | 0 | 0 | 34.4067
1518 | 0 | 3.0458 | 6.294 | 27.0999 | 0 | 36.4398 | 0 | 0 | 27.0999
1519 | 0 | 3.638 | 4.7537 | 30.0618 | 0 | 38.4535 | 0 | 0 | 30.0618
1520 | 0 | 2.9462 | 4.893 | 34.2327 | 22.7326 | 64.8044 | 0 | 0 | 56.9653
1521 | 0 | 2.7208 | 4.392 | 27.3737 | 20.5892 | 55.0757 | 0 | 0 | 47.9629
1522 | 0 | 3.0531 | 4.0362 | 31.5318 | 13.3809 | 52.002 | 0 | 0 | 44.9127
1523 | 0 | 2.8777 | 3.4293 | 14.9364 | 18.997 | 40.2404 | 0 | 0 | 33.9334
1524 | 0 | 2.7099 | 4.981 | 32.0028 | 20.1675 | 59.8612 | 0 | 0 | 52.1703
1525 | 0 | 3.0897 | 5.4691 | 24.1177 | 8.2464 | 40.9228 | 0 | 0 | 32.3641
1526 | 0 | 3.1449 | 7.1527 | 31.4122 | 21.9173 | 63.6271 | 0 | 0 | 53.3295
1527 | 0 | 2.9908 | 8.9557 | 35.3236 | 11.0917 | 58.3618 | 0 | 0 | 46.4153
1528 | 0 | 3.0964 | 9.8166 | 33.694 | 11.371 | 57.978 | 0 | 0 | 45.0649
1529 | 0 | 2.883 | 9.5637 | 30.1895 | 17.4607 | 60.0969 | 0 | 0 | 47.6501
1530 | 0 | 2.98 | 9.3762 | 30.4767 | 6.9889 | 49.8217 | 0 | 0 | 37.4655
1531 | 0 | 3.5688 | 7.102 | 29.1111 | 16.1945 | 55.9764 | 0 | 0 | 45.3056
1532 | 0 | 3.2797 | 6.35 | 32.4877 | 0 | 42.1174 | 0 | 0 | 32.4877
1533 | 0 | 3.3161 | 7.2486 | 27.2338 | 0 | 37.7985 | 0 | 0 | 27.2338
1534 | 0 | 2.8614 | 5.073 | 31.8474 | 0 | 39.7818 | 0 | 0 | 31.8474
1535 | 0 | 2.9131 | 7.0484 | 26.6374 | 0 | 36.5989 | 0 | 0 | 26.6374
1536 | 0 | 2.1982 | 10.0215 | 39.1157 | 0 | 51.3355 | 0 | 0 | 39.1157
1537 | 0 | 3.0703 | 9.8276 | 36.2639 | 0 | 49.1619 | 0 | 0 | 36.2639
1538 | 0 | 3.182 | 11.4456 | 30.9167 | 0 | 45.5444 | 0 | 0 | 30.9167
1539 | 0 | 2.807 | 9.7696 | 26.7791 | 0 | 39.3558 | 0 | 0 | 26.7791
1540 | 0 | 2.6458 | 8.9063 | 31.4124 | 0 | 42.9645 | 0 | 0 | 31.4124
1541 | 0 | 2.806 | 7.8657 | 23.3627 | 0 | 34.0344 | 0 | 0 | 23.3627
1542 | 0 | 3.1286 | 7.5277 | 29.5452 | 0 | 40.2015 | 0 | 200 | 229.5452
1543 | 0 | 2.8696 | 5.8588 | 28.413 | 0 | 37.1414 | 200 | 0 | 228.413
1544 | 7.0318 | 2.9174 | 4.893 | 35.122 | 13.9077 | 63.8719 | 0 | 0 | 56.0616
1545 | 30.3846 | 3.5625 | 4.1204 | 24.5996 | 8.4643 | 71.1314 | 0 | 0 | 63.4485
1546 | 41.7324 | 3.0646 | 3.8331 | 27.8963 | 9.0929 | 85.6193 | 0 | 0 | 78.7215
1547 | 10.3544 | 2.6877 | 3.6911 | 34.3799 | 11.3609 | 62.4739 | 0 | 0 | 56.0951
1548 | 3.2106 | 2.7329 | 3.7676 | 24.9368 | 22.8795 | 57.5274 | 0 | 0 | 51.0268
1549 | 0.75171 | 3.0456 | 3.7833 | 33.1381 | 10.3125 | 51.0312 | 0 | 0 | 44.2024
1550 | 2.2286 | 2.9682 | 3.6209 | 31.4286 | 15.4773 | 55.7235 | 0 | 0 | 49.1345
1551 | 0 | 2.4883 | 4.7481 | 32.2473 | 2.8938 | 42.3775 | 0 | 0 | 35.1411
1552 | 0 | 2.8071 | 5.9348 | 32.8273 | 14.8577 | 56.4269 | 0 | 0 | 47.685
1553 | 0 | 2.6866 | 6.2564 | 26.6332 | 12.1731 | 47.7493 | 0 | 0 | 38.8063
1554 | 0 | 2.5533 | 6.3695 | 23.0407 | 4.5027 | 36.4661 | 0 | 0 | 27.5434
1555 | 0 | 2.6697 | 6.9049 | 30.7392 | 20.2163 | 60.5301 | 0 | 0 | 50.9555
1556 | 0 | 2.7777 | 8.3451 | 27.4479 | 0 | 38.5707 | 0 | 0 | 27.4479
1557 | 0 | 3.1214 | 7.8949 | 29.5776 | 0 | 40.5939 | 0 | 0 | 29.5776
1558 | 0 | 2.5651 | 9.0119 | 30.2139 | 0 | 41.7909 | 0 | 0 | 30.2139
1559 | 0 | 2.7181 | 9.7262 | 29.9906 | 0 | 42.4349 | 0 | 0 | 29.9906
1560 | 0 | 3.2274 | 10.9083 | 27.7837 | 0 | 41.9194 | 0 | 0 | 27.7837
1561 | 0 | 2.8434 | 13.6825 | 37.0385 | 0 | 53.5644 | 0 | 0 | 37.0385
1562 | 0 | 2.7354 | 15.4398 | 31.7854 | 0 | 49.9606 | 0 | 0 | 31.7854
1563 | 0 | 3.1721 | 12.7202 | 32.7945 | 0 | 48.6868 | 0 | 0 | 32.7945
1564 | 0 | 3.2314 | 11.2368 | 28.146 | 0 | 42.6142 | 0 | 0 | 28.146
1565 | 0 | 2.9993 | 8.9139 | 28.7611 | 0 | 40.6743 | 0 | 0 | 28.7611
1566 | 0 | 3.4353 | 6.7295 | 29.2497 | 0 | 39.4144 | 0 | 0 | 29.2497
1567 | 0 | 3.1035 | 5.4904 | 22.5559 | 0 | 31.1498 | 0 | 0 | 22.5559
1568 | 0 | 3.1802 | 5.8526 | 34.3439 | 13.9307 | 57.3074 | 0 | 0 | 48.2746
1569 | 0 | 2.2311 | 5.4785 | 35.7852 | 9.5769 | 53.0717 | 0 | 0 | 45.3621
1570 | 0 | 3.3899 | 5.5249 | 33.5226 | 13.6603 | 56.0976 | 0 | 200 | 247.1829
1571 | 0 | 2.9165 | 5.5892 | 27.2301 | 12.4431 | 48.1789 | 0 | 0 | 39.6731
1572 | 0 | 2.6942 | 5.891 | 34.621 | 14.5483 | 57.7546 | 0 | 0 | 49.1693
1573 | 0 | 2.589 | 5.2029 | 31.1574 | 11.0886 | 50.0379 | 0 | 0 | 42.246
1574 | 0 | 3.1075 | 5.3457 | 37.2844 | 14.5701 | 60.3077 | 0 | 0 | 51.8545
1575 | 0 | 2.2191 | 5.9503 | 28.4171 | 12.0099 | 48.5964 | 0 | 0 | 40.4271
1576 | 0 | 3.2252 | 5.1774 | 23.9795 | 22.4423 | 54.8244 | 0 | 0 | 46.4218
1577 | 0 | 3.4385 | 5.116 | 27.7854 | 8.9788 | 45.3187 | 0 | 0 | 36.7641
1578 | 0 | 3.437 | 4.4763 | 26.3062 | 9.6344 | 43.8538 | 0 | 0 | 35.9406
1579 | 0 | 2.6748 | 3.7501 | 31.9256 | 17.9647 | 56.3153 | 0 | 0 | 49.8903
1580 | 0 | 3.2062 | 3.8344 | 26.8571 | 0 | 33.8977 | 0 | 0 | 26.8571
1581 | 0 | 3.0529 | 3.7744 | 24.5774 | 0 | 31.4047 | 0 | 0 | 24.5774
1582 | 0 | 3.3525 | 4.5907 | 33.095 | 0 | 41.0382 | 0 | 0 | 33.095
1583 | 0 | 2.4921 | 5.3444 | 24.9176 | 0 | 32.7541 | 0 | 0 | 24.9176
1584 | 0 | 3.0728 | 6.4743 | 33.6072 | 0 | 43.1542 | 0 | 0 | 33.6072
1585 | 0 | 2.8993 | 7.7987 | 33.1101 | 0 | 43.8081 | 0 | 0 | 33.1101
1586 | 0 | 2.778 | 10.8611 | 35.8479 | 0 | 49.487 | 0 | 0 | 35.8479
1587 | 0 | 3.4774 | 9.3598 | 36.0878 | 0 | 48.9251 | 0 | 0 | 36.0878
1588 | 0 | 2.9593 | 8.4265 | 30.9532 | 0 | 42.339 | 0 | 0 | 30.9532
1589 | 0 | 3.0672 | 8.4946 | 34.6234 | 0 | 46.1853 | 0 | 0 | 34.6234
1590 | 0 | 2.828 | 8.5437 | 29.7346 | 0 | 41.1063 | 0 | 0 | 29.7346
1591 | 0 | 3.0301 | 8.8796 | 24.7515 | 0 | 36.6612 | 0 | 0 | 24.7515
1592 | 0 | 3.1422 | 8.6629 | 26.4095 | 14.1759 | 52.3904 | 0 | 0 | 40.5854
1593 | 0 | 2.6835 | 8.2625 | 27.6358 | 13.4807 | 52.0625 | 0 | 0 | 41.1165
1594 | 0 | 2.4623 | 6.6752 | 34.6183 | 16.4621 | 60.2179 | 0 | 0 | 51.0804
1595 | 0 | 3.3783 | 5.9819 | 34.1972 | 15.7534 | 59.3109 | 0 | 0 | 49.9506
1596 | 0 | 2.8669 | 6.0427 | 34.0098 | 17.3533 | 60.2727 | 0 | 0 | 51.363
1597 | 0 | 3.3608 | 4.7593 | 22.2412 | 8.2244 | 38.5857 | 0 | 0 | 30.4656
1598 | 0 | 3.3566 | 5.6743 | 29.5855 | 11.3407 | 49.9571 | 0 | 0 | 40.9262
1599 | 0 | 3.5056 | 5.6927 | 30.9898 | 10.0228 | 50.2109 | 0 | 0 | 41.0126
1600 | 0 | 2.7898 | 4.8934 | 39.3033 | 7.9621 | 54.9486 | 0 | 0 | 47.2654
1601 | 0 | 2.593 | 4.8879 | 27.2928 | 7.9646 | 42.7383 | 0 | 0 | 35.2574
1602 | 0 | 2.8544 | 5.8126 | 33.7971 | 11.8078 | 54.272 | 0 | 200 | 245.605
1603 | 0 | 2.6273 | 4.243 | 37.8454 | 2.0822 | 46.798 | 0 | 0 | 39.9277
1604 | 0 | 2.9027 | 3.6609 | 26.4766 | 0 | 33.0403 | 0 | 0 | 26.4766
1605 | 0 | 3.0063 | 4.34 | 35.5327 | 0 | 42.8789 | 0 | 0 | 35.5327
1606 | 0 | 3.7174 | 4.9122 | 31.4867 | 0 | 40.1163 | 0 | 0 | 31.4867
1607 | 0 | 2.6197 | 5.5878 | 32.1143 | 0 | 40.3219 | 0 | 0 | 32.1143
1608 | 0 | 2.6696 | 6.7161 | 21.2597 | 0 | 30.6455 | 0 | 0 | 21.2597
1609 | 0 | 2.9373 | 8.8132 | 28.4663 | 0 | 40.2168 | 0 | 0 | 28.4663
1610 | 0 | 3.1751 | 11.7379 | 34.9075 | 0 | 49.8205 | 0 | 0 | 34.9075
1611 | 0 | 2.7142 | 9.4418 | 28.4701 | 0 | 40.6261 | 200 | 0 | 228.4701
1612 | 0 | 2.9997 | 8.7006 | 40.7128 | 0 | 52.4131 | 0 | 0 | 40.7128
1613 | 0 | 3.3759 | 8.6344 | 30.0395 | 0 | 42.0498 | 0 | 0 | 30.0395
1614 | 0 | 3.3712 | 7.6729 | 30.7758 | 0 | 41.8199 | 0 | 0 | 30.7758
1615 | 0 | 3.1071 | 7.406 | 36.511 | 0 | 47.0242 | 0 | 0 | 36.511
1616 | 0 | 3.3913 | 6.4695 | 34.7113 | 12.2343 | 56.8063 | 0 | 0 | 46.9455
1617 | 0 | 2.8431 | 5.6822 | 36.817 | 14.4357 | 59.778 | 0 | 0 | 51.2527
1618 | 0 | 3.1113 | 5.2542 | 33.274 | 16.9508 | 58.5903 | 0 | 0 | 50.2248
1619 | 0 | 3.241 | 4.3456 | 22.4719 | 8.665 | 38.7236 | 0 | 0 | 31.1369
1620 | 0 | 2.9429 | 3.8435 | 29.229 | 11.3569 | 47.3722 | 0 | 0 | 40.5859
1621 | 0 | 2.8421 | 4.1382 | 28.5477 | 11.2278 | 46.7557 | 0 | 0 | 39.7755
1622 | 0 | 2.5594 | 4.935 | 25.7457 | 13.4682 | 46.7083 | 0 | 0 | 39.2139
1623 | 0 | 2.7829 | 4.2329 | 26.2259 | 22.7307 | 55.9725 | 0 | 0 | 48.9566
1624 | 0 | 2.8018 | 4.3253 | 24.4236 | 9.4426 | 40.9933 | 0 | 0 | 33.8662
1625 | 0 | 2.6568 | 4.7739 | 21.9338 | 6.7978 | 36.1623 | 0 | 0 | 28.7317
1626 | 0 | 3.2446 | 3.8081 | 29.9192 | 9.1847 | 46.1566 | 0 | 0 | 39.1039
1627 | 0 | 2.8281 | 1.9531 | 32.1922 | 9.7477 | 46.7211 | 0 | 0 | 41.9399
1628 | 0 | 3.232 | 1.5255 | 27.7553 | 0 | 32.5127 | 0 | 0 | 27.7553
1629 | 0 | 3.1948 | 1.2767 | 35.3577 | 0 | 39.8292 | 0 | 0 | 35.3577
1630 | 0 | 2.5698 | 1.3195 | 29.7552 | 0 | 33.6446 | 0 | 0 | 29.7552
1631 | 0 | 3.0648 | 1.5339 | 26.9766 | 0 | 31.5753 | 0 | 0 | 26.9766
1632 | 0 | 3.0914 | 1.3615 | 36.4314 | 0 | 40.8843 | 0 | 0 | 36.4314
1633 | 0 | 3.1792 | 1.7973 | 27.2436 | 0 | 32.2202 | 0 | 0 | 27.2436
1634 | 0 | 2.9602 | 2.1992 | 32.0459 | 0 | 37.2053 | 0 | 0 | 32.0459
1635 | 0 | 2.8236 | 1.9945 | 27.9961 | 0 | 32.8142 | 0 | 0 | 27.9961
1636 | 0 | 2.4415 | 3.6751 | 40.4501 | 0 | 46.5667 | 0 | 0 | 40.4501
1637 | 0 | 2.7642 | 4.2084 | 35.8916 | 0 | 42.8642 | 0 | 0 | 35.8916
1638 | 0 | 2.8134 | 3.8965 | 29.9987 | 0 | 36.7085 | 0 | 0 | 29.9987
1639 | 0 | 2.9158 | 2.2331 | 30.6296 | 0 | 35.7785 | 0 | 0 | 30.6296
1640 | 0 | 2.8791 | 2.4639 | 27.4247 | 14.0729 | 46.8406 | 0 | 0 | 41.4976
1641 | 0 | 3.2349 | 1.9857 | 38.2064 | 11.6465 | 55.0735 | 0 | 0 | 49.8529
1642 | 0 | 2.7131 | 1.7436 | 37.3792 | 7.6895 | 49.5255 | 0 | 0 | 45.0688
1643 | 0 | 3.4098 | 1.9834 | 36.9508 | 12.7817 | 55.1256 | 0 | 0 | 49.7324
1644 | 0 | 2.9134 | 2.2739 | 30.0426 | 19.6381 | 54.868 | 0 | 0 | 49.6807
1645 | 0 | 2.7945 | 2.4752 | 24.3948 | 12.7749 | 42.4393 | 0 | 0 | 37.1697
1646 | 0 | 2.8349 | 1.8702 | 22.0115 | 11.8082 | 38.5248 | 0 | 0 | 33.8197
1647 | 0 | 3.0329 | 2.2301 | 30.5944 | 13.6576 | 49.5151 | 0 | 0 | 44.2521
1648 | 0 | 3.1944 | 2.3118 | 34.1623 | 15.7385 | 55.4071 | 0 | 0 | 49.9008
1649 | 0 | 3.4934 | 1.9 | 29.2421 | 21.7197 | 56.3552 | 0 | 0 | 50.9619
1650 | 0 | 3.1036 | 1.9367 | 28.5199 | 12.8534 | 46.4137 | 0 | 0 | 41.3734
1651 | 0 | 2.5264 | 1.5167 | 25.1288 | 7.6535 | 36.8254 | 0 | 0 | 32.7823
1652 | 0 | 2.8054 | 1.4117 | 34.174 | 0 | 38.391 | 0 | 0 | 34.174
1653 | 0 | 3.6146 | 1.1486 | 36.8405 | 0 | 41.6037 | 0 | 200 | 236.8405
1654 | 0 | 2.51 | 1.2344 | 29.2427 | 0 | 32.987 | 0 | 0 | 29.2427
1655 | 0 | 2.807 | 1.1264 | 21.9321 | 0 | 25.8655 | 0 | 0 | 21.9321
1656 | 0 | 2.9588 | 3.103 | 39.499 | 0 | 45.5607 | 0 | 0 | 39.499
1657 | 0 | 3.0488 | 4.504 | 34.751 | 0 | 42.3039 | 0 | 0 | 34.751
1658 | 0 | 3.2891 | 2.1636 | 32.4425 | 0 | 37.8952 | 0 | 0 | 32.4425
1659 | 0 | 3.1456 | 1.767 | 28.4048 | 0 | 33.3174 | 0 | 0 | 28.4048
1660 | 0 | 2.2846 | 2.6204 | 26.5259 | 0 | 31.431 | 0 | 0 | 26.5259
1661 | 0 | 2.584 | 4.1246 | 35.7827 | 0 | 42.4913 | 0 | 0 | 35.7827
1662 | 0 | 2.9852 | 4.0143 | 41.9766 | 0 | 48.9762 | 0 | 0 | 41.9766
1663 | 0 | 2.3536 | 3.7797 | 27.6151 | 0 | 33.7484 | 0 | 0 | 27.6151
1664 | 0 | 2.9384 | 3.255 | 33.2126 | 3.4377 | 42.8437 | 0 | 0 | 36.6502
1665 | 0 | 3.2574 | 2.879 | 28.7411 | 6.5814 | 41.4589 | 0 | 0 | 35.3225
1666 | 0 | 2.9321 | 2.5613 | 29.1235 | 18.2891 | 52.906 | 0 | 0 | 47.4126
1667 | 0 | 3.1154 | 2.0266 | 20.0828 | 5.3318 | 30.5566 | 0 | 0 | 25.4146
1668 | 0 | 3.1822 | 1.8335 | 29.6953 | 5.3287 | 40.0397 | 0 | 0 | 35.024
1669 | 0 | 2.6223 | 2.4275 | 30.8891 | 12.0297 | 47.9685 | 0 | 0 | 42.9188
1670 | 0 | 2.9895 | 2.6713 | 31.6731 | 9.4931 | 46.8269 | 0 | 0 | 41.1662
1671 | 0 | 2.7577 | 4.5687 | 30.2956 | 6.2263 | 43.8483 | 0 | 0 | 36.5219
1672 | 0 | 2.5134 | 4.1175 | 32.4901 | 11.8763 | 50.9973 | 0 | 0 | 44.3664
1673 | 0 | 3.105 | 2.5985 | 33.4149 | 20.4745 | 59.5928 | 0 | 0 | 53.8893
1674 | 0 | 2.3432 | 2.1706 | 26.3704 | 12.7869 | 43.6711 | 0 | 0 | 39.1573
1675 | 0 | 2.804 | 1.877 | 34.339 | 19.9012 | 58.9212 | 0 | 0 | 54.2402
1676 | 0 | 3.2516 | 1.239 | 33.0628 | 0 | 37.5534 | 0 | 0 | 33.0628
1677 | 0 | 2.8276 | 1.6738 | 27.0138 | 0 | 31.5152 | 0 | 0 | 27.0138
1678 | 0 | 2.7537 | 2.2595 | 38.4173 | 0 | 43.4305 | 0 | 0 | 38.4173
1679 | 0 | 2.8836 | 1.5306 | 30.9903 | 0 | 35.4045 | 200 | 0 | 230.9903
1680 | 0 | 3.007 | 2.0402 | 34.4672 | 0 | 39.5144 | 0 | 0 | 34.4672
1681 | 0 | 3.497 | 3.1323 | 37.8145 | 0 | 44.4438 | 0 | 0 | 37.8145
1682 | 0 | 2.2888 | 5.6978 | 29.8473 | 0 | 37.834 | 0 | 0 | 29.8473
1683 | 0 | 3.3019 | 5.4257 | 28.2225 | 0 | 36.9501 | 0 | 0 | 28.2225
1684 | 0 | 2.9609 | 4.8622 | 30.3241 | 0 | 38.1472 | 0 | 0 | 30.3241
1685 | 0 | 2.6659 | 4.5112 | 36.6134 | 0 | 43.7905 | 0 | 0 | 36.6134
1686 | 0 | 2.0661 | 2.8107 | 23.2582 | 0 | 28.1351 | 0 | 0 | 23.2582
1687 | 0 | 2.8337 | 2.3223 | 31.2376 | 0 | 36.3936 | 0 | 0 | 31.2376
1688 | 0 | 2.743 | 2.0141 | 29.0357 | 19.2194 | 53.0123 | 0 | 0 | 48.2551
1689 | 0 | 3.2534 | 1.9476 | 33.3129 | 9.1559 | 47.6698 | 0 | 0 | 42.4688
1690 | 0 | 3.7681 | 1.7611 | 35.477 | 15.1033 | 56.1095 | 0 | 0 | 50.5803
1691 | 0 | 3.5433 | 2.0548 | 32.929 | 9.5494 | 48.0765 | 0 | 0 | 42.4784
1692 | 0 | 2.9236 | 1.3773 | 32.2736 | 8.1431 | 44.7176 | 0 | 0 | 40.4167
1693 | 0 | 3.5383 | 2.3299 | 31.2569 | 20.8652 | 57.9902 | 0 | 0 | 52.1221
1694 | 0 | 3.0682 | 2.5531 | 34.5699 | 15.1232 | 55.3143 | 0 | 0 | 49.6931
1695 | 0 | 2.9395 | 2.5155 | 33.518 | 7.8143 | 46.7873 | 0 | 0 | 41.3322
1696 | 0 | 3.3856 | 1.9886 | 33.5461 | 13.4809 | 52.4013 | 0 | 0 | 47.027
1697 | 0 | 2.7883 | 2.2272 | 26.3527 | 5.9693 | 37.3375 | 0 | 0 | 32.322
1698 | 0 | 3.0056 | 2.1199 | 33.4421 | 24.5297 | 63.0972 | 0 | 0 | 57.9718
1699 | 0 | 2.7325 | 1.5861 | 27.4468 | 17.0779 | 48.8433 | 0 | 0 | 44.5247
1700 | 0 | 2.6074 | 1.239 | 28.7272 | 0 | 32.5736 | 0 | 0 | 28.7272
1701 | 0 | 3.0422 | 1.0185 | 34.0732 | 0 | 38.134 | 0 | 0 | 34.0732
1702 | 0 | 2.9926 | 1.0722 | 35.8907 | 0 | 39.9555 | 0 | 0 | 35.8907
1703 | 0 | 3.214 | 1.2061 | 45.1241 | 0 | 49.5442 | 0 | 0 | 45.1241
1704 | 0 | 2.7752 | 2.2821 | 31.2926 | 0 | 36.3499 | 0 | 0 | 31.2926
1705 | 0 | 2.8303 | 3.6395 | 27.6197 | 0 | 34.0895 | 0 | 0 | 27.6197
1706 | 0 | 2.9516 | 7.0617 | 26.0867 | 0 | 36.1 | 0 | 0 | 26.0867
1707 | 0 | 3.1252 | 6.8191 | 27.1478 | 0 | 37.092 | 0 | 0 | 27.1478
1708 | 0 | 3.5336 | 8.3579 | 30.1167 | 0 | 42.0083 | 0 | 0 | 30.1167
1709 | 0 | 2.8517 | 9.2634 | 31.1995 | 0 | 43.3146 | 0 | 0 | 31.1995
1710 | 0 | 2.5915 | 9.4871 | 33.4659 | 0 | 45.5444 | 0 | 0 | 33.4659
1711 | 0 | 2.9906 | 9.5427 | 30.7657 | 0 | 43.299 | 0 | 0 | 30.7657
1712 | 0 | 2.6796 | 9.0056 | 37.1604 | 13.793 | 62.6387 | 0 | 200 | 250.9535
1713 | 0 | 2.9844 | 8.602 | 29.3561 | -1.3167 | 39.6258 | 0 | 0 | 28.0395
1714 | 0 | 3.0062 | 8.0286 | 31.504 | 0.077693 | 42.6165 | 0 | 0 | 31.5817
1715 | 0 | 2.9412 | 7.2255 | 23.5212 | 13.1301 | 46.818 | 0 | 0 | 36.6513
1716 | 0 | 3.2151 | 6.1944 | 28.0428 | 7.3255 | 44.7777 | 0 | 0 | 35.3682
1717 | 15.4289 | 2.8335 | 5.6465 | 23.4255 | 11.2433 | 58.5777 | 0 | 0 | 50.0977
1718 | 48.7382 | 3.1013 | 5.4278 | 30.1172 | 10.9294 | 98.3139 | 0 | 0 | 89.7848
1719 | 28.3627 | 2.7326 | 6.0361 | 20.0014 | 10.4211 | 67.554 | 0 | 0 | 58.7852
1720 | 0 | 2.5209 | 6.3135 | 31.699 | 20.3467 | 60.88 | 0 | 0 | 52.0456
1721 | 0 | 3.2275 | 6.1424 | 29.7196 | 16.6585 | 55.7481 | 0 | 0 | 46.3781
1722 | 0 | 2.3409 | 5.2558 | 33.2916 | 20.6927 | 61.581 | 0 | 0 | 53.9843
1723 | 0 | 3.3263 | 4.243 | 32.2298 | 8.2928 | 48.092 | 0 | 0 | 40.5227
1724 | 0 | 3.4078 | 4.0079 | 26.3758 | 0 | 33.7915 | 0 | 0 | 26.3758
1725 | 0 | 3.3206 | 4.0168 | 36.3956 | 0 | 43.733 | 0 | 0 | 36.3956
1726 | 0 | 3.041 | 4.4299 | 36.4512 | 0 | 43.9222 | 0 | 0 | 36.4512
1727 | 0 | 3.2172 | 6.0747 | 27.3874 | 0 | 36.6793 | 0 | 0 | 27.3874
1728 | 0 | 2.9242 | 8.1673 | 32.8739 | 0 | 43.9653 | 0 | 0 | 32.8739
1729 | 0 | 3.1913 | 11.5522 | 23.7499 | 0 | 38.4933 | 0 | 0 | 23.7499
1730 | 0 | 2.9748 | 13.1991 | 30.4381 | 0 | 46.612 | 0 | 0 | 30.4381
1731 | 0 | 2.9452 | 10.9171 | 31.2 | 0 | 45.0623 | 0 | 0 | 31.2
1732 | 0 | 2.5933 | 9.6603 | 31.4411 | 0 | 43.6947 | 0 | 0 | 31.4411
1733 | 0.12187 | 2.9167 | 8.3549 | 32.3937 | 0 | 43.7871 | 0 | 0 | 32.5156
1734 | 20.3786 | 2.9211 | 7.8906 | 30.9302 | 0 | 62.1205 | 0 | 0 | 51.3089
1735 | 54.5982 | 2.65 | 7.4797 | 33.9458 | 0 | 98.6737 | 0 | 0 | 88.544
1736 | 0.9416 | 2.9516 | 6.8807 | 33.9895 | 12.6663 | 57.4297 | 0 | 0 | 47.5974
1737 | 0 | 3.3194 | 6.497 | 28.5396 | 18.5814 | 56.9374 | 0 | 0 | 47.121
1738 | 0.76217 | 3.0366 | 5.7955 | 23.4261 | 11.3257 | 44.3462 | 0 | 0 | 35.514
1739 | 23.5759 | 2.4819 | 5.3274 | 27.4896 | 21.2155 | 80.0903 | 0 | 0 | 72.281
1740 | 84.1491 | 2.5877 | 5.3602 | 31.1405 | 10.3444 | 133.5818 | 0 | 0 | 125.6339
1741 | 88.1379 | 2.6398 | 6.4451 | 27.7372 | -0.62075 | 124.3391 | 0 | 0 | 115.2543
1742 | 61.349 | 2.9058 | 5.7564 | 28.7986 | 21.0248 | 119.8346 | 0 | 200 | 311.1724
1743 | 5.0204 | 2.6943 | 6.6372 | 35.782 | 18.9709 | 69.1048 | 0 | 0 | 59.7733
1744 | 0 | 3.0159 | 7.1656 | 29.1859 | 12.3501 | 51.7175 | 0 | 0 | 41.536
1745 | 0 | 3.2632 | 7.739 | 27.2812 | 19.3337 | 57.6171 | 0 | 0 | 46.6149
1746 | 0 | 3.2536 | 7.5944 | 35.4829 | 7.7903 | 54.1213 | 200 | 0 | 243.2733
1747 | 0 | 2.9746 | 6.8063 | 30.6686 | 16.4248 | 56.8743 | 0 | 0 | 47.0934
1748 | 0 | 2.7993 | 6.4368 | 33.4122 | 0 | 42.6483 | 0 | 0 | 33.4122
1749 | 0 | 2.7108 | 6.3598 | 34.4947 | 0 | 43.5654 | 0 | 0 | 34.4947
1750 | 0 | 3.3349 | 6.5199 | 36.4885 | 0 | 46.3433 | 0 | 0 | 36.4885
1751 | 0 | 3.1186 | 6.9673 | 40.6367 | 0 | 50.7226 | 0 | 0 | 40.6367
1752 | 0 | 3.1217 | 7.8448 | 30.2776 | 0 | 41.2441 | 0 | 0 | 30.2776
1753 | 0 | 2.5319 | 9.9291 | 28.8369 | 0 | 41.2979 | 0 | 0 | 28.8369
1754 | 0 | 2.9064 | 11.4456 | 22.7174 | 0 | 37.0694 | 0 | 0 | 22.7174
1755 | 0 | 3.2087 | 8.95 | 35.0865 | 0 | 47.2452 | 0 | 0 | 35.0865
1756 | 0 | 2.6953 | 7.9467 | 21.3687 | 0 | 32.0107 | 0 | 0 | 21.3687
1757 | 0 | 3.2944 | 7.7259 | 27.3437 | 0 | 38.364 | 0 | 0 | 27.3437
1758 | 0 | 3.2588 | 6.4392 | 31.607 | 0 | 41.3051 | 0 | 0 | 31.607
1759 | 16.621 | 2.7319 | 5.4168 | 28.9454 | 0 | 53.7151 | 0 | 0 | 45.5664
1760 | 73.4522 | 3.3005 | 5.6469 | 31.3609 | 14.1868 | 127.9473 | 0 | 0 | 118.9999
1761 | 56.4956 | 3.3682 | 5.2748 | 27.6999 | 10.2301 | 103.0686 | 0 | 0 | 94.4256
1762 | 13.6876 | 2.9881 | 4.8482 | 27.4535 | 21.4637 | 70.441 | 0 | 0 | 62.6047
1763 | 48.7061 | 2.7683 | 4.2147 | 30.1133 | 22.9374 | 108.7398 | 0 | 0 | 101.7567
1764 | 67.9861 | 3.0946 | 3.5401 | 31.8176 | 21.8331 | 128.2716 | 0 | 0 | 121.6368
1765 | 57.8708 | 2.8966 | 2.9847 | 23.0241 | 15.1169 | 101.893 | 0 | 0 | 96.0117
1766 | 0.40814 | 2.5721 | 3.3744 | 34.6443 | 9.1886 | 50.1877 | 0 | 0 | 44.2411
1767 | 0 | 2.9175 | 4.2329 | 16.1365 | 13.695 | 36.9818 | 0 | 0 | 29.8314
1768 | 0 | 2.9994 | 4.3253 | 38.5839 | 11.6704 | 57.5789 | 0 | 0 | 50.2543
1769 | 0 | 2.9273 | 4.2036 | 29.4764 | 19.6815 | 56.2888 | 0 | 0 | 49.1579
1770 | 0 | 2.6677 | 3.4741 | 17.3323 | 14.007 | 37.4811 | 0 | 0 | 31.3393
1771 | 0 | 2.799 | 3.7501 | 24.5097 | 7.6218 | 38.6805 | 0 | 0 | 32.1315
1772 | 0 | 3.0586 | 3.8344 | 30.8179 | 0 | 37.711 | 0 | 0 | 30.8179
1773 | 0 | 2.3034 | 4.0168 | 29.5241 | 0 | 35.8443 | 0 | 0 | 29.5241
1774 | 0 | 2.7703 | 4.3495 | 17.2187 | 0 | 24.3385 | 0 | 0 | 17.2187
1775 | 0 | 3.2988 | 4.7764 | 27.2581 | 0 | 35.3333 | 0 | 0 | 27.2581
1776 | 0 | 2.9857 | 5.5069 | 32.6561 | 0 | 41.1487 | 0 | 200 | 232.6561
1777 | 0 | 3.2386 | 7.4944 | 19.5913 | 0 | 30.3243 | 0 | 0 | 19.5913
1778 | 0 | 2.806 | 10.5688 | 36.3607 | 0 | 49.7355 | 0 | 0 | 36.3607
1779 | 0 | 2.5313 | 9.9336 | 34.9225 | 0 | 47.3873 | 0 | 0 | 34.9225
1780 | 0 | 3.2966 | 10.5513 | 33.5008 | 0 | 47.3488 | 0 | 0 | 33.5008
1781 | 2.1126 | 2.6505 | 10.731 | 28.8514 | 0 | 44.3455 | 0 | 0 | 30.964
1782 | 30.7368 | 2.684 | 10.7933 | 32.8768 | 0 | 77.091 | 0 | 0 | 63.6136
1783 | 99.3582 | 3.2843 | 11.1636 | 40.2751 | 0 | 154.0811 | 0 | 0 | 139.6332
1784 | 59.9936 | 2.615 | 10.9933 | 37.2609 | 13.4023 | 124.2651 | 0 | 0 | 110.6568
1785 | 4.9302 | 3.3373 | 10.7748 | 29.4943 | 14.9749 | 63.5115 | 0 | 0 | 49.3994
1786 | 26.9387 | 3.0339 | 10.194 | 30.8261 | 14.0132 | 85.0059 | 0 | 0 | 71.778
1787 | 42.058 | 2.8685 | 9.2545 | 29.0766 | 12.0367 | 95.2944 | 0 | 0 | 83.1714
1788 | 0 | 2.748 | 9.0003 | 31.9943 | 16.9369 | 60.6795 | 0 | 0 | 48.9312
1789 | 0 | 2.553 | 9.3731 | 28.6583 | 15.6259 | 56.2102 | 0 | 0 | 44.2842
1790 | 0 | 2.7106 | 8.9597 | 30.2391 | 12.3787 | 54.2881 | 0 | 0 | 42.6178
1791 | 0 | 3.0375 | 9.9002 | 31.6908 | 15.285 | 59.9136 | 0 | 0 | 46.9758
1792 | 0 | 2.6441 | 10.4793 | 30.7882 | 12.4672 | 56.3788 | 0 | 0 | 43.2553
1793 | 0 | 2.7724 | 11.1604 | 29.9373 | 8.1058 | 51.9758 | 0 | 0 | 38.043
1794 | 0 | 3.0087 | 10.3785 | 31.5538 | 1.8113 | 46.7522 | 0 | 0 | 33.365
1795 | 0 | 3.4186 | 8.8232 | 32.566 | 8.5816 | 53.3894 | 0 | 0 | 41.1476
1796 | 0 | 2.6358 | 8.2711 | 18.5972 | 0 | 29.5041 | 0 | 200 | 218.5972
1797 | 0 | 2.7008 | 7.9875 | 38.0471 | 0 | 48.7354 | 0 | 0 | 38.0471
1798 | 0 | 2.9253 | 7.8011 | 38.8737 | 0 | 49.6001 | 0 | 0 | 38.8737
1799 | 0 | 3.1225 | 8.1649 | 28.3128 | 0 | 39.6002 | 0 | 0 | 28.3128
1800 | 0 | 2.8922 | 9.3809 | 23.6714 | 0 | 35.9446 | 0 | 0 | 23.6714
1801 | 0 | 2.4011 | 9.362 | 42.4537 | 0 | 54.2168 | 0 | 0 | 42.4537
1802 | 0 | 3.2042 | 10.372 | 39.9028 | 0 | 53.479 | 0 | 0 | 39.9028
1803 | 0 | 3.029 | 12.3036 | 28.977 | 0 | 44.3095 | 0 | 0 | 28.977
1804 | 0 | 3.0255 | 13.0404 | 36.7476 | 0 | 52.8136 | 0 | 0 | 36.7476
1805 | 0 | 2.3782 | 13.3183 | 23.6316 | 0 | 39.3281 | 0 | 0 | 23.6316
1806 | 0 | 2.8142 | 12.9141 | 22.2919 | 0 | 38.0202 | 0 | 0 | 22.2919
1807 | 0 | 2.668 | 12.9888 | 24.0053 | 0 | 39.6621 | 0 | 0 | 24.0053
1808 | 0 | 2.7745 | 12.141 | 31.9155 | 21.2024 | 68.0334 | 0 | 0 | 53.1179
1809 | 0 | 2.5395 | 11.9586 | 24.4099 | 3.0213 | 41.9294 | 0 | 0 | 27.4312
1810 | 0 | 2.65 | 10.8724 | 26.9808 | 10.9921 | 51.4954 | 0 | 0 | 37.9729
1811 | 0 | 2.6861 | 9.5771 | 24.5186 | 7.9624 | 44.7441 | 0 | 0 | 32.4809
1812 | 0 | 2.8478 | 9.4307 | 30.8528 | 9.0821 | 52.2134 | 0 | 0 | 39.9349
1813 | 0 | 3.2719 | 9.2815 | 30.0912 | 7.7561 | 50.4007 | 0 | 0 | 37.8473
1814 | 0 | 3.2471 | 9.0392 | 31.0524 | 21.142 | 64.4808 | 0 | 0 | 52.1944
1815 | 0 | 3.3223 | 9.7108 | 30.9779 | 16.1418 | 60.1527 | 200 | 200 | 447.1197
1816 | 0 | 3.1711 | 10.4972 | 28.4259 | 18.3231 | 60.4173 | 0 | 0 | 46.7489
1817 | 0 | 2.972 | 11.05 | 22.8513 | 11.6597 | 48.533 | 0 | 0 | 34.511
1818 | 0 | 2.881 | 11.1816 | 35.644 | 18.6097 | 68.3163 | 0 | 0 | 54.2537
1819 | 0 | 2.8866 | 10.2612 | 28.7536 | 1.7861 | 43.6873 | 0 | 0 | 30.5396
1820 | 0 | 2.7707 | 9.7839 | 36.8594 | 0 | 49.414 | 0 | 0 | 36.8594
1821 | 0 | 2.9255 | 9.144 | 29.7895 | 0 | 41.859 | 0 | 0 | 29.7895
1822 | 0 | 2.5735 | 8.7825 | 31.2622 | 0 | 42.6181 | 0 | 0 | 31.2622
1823 | 0 | 3.0939 | 9.1357 | 34.5177 | 0 | 46.7473 | 0 | 0 | 34.5177
1824 | 0 | 2.7736 | 9.8247 | 25.2956 | 0 | 37.8939 | 0 | 0 | 25.2956
1825 | 0 | 3.7834 | 9.1004 | 31.941 | 0 | 44.8247 | 0 | 0 | 31.941
1826 | 0 | 2.7063 | 8.6806 | 32.8599 | 0 | 44.2468 | 0 | 0 | 32.8599
1827 | 0 | 2.6809 | 8.3226 | 29.2657 | 0 | 40.2692 | 0 | 0 | 29.2657
1828 | 0 | 3.2118 | 8.9708 | 37.7729 | 0 | 49.9555 | 0 | 0 | 37.7729
1829 | 0 | 3.355 | 10.2442 | 39.9101 | 0 | 53.5093 | 0 | 0 | 39.9101
1830 | 0 | 3.1828 | 10.2567 | 35.3465 | 0 | 48.7859 | 0 | 0 | 35.3465
1831 | 0 | 2.5239 | 10.4885 | 39.1146 | 0 | 52.127 | 0 | 0 | 39.1146
1832 | 0 | 2.569 | 10.486 | 31.8487 | 18.0276 | 62.9313 | 0 | 0 | 49.8763
1833 | 0 | 2.6707 | 10.0892 | 26.0213 | 7.7468 | 46.5279 | 0 | 0 | 33.7681
1834 | 0 | 2.762 | 9.6945 | 29.8081 | 14.6611 | 56.9256 | 0 | 0 | 44.4691
1835 | 0 | 2.5994 | 9.1248 | 35.5464 | 10.7586 | 58.0292 | 0 | 200 | 246.305
1836 | 0 | 2.7209 | 9.2112 | 35.8483 | 23.546 | 71.3263 | 0 | 0 | 59.3942
1837 | 0 | 2.8617 | 10.2677 | 34.364 | 9.2358 | 56.7292 | 0 | 0 | 43.5998
1838 | 0 | 2.4697 | 10.5992 | 27.7759 | 14.3066 | 55.1514 | 0 | 0 | 42.0825
1839 | 0 | 3.3333 | 10.9909 | 24.1369 | 10.453 | 48.9141 | 0 | 0 | 34.5899
1840 | 0 | 2.745 | 12.2122 | 37.107 | 13.6694 | 65.7336 | 0 | 0 | 50.7764
1841 | 0 | 2.8589 | 13.0444 | 37.0706 | 10.3683 | 63.3422 | 0 | 0 | 47.4389
1842 | 0 | 2.7214 | 12.9084 | 38.7817 | 17.4839 | 71.8953 | 0 | 0 | 56.2656
1843 | 0 | 3.1725 | 10.5525 | 30.0231 | 16.946 | 60.6942 | 0 | 0 | 46.9691
1844 | 0 | 2.6576 | 9.9065 | 35.1815 | 0 | 47.7456 | 0 | 0 | 35.1815
1845 | 0 | 2.4147 | 10.0764 | 21.857 | 0 | 34.3481 | 0 | 0 | 21.857
1846 | 0 | 2.9207 | 10.2177 | 32.7919 | 0 | 45.9303 | 0 | 0 | 32.7919
1847 | 0 | 3.0528 | 11.1056 | 32.9264 | 0 | 47.0848 | 0 | 0 | 32.9264
1848 | 0 | 2.6971 | 12.1982 | 31.8867 | 0 | 46.782 | 0 | 0 | 31.8867
1849 | 0 | 2.5907 | 15.8128 | 35.2066 | 0 | 53.6101 | 0 | 0 | 35.2066
1850 | 0 | 2.4109 | 17.583 | 25.743 | 0 | 45.7369 | 0 | 0 | 25.743
1851 | 0 | 2.2736 | 14.6873 | 34.0696 | 0 | 51.0305 | 0 | 0 | 34.0696
1852 | 0 | 2.762 | 12.7447 | 31.7525 | 0 | 47.2593 | 0 | 200 | 231.7525
1853 | 0 | 2.6045 | 12.8974 | 38.2959 | 0 | 53.7978 | 0 | 0 | 38.2959
1854 | 0 | 3.2876 | 12.0996 | 21.5926 | 0 | 36.9797 | 0 | 0 | 21.5926
1855 | 0 | 3.4521 | 11.6793 | 25.6548 | 0 | 40.7862 | 0 | 0 | 25.6548
1856 | 0 | 3.1874 | 10.7192 | 35.8805 | 13.3312 | 63.1183 | 0 | 0 | 49.2117
1857 | 0 | 3.0579 | 9.8242 | 32.7336 | 11.8003 | 57.416 | 0 | 0 | 44.534
1858 | 0 | 3.4868 | 9.1113 | 34.9056 | 30.7007 | 78.2045 | 0 | 0 | 65.6063
1859 | 0 | 3.2222 | 8.1418 | 37.3994 | 14.2489 | 63.0123 | 0 | 0 | 51.6483
1860 | 0 | 3.1323 | 8.3178 | 36.3837 | 25.4298 | 73.2635 | 0 | 0 | 61.8134
1861 | 0 | 2.8808 | 9.2844 | 30.0089 | 17.1932 | 59.3672 | 0 | 0 | 47.2021
1862 | 0 | 3.2282 | 9.6168 | 29.6894 | 11.0565 | 53.5908 | 0 | 0 | 40.7458
1863 | 0.032502 | 2.7239 | 11.7035 | 34.2157 | 17.75 | 66.4257 | 0 | 0 | 51.9982
1864 | 0.070335 | 2.7632 | 12.8463 | 27.9403 | 4.8182 | 48.4384 | 0 | 0 | 32.8289
1865 | 0 | 3.3223 | 14.8098 | 35.5368 | 7.8524 | 61.5213 | 0 | 0 | 43.3892
1866 | 0 | 2.8148 | 12.6057 | 26.7693 | 8.0126 | 50.2024 | 0 | 0 | 34.7819
1867 | 0 | 2.8731 | 9.8624 | 39.1941 | 5.7486 | 57.6784 | 0 | 0 | 44.9428
1868 | 0 | 3.218 | 8.1716 | 34.8618 | 0 | 46.2514 | 0 | 0 | 34.8618
1869 | 0 | 2.8239 | 6.9254 | 21.6637 | 0 | 31.4129 | 0 | 0 | 21.6637
1870 | 0 | 2.8182 | 6.4396 | 31.4166 | 0 | 40.6744 | 0 | 0 | 31.4166
1871 | 0 | 2.8783 | 6.0747 | 38.5289 | 0 | 47.4819 | 0 | 0 | 38.5289
1872 | 0 | 2.665 | 7.5223 | 30.8286 | 0 | 41.0158 | 0 | 200 | 230.8286
1873 | 0 | 3.6976 | 10.1319 | 27.1802 | 0 | 41.0097 | 0 | 0 | 27.1802
1874 | 0 | 2.4943 | 12.1275 | 32.3422 | 0 | 46.964 | 0 | 0 | 32.3422
1875 | 0 | 3.1621 | 10.0975 | 32.4888 | 0 | 45.7483 | 0 | 0 | 32.4888
1876 | 0 | 2.6233 | 9.0434 | 30.6076 | 0 | 42.2743 | 0 | 0 | 30.6076
1877 | 2.0066 | 2.6235 | 8.9838 | 31.2349 | 0 | 44.8489 | 0 | 0 | 33.2415
1878 | 28.8989 | 3.0529 | 8.0357 | 24.1798 | 0 | 64.1672 | 0 | 0 | 53.0787
1879 | 92.6376 | 3.0801 | 7.7744 | 28.0189 | 0 | 131.511 | 0 | 0 | 120.6565
1880 | 84.1195 | 3.1885 | 7.7718 | 27.7665 | 5.8666 | 128.7129 | 0 | 0 | 117.7526
1881 | 78.7198 | 3.1762 | 7.2439 | 34.2994 | 10.0114 | 133.4508 | 0 | 0 | 123.0306
1882 | 40.0659 | 2.8361 | 6.8106 | 25.8878 | 11.5647 | 87.1651 | 0 | 0 | 77.5184
1883 | 0 | 2.8582 | 5.9819 | 29.2297 | 18.6056 | 56.6754 | 0 | 0 | 47.8353
1884 | 0 | 2.9894 | 5.8152 | 29.831 | 9.8848 | 48.5204 | 200 | 0 | 239.7158
1885 | 0 | 2.1976 | 6.7113 | 37.8931 | 12.0084 | 58.8104 | 0 | 0 | 49.9015
1886 | 0 | 3.0779 | 7.6455 | 38.5065 | 16.5012 | 65.7311 | 0 | 0 | 55.0077
1887 | 0 | 2.8969 | 9.2992 | 24.699 | 7.9208 | 44.8159 | 0 | 0 | 32.6199
1888 | 0 | 3.2991 | 10.574 | 27.3268 | 11.7569 | 52.9568 | 0 | 0 | 39.0837
1889 | 0 | 3.0565 | 14.1255 | 29.5093 | 10.0299 | 56.7213 | 0 | 0 | 39.5392
1890 | 0 | 2.967 | 11.158 | 25.7183 | 20.7815 | 60.6248 | 0 | 0 | 46.4998
1891 | 0 | 2.9177 | 8.8766 | 33.0094 | 13.7188 | 58.5225 | 0 | 0 | 46.7282
1892 | 0 | 2.9254 | 8.5186 | 29.8667 | 0 | 41.3108 | 0 | 0 | 29.8667
1893 | 0 | 2.7496 | 8.1373 | 22.2939 | 0 | 33.1808 | 0 | 0 | 22.2939
1894 | 0 | 2.8069 | 8.8511 | 34.0707 | 0 | 45.7287 | 0 | 0 | 34.0707
1895 | 0 | 3.1173 | 9.3205 | 25.7745 | 0 | 38.2123 | 0 | 200 | 225.7745
1896 | 0 | 3.0065 | 8.4898 | 31.2788 | 0 | 42.775 | 0 | 0 | 31.2788
1897 | 0 | 3.6256 | 11.3493 | 23.9903 | 0 | 38.9651 | 0 | 0 | 23.9903
1898 | 0 | 2.6936 | 13.9785 | 28.8543 | 0 | 45.5264 | 0 | 0 | 28.8543
1899 | 0 | 2.996 | 12.3924 | 27.5433 | 0 | 42.9316 | 0 | 0 | 27.5433
1900 | 0 | 3.3292 | 11.2368 | 31.6933 | 0 | 46.2593 | 0 | 0 | 31.6933
1901 | 0 | 3.2047 | 9.7526 | 29.2861 | 0 | 42.2434 | 0 | 0 | 29.2861
1902 | 0 | 2.5374 | 7.818 | 35.2188 | 0 | 45.5741 | 0 | 0 | 35.2188
1903 | 0 | 2.6187 | 7.9218 | 32.6395 | 0 | 43.1799 | 0 | 0 | 32.6395
1904 | 0 | 3.0423 | 7.8403 | 37.5302 | 5.2902 | 53.703 | 0 | 0 | 42.8204
1905 | 0 | 2.9415 | 7.855 | 24.4898 | 13.9681 | 49.2543 | 0 | 0 | 38.4578
1906 | 0 | 3.5805 | 7.1489 | 32.7461 | 10.4938 | 53.9693 | 0 | 0 | 43.2399
1907 | 0 | 2.9585 | 6.4401 | 26.6015 | 3.3823 | 39.3824 | 0 | 0 | 29.9838
1908 | 0 | 2.5077 | 5.9669 | 26.6841 | 17.0421 | 52.2008 | 0 | 0 | 43.7262
1909 | 0 | 2.9682 | 6.8887 | 27.4522 | 10.943 | 48.2521 | 0 | 0 | 38.3952
1910 | 0 | 3.0255 | 7.2348 | 33.2132 | 9.7138 | 53.1873 | 0 | 0 | 42.927
1911 | 0 | 2.8615 | 8.5263 | 26.956 | 13.7059 | 52.0498 | 0 | 0 | 40.6619
1912 | 0 | 3.2147 | 7.5443 | 30.6026 | 16.6973 | 58.0589 | 0 | 0 | 47.2999
1913 | 0 | 2.5897 | 7.739 | 29.1771 | 23.6903 | 63.196 | 0 | 0 | 52.8673
1914 | 0 | 2.6911 | 6.2581 | 27.1119 | 20.6599 | 56.721 | 0 | 0 | 47.7718
1915 | 0 | 2.8603 | 5.0317 | 35.0139 | 11.0013 | 53.9072 | 0 | 0 | 46.0152
1916 | 0 | 3.063 | 4.5284 | 25.9611 | 0 | 33.5524 | 0 | 0 | 25.9611
1917 | 0 | 3.0072 | 4.5016 | 29.9907 | 0 | 37.4994 | 0 | 0 | 29.9907
1918 | 0 | 2.5454 | 4.6711 | 29.4502 | 0 | 36.6667 | 0 | 0 | 29.4502
1919 | 0 | 3.0365 | 4.9387 | 25.5132 | 0 | 33.4884 | 0 | 0 | 25.5132
1920 | 0 | 2.7299 | 5.4262 | 28.4148 | 0 | 36.5709 | 0 | 0 | 28.4148
1921 | 0 | 3.2428 | 7.0886 | 28.7024 | 0 | 39.0338 | 0 | 200 | 228.7024
1922 | 0 | 2.796 | 9.5946 | 32.5664 | 0 | 44.957 | 0 | 0 | 32.5664
1923 | 0 | 2.9832 | 8.4583 | 29.0187 | 0 | 40.4601 | 0 | 0 | 29.0187
1924 | 0 | 3.1207 | 8.1523 | 30.9514 | 0 | 42.2244 | 0 | 0 | 30.9514
1925 | 0 | 3.863 | 7.7958 | 34.1517 | 0 | 45.8105 | 0 | 0 | 34.1517
1926 | 0 | 2.2844 | 7.1649 | 32.7748 | 0 | 42.2241 | 0 | 0 | 32.7748
1927 | 15.5206 | 3.1337 | 7.3324 | 25.8207 | 0 | 51.8073 | 0 | 0 | 41.3413
1928 | 62.2853 | 3.1621 | 7.9774 | 29.1157 | 6.9177 | 109.4582 | 0 | 0 | 98.3187
1929 | 90.4204 | 2.804 | 6.9044 | 28.073 | 19.3228 | 147.5246 | 0 | 0 | 137.8162
1930 | 95.3414 | 2.9642 | 5.7955 | 25.9388 | 18.3993 | 148.4393 | 0 | 0 | 139.6796
1931 | 90.3285 | 3.279 | 5.0002 | 35.8989 | 16.1938 | 150.7004 | 0 | 0 | 142.4212
1932 | 67.2599 | 2.6129 | 4.2985 | 31.5628 | 10.5087 | 116.2427 | 0 | 0 | 109.3313
1933 | 57.2829 | 2.9732 | 4.2269 | 34.467 | 22.6195 | 121.5695 | 0 | 0 | 114.3694
1934 | 1.7645 | 3.1051 | 4.3601 | 31.7556 | 18.9502 | 59.9356 | 0 | 0 | 52.4704
1935 | 0 | 2.5307 | 5.1774 | 26.5958 | 7.337 | 41.641 | 0 | 0 | 33.9329
1936 | 0 | 3.1416 | 5.8401 | 38.1179 | 17.1228 | 64.2224 | 0 | 0 | 55.2407
1937 | 0 | 3.3099 | 6.8267 | 30.7007 | 17.373 | 58.2102 | 0 | 0 | 48.0737
1938 | 0 | 3.3116 | 6.2581 | 24.823 | 13.2588 | 47.6515 | 0 | 0 | 38.0818
1939 | 0 | 2.4715 | 4.243 | 35.5958 | 13.3213 | 55.6316 | 0 | 0 | 48.9171
1940 | 0 | 2.5614 | 3.4007 | 33.0719 | 0 | 39.034 | 0 | 0 | 33.0719
1941 | 0 | 3.3186 | 3.2089 | 26.854 | 0 | 33.3815 | 0 | 0 | 26.854
1942 | 0 | 2.3317 | 3.3045 | 26.4825 | 0 | 32.1187 | 0 | 0 | 26.4825
1943 | 0 | 3.2492 | 3.6404 | 29.0185 | 0 | 35.9081 | 0 | 0 | 29.0185
1944 | 0 | 3.2012 | 4.2976 | 32.975 | 0 | 40.4738 | 0 | 0 | 32.975
1945 | 0 | 2.7225 | 5.7698 | 27.6152 | 0 | 36.1075 | 0 | 0 | 27.6152
1946 | 0 | 2.6174 | 8.9127 | 25.1603 | 0 | 36.6903 | 0 | 0 | 25.1603
1947 | 0 | 3.079 | 7.8845 | 42.635 | 0 | 53.5985 | 0 | 0 | 42.635
1948 | 0 | 3.1113 | 7.5354 | 28.7569 | 0 | 39.4036 | 0 | 0 | 28.7569
1949 | 0 | 2.9805 | 8.4946 | 32.1692 | 0 | 43.6444 | 0 | 0 | 32.1692
1950 | 0 | 3.5252 | 8.3985 | 27.1946 | 0 | 39.1184 | 0 | 0 | 27.1946
1951 | 0 | 2.7777 | 8.2165 | 26.8986 | 0 | 37.8928 | 200 | 0 | 226.8986
1952 | 0 | 2.8038 | 8.1831 | 33.3602 | 13.2503 | 57.5975 | 0 | 200 | 246.6106
1953 | 0 | 2.8085 | 7.7871 | 30.7102 | -0.24439 | 41.0614 | 0 | 0 | 30.4658
1954 | 0 | 2.4939 | 7.2166 | 32.8945 | 8.2834 | 50.8885 | 0 | 0 | 41.178
1955 | 0 | 2.5249 | 6.1128 | 31.6688 | 10.4891 | 50.7956 | 0 | 0 | 42.1579
1956 | 0 | 3.1848 | 5.436 | 35.2012 | 12.8227 | 56.6448 | 0 | 0 | 48.0239
1957 | 0 | 2.7056 | 4.7593 | 28.0768 | 6.4023 | 41.944 | 0 | 0 | 34.4791
1958 | 0 | 2.389 | 4.7708 | 30.4234 | 10.8287 | 48.4119 | 0 | 0 | 41.2522
1959 | 0 | 3.2357 | 5.0916 | 27.9059 | 9.2042 | 45.4374 | 0 | 0 | 37.1101
1960 | 0 | 2.815 | 5.0827 | 28.696 | 14.6759 | 51.2696 | 0 | 0 | 43.3719
1961 | 0 | 2.3687 | 5.0019 | 39.5374 | 9.8927 | 56.8006 | 0 | 0 | 49.43
1962 | 0 | 3.0824 | 4.2536 | 34.75 | 12.9073 | 54.9932 | 0 | 0 | 47.6573
1963 | 0 | 2.9548 | 2.2195 | 36.9628 | 19.6993 | 61.8363 | 0 | 0 | 56.662
1964 | 0 | 2.1092 | 1.7504 | 24.4756 | 0 | 28.3352 | 0 | 0 | 24.4756
1965 | 0 | 2.8721 | 2.3226 | 34.0936 | 0 | 39.2882 | 0 | 0 | 34.0936
1966 | 0 | 2.8806 | 2.5052 | 31.4487 | 0 | 36.8345 | 0 | 0 | 31.4487
1967 | 0 | 2.4539 | 3.0075 | 34.5531 | 0 | 40.0145 | 0 | 0 | 34.5531
1968 | 0 | 2.7871 | 3.2445 | 22.5081 | 0 | 28.5397 | 0 | 0 | 22.5081
1969 | 0 | 2.8117 | 3.2441 | 31.22 | 0 | 37.2759 | 0 | 0 | 31.22
1970 | 0 | 3.2692 | 2.1992 | 25.2947 | 0 | 30.7632 | 0 | 0 | 25.2947
1971 | 0 | 3.2342 | 1.9945 | 33.8394 | 0 | 39.068 | 0 | 0 | 33.8394
1972 | 0 | 2.9645 | 3.6751 | 30.5588 | 0 | 37.1984 | 0 | 0 | 30.5588
1973 | 0 | 2.8666 | 7.1613 | 28.2815 | 0 | 38.3093 | 0 | 0 | 28.2815
1974 | 0 | 2.6621 | 6.5068 | 30.3601 | 0 | 39.5291 | 0 | 0 | 30.3601
1975 | 0 | 2.8535 | 5.2243 | 34.7608 | 0 | 42.8386 | 0 | 0 | 34.7608
1976 | 0 | 3.3174 | 5.2715 | 31.7446 | 11.04 | 51.3735 | 0 | 0 | 42.7847
1977 | 0 | 3.2425 | 4.3041 | 30.5508 | 21.6494 | 59.7469 | 0 | 0 | 52.2002
1978 | 0 | 2.8296 | 3.822 | 37.5171 | 7.8368 | 52.0055 | 0 | 0 | 45.3539
1979 | 0 | 2.904 | 2.2619 | 28.8901 | 14.4507 | 48.5067 | 0 | 0 | 43.3408
1980 | 0 | 3.1354 | 2.2739 | 32.7708 | 15.29 | 53.4701 | 0 | 0 | 48.0608
1981 | 0 | 2.7923 | 2.4752 | 26.7337 | 8.0919 | 40.0931 | 0 | 0 | 34.8256
1982 | 0 | 3.0738 | 1.8702 | 25.2234 | 8.9249 | 39.0923 | 0 | 0 | 34.1483
1983 | 0 | 2.9523 | 3.7344 | 33.963 | 10.6517 | 51.3013 | 0 | 0 | 44.6147
1984 | 0 | 2.8463 | 5.1099 | 31.1868 | 21.2737 | 60.4167 | 0 | 0 | 52.4606
1985 | 0 | 2.7391 | 7.1766 | 36.2063 | 12.7854 | 58.9074 | 0 | 0 | 48.9917
1986 | 0 | 2.5421 | 7.7729 | 32.3145 | 12.9975 | 55.627 | 0 | 0 | 45.312
1987 | 0 | 2.6277 | 7.6004 | 27.395 | 17.2723 | 54.8954 | 0 | 0 | 44.6673
1988 | 0 | 2.9262 | 7.4024 | 25.6898 | 0 | 36.0184 | 0 | 0 | 25.6898
1989 | 0 | 2.8265 | 6.9668 | 33.5434 | 0 | 43.3368 | 0 | 0 | 33.5434
1990 | 0 | 2.8901 | 7.4487 | 34.2507 | 0 | 44.5894 | 0 | 0 | 34.2507
1991 | 0 | 2.7747 | 8.2346 | 31.3138 | 0 | 42.3232 | 0 | 0 | 31.3138
1992 | 0 | 2.9403 | 8.0607 | 38.0566 | 0 | 49.0577 | 0 | 0 | 38.0566
1993 | 0 | 3.1995 | 6.4629 | 32.4601 | 0 | 42.1225 | 0 | 0 | 32.4601
1994 | 0 | 2.7565 | 4.0322 | 34.781 | 0 | 41.5696 | 0 | 200 | 234.781
1995 | 0 | 3.1455 | 3.3536 | 30.1585 | 0 | 36.6576 | 0 | 0 | 30.1585
1996 | 0 | 2.8094 | 5.6545 | 32.8412 | 0 | 41.3051 | 0 | 0 | 32.8412
1997 | 0 | 2.994 | 5.1848 | 40.1665 | 0 | 48.3453 | 0 | 0 | 40.1665
1998 | 0 | 2.9692 | 5.5796 | 20.3379 | 0 | 28.8868 | 0 | 0 | 20.3379
1999 | 0 | 3.0069 | 5.321 | 27.5042 | 0 | 35.8322 | 0 | 0 | 27.5042
2000 | 0 | 3.0336 | 4.7416 | 30.8367 | 1.75 | 40.362 | 0 | 0 | 32.5867
2001 | 0 | 2.9051 | 4.0474 | 23.9825 | 4.3869 | 35.3219 | 0 | 0 | 28.3694
2002 | 0 | 2.9507 | 3.9786 | 33.775 | 7.4943 | 48.1987 | 0 | 0 | 41.2693
2003 | 0 | 3.1534 | 3.9482 | 38.099 | 16.951 | 62.1515 | 0 | 0 | 55.05
2004 | 0 | 3.2346 | 3.9209 | 29.3893 | 10.4168 | 46.9616 | 0 | 0 | 39.8061
2005 | 0 | 3.3484 | 3.473 | 32.9765 | 11.4203 | 51.2181 | 0 | 0 | 44.3968
2006 | 0 | 3.4152 | 4.1909 | 28.7779 | 16.1994 | 52.5835 | 0 | 0 | 44.9774
2007 | 0 | 2.7891 | 6.1931 | 26.5044 | 25.4795 | 60.9661 | 0 | 0 | 51.9839
2008 | 0 | 3.4736 | 6.8238 | 33.7658 | 16.7635 | 60.8267 | 0 | 0 | 50.5294
2009 | 0 | 3.4497 | 6.7228 | 27.8369 | 28.1951 | 66.2044 | 0 | 0 | 56.0319
2010 | 0 | 2.9916 | 6.3133 | 25.7063 | 23.7457 | 58.757 | 0 | 0 | 49.452
2011 | 0 | 2.5444 | 4.3549 | 37.1461 | 8.392 | 52.4374 | 0 | 0 | 45.5382
2012 | 0 | 3.1629 | 5.0671 | 33.0368 | 0 | 41.2668 | 0 | 0 | 33.0368
2013 | 0 | 3.0745 | 5.3142 | 32.8028 | 0 | 41.1914 | 0 | 0 | 32.8028
2014 | 0 | 3.2034 | 6.4804 | 21.5492 | 0 | 31.2331 | 0 | 0 | 21.5492
2015 | 0 | 2.8771 | 7.3611 | 32.8884 | 0 | 43.1266 | 0 | 0 | 32.8884
2016 | 0 | 2.7689 | 10.6392 | 33.2787 | 0 | 46.6868 | 0 | 0 | 33.2787
2017 | 0 | 3.1611 | 12.6146 | 31.4783 | 0 | 47.254 | 0 | 0 | 31.4783
2018 | 0 | 3.0474 | 10.8351 | 33.4113 | 0 | 47.2938 | 0 | 0 | 33.4113
2019 | 0 | 3.1258 | 10.5513 | 26.1812 | 0 | 39.8584 | 200 | 0 | 226.1812
2020 | 0 | 2.9215 | 10.8707 | 32.3386 | 0 | 46.1308 | 0 | 0 | 32.3386
2021 | 0 | 2.9716 | 10.503 | 30.1305 | 0 | 43.6051 | 0 | 0 | 30.1305
2022 | 0 | 2.7863 | 9.8374 | 32.3429 | 0 | 44.9666 | 0 | 0 | 32.3429
2023 | 0 | 3.3419 | 8.937 | 35.7432 | 0 | 48.0222 | 0 | 0 | 35.7432
2024 | 0 | 3.1916 | 7.1081 | 31.941 | 21.7624 | 64.0031 | 0 | 200 | 253.7034
2025 | 0 | 2.8228 | 6.2692 | 32.5059 | 12.037 | 53.6349 | 0 | 0 | 44.5429
2026 | 0 | 2.6163 | 5.3929 | 31.7095 | 12.3093 | 52.028 | 0 | 0 | 44.0188
2027 | 0 | 3.6238 | 4.071 | 27.6371 | 17.2278 | 52.5597 | 0 | 0 | 44.865
2028 | 0 | 3.5347 | 3.2509 | 37.0118 | 16.3186 | 60.116 | 0 | 0 | 53.3303
2029 | 0 | 3.1052 | 3.4566 | 35.8724 | 15.8649 | 58.2991 | 0 | 0 | 51.7373
2030 | 0 | 3.4265 | 5.435 | 25.2424 | 11.8354 | 45.9394 | 0 | 0 | 37.0778
2031 | 0 | 3.2854 | 5.0827 | 27.2904 | 8.7913 | 44.4498 | 0 | 0 | 36.0817
2032 | 0 | 2.8344 | 5.4581 | 29.6242 | 9.923 | 47.8398 | 0 | 0 | 39.5472
2033 | 0 | 2.8262 | 5.1445 | 22.5281 | 10.4036 | 40.9023 | 0 | 0 | 32.9316
2034 | 0 | 3.0234 | 6.0176 | 29.0828 | 13.5021 | 51.6259 | 0 | 0 | 42.5849
2035 | 0 | 2.784 | 4.0947 | 30.9646 | 5.8136 | 43.6569 | 0 | 0 | 36.7782
2036 | 0 | 3.0246 | 4.1784 | 27.2888 | 0 | 34.4917 | 0 | 0 | 27.2888
2037 | 0 | 2.5454 | 5.073 | 34.2568 | 0 | 41.8751 | 0 | 0 | 34.2568
2038 | 0 | 2.9299 | 5.7501 | 29.0374 | 0 | 37.7175 | 0 | 0 | 29.0374
2039 | 0 | 3.3112 | 6.7968 | 30.5627 | 0 | 40.6707 | 0 | 0 | 30.5627
2040 | 0 | 2.9622 | 10.6392 | 30.3329 | 0 | 43.9343 | 0 | 0 | 30.3329
2041 | 0 | 2.7205 | 13.0043 | 28.5312 | 0 | 44.256 | 0 | 0 | 28.5312
2042 | 0 | 3.2229 | 11.163 | 34.3863 | 0 | 48.7722 | 0 | 0 | 34.3863
2043 | 0 | 2.8122 | 10.003 | 30.1765 | 0 | 42.9916 | 0 | 0 | 30.1765
2044 | 0 | 3.0894 | 8.8441 | 28.49 | 0 | 40.4235 | 0 | 0 | 28.49
2045 | 0 | 3.0796 | 7.3826 | 33.2326 | 0 | 43.6948 | 0 | 0 | 33.2326
2046 | 0 | 3.0273 | 6.0799 | 37.4154 | 0 | 46.5225 | 0 | 0 | 37.4154
2047 | 0 | 2.9027 | 6.3324 | 34.0432 | 0 | 43.2782 | 0 | 0 | 34.0432
2048 | 0 | 3.0442 | 5.9538 | 30.7587 | 7.2803 | 47.0369 | 0 | 0 | 38.0389
2049 | 0 | 3.4593 | 5.1865 | 24.9294 | 13.3573 | 46.9325 | 0 | 0 | 38.2867
2050 | 0 | 3.2443 | 4.6074 | 34.6086 | 10.4561 | 52.9164 | 0 | 0 | 45.0647
2051 | 0.19497 | 2.704 | 4.2226 | 32.416 | 11.1234 | 50.661 | 0 | 0 | 43.7343
2052 | 8.8237 | 3.1636 | 4.0494 | 26.7661 | 10.9695 | 53.7724 | 0 | 0 | 46.5593
2053 | 25.2416 | 2.7972 | 4.4422 | 32.4619 | 19.7787 | 84.7217 | 0 | 0 | 77.4823
2054 | 7.7406 | 2.7152 | 5.0916 | 28.4612 | 20.3529 | 64.3614 | 0 | 0 | 56.5547
2055 | 52.7045 | 3.1816 | 5.0827 | 37.7004 | 10.6425 | 109.3117 | 0 | 0 | 101.0474
2056 | 56.8069 | 3.1815 | 4.5458 | 26.6977 | 4.7071 | 95.939 | 0 | 0 | 88.2117
2057 | 0 | 2.776 | 3.6968 | 30.1542 | 16.3508 | 52.9778 | 0 | 0 | 46.505
2058 | 0 | 2.9992 | 2.6656 | 32.4488 | 16.0048 | 54.1185 | 0 | 0 | 48.4536
2059 | 0 | 2.4471 | 2.4465 | 31.5022 | 7.6589 | 44.0547 | 0 | 200 | 239.1611
2060 | 0 | 2.882 | 2.4009 | 23.4436 | 0 | 28.7266 | 0 | 0 | 23.4436
2061 | 0 | 2.9765 | 2.5007 | 29.8544 | 0 | 35.3315 | 0 | 0 | 29.8544
2062 | 0 | 3.1702 | 2.9101 | 28.4945 | 0 | 34.5748 | 0 | 0 | 28.4945
2063 | 0 | 3.0661 | 3.7332 | 31.166 | 0 | 37.9653 | 0 | 0 | 31.166
2064 | 0 | 2.9968 | 5.0597 | 28.4689 | 0 | 36.5254 | 0 | 0 | 28.4689
2065 | 0 | 3.2249 | 7.7437 | 28.5725 | 0 | 39.541 | 0 | 0 | 28.5725
2066 | 0 | 3.4416 | 6.983 | 32.5545 | 0 | 42.9791 | 0 | 0 | 32.5545
2067 | 0 | 2.1894 | 7.0556 | 31.2581 | 0 | 40.5031 | 0 | 0 | 31.2581
2068 | 11.8407 | 3.381 | 7.5861 | 33.871 | 0 | 56.6788 | 0 | 0 | 45.7117
2069 | 59.256 | 2.4905 | 7.0197 | 32.6985 | 0 | 101.4647 | 0 | 0 | 91.9545
2070 | 91.1369 | 2.9281 | 7.0377 | 37.5763 | 0 | 138.6789 | 0 | 0 | 128.7132
2071 | 75.4637 | 2.4208 | 8.1145 | 34.9614 | 0 | 120.9604 | 0 | 0 | 110.4251
2072 | 68.9358 | 3.0222 | 7.4476 | 34.1463 | 10.9708 | 124.5226 | 0 | 0 | 114.0528
2073 | 79.0351 | 2.6694 | 7.2166 | 33.5172 | 19.7776 | 142.2158 | 0 | 0 | 132.3298
2074 | 87.4024 | 2.7507 | 6.571 | 27.8935 | 14.4318 | 139.0494 | 0 | 0 | 129.7277
2075 | 87.3017 | 2.9216 | 5.8152 | 28.511 | 11.8921 | 136.4416 | 0 | 0 | 127.7049
2076 | 83.3548 | 2.9446 | 5.2029 | 37.3051 | 11.4564 | 140.2639 | 0 | 0 | 132.1164
2077 | 73.9839 | 2.8709 | 5.3457 | 30.2733 | 5.7173 | 118.1911 | 0 | 0 | 109.9745
2078 | 14.8635 | 3.0312 | 6.4655 | 33.1105 | 12.9007 | 70.3714 | 0 | 0 | 60.8747
2079 | 0 | 2.7949 | 7.2603 | 33.288 | 15.2837 | 58.6269 | 0 | 0 | 48.5717
2080 | 0 | 2.79 | 7.625 | 32.2418 | 17.4453 | 60.1021 | 0 | 0 | 49.6871
2081 | 0 | 2.7147 | 6.2581 | 31.5818 | 13.9919 | 54.5465 | 0 | 0 | 45.5737
2082 | 0 | 3.186 | 4.736 | 31.6065 | 10.9709 | 50.4994 | 0 | 0 | 42.5775
2083 | 0 | 2.9505 | 4.2681 | 29.0503 | 15.0784 | 51.3474 | 0 | 0 | 44.1287
2084 | 0 | 2.6496 | 4.0168 | 28.5645 | 0 | 35.2309 | 0 | 0 | 28.5645
2085 | 0 | 2.8359 | 4.1888 | 36.4933 | 0 | 43.5179 | 0 | 0 | 36.4933
2086 | 0 | 2.4719 | 4.6953 | 35.5242 | 0 | 42.6913 | 0 | 0 | 35.5242
2087 | 0 | 3.1217 | 5.5069 | 24.2516 | 0 | 32.8802 | 200 | 0 | 224.2516
2088 | 0 | 2.8456 | 7.4944 | 35.9158 | 0 | 46.2558 | 0 | 0 | 35.9158
2089 | 0 | 2.4727 | 10.2766 | 28.1219 | 0 | 40.8712 | 0 | 0 | 28.1219
2090 | 0 | 2.3995 | 8.95 | 30.6469 | 0 | 41.9965 | 0 | 0 | 30.6469
2091 | 0 | 2.0342 | 8.2208 | 29.9675 | 0 | 40.2225 | 0 | 200 | 229.9675
2092 | 14.1045 | 2.4115 | 8.3549 | 26.0208 | 0 | 50.8917 | 0 | 0 | 40.1253
2093 | 67.9818 | 3.1246 | 7.6003 | 36.7958 | 0 | 115.5025 | 0 | 0 | 104.7776
2094 | 85.1941 | 3.1029 | 7.9955 | 28.1997 | 0 | 124.4922 | 0 | 0 | 113.3938
2095 | 76.1911 | 2.6608 | 7.0864 | 33.9027 | 0 | 119.8409 | 0 | 0 | 110.0938
2096 | 56.6136 | 3.1114 | 6.6328 | 29.4967 | 10.598 | 106.4525 | 0 | 0 | 96.7082
2097 | 66.2298 | 3.0708 | 5.8632 | 37.6109 | -0.58257 | 112.1921 | 0 | 0 | 103.2581
2098 | 92.2078 | 2.7871 | 4.4765 | 35.9978 | 5.442 | 140.9112 | 0 | 0 | 133.6476
2099 | 61.5424 | 2.8762 | 4.071 | 26.075 | 3.9853 | 98.5499 | 0 | 0 | 91.6027
2100 | 53.6272 | 3.0618 | 2.9847 | 28.8044 | 10.4733 | 98.9515 | 0 | 0 | 92.905
2101 | 78.047 | 3.2753 | 5.6743 | 35.8691 | 16.7225 | 139.5882 | 0 | 0 | 130.6387
2102 | 52.2723 | 2.9565 | 7.9253 | 25.6005 | 4.4053 | 93.1598 | 0 | 0 | 82.2781
2103 | 0 | 3.7139 | 9.6272 | 25.4378 | 15.6962 | 54.4751 | 0 | 0 | 41.1339
2104 | 0 | 3.4028 | 10.7042 | 28.9812 | 19.0699 | 62.1581 | 0 | 0 | 48.0511
2105 | 6.1612 | 2.5587 | 7.0376 | 30.5365 | 34.8222 | 81.1162 | 0 | 0 | 71.5199
2106 | 39.407 | 2.9502 | 4.1444 | 30.4495 | 12.7459 | 89.697 | 0 | 0 | 82.6024
2107 | 86.7473 | 2.6962 | 3.9212 | 31.9818 | 9.2605 | 134.6069 | 0 | 0 | 127.9896
2108 | 81.9763 | 2.8685 | 3.3704 | 39.5347 | 0 | 127.75 | 0 | 0 | 121.511
2109 | 98.8762 | 2.8222 | 3.7064 | 34.2283 | 0 | 139.6332 | 0 | 0 | 133.1046
2110 | 95.0073 | 2.6835 | 4.6141 | 32.7191 | 0 | 135.024 | 0 | 0 | 127.7264
2111 | 79.8273 | 3.3798 | 5.5875 | 28.6775 | 0 | 117.472 | 0 | 0 | 108.5048
2112 | 22.8514 | 2.8944 | 7.3929 | 24.3714 | 0 | 57.5101 | 0 | 0 | 47.2228
2113 | 8.5973 | 2.7386 | 10.0817 | 40.5619 | 0 | 61.9795 | 0 | 0 | 49.1592
2114 | 39.8062 | 3.2545 | 8.7861 | 31.0213 | 0 | 82.8681 | 0 | 0 | 70.8274
2115 | 45.8414 | 3.1321 | 8.2208 | 32.0659 | 0 | 89.2603 | 0 | 0 | 77.9073
2116 | 0 | 2.8124 | 7.656 | 27.068 | 0 | 37.5364 | 0 | 0 | 27.068
2117 | 0 | 3.0919 | 6.5843 | 36.8691 | 0 | 46.5453 | 0 | 0 | 36.8691
2118 | 0 | 3.3784 | 4.68 | 32.2428 | 0 | 40.3011 | 0 | 0 | 32.2428
2119 | 0 | 2.8261 | 4.6188 | 23.7445 | 0 | 31.1894 | 0 | 0 | 23.7445
2120 | 7.5806 | 3.4586 | 3.4414 | 34.3755 | 9.8543 | 58.7104 | 0 | 0 | 51.8104
2121 | 43.9346 | 3.4281 | 2.8181 | 38.544 | 22.0952 | 110.8201 | 0 | 0 | 104.5738
2122 | 84.6031 | 2.7358 | 2.1203 | 29.1727 | 17.8941 | 136.5261 | 0 | 0 | 131.67
2123 | 34.6533 | 3.7016 | 1.3773 | 25.0873 | 14.528 | 79.3474 | 0 | 0 | 74.2685
2124 | 0 | 2.6005 | 2.3299 | 30.4967 | 18.0067 | 53.4338 | 0 | 0 | 48.5033
2125 | 0 | 2.7855 | 2.3888 | 29.4831 | 13.8233 | 48.4807 | 0 | 0 | 43.3064
2126 | 0 | 3.3689 | 2.0295 | 27.2559 | 18.1029 | 50.7572 | 0 | 0 | 45.3589
2127 | 0 | 2.7887 | 1.9886 | 26.4415 | 4.7098 | 35.9287 | 0 | 0 | 31.1513
2128 | 0 | 2.8782 | 2.2272 | 35.2994 | 13.9314 | 54.3362 | 0 | 0 | 49.2308
2129 | 0 | 2.5655 | 2.1199 | 24.2174 | 18.6696 | 47.5724 | 0 | 0 | 42.887
2130 | 0 | 2.9249 | 1.9531 | 31.3897 | 15.4586 | 51.7262 | 0 | 0 | 46.8483
2131 | 0 | 3.0215 | 1.5255 | 31.9285 | 8.8323 | 45.3077 | 0 | 200 | 240.7608
2132 | 0 | 3.0176 | 1.1504 | 29.4714 | 0 | 33.6394 | 0 | 0 | 29.4714
2133 | 0 | 2.855 | 1.3195 | 30.3076 | 0 | 34.4821 | 0 | 0 | 30.3076
2134 | 0 | 3.4156 | 3.0811 | 27.1001 | 0 | 33.5969 | 0 | 0 | 27.1001
2135 | 0 | 2.9327 | 4.4214 | 34.632 | 0 | 41.9861 | 0 | 0 | 34.632
2136 | 0 | 3.122 | 4.0387 | 25.8187 | 0 | 32.9794 | 0 | 0 | 25.8187
2137 | 0 | 2.7205 | 2.1992 | 29.3839 | 0 | 34.3036 | 0 | 0 | 29.3839
2138 | 0 | 3.0724 | 1.9945 | 27.2693 | 0 | 32.3362 | 0 | 0 | 27.2693
2139 | 0 | 2.9366 | 3.6751 | 23.1126 | 0 | 29.7243 | 0 | 0 | 23.1126
2140 | 0 | 3.0193 | 5.7791 | 34.5605 | 0 | 43.3589 | 0 | 0 | 34.5605
2141 | 0 | 3.2162 | 5.5576 | 38.4306 | 0 | 47.2044 | 0 | 0 | 38.4306
2142 | 0 | 2.7862 | 4.9061 | 30.5288 | 0 | 38.2211 | 0 | 0 | 30.5288
2143 | 0 | 2.5066 | 4.9131 | 23.2885 | 0 | 30.7082 | 0 | 0 | 23.2885
2144 | 0 | 2.947 | 4.3041 | 25.0524 | 13.6018 | 45.9054 | 0 | 0 | 38.6542
2145 | 0 | 2.5146 | 3.822 | 29.0319 | 11.0261 | 46.3947 | 0 | 0 | 40.0581
2146 | 0 | 2.8268 | 2.1335 | 32.799 | 12.1765 | 49.9358 | 0 | 0 | 44.9755
2147 | 0 | 2.9515 | 2.2739 | 30.023 | 16.5595 | 51.808 | 0 | 0 | 46.5826
2148 | 0 | 2.6769 | 2.4752 | 33.0739 | 1.4464 | 39.6724 | 0 | 0 | 34.5203
2149 | 0 | 3.1181 | 1.8702 | 30.876 | 18.4666 | 54.3309 | 0 | 0 | 49.3426
2150 | 0 | 2.612 | 2.2301 | 38.9769 | 20.3538 | 64.1728 | 0 | 0 | 59.3306
2151 | 0 | 3.1178 | 2.3118 | 29.2537 | 11.1112 | 45.7945 | 0 | 0 | 40.3649
2152 | 0 | 3.2235 | 2.3348 | 31.9847 | 14.8017 | 52.3446 | 0 | 0 | 46.7864
2153 | 0 | 2.9707 | 2.2339 | 25.1798 | 9.4482 | 39.8326 | 0 | 0 | 34.6281
2154 | 0 | 3.033 | 2.1838 | 29.1028 | 17.0299 | 51.3495 | 0 | 0 | 46.1327
2155 | 0 | 3.3378 | 2.2867 | 28.4827 | 13.2985 | 47.4058 | 200 | 0 | 241.7813
2156 | 0 | 2.4274 | 3.2731 | 28.7473 | 0 | 34.4479 | 0 | 0 | 28.7473
2157 | 0 | 2.5856 | 3.1176 | 26.5596 | 0 | 32.2627 | 0 | 0 | 26.5596
2158 | 0 | 2.4625 | 3.4419 | 30.6268 | 0 | 36.5312 | 0 | 0 | 30.6268
2159 | 0 | 2.9602 | 4.0426 | 38.9492 | 0 | 45.952 | 0 | 0 | 38.9492
2160 | 0 | 2.7555 | 4.8324 | 27.9538 | 0 | 35.5417 | 0 | 0 | 27.9538
2161 | 0 | 3.0919 | 2.1636 | 32.2826 | 0 | 37.5382 | 0 | 0 | 32.2826
2162 | 0 | 2.5661 | 4.35 | 28.1898 | 0 | 35.1059 | 0 | 0 | 28.1898
2163 | 0 | 2.9074 | 6.2361 | 24.0793 | 0 | 33.2228 | 0 | 0 | 24.0793
2164 | 0 | 3.3167 | 8.0728 | 21.2136 | 0 | 32.6031 | 0 | 0 | 21.2136
2165 | 0 | 3.4346 | 7.9158 | 28.362 | 0 | 39.7123 | 0 | 0 | 28.362
2166 | 0 | 2.6692 | 7.6523 | 23.776 | 0 | 34.0975 | 0 | 0 | 23.776
2167 | 0 | 2.9185 | 6.8977 | 34.0159 | 0 | 43.8322 | 0 | 0 | 34.0159
2168 | 0 | 3.1857 | 6.6043 | 26.086 | 7.0675 | 42.9435 | 0 | 0 | 33.1535
2169 | 0 | 3.2346 | 6.2468 | 31.5356 | 21.0447 | 62.0617 | 0 | 0 | 52.5802
2170 | 0 | 3.5198 | 5.8715 | 27.926 | -2.2792 | 35.038 | 0 | 0 | 25.6467
2171 | 0 | 2.549 | 5.5969 | 24.7193 | 17.999 | 50.8641 | 0 | 0 | 42.7183
2172 | 0 | 2.7016 | 5.4142 | 25.9385 | 16.5827 | 50.6371 | 0 | 0 | 42.5212
2173 | 0 | 3.127 | 4.8982 | 28.9906 | 9.5717 | 46.5874 | 0 | 0 | 38.5622
2174 | 0 | 3.0218 | 5.3243 | 25.2195 | 12.4888 | 46.0543 | 0 | 0 | 37.7082
2175 | 0 | 3.0276 | 5.8818 | 35.7372 | 15.006 | 59.6525 | 0 | 0 | 50.7431
2176 | 0 | 3.4462 | 6.7064 | 24.4989 | 11.4447 | 46.0962 | 0 | 0 | 35.9436
2177 | 0 | 2.7806 | 5.4604 | 35.3894 | 17.9099 | 61.5403 | 0 | 0 | 53.2993
2178 | 0 | 2.4926 | 5.3197 | 32.3696 | 21.0137 | 61.1957 | 0 | 200 | 253.3833
2179 | 0 | 3.2046 | 6.344 | 28.1097 | 7.4955 | 45.1537 | 0 | 0 | 35.6051
2180 | 0 | 2.9197 | 6.7956 | 35.8393 | 0 | 45.5546 | 0 | 0 | 35.8393
2181 | 0 | 2.8644 | 6.3858 | 29.5165 | 0 | 38.7666 | 0 | 0 | 29.5165
2182 | 0 | 2.8969 | 6.9566 | 27.2136 | 0 | 37.0672 | 0 | 0 | 27.2136
2183 | 0 | 3.2844 | 7.2228 | 21.835 | 0 | 32.3421 | 0 | 0 | 21.835
2184 | 0 | 2.5019 | 6.5286 | 30.8103 | 0 | 39.8408 | 0 | 0 | 30.8103
2185 | 0 | 3.605 | 3.1364 | 26.4346 | 0 | 33.176 | 0 | 0 | 26.4346
2186 | 0 | 2.5932 | 3.3171 | 32.9183 | 0 | 38.8285 | 0 | 0 | 32.9183
2187 | 0 | 3.0521 | 4.4623 | 18.5639 | 0 | 26.0783 | 0 | 0 | 18.5639
2188 | 0 | 3.0582 | 6.8883 | 30.0732 | 0 | 40.0197 | 0 | 0 | 30.0732
2189 | 0 | 2.7587 | 6.0138 | 26.4375 | 0 | 35.21 | 0 | 0 | 26.4375
2190 | 0 | 3.0122 | 6.2342 | 24.7729 | 0 | 34.0193 | 0 | 0 | 24.7729
2191 | 0 | 2.6128 | 5.6473 | 22.0975 | 0 | 30.3575 | 0 | 0 | 22.0975
2192 | 0 | 2.9897 | 4.7416 | 23.9638 | 11.7429 | 43.438 | 0 | 0 | 35.7067
2193 | 0 | 3.0112 | 4.2257 | 20.9625 | 16.2927 | 44.492 | 0 | 0 | 37.2552
2194 | 0 | 3.2325 | 3.3871 | 27.8344 | 19.4711 | 53.9251 | 0 | 0 | 47.3055
2195 | 0 | 3.0015 | 2.7434 | 26.1335 | 22.2418 | 54.1202 | 0 | 0 | 48.3753
2196 | 0 | 2.9101 | 2.0907 | 26.5318 | 8.6688 | 40.2014 | 0 | 0 | 35.2005
2197 | 0 | 3.3526 | 2.2196 | 33.5268 | 16.6216 | 55.7207 | 0 | 0 | 50.1484
2198 | 0 | 2.7852 | 2.2605 | 27.5234 | 11.616 | 44.1851 | 0 | 0 | 39.1395
2199 | 0 | 2.9691 | 2.1706 | 30.879 | 10.9118 | 46.9306 | 0 | 0 | 41.7908
2200 | 0 | 3.1093 | 2.1677 | 26.3518 | 14.2329 | 45.8617 | 0 | 0 | 40.5847
2201 | 0 | 2.5638 | 2.1706 | 31.8046 | 19.9975 | 56.5365 | 0 | 0 | 51.8021
2202 | 0 | 3.2431 | 1.5861 | 27.8737 | 1.337 | 34.0399 | 0 | 0 | 29.2107
2203 | 0 | 2.7586 | 1.239 | 28.9172 | 10.9016 | 43.8164 | 0 | 0 | 39.8188
2204 | 0 | 2.8643 | 1.0185 | 27.7327 | 0 | 31.6156 | 0 | 0 | 27.7327
2205 | 0 | 3.2817 | 1.0722 | 31.6073 | 0 | 35.9612 | 0 | 0 | 31.6073
2206 | 0 | 3.0307 | 1.1947 | 27.6616 | 0 | 31.887 | 0 | 0 | 27.6616
2207 | 0 | 2.4048 | 1.2542 | 27.3696 | 0 | 31.0287 | 0 | 0 | 27.3696
2208 | 0 | 2.7192 | 2.7569 | 33.2374 | 0 | 38.7135 | 0 | 0 | 33.2374
2209 | 0 | 3.0291 | 4.3028 | 32.9861 | 0 | 40.318 | 0 | 0 | 32.9861
2210 | 0 | 3.2755 | 4.1144 | 28.9539 | 0 | 36.3437 | 0 | 0 | 28.9539
2211 | 13.0975 | 3.0563 | 4.1082 | 33.5164 | 0 | 53.7785 | 0 | 0 | 46.6139
2212 | 63.4753 | 2.9289 | 3.8123 | 32.4061 | 0 | 102.6226 | 0 | 0 | 95.8814
2213 | 102.1441 | 3.275 | 2.9559 | 21.3563 | 0 | 129.7312 | 0 | 0 | 123.5004
2214 | 87.5057 | 2.9235 | 1.8545 | 29.1077 | 0 | 121.3913 | 0 | 0 | 116.6134
2215 | 93.0083 | 3.0668 | 1.8626 | 37.1651 | 0 | 135.1028 | 0 | 0 | 130.1734
2216 | 83.0693 | 2.5355 | 1.8002 | 25.4496 | 7.9231 | 120.7777 | 0 | 0 | 116.442
2217 | 82.0657 | 2.6565 | 1.7611 | 20.3996 | 10.2137 | 117.0966 | 0 | 0 | 112.679
2218 | 80.6581 | 2.9982 | 1.7681 | 30.911 | 15.3999 | 131.7352 | 0 | 0 | 126.9689
2219 | 72.1539 | 2.9322 | 1.3773 | 33.1034 | 10.699 | 120.2658 | 0 | 0 | 115.9563
2220 | 73.7654 | 2.9458 | 2.3299 | 29.6606 | 20.2846 | 128.9863 | 0 | 0 | 123.7106
2221 | 34.8171 | 3.3681 | 2.3888 | 24.4042 | 13.5278 | 78.506 | 0 | 0 | 72.7491
2222 | 0 | 2.7508 | 2.0295 | 24.7592 | 5.7189 | 35.2583 | 0 | 0 | 30.478
2223 | 0 | 2.6216 | 1.9886 | 31.9473 | 0.92185 | 37.4794 | 200 | 0 | 232.8692
2224 | 0 | 3.0573 | 2.2272 | 32.1644 | 18.7601 | 56.2091 | 0 | 0 | 50.9246
2225 | 0 | 2.7007 | 2.1199 | 23.8606 | 13.3729 | 42.0541 | 0 | 0 | 37.2336
2226 | 0 | 2.7628 | 1.5861 | 32.866 | 8.2721 | 45.487 | 0 | 0 | 41.1381
2227 | 0 | 2.9493 | 1.239 | 22.144 | 13.3086 | 39.641 | 0 | 0 | 35.4527
2228 | 0 | 3.1246 | 1.0185 | 34.5234 | 0 | 38.6665 | 0 | 0 | 34.5234
2229 | 0 | 2.8401 | 1.0722 | 32.6866 | 0 | 36.599 | 0 | 0 | 32.6866
2230 | 0 | 3.0207 | 1.1947 | 30.9781 | 0 | 35.1936 | 0 | 0 | 30.9781
2231 | 0 | 2.5876 | 1.9596 | 32.3478 | 0 | 36.8951 | 0 | 0 | 32.3478
2232 | 0 | 3.3009 | 2.9294 | 29.6562 | 0 | 35.8865 | 0 | 0 | 29.6562
2233 | 0 | 3.3131 | 5.8927 | 36.6968 | 0 | 45.9026 | 0 | 0 | 36.6968
2234 | 0 | 2.9215 | 5.1798 | 33.0205 | 0 | 41.1218 | 0 | 0 | 33.0205
2235 | 0 | 3.1462 | 5.342 | 33.309 | 0 | 41.7972 | 0 | 0 | 33.309
2236 | 0 | 2.7981 | 5.21 | 20.1257 | 0 | 28.1338 | 0 | 0 | 20.1257
2237 | 5.7631 | 3.5938 | 4.0444 | 25.0933 | 0 | 38.4946 | 0 | 0 | 30.8564
2238 | 17.8511 | 2.9666 | 2.9854 | 29.8565 | 0 | 53.6596 | 0 | 0 | 47.7076
2239 | 14.5484 | 2.7554 | 3.2479 | 33.2992 | 0 | 53.8509 | 0 | 200 | 247.8476
2240 | 0 | 2.9763 | 2.5587 | 36.9561 | 18.5505 | 61.0417 | 0 | 0 | 55.5066
2241 | 1.8029 | 2.6668 | 3.5625 | 29.0311 | 17.3442 | 54.4075 | 0 | 0 | 48.1782
2242 | 25.503 | 3.291 | 2.1857 | 29.5386 | 16.1662 | 76.6846 | 0 | 0 | 71.2078
2243 | 73.5706 | 2.9643 | 1.3773 | 32.246 | 15.9781 | 126.1363 | 0 | 0 | 121.7947
2244 | 58.5323 | 2.8999 | 2.3299 | 26.0819 | 8.775 | 98.6191 | 0 | 0 | 93.3893
2245 | 0 | 3.2689 | 2.3888 | 33.0112 | 12.2277 | 50.8966 | 0 | 0 | 45.2389
2246 | 0 | 2.8557 | 4.4905 | 26.6119 | 11.2948 | 45.253 | 0 | 0 | 37.9067
2247 | 0 | 3.1623 | 2.8104 | 28.7933 | 7.3389 | 42.105 | 0 | 0 | 36.1322
2248 | 0 | 2.8971 | 2.2272 | 33.4392 | 9.1771 | 47.7407 | 0 | 0 | 42.6163
2249 | 0 | 3.8476 | 2.1199 | 37.3143 | 15.2125 | 58.4943 | 0 | 0 | 52.5267
2250 | 0 | 3.0803 | 1.5861 | 33.6562 | 20.6522 | 58.9748 | 0 | 0 | 54.3084
2251 | 0 | 3.1074 | 1.239 | 26.8254 | 19.147 | 50.3189 | 0 | 0 | 45.9725
2252 | 0 | 2.8814 | 1.0185 | 29.5584 | 0 | 33.4584 | 0 | 0 | 29.5584
2253 | 0 | 2.9782 | 1.0722 | 28.6757 | 0 | 32.7261 | 0 | 0 | 28.6757
2254 | 0 | 2.7466 | 1.1947 | 34.0943 | 0 | 38.0357 | 0 | 0 | 34.0943
2255 | 0 | 2.7629 | 1.3953 | 20.8262 | 0 | 24.9845 | 0 | 0 | 20.8262
2256 | 0 | 3.1544 | 2.7569 | 28.4394 | 0 | 34.3507 | 0 | 0 | 28.4394
2257 | 0 | 3.0899 | 7.0617 | 28.9868 | 0 | 39.1385 | 0 | 0 | 28.9868
2258 | 0 | 2.566 | 6.8191 | 22.4855 | 0 | 31.8705 | 0 | 0 | 22.4855
2259 | 0 | 3.1937 | 7.6039 | 31.7433 | 0 | 42.5409 | 0 | 0 | 31.7433
2260 | 6.402 | 3.465 | 8.3549 | 29.9123 | 0 | 48.1341 | 0 | 0 | 36.3142
2261 | 35.7858 | 3.0219 | 9.0517 | 24.7821 | 0 | 72.6415 | 0 | 0 | 60.568
2262 | 81.9673 | 3.0393 | 9.248 | 29.2457 | 0 | 123.5002 | 0 | 0 | 111.2129
2263 | 33.1509 | 3.0829 | 9.0056 | 24.1318 | 0 | 69.3712 | 0 | 0 | 57.2827
2264 | 43.9877 | 2.7712 | 8.7378 | 31.0022 | 16.4229 | 102.9218 | 0 | 0 | 91.4128
2265 | 67.7776 | 3.3029 | 6.6752 | 29.358 | 7.1672 | 114.281 | 0 | 0 | 104.3029
2266 | 45.2579 | 2.8686 | 5.9819 | 31.0402 | 7.6639 | 92.8125 | 0 | 0 | 83.962
2267 | 3.8973 | 3.0028 | 4.6777 | 35.3618 | 7.7873 | 54.7268 | 0 | 0 | 47.0464
2268 | 12.4406 | 2.6535 | 3.7833 | 27.7063 | 4.6985 | 51.2822 | 0 | 0 | 44.8454
2269 | 0 | 3.3544 | 4.935 | 24.0209 | 10.6589 | 42.9693 | 0 | 0 | 34.6798
2270 | 0 | 3.0162 | 7.2383 | 31.7238 | 11.1678 | 53.1461 | 0 | 0 | 42.8916
2271 | 0 | 2.3603 | 9.2485 | 22.7942 | 20.8407 | 55.2438 | 0 | 0 | 43.6349
2272 | 0 | 2.8311 | 11.0463 | 26.4501 | 13.3636 | 53.6912 | 0 | 0 | 39.8137
2273 | 0 | 3.5024 | 9.933 | 26.0915 | 13.6818 | 53.2088 | 0 | 0 | 39.7734
2274 | 0 | 2.7624 | 8.3837 | 27.122 | 13.1017 | 51.3697 | 0 | 0 | 40.2237
2275 | 0 | 3.2911 | 8.1716 | 26.9091 | 12.9094 | 51.2813 | 0 | 0 | 39.8185
2276 | 0 | 2.3577 | 7.7333 | 32.7615 | 0 | 42.8526 | 0 | 0 | 32.7615
2277 | 0 | 2.5144 | 7.565 | 30.1012 | 0 | 40.1805 | 0 | 200 | 230.1012
2278 | 0 | 2.7383 | 8.2656 | 23.5815 | 0 | 34.5854 | 0 | 0 | 23.5815
2279 | 0 | 2.995 | 9.9409 | 31.6688 | 0 | 44.6047 | 0 | 0 | 31.6688
2280 | 0 | 2.9706 | 13.6825 | 24.7377 | 0 | 41.3908 | 0 | 0 | 24.7377
2281 | 0 | 2.7528 | 13.4914 | 23.1437 | 0 | 39.3879 | 0 | 0 | 23.1437
2282 | 0 | 2.7137 | 9.4418 | 24.685 | 0 | 36.8405 | 0 | 0 | 24.685
2283 | 0 | 2.7763 | 7.3983 | 24.9693 | 0 | 35.1439 | 0 | 0 | 24.9693
2284 | 2.4962 | 3.0834 | 6.9572 | 23.0046 | 0 | 35.5414 | 0 | 0 | 25.5009
2285 | 17.5069 | 2.869 | 5.5684 | 25.4963 | 0 | 51.4405 | 0 | 0 | 43.0031
2286 | 60.5354 | 3.026 | 4.68 | 29.5391 | 0 | 97.7804 | 0 | 0 | 90.0744
2287 | 69.0397 | 2.8666 | 4.2075 | 28.4985 | 0 | 104.6123 | 0 | 0 | 97.5382
2288 | 2.7291 | 2.6545 | 2.9661 | 29.4458 | 17.2503 | 55.0458 | 0 | 0 | 49.4252
2289 | 0 | 2.7075 | 2.1414 | 30.9513 | 18.1965 | 53.9967 | 0 | 0 | 49.1478
2290 | 0 | 3.3988 | 1.7681 | 26.5494 | 15.1041 | 46.8204 | 200 | 0 | 241.6535
2291 | 0 | 3.1877 | 1.3773 | 20.7828 | 21.4789 | 46.8267 | 0 | 0 | 42.2617
2292 | 0 | 2.583 | 2.3299 | 30.5349 | 16.5411 | 51.9889 | 0 | 0 | 47.076
2293 | 0 | 2.9594 | 2.3888 | 25.5271 | 9.8866 | 40.7619 | 0 | 0 | 35.4137
2294 | 0 | 3.0306 | 2.0295 | 33.0961 | 13.4623 | 51.6185 | 0 | 0 | 46.5585
2295 | 0 | 2.5408 | 1.9886 | 26.4448 | 12.5496 | 43.5238 | 0 | 0 | 38.9944
2296 | 0 | 2.6127 | 2.2272 | 25.8314 | 22.9036 | 53.5749 | 0 | 0 | 48.735
2297 | 0 | 2.8943 | 2.1199 | 27.3828 | 13.4136 | 45.8106 | 0 | 0 | 40.7964
2298 | 0 | 2.6947 | 1.9531 | 29.3345 | 10.5772 | 44.5595 | 0 | 0 | 39.9117
2299 | 0 | 2.8422 | 1.5255 | 22.858 | 20.683 | 47.9087 | 0 | 0 | 43.5411
2300 | 0 | 3.6343 | 1.1504 | 30.3588 | 0 | 35.1434 | 0 | 0 | 30.3588
2301 | 0.15216 | 2.6871 | 1.1994 | 26.5538 | 0 | 30.5925 | 0 | 0 | 26.706
2302 | 22.5304 | 2.7035 | 1.9023 | 31.959 | 0 | 59.0952 | 0 | 0 | 54.4894
2303 | 92.6771 | 3.2101 | 2.4039 | 38.3349 | 0 | 136.626 | 0 | 0 | 131.0121
2304 | 77.7225 | 3.4902 | 3.8797 | 32.7396 | 0 | 117.8321 | 0 | 0 | 110.4621
2305 | 55.2245 | 3.154 | 2.1992 | 28.1843 | 0 | 88.7621 | 0 | 0 | 83.4088
2306 | 18.5231 | 3.0403 | 1.9945 | 29.3451 | 0 | 52.903 | 0 | 0 | 47.8682
2307 | 0 | 2.8594 | 3.6751 | 27.0205 | 0 | 33.555 | 0 | 0 | 27.0205
2308 | 0 | 2.5103 | 3.2685 | 33.4085 | 0 | 39.1873 | 0 | 0 | 33.4085
2309 | 0 | 3.0103 | 2.6595 | 27.5147 | 0 | 33.1845 | 0 | 0 | 27.5147
2310 | 0 | 3.0847 | 2.1561 | 28.4989 | 0 | 33.7396 | 0 | 0 | 28.4989
2311 | 0 | 2.8171 | 1.9466 | 25.4537 | 0 | 30.2175 | 0 | 0 | 25.4537
2312 | 0.11369 | 3.098 | 1.9857 | 20.3271 | 15.2003 | 40.7248 | 0 | 0 | 35.6411
2313 | 19.5398 | 3.0119 | 1.7436 | 34.3068 | 19.1242 | 77.7263 | 0 | 0 | 72.9708
2314 | 91.8663 | 3.1672 | 1.9834 | 26.9461 | 12.4554 | 136.4184 | 0 | 0 | 131.2678
2315 | 67.776 | 2.7642 | 2.2739 | 34.3375 | 22.4613 | 129.6129 | 0 | 0 | 124.5748
2316 | 54.4367 | 2.7219 | 2.4752 | 29.3786 | 6.8439 | 95.8562 | 0 | 0 | 90.6592
2317 | 59.345 | 2.92 | 1.8702 | 28.9495 | 20.3731 | 113.4578 | 0 | 0 | 108.6676
2318 | 25.4102 | 2.8627 | 2.2301 | 20.9429 | 17.9784 | 69.4244 | 0 | 0 | 64.3315
2319 | 43.1985 | 2.7551 | 2.3118 | 28.0394 | 12.8657 | 89.1705 | 0 | 0 | 84.1036
2320 | 8.0646 | 3.2271 | 1.9 | 26.3303 | 12.1858 | 51.7077 | 0 | 0 | 46.5807
2321 | 0 | 3.1453 | 1.9367 | 34.7086 | 10.7331 | 50.5237 | 0 | 0 | 45.4417
2322 | 0 | 3.2317 | 1.5167 | 37.6106 | 8.1509 | 50.5099 | 0 | 0 | 45.7615
2323 | 0 | 3.2255 | 1.4117 | 23.207 | 16.1673 | 44.0114 | 0 | 0 | 39.3742
2324 | 0 | 3.5853 | 1.5853 | 25.5003 | 0 | 30.6708 | 0 | 0 | 25.5003
2325 | 0 | 2.7753 | 1.5924 | 29.4128 | 0 | 33.7805 | 0 | 0 | 29.4128
2326 | 0 | 3.2922 | 2.2469 | 28.8686 | 0 | 34.4078 | 0 | 0 | 28.8686
2327 | 0 | 3.2788 | 2.6693 | 32.1671 | 0 | 38.1152 | 0 | 0 | 32.1671
2328 | 0 | 2.8975 | 4.2305 | 40.8928 | 0 | 48.0208 | 0 | 0 | 40.8928
2329 | 0 | 2.9639 | 2.1636 | 24.8095 | 0 | 29.9371 | 0 | 0 | 24.8095
2330 | 0 | 3.0439 | 1.767 | 41.294 | 0 | 46.1048 | 0 | 0 | 41.294
2331 | 0 | 3.1608 | 2.6204 | 29.9235 | 0 | 35.7046 | 0 | 0 | 29.9235
2332 | 0 | 3.5186 | 2.6397 | 30.6357 | 0 | 36.794 | 0 | 0 | 30.6357
2333 | 0 | 2.5464 | 2.3626 | 35.7296 | 0 | 40.6386 | 0 | 0 | 35.7296
2334 | 0 | 3.3469 | 1.8189 | 21.7726 | 0 | 26.9384 | 0 | 0 | 21.7726
2335 | 0 | 2.8695 | 1.9431 | 21.8193 | 0 | 26.6319 | 0 | 0 | 21.8193
2336 | 0 | 2.3112 | 1.9321 | 32.3428 | 17.7706 | 54.3566 | 0 | 0 | 50.1134
2337 | 0 | 2.8353 | 1.7582 | 32.6004 | 4.4909 | 41.6848 | 0 | 0 | 37.0913
2338 | 0 | 2.9831 | 1.4747 | 31.3008 | 0.034379 | 35.793 | 0 | 0 | 31.3352
2339 | 0 | 2.7986 | 1.8335 | 22.4566 | 11.4536 | 38.5422 | 0 | 0 | 33.9102
2340 | 0 | 2.5893 | 2.0907 | 28.6791 | 7.7916 | 41.1508 | 0 | 0 | 36.4707
2341 | 0 | 3.2614 | 2.2196 | 24.2488 | 12.5119 | 42.2417 | 0 | 0 | 36.7607
2342 | 0 | 2.8929 | 2.2605 | 34.7523 | 20.0621 | 59.9678 | 0 | 0 | 54.8145
2343 | 0 | 2.9607 | 2.1706 | 30.5078 | 13.534 | 49.1731 | 0 | 200 | 244.0418
2344 | 0 | 2.7959 | 2.1677 | 33.778 | 18.4628 | 57.2045 | 0 | 0 | 52.2409
2345 | 0 | 3.0601 | 2.1706 | 26.9861 | 8.2557 | 40.4727 | 0 | 0 | 35.2419
2346 | 0 | 2.5719 | 1.5861 | 28.501 | 14.8035 | 47.4625 | 0 | 0 | 43.3045
2347 | 0 | 3.2124 | 1.239 | 11.6176 | 15.2945 | 31.3635 | 0 | 0 | 26.9121
2348 | 0 | 3.1125 | 1.0185 | 20.0163 | 0 | 24.1473 | 0 | 0 | 20.0163
2349 | 0 | 2.4261 | 1.0722 | 24.8923 | 0 | 28.3906 | 0 | 0 | 24.8923
2350 | 0 | 2.5755 | 1.1947 | 21.5522 | 0 | 25.3224 | 0 | 0 | 21.5522
2351 | 0 | 2.8775 | 1.7178 | 24.9351 | 0 | 29.5303 | 0 | 0 | 24.9351
2352 | 0 | 2.9206 | 3.0308 | 30.6189 | 0 | 36.5703 | 0 | 0 | 30.6189
2353 | 0 | 2.6098 | 5.8927 | 26.6618 | 0 | 35.1642 | 0 | 0 | 26.6618
2354 | 0 | 2.8083 | 5.0979 | 33.368 | 0 | 41.2742 | 0 | 0 | 33.368
2355 | 0 | 2.6042 | 4.9307 | 30.4894 | 0 | 38.0244 | 0 | 0 | 30.4894
2356 | 0 | 3.12 | 4.5112 | 31.2634 | 0 | 38.8945 | 0 | 0 | 31.2634
2357 | 0 | 3.1022 | 3.609 | 31.2964 | 0 | 38.0076 | 0 | 0 | 31.2964
2358 | 0 | 3.2063 | 2.2486 | 25.7896 | 0 | 31.2445 | 200 | 0 | 225.7896
2359 | 2.9098 | 2.7253 | 1.877 | 29.1233 | 0 | 36.6354 | 0 | 0 | 32.0331
2360 | 13.1251 | 3.031 | 1.8002 | 31.5767 | 10.6546 | 60.1876 | 0 | 0 | 55.3564
2361 | 20.6421 | 2.8561 | 1.7611 | 25.8037 | 17.2976 | 68.3606 | 0 | 0 | 63.7434
2362 | 0 | 2.6782 | 1.7681 | 31.2471 | 24.2753 | 59.9687 | 0 | 0 | 55.5224
2363 | 0 | 3.4694 | 1.3773 | 25.2812 | 12.3978 | 42.5256 | 0 | 0 | 37.6789
2364 | 0 | 2.8054 | 2.3299 | 22.1961 | 17.6377 | 44.969 | 0 | 0 | 39.8337
2365 | 0 | 3.3675 | 2.3888 | 32.178 | 12.253 | 50.1873 | 0 | 0 | 44.431
2366 | 0 | 2.7559 | 2.0295 | 31.0803 | 13.4409 | 49.3066 | 0 | 0 | 44.5212
2367 | 0 | 3.3338 | 1.9886 | 29.354 | 1.7589 | 36.4354 | 0 | 0 | 31.113
2368 | 0 | 3.669 | 2.2272 | 26.6532 | 23.8969 | 56.4464 | 0 | 0 | 50.5501
2369 | 7.0401 | 2.999 | 2.1199 | 25.3608 | 19.8311 | 57.3509 | 0 | 0 | 52.232
2370 | 32.0294 | 2.835 | 1.5861 | 30.6109 | 15.358 | 82.4195 | 0 | 0 | 77.9983
2371 | 34.3814 | 3.1736 | 1.239 | 29.0319 | 10.6402 | 78.4661 | 0 | 0 | 74.0535
2372 | 37.9015 | 2.808 | 1.0185 | 32.8989 | 0 | 74.627 | 0 | 0 | 70.8004
2373 | 78.8261 | 3.3173 | 1.0722 | 33.1343 | 0 | 116.3499 | 0 | 0 | 111.9604
2374 | 56.1795 | 2.8954 | 1.1947 | 24.6372 | 0 | 84.9068 | 0 | 0 | 80.8167
2375 | 0 | 2.4469 | 1.2542 | 28.8989 | 0 | 32.6 | 0 | 0 | 28.8989
2376 | 0 | 2.8111 | 2.7569 | 36.5467 | 0 | 42.1147 | 0 | 0 | 36.5467
2377 | 0 | 3.1069 | 4.3028 | 22.9338 | 0 | 30.3435 | 0 | 0 | 22.9338
2378 | 0 | 3.0932 | 3.0702 | 34.6197 | 0 | 40.7831 | 0 | 0 | 34.6197
2379 | 0 | 2.7328 | 2.3713 | 31.9934 | 0 | 37.0975 | 0 | 0 | 31.9934
2380 | 0 | 2.4587 | 2.2727 | 33.8615 | 0 | 38.593 | 0 | 0 | 33.8615
2381 | 1.4476 | 3.1127 | 2.0277 | 26.6577 | 0 | 33.2458 | 0 | 0 | 28.1053
2382 | 5.2278 | 3.3161 | 1.8545 | 29.2036 | 0 | 39.602 | 0 | 0 | 34.4314
2383 | 15.8494 | 3.391 | 1.8626 | 27.7598 | 0 | 48.8629 | 0 | 0 | 43.6092
2384 | 29.3527 | 2.9931 | 1.8002 | 34.8101 | 17.8449 | 86.801 | 0 | 0 | 82.0077
2385 | 28.5319 | 2.9436 | 1.7611 | 20.6704 | 19.4832 | 73.3902 | 0 | 0 | 68.6855
2386 | 13.2836 | 3.3814 | 1.7681 | 27.5073 | 13.8106 | 59.751 | 0 | 0 | 54.6015
2387 | 60.786 | 2.658 | 1.3773 | 34.1245 | 7.5757 | 106.5215 | 0 | 0 | 102.4862
2388 | 25.7708 | 3.2764 | 2.3299 | 22.8947 | 12.6717 | 66.9435 | 0 | 0 | 61.3371
2389 | 1.49 | 2.3619 | 2.3888 | 30.825 | 18.3983 | 55.464 | 0 | 0 | 50.7133
2390 | 3.9099 | 2.4325 | 2.0295 | 30.4878 | 17.3101 | 56.1699 | 0 | 0 | 51.7079
2391 | 0 | 2.6485 | 1.9886 | 40.8314 | 11.9084 | 57.377 | 0 | 0 | 52.7399
2392 | 0 | 3.296 | 2.2272 | 40.0182 | 6.7822 | 52.3237 | 0 | 0 | 46.8004
2393 | 0 | 2.9558 | 2.1199 | 27.2485 | 15.7425 | 48.0667 | 0 | 0 | 42.991
2394 | 0 | 2.9344 | 1.5861 | 33.0315 | 16.1002 | 53.6524 | 0 | 0 | 49.1318
2395 | 0 | 2.7284 | 1.239 | 37.1119 | 10.8738 | 51.9532 | 0 | 0 | 47.9858
2396 | 0 | 2.6927 | 1.0185 | 35.0971 | 0 | 38.8083 | 0 | 0 | 35.0971
2397 | 0 | 2.9715 | 1.0722 | 30.3096 | 0 | 34.3533 | 0 | 0 | 30.3096
2398 | 0 | 2.8701 | 1.1947 | 37.6852 | 0 | 41.75 | 0 | 0 | 37.6852
2399 | 0 | 2.9878 | 2.1209 | 29.4385 | 0 | 34.5472 | 0 | 0 | 29.4385
2400 | 0 | 3.2802 | 3.6395 | 23.708 | 0 | 30.6276 | 0 | 0 | 23.708
2401 | 0 | 3.3606 | 6.5746 | 25.6287 | 0 | 35.5639 | 0 | 0 | 25.6287
2402 | 0 | 3.1541 | 4.934 | 23.7159 | 0 | 31.8039 | 0 | 0 | 23.7159
2403 | 0 | 2.8143 | 4.7251 | 25.3371 | 0 | 32.8765 | 0 | 0 | 25.3371
2404 | 5.6321 | 3.7045 | 4.581 | 25.4157 | 0 | 39.3334 | 0 | 0 | 31.0478
2405 | 35.323 | 3.4965 | 3.0285 | 35.8654 | 0 | 77.7133 | 0 | 0 | 71.1884
2406 | 54.3542 | 3.3464 | 2.396 | 32.8909 | 0 | 92.9875 | 0 | 0 | 87.2451
2407 | 0.089311 | 2.8518 | 1.8626 | 32.2375 | 0 | 37.0413 | 0 | 0 | 32.3268
2408 | 0 | 3.1427 | 1.8002 | 35.6631 | 22.1444 | 62.7504 | 0 | 0 | 57.8075
2409 | 0 | 2.5522 | 1.7611 | 27.1098 | 11.7772 | 43.2003 | 0 | 0 | 38.887
2410 | 15.1956 | 2.8214 | 1.7681 | 25.3401 | 4.5939 | 49.719 | 0 | 0 | 45.1295
2411 | 68.485 | 2.4111 | 1.3773 | 30.4069 | 10.9114 | 113.5916 | 0 | 0 | 109.8033
2412 | 61.3737 | 2.4637 | 2.3299 | 28.2728 | 7.7571 | 102.1973 | 0 | 0 | 97.4037
2413 | 5.0085 | 2.6704 | 2.3888 | 29.3322 | 20.6551 | 60.055 | 0 | 0 | 54.9958
2414 | 0 | 2.983 | 2.0295 | 26.5392 | 23.4325 | 54.9843 | 0 | 0 | 49.9718
2415 | 0 | 2.5285 | 1.9886 | 24.8554 | 12.6106 | 41.9832 | 0 | 0 | 37.466
2416 | 0 | 3.076 | 2.2272 | 30.3972 | 8.4588 | 44.1592 | 0 | 0 | 38.856
2417 | 0 | 3.0493 | 2.1199 | 29.8577 | 6.3832 | 41.4101 | 0 | 0 | 36.2409
2418 | 0 | 2.7738 | 1.5861 | 26.4549 | 13.2917 | 44.1066 | 0 | 0 | 39.7466
2419 | 0 | 3.1452 | 1.239 | 30.3375 | 12.8305 | 47.5522 | 0 | 0 | 43.168
2420 | 0 | 2.8087 | 1.0274 | 24.0548 | 0 | 27.8909 | 0 | 0 | 24.0548
2421 | 0 | 2.8357 | 1.6164 | 24.5732 | 0 | 29.0253 | 0 | 0 | 24.5732
2422 | 0 | 3.2431 | 1.5306 | 30.5812 | 0 | 35.3549 | 0 | 0 | 30.5812
2423 | 0 | 2.9718 | 2.2821 | 25.1417 | 0 | 30.3956 | 0 | 0 | 25.1417
2424 | 0 | 3.3383 | 2.7569 | 29.0126 | 0 | 35.1078 | 0 | 0 | 29.0126
2425 | 0 | 3.0421 | 5.6978 | 37.7834 | 0 | 46.5233 | 200 | 0 | 237.7834
2426 | 0 | 2.6008 | 5.0159 | 30.311 | 0 | 37.9277 | 0 | 0 | 30.311
2427 | 0 | 2.833 | 5.6162 | 23.4418 | 0 | 31.891 | 0 | 200 | 223.4418
2428 | 1.2664 | 2.912 | 5.6992 | 35.6799 | 0 | 45.5575 | 0 | 0 | 36.9463
2429 | 23.0815 | 2.8098 | 5.2055 | 23.6997 | 0 | 54.7966 | 0 | 0 | 46.7813
2430 | 73.2807 | 3.1766 | 3.7222 | 26.0577 | 0 | 106.2372 | 0 | 0 | 99.3384
2431 | 77.5882 | 2.9967 | 4.8244 | 20.4997 | 0 | 105.909 | 0 | 0 | 98.0879
2432 | 50.1368 | 2.8715 | 4.392 | 26.6925 | 12.8231 | 96.916 | 0 | 0 | 89.6524
2433 | 0 | 3.0921 | 2.8858 | 24.4405 | 12.7233 | 43.1416 | 0 | 0 | 37.1638
2434 | 17.1094 | 2.8689 | 1.7681 | 28.4765 | 13.8985 | 64.1214 | 0 | 0 | 59.4843
2435 | 63.6432 | 2.9672 | 1.3773 | 28.9009 | 14.4193 | 111.3078 | 0 | 0 | 106.9633
2436 | 74.1573 | 3.2413 | 2.3299 | 39.6547 | 10.722 | 130.1052 | 0 | 0 | 124.534
2437 | 37.844 | 3.0116 | 2.3888 | 23.6519 | 21.515 | 88.4114 | 0 | 0 | 83.0109
2438 | 0 | 3.4344 | 2.0295 | 35.4177 | 20.198 | 61.0796 | 0 | 0 | 55.6157
2439 | 0 | 2.8197 | 1.9886 | 23.9555 | 10.0972 | 38.8611 | 0 | 0 | 34.0527
2440 | 0 | 2.609 | 2.2272 | 32.9912 | 10.146 | 47.9735 | 0 | 0 | 43.1372
2441 | 0 | 2.8236 | 2.1199 | 29.0457 | 16.5822 | 50.5714 | 0 | 0 | 45.6278
2442 | 0 | 3.0876 | 1.5861 | 21.71 | 23.9217 | 50.3054 | 0 | 0 | 45.6317
2443 | 0 | 2.7497 | 1.239 | 23.3651 | 14.9721 | 42.3259 | 0 | 0 | 38.3372
2444 | 0 | 2.6477 | 1.0185 | 31.047 | 0 | 34.7132 | 0 | 0 | 31.047
2445 | 0 | 3.1409 | 2.4203 | 19.8084 | 0 | 25.3695 | 0 | 0 | 19.8084
2446 | 0 | 3.1615 | 2.3421 | 25.8036 | 0 | 31.3071 | 0 | 0 | 25.8036
2447 | 0 | 3.1794 | 4.217 | 28.5413 | 0 | 35.9376 | 0 | 0 | 28.5413
2448 | 0 | 3.3862 | 6.7843 | 34.3987 | 0 | 44.5691 | 0 | 0 | 34.3987
2449 | 0 | 3.4209 | 6.8669 | 29.4832 | 0 | 39.771 | 0 | 0 | 29.4832
2450 | 0 | 2.5297 | 3.0702 | 36.2673 | 0 | 41.8672 | 0 | 0 | 36.2673
2451 | 0 | 2.7484 | 2.3713 | 23.5957 | 0 | 28.7154 | 0 | 0 | 23.5957
2452 | 0 | 3.2127 | 2.4146 | 21.7174 | 0 | 27.3447 | 0 | 0 | 21.7174
2453 | 0 | 2.7777 | 2.0277 | 38.6022 | 0 | 43.4077 | 0 | 0 | 38.6022
2454 | 12.2021 | 2.8093 | 1.8545 | 22.4227 | 0 | 39.2886 | 0 | 0 | 34.6248
2455 | 55.6281 | 2.8603 | 1.8626 | 26.8297 | 0 | 87.1807 | 0 | 0 | 82.4578
2456 | 35.4108 | 2.8908 | 1.8002 | 22.9441 | 20.8036 | 83.8495 | 0 | 0 | 79.1585
2457 | 11.0243 | 3.1899 | 1.7611 | 29.355 | 6.4461 | 51.7765 | 0 | 0 | 46.8254
2458 | 9.1692 | 2.6655 | 1.7681 | 24.1977 | 21.1644 | 58.965 | 0 | 0 | 54.5313
2459 | 0 | 3.1717 | 1.3773 | 38.2039 | 10.8478 | 53.6006 | 0 | 0 | 49.0517
2460 | 0 | 2.9599 | 2.3299 | 34.4091 | 23.3459 | 63.0448 | 0 | 0 | 57.755
2461 | 0 | 3.3351 | 2.3888 | 38.6255 | 2.1358 | 46.4853 | 0 | 0 | 40.7614
2462 | 0 | 2.8259 | 2.0295 | 27.0319 | 26.0384 | 57.9257 | 0 | 0 | 53.0703
2463 | 0 | 2.9431 | 1.9886 | 33.1447 | 23.7853 | 61.8617 | 0 | 0 | 56.93
2464 | 0 | 3.2599 | 2.2272 | 36.5392 | 17.5782 | 59.6046 | 0 | 0 | 54.1174
2465 | 0 | 3.3678 | 2.1199 | 25.5359 | 18.5137 | 49.5373 | 0 | 0 | 44.0496
2466 | 0 | 3.2958 | 1.9531 | 37.2187 | 11.4917 | 53.9593 | 0 | 0 | 48.7104
2467 | 0 | 2.9873 | 1.5255 | 25.8341 | 13.5598 | 43.9066 | 0 | 0 | 39.3939
2468 | 0 | 2.3794 | 1.1504 | 29.1357 | 0 | 32.6655 | 0 | 0 | 29.1357
2469 | 0 | 3.4533 | 1.1994 | 31.2682 | 0 | 35.9209 | 0 | 0 | 31.2682
2470 | 0 | 2.8405 | 1.0675 | 29.6909 | 0 | 33.5989 | 0 | 0 | 29.6909
2471 | 0 | 2.9165 | 1.3615 | 27.4234 | 0 | 31.7014 | 0 | 0 | 27.4234
2472 | 0 | 2.7674 | 1.7973 | 28.8353 | 0 | 33.4 | 0 | 0 | 28.8353
2473 | 0 | 2.3456 | 2.1992 | 29.1477 | 0 | 33.6925 | 0 | 0 | 29.1477
2474 | 0 | 2.6348 | 1.9945 | 30.5527 | 0 | 35.182 | 0 | 0 | 30.5527
2475 | 0 | 2.9742 | 3.6751 | 35.0441 | 0 | 41.6934 | 0 | 0 | 35.0441
2476 | 0 | 3.0346 | 5.2765 | 23.0923 | 0 | 31.4034 | 0 | 0 | 23.0923
2477 | 0 | 3.2399 | 5.3203 | 32.8738 | 0 | 41.434 | 0 | 0 | 32.8738
2478 | 0 | 2.7782 | 4.397 | 29.8721 | 0 | 37.0472 | 0 | 0 | 29.8721
2479 | 0 | 2.8384 | 4.4352 | 33.2339 | 0 | 40.5075 | 0 | 0 | 33.2339
2480 | 0 | 3.1046 | 3.1365 | 23.1929 | 17.9729 | 47.4069 | 0 | 0 | 41.1658
2481 | 0 | 2.7884 | 2.7976 | 35.6882 | 14.8783 | 56.1525 | 0 | 0 | 50.5666
2482 | 0 | 3.4235 | 1.9834 | 41.3005 | 4.5231 | 51.2304 | 0 | 0 | 45.8236
2483 | 0 | 2.9107 | 2.2739 | 32.1679 | 25.5979 | 62.9505 | 0 | 0 | 57.7658
2484 | 0 | 3.3107 | 2.4752 | 28.9355 | 16.2285 | 50.9498 | 0 | 0 | 45.164
2485 | 0 | 2.9651 | 1.8702 | 30.9988 | 9.4102 | 45.2444 | 0 | 0 | 40.409
2486 | 0 | 2.4645 | 2.2301 | 23.698 | 12.4316 | 40.8243 | 0 | 0 | 36.1296
2487 | 0 | 3.0865 | 2.3118 | 27.4609 | 20.8413 | 53.7005 | 0 | 0 | 48.3022
2488 | 0 | 2.8511 | 2.9158 | 31.0894 | 13.9799 | 50.8361 | 0 | 0 | 45.0692
2489 | 0 | 2.6889 | 2.3404 | 30.1497 | 18.1847 | 53.3637 | 0 | 0 | 48.3344
2490 | 0 | 3.1091 | 2.1838 | 22.3656 | -0.54284 | 27.1157 | 0 | 0 | 21.8228
2491 | 0 | 3.3705 | 1.4117 | 30.8541 | 6.3141 | 41.9504 | 0 | 0 | 37.1682
2492 | 0 | 2.6526 | 1.1486 | 25.8092 | 0 | 29.6103 | 0 | 0 | 25.8092
2493 | 0 | 3.2132 | 1.2344 | 24.5988 | 0 | 29.0464 | 200 | 0 | 224.5988
2494 | 0 | 3.1888 | 1.1264 | 29.9883 | 0 | 34.3035 | 0 | 0 | 29.9883
2495 | 0 | 3.1039 | 1.1609 | 23.9003 | 0 | 28.1651 | 0 | 0 | 23.9003
2496 | 0 | 2.9752 | 2.3153 | 39.3494 | 0 | 44.6399 | 0 | 0 | 39.3494
2497 | 0 | 2.3123 | 2.1636 | 30.1971 | 0 | 34.6731 | 0 | 0 | 30.1971
2498 | 0 | 2.7325 | 1.767 | 25.9938 | 0 | 30.4932 | 0 | 0 | 25.9938
2499 | 0 | 2.8741 | 2.6204 | 30.267 | 0 | 35.7614 | 0 | 0 | 30.267
2500 | 0 | 3.2599 | 3.187 | 28.3972 | 0 | 34.8441 | 0 | 0 | 28.3972
2501 | 0 | 2.8176 | 2.5025 | 30.3701 | 0 | 35.6903 | 0 | 0 | 30.3701
2502 | 4.5644 | 2.9866 | 2.3616 | 33.7361 | 0 | 43.6487 | 0 | 0 | 38.3005
2503 | 15.5344 | 3.0306 | 1.9431 | 33.1114 | 0 | 53.6196 | 0 | 0 | 48.6458
2504 | 2.4702 | 2.7418 | 1.9321 | 31.4485 | 19.4759 | 58.0683 | 0 | 0 | 53.3945
2505 | 0 | 3.1534 | 1.7582 | 23.74 | 9.5978 | 38.2495 | 0 | 0 | 33.3378
2506 | 0 | 3.4837 | 1.4747 | 25.994 | 22.1146 | 53.067 | 0 | 0 | 48.1086
2507 | 0 | 2.7335 | 1.8335 | 31.9186 | 16.9691 | 53.4547 | 0 | 0 | 48.8877
2508 | 0 | 2.7401 | 2.0907 | 27.4513 | 19.212 | 51.4941 | 0 | 200 | 246.6632
2509 | 0 | 3.0822 | 2.2196 | 21.0436 | 8.7993 | 35.1447 | 0 | 0 | 29.8429
2510 | 0 | 3.1405 | 2.2605 | 33.9952 | 20.1648 | 59.5609 | 0 | 0 | 54.1599
2511 | 0 | 3.0584 | 2.1706 | 29.3891 | 11.9116 | 46.5299 | 0 | 0 | 41.3008
2512 | 0 | 3.3465 | 2.1677 | 32.707 | 9.2343 | 47.4555 | 0 | 0 | 41.9413
2513 | 0 | 2.8571 | 2.1706 | 22.8989 | 12.2946 | 40.2212 | 0 | 0 | 35.1935
2514 | 0 | 3.1159 | 1.5861 | 30.2531 | 8.8714 | 43.8265 | 0 | 0 | 39.1245
2515 | 0 | 2.9728 | 1.239 | 35.0471 | 12.5684 | 51.8274 | 0 | 0 | 47.6156
2516 | 0 | 2.8686 | 1.0185 | 31.5275 | 0 | 35.4146 | 0 | 0 | 31.5275
2517 | 0 | 2.5973 | 1.0722 | 22.653 | 0 | 26.3225 | 0 | 0 | 22.653
2518 | 0 | 2.5742 | 1.1947 | 30.235 | 0 | 34.0039 | 0 | 0 | 30.235
2519 | 0 | 2.8145 | 1.2542 | 27.1721 | 0 | 31.2408 | 0 | 0 | 27.1721
2520 | 0 | 2.328 | 2.7569 | 34.8835 | 0 | 39.9684 | 0 | 0 | 34.8835
2521 | 0 | 3.2115 | 4.3028 | 24.8109 | 0 | 32.3252 | 0 | 0 | 24.8109
2522 | 7.2211 | 3.0948 | 3.0702 | 26.0734 | 0 | 39.4595 | 0 | 0 | 33.2945
2523 | 43.6174 | 3.2145 | 3.0801 | 33.2773 | 0 | 83.1892 | 0 | 0 | 76.8946
2524 | 94.8384 | 3.4423 | 3.6027 | 21.5598 | 0 | 123.4431 | 0 | 0 | 116.3982
2525 | 72.8042 | 2.7103 | 2.0277 | 21.5749 | 0 | 99.1172 | 0 | 0 | 94.3791
2526 | 72.3356 | 3.3545 | 1.8545 | 23.0454 | 0 | 100.59 | 0 | 0 | 95.381
2527 | 69.2331 | 3.2041 | 2.2198 | 26.9624 | 0 | 101.6194 | 0 | 0 | 96.1956
2528 | 64.0066 | 3.2471 | 1.8002 | 32.2288 | 9.562 | 110.8447 | 0 | 0 | 105.7974
2529 | 71.9911 | 2.7225 | 1.7611 | 24.4773 | 20.9266 | 121.8787 | 0 | 0 | 117.395
2530 | 39.6028 | 2.6479 | 1.7681 | 30.2248 | 25.1612 | 99.4049 | 0 | 0 | 94.9888
2531 | 38.7217 | 2.9313 | 1.3773 | 21.5541 | 20.9228 | 85.5072 | 0 | 0 | 81.1987
2532 | 82.8591 | 3.3348 | 2.3299 | 29.6642 | 18.798 | 136.986 | 0 | 0 | 131.3214
2533 | 110.5812 | 2.1983 | 2.3888 | 19.1798 | 18.1589 | 152.507 | 0 | 0 | 147.9199
2534 | 63.9007 | 2.686 | 2.0295 | 27.607 | 16.3288 | 112.5521 | 0 | 0 | 107.8365
2535 | 0 | 2.2964 | 3.3785 | 28.3821 | 6.0908 | 40.1478 | 0 | 0 | 34.4729
2536 | 0 | 2.9183 | 4.4317 | 33.5136 | 14.0063 | 54.8699 | 0 | 0 | 47.5199
2537 | 0 | 2.5578 | 4.2536 | 29.2934 | 27.4251 | 63.5299 | 0 | 0 | 56.7185
2538 | 0 | 2.7296 | 3.9473 | 31.1832 | 6.0477 | 43.9078 | 0 | 0 | 37.2309
2539 | 0 | 3.2352 | 3.8344 | 28.4754 | 21.2844 | 56.8295 | 0 | 0 | 49.7598
2540 | 0 | 2.4328 | 3.936 | 27.588 | 0 | 33.9567 | 0 | 0 | 27.588
2541 | 0 | 3.3171 | 2.7418 | 28.3881 | 0 | 34.447 | 0 | 0 | 28.3881
2542 | 0 | 2.8091 | 3.397 | 35.7501 | 0 | 41.9562 | 0 | 0 | 35.7501
2543 | 0 | 2.2529 | 4.4588 | 24.4065 | 0 | 31.1183 | 0 | 0 | 24.4065
2544 | 0 | 2.7145 | 6.4799 | 23.8449 | 0 | 33.0393 | 0 | 0 | 23.8449
2545 | 0 | 3.5866 | 6.2824 | 30.7341 | 0 | 40.6031 | 0 | 0 | 30.7341
2546 | 0 | 2.8382 | 3.7045 | 29.3453 | 0 | 35.8881 | 0 | 0 | 29.3453
2547 | 0 | 3.0375 | 2.6003 | 33.1973 | 0 | 38.8351 | 0 | 0 | 33.1973
2548 | 10.6424 | 2.3512 | 2.2727 | 31.0588 | 0 | 46.3251 | 0 | 0 | 41.7012
2549 | 45.6069 | 3.2382 | 2.0277 | 27.8868 | 0 | 78.7595 | 0 | 0 | 73.4936
2550 | 71.0287 | 3.0439 | 1.8545 | 27.9075 | 0 | 103.8345 | 0 | 0 | 98.9362
2551 | 72.7366 | 3.4714 | 1.8626 | 31.5112 | 0 | 109.5818 | 0 | 0 | 104.2478
2552 | 47.215 | 2.5584 | 1.8002 | 31.425 | 17.0281 | 100.0267 | 0 | 0 | 95.6681
2553 | 45.4664 | 2.9798 | 1.7611 | 33.4535 | 13.979 | 97.6399 | 0 | 0 | 92.899
2554 | 70.9894 | 3.1695 | 1.7681 | 34.1006 | 3.1785 | 113.206 | 0 | 0 | 108.2684
2555 | 94.6184 | 3.1916 | 1.3773 | 24.6027 | 11.8618 | 135.6517 | 0 | 0 | 131.0829
2556 | 80.0762 | 2.5664 | 2.3299 | 36.2947 | 17.7246 | 138.9919 | 0 | 0 | 134.0955
2557 | 102.7258 | 3.4764 | 2.3888 | 25.4009 | 19.6102 | 153.602 | 0 | 0 | 147.7369
2558 | 60.547 | 2.5681 | 2.0295 | 27.4716 | 13.6693 | 106.2854 | 0 | 0 | 101.6878
2559 | 35.9496 | 2.926 | 1.9886 | 32.3059 | 9.8638 | 83.034 | 0 | 0 | 78.1193
2560 | 0 | 3.4595 | 2.2272 | 36.0202 | 10.9766 | 52.6835 | 0 | 0 | 46.9968
2561 | 0 | 2.8869 | 2.1199 | 22.3476 | 15.349 | 42.7034 | 200 | 0 | 237.6966
2562 | 0 | 2.7596 | 1.5861 | 33.7074 | 16.15 | 54.2032 | 0 | 0 | 49.8575
2563 | 0 | 2.3909 | 1.4923 | 31.3937 | 15.9399 | 51.2168 | 0 | 0 | 47.3336
2564 | 0 | 3.1195 | 2.5625 | 24.4986 | 0 | 30.1806 | 0 | 0 | 24.4986
2565 | 0 | 2.7665 | 1.6968 | 24.0518 | 0 | 28.515 | 0 | 0 | 24.0518
2566 | 0 | 2.9879 | 3.2347 | 25.7981 | 0 | 32.0206 | 0 | 0 | 25.7981
2567 | 0 | 2.8647 | 4.0557 | 26.153 | 0 | 33.0735 | 0 | 0 | 26.153
2568 | 0 | 2.8837 | 5.6684 | 23.2091 | 0 | 31.7611 | 0 | 0 | 23.2091
2569 | 0 | 2.9954 | 5.3082 | 26.5265 | 0 | 34.8301 | 0 | 0 | 26.5265
2570 | 0 | 3.1203 | 3.0702 | 32.6301 | 0 | 38.8205 | 0 | 0 | 32.6301
2571 | 0 | 2.8606 | 2.3713 | 41.3332 | 0 | 46.5651 | 0 | 0 | 41.3332
2572 | 9.2847 | 2.5052 | 2.2727 | 25.9352 | 0 | 39.9979 | 0 | 0 | 35.22
2573 | 50.1484 | 3.1272 | 2.0277 | 34.0313 | 0 | 89.3346 | 0 | 0 | 84.1796
2574 | 51.5046 | 2.6531 | 1.8545 | 22.2528 | 0 | 78.265 | 0 | 0 | 73.7574
2575 | 58.337 | 2.8831 | 1.8626 | 26.2097 | 0 | 89.2925 | 0 | 0 | 84.5468
2576 | 58.656 | 2.4903 | 1.8002 | 27.8521 | 12.0731 | 102.8718 | 0 | 0 | 98.5812
2577 | 47.844 | 2.8476 | 1.7611 | 35.1983 | 17.9272 | 105.5783 | 0 | 0 | 100.9695
2578 | 46.2669 | 2.7586 | 1.7681 | 24.6663 | 21.0481 | 96.508 | 0 | 0 | 91.9812
2579 | 93.1012 | 3.4718 | 1.3773 | 32.5207 | 17.2831 | 147.754 | 0 | 0 | 142.905
2580 | 92.4782 | 3.1945 | 2.3299 | 27.9944 | 6.8457 | 132.8426 | 0 | 0 | 127.3182
2581 | 89.9415 | 2.6191 | 2.3888 | 28.6766 | 15.1857 | 138.8118 | 0 | 0 | 133.8038
2582 | 69.5295 | 2.646 | 2.0295 | 33.6857 | 25.2084 | 133.099 | 0 | 0 | 128.4236
2583 | 25.091 | 2.9664 | 1.9886 | 28.6743 | 16.2912 | 75.0116 | 0 | 0 | 70.0565
2584 | 0 | 2.6943 | 2.2272 | 24.9515 | 20.1228 | 49.9959 | 0 | 0 | 45.0743
2585 | 0 | 3.1646 | 2.1199 | 35.3373 | 9.5314 | 50.1533 | 0 | 0 | 44.8688
2586 | 0 | 3.0616 | 1.5861 | 30.0917 | 11.7376 | 46.477 | 0 | 0 | 41.8293
2587 | 0 | 2.8053 | 1.239 | 24.2349 | 16.1368 | 44.4161 | 0 | 0 | 40.3717
2588 | 0 | 2.6744 | 1.0185 | 25.5982 | 0 | 29.2911 | 0 | 0 | 25.5982
2589 | 0 | 2.9359 | 1.0722 | 27.202 | 0 | 31.2101 | 0 | 200 | 227.202
2590 | 0 | 3.3294 | 1.4495 | 37.888 | 0 | 42.6669 | 0 | 0 | 37.888
2591 | 0 | 2.385 | 1.3953 | 25.6795 | 0 | 29.4599 | 0 | 0 | 25.6795
2592 | 0 | 3.0418 | 2.7569 | 23.3622 | 0 | 29.1609 | 0 | 0 | 23.3622
2593 | 0 | 2.6747 | 4.3028 | 21.3957 | 0 | 28.3732 | 0 | 0 | 21.3957
2594 | 0 | 2.8503 | 3.0702 | 28.451 | 0 | 34.3714 | 0 | 0 | 28.451
2595 | 0 | 3.0905 | 2.3713 | 29.2376 | 0 | 34.6994 | 0 | 0 | 29.2376
2596 | 0 | 2.8656 | 2.2727 | 23.5652 | 0 | 28.7035 | 0 | 0 | 23.5652
2597 | 11.1195 | 2.3704 | 2.0277 | 24.7157 | 0 | 40.2334 | 0 | 0 | 35.8353
2598 | 51.5121 | 2.759 | 1.8545 | 10.9469 | 0 | 67.0724 | 0 | 0 | 62.4589
2599 | 81.3846 | 2.6431 | 1.8626 | 30.236 | 0 | 116.1263 | 0 | 0 | 111.6206
2600 | 73.8765 | 3.4787 | 1.8002 | 25.5588 | 18.5675 | 123.2817 | 0 | 0 | 118.0028
2601 | 35.6609 | 3.0197 | 1.7611 | 26.1337 | 20.7156 | 87.2911 | 0 | 0 | 82.5103
2602 | 6.1186 | 3.4957 | 1.7681 | 19.482 | 5.2701 | 36.1344 | 0 | 0 | 30.8706
2603 | 12.1433 | 3.1473 | 1.3773 | 30.1235 | 19.0311 | 65.8225 | 0 | 0 | 61.2979
2604 | 45.5575 | 3.209 | 2.3299 | 37.4772 | 13.5998 | 102.1734 | 0 | 0 | 96.6345
2605 | 60.3408 | 3.4 | 2.3888 | 33.1998 | 8.8128 | 108.1422 | 0 | 0 | 102.3534
2606 | 72.9155 | 3.3313 | 2.0295 | 32.3621 | 21.2037 | 131.8422 | 0 | 0 | 126.4814
2607 | 10.3726 | 2.9575 | 1.9886 | 30.732 | 18.4962 | 64.547 | 0 | 0 | 59.6008
2608 | 0 | 3.243 | 2.2272 | 28.3846 | 13.1953 | 47.0501 | 0 | 0 | 41.5799
2609 | 0 | 3.3578 | 2.1199 | 33.0422 | 10.6307 | 49.1506 | 0 | 0 | 43.6729
2610 | 0 | 3.1627 | 1.5861 | 34.0456 | 14.2621 | 53.0565 | 0 | 0 | 48.3077
2611 | 0 | 2.5853 | 1.239 | 38.7689 | 17.6392 | 60.2325 | 0 | 0 | 56.4081
2612 | 0 | 2.8357 | 1.0185 | 29.9284 | 0 | 33.7826 | 0 | 0 | 29.9284
2613 | 0 | 3.2054 | 1.0722 | 32.3459 | 0 | 36.6235 | 0 | 0 | 32.3459
2614 | 0 | 3.1181 | 1.1947 | 32.2542 | 0 | 36.5671 | 0 | 0 | 32.2542
2615 | 0 | 3.0001 | 1.2542 | 33.2158 | 0 | 37.4701 | 0 | 0 | 33.2158
2616 | 0 | 2.6648 | 2.7569 | 26.4251 | 0 | 31.8468 | 0 | 0 | 26.4251
2617 | 0 | 3.2498 | 4.3028 | 20.4741 | 0 | 28.0266 | 0 | 0 | 20.4741
2618 | 0 | 2.5417 | 3.0702 | 21.4293 | 0 | 27.0411 | 0 | 0 | 21.4293
2619 | 0 | 3.0033 | 2.3713 | 27.4835 | 0 | 32.8581 | 0 | 0 | 27.4835
2620 | 0 | 2.3937 | 2.2727 | 17.8485 | 0 | 22.515 | 0 | 0 | 17.8485
2621 | 7.553 | 2.743 | 2.0277 | 35.16 | 0 | 47.4837 | 0 | 0 | 42.713
2622 | 43.4998 | 2.9145 | 1.8545 | 26.3573 | 0 | 74.6261 | 0 | 0 | 69.8571
2623 | 31.7674 | 2.4825 | 1.8626 | 35.0727 | 0 | 71.1852 | 0 | 0 | 66.8401
2624 | 2.2 | 2.8095 | 1.8002 | 31.0313 | 11.551 | 49.392 | 0 | 0 | 44.7823
2625 | 0 | 3.1311 | 1.7611 | 27.776 | 11.6978 | 44.3661 | 0 | 0 | 39.4739
2626 | 0 | 2.824 | 1.7681 | 36.6722 | 13.9806 | 55.245 | 0 | 0 | 50.6529
2627 | 0 | 3.145 | 1.3773 | 36.3329 | 13.9283 | 54.7834 | 0 | 0 | 50.2611
2628 | 0 | 2.5668 | 2.3299 | 29.5568 | 8.8851 | 43.3387 | 0 | 0 | 38.442
2629 | 0 | 2.7199 | 2.3888 | 30.0211 | 15.9389 | 51.0688 | 200 | 0 | 245.9601
2630 | 0 | 2.9138 | 2.0295 | 28.6577 | 15.4267 | 49.0278 | 0 | 0 | 44.0844
2631 | 0 | 2.5194 | 1.9886 | 35.2788 | 11.5671 | 51.3539 | 0 | 0 | 46.8459
2632 | 0 | 3.0472 | 2.2272 | 25.7722 | 14.9775 | 46.0241 | 0 | 0 | 40.7497
2633 | 0 | 2.9937 | 2.1199 | 26.8635 | 5.0584 | 37.0355 | 0 | 0 | 31.9219
2634 | 0 | 2.5192 | 1.9531 | 31.039 | 12.9233 | 48.4345 | 0 | 0 | 43.9623
2635 | 0 | 3.0119 | 1.5255 | 31.7356 | 14.926 | 51.199 | 0 | 0 | 46.6616
2636 | 0 | 2.6927 | 1.1504 | 24.796 | 0 | 28.639 | 0 | 0 | 24.796
2637 | 0 | 3.5035 | 1.1994 | 24.5879 | 0 | 29.2908 | 0 | 0 | 24.5879
2638 | 0 | 2.8079 | 1.0675 | 27.4403 | 0 | 31.3157 | 0 | 0 | 27.4403
2639 | 0 | 3.6534 | 1.3615 | 32.3417 | 0 | 37.3566 | 0 | 0 | 32.3417
2640 | 0 | 2.9762 | 2.2907 | 30.4274 | 0 | 35.6942 | 0 | 0 | 30.4274
2641 | 0 | 3.0911 | 2.1992 | 28.5102 | 0 | 33.8005 | 0 | 0 | 28.5102
2642 | 6.4049 | 3.0119 | 1.9945 | 28.6005 | 0 | 40.0119 | 0 | 0 | 35.0055
2643 | 31.4601 | 3.2925 | 3.6751 | 27.5899 | 0 | 66.0176 | 0 | 0 | 59.05
2644 | 57.3039 | 3.3881 | 3.2685 | 26.8464 | 0 | 90.807 | 0 | 0 | 84.1503
2645 | 61.7352 | 2.8302 | 2.6595 | 20.4818 | 0 | 87.7066 | 0 | 0 | 82.2169
2646 | 65.0542 | 2.8026 | 2.1561 | 35.5102 | 0 | 105.523 | 0 | 0 | 100.5643
2647 | 59.4904 | 2.4893 | 1.9466 | 18.9724 | 0 | 82.8986 | 0 | 0 | 78.4627
2648 | 45.5328 | 2.9837 | 1.9857 | 23.8483 | 14.1351 | 88.4856 | 0 | 0 | 83.5162
2649 | 40.8925 | 3.3177 | 1.7436 | 29.513 | 12.7778 | 88.2446 | 0 | 0 | 83.1833
2650 | 49.4147 | 3.2875 | 1.9834 | 30.1814 | 9.6442 | 94.5113 | 0 | 0 | 89.2404
2651 | 53.5503 | 3.0288 | 2.2739 | 26.4642 | 21.1837 | 106.5011 | 0 | 0 | 101.1983
2652 | 25.6435 | 2.8342 | 2.4752 | 36.8218 | 12.6048 | 80.3794 | 0 | 0 | 75.0701
2653 | 0 | 3.3714 | 1.8702 | 31.8479 | 4.7416 | 41.8311 | 0 | 0 | 36.5895
2654 | 0 | 2.8418 | 2.2301 | 40.6621 | 17.8186 | 63.5527 | 0 | 0 | 58.4808
2655 | 0 | 2.9635 | 2.3118 | 19.6692 | 14.2465 | 39.191 | 0 | 0 | 33.9157
2656 | 0 | 2.8435 | 1.9 | 29.4649 | 4.6929 | 38.9013 | 0 | 0 | 34.1579
2657 | 0 | 3.2212 | 1.9367 | 25.3432 | 7.4739 | 37.9751 | 0 | 0 | 32.8172
2658 | 0 | 3.0901 | 1.5167 | 32.6979 | 30.1575 | 67.4622 | 0 | 0 | 62.8554
2659 | 0 | 2.6289 | 1.4117 | 26.1309 | 12.596 | 42.7675 | 0 | 0 | 38.7269
2660 | 0 | 3.1941 | 1.1486 | 29.4923 | 0 | 33.835 | 0 | 0 | 29.4923
2661 | 0 | 2.9274 | 1.2344 | 27.2716 | 0 | 31.4334 | 0 | 0 | 27.2716
2662 | 0 | 3.0092 | 1.3331 | 27.0386 | 0 | 31.3809 | 0 | 0 | 27.0386
2663 | 0 | 2.7008 | 2.6693 | 25.7662 | 0 | 31.1363 | 0 | 0 | 25.7662
2664 | 0 | 2.5843 | 2.7531 | 27.2754 | 0 | 32.6128 | 0 | 0 | 27.2754
2665 | 0 | 3.049 | 2.1636 | 32.7591 | 0 | 37.9717 | 0 | 0 | 32.7591
2666 | 0 | 2.993 | 1.767 | 24.8575 | 0 | 29.6175 | 0 | 0 | 24.8575
2667 | 0 | 3.0102 | 2.6204 | 21.7247 | 0 | 27.3553 | 0 | 0 | 21.7247
2668 | 0 | 2.6288 | 2.6397 | 33.118 | 0 | 38.3865 | 0 | 0 | 33.118
2669 | 0 | 3.0691 | 2.3626 | 28.3461 | 0 | 33.7778 | 0 | 0 | 28.3461
2670 | 0 | 2.691 | 1.8189 | 24.5429 | 0 | 29.0528 | 0 | 0 | 24.5429
2671 | 0 | 2.6423 | 1.9431 | 29.8963 | 0 | 34.4817 | 0 | 0 | 29.8963
2672 | 0 | 3.2888 | 1.9321 | 33.2218 | 15.8357 | 54.2784 | 0 | 0 | 49.0575
2673 | 0 | 3.4422 | 1.7582 | 25.495 | 14.0221 | 44.7174 | 0 | 0 | 39.517
2674 | 0 | 2.6715 | 1.4747 | 27.9583 | 4.082 | 36.1865 | 0 | 0 | 32.0403
2675 | 0 | 2.7068 | 1.8335 | 35.5334 | 18.8465 | 58.9203 | 0 | 0 | 54.3799
2676 | 0 | 2.8234 | 2.0907 | 30.4953 | 18.7349 | 54.1443 | 0 | 0 | 49.2301
2677 | 0 | 3.235 | 2.2196 | 29.5867 | 11.7656 | 46.807 | 0 | 0 | 41.3523
2678 | 0 | 2.9184 | 2.2605 | 41.801 | 21.7666 | 68.7464 | 0 | 0 | 63.5676
2679 | 0 | 2.8411 | 2.1706 | 36.7426 | 14.3623 | 56.1166 | 0 | 0 | 51.1049
2680 | 0 | 2.4509 | 2.1677 | 36.7759 | 16.9045 | 58.2991 | 0 | 0 | 53.6804
2681 | 0 | 2.8741 | 2.1706 | 33.6006 | 3.1653 | 41.8107 | 0 | 0 | 36.7659
2682 | 0 | 2.9689 | 1.5861 | 40.5122 | 9.7704 | 54.8376 | 0 | 0 | 50.2826
2683 | 0 | 2.8636 | 1.239 | 31.2996 | 13.5632 | 48.9654 | 0 | 0 | 44.8628
2684 | 0 | 3.0404 | 1.0185 | 25.6437 | 0 | 29.7027 | 0 | 0 | 25.6437
2685 | 0 | 2.7658 | 1.0722 | 31.7519 | 0 | 35.5899 | 0 | 0 | 31.7519
2686 | 0 | 3.155 | 1.1947 | 32.5171 | 0 | 36.8668 | 0 | 0 | 32.5171
2687 | 0 | 2.912 | 1.2542 | 29.2977 | 0 | 33.464 | 0 | 0 | 29.2977
2688 | 0 | 3.075 | 2.7569 | 30.3591 | 0 | 36.191 | 0 | 200 | 230.3591
2689 | 0 | 2.7441 | 4.3028 | 28.7379 | 0 | 35.7847 | 0 | 0 | 28.7379
2690 | 0 | 2.8095 | 3.0702 | 26.5907 | 0 | 32.4704 | 0 | 0 | 26.5907
2691 | 2.9352 | 2.8097 | 2.5317 | 20.6302 | 0 | 28.9068 | 0 | 0 | 23.5654
2692 | 36.2098 | 2.5867 | 2.6941 | 29.6255 | 0 | 71.1161 | 0 | 0 | 65.8353
2693 | 100.9694 | 3.2913 | 2.0277 | 24.8071 | 0 | 131.0955 | 0 | 0 | 125.7765
2694 | 101.6883 | 2.762 | 1.8545 | 28.0835 | 0 | 134.3883 | 0 | 0 | 129.7718
2695 | 73.7988 | 3.1132 | 1.8626 | 27.0111 | 0 | 105.7856 | 0 | 0 | 100.8098
2696 | 81.4533 | 2.5571 | 1.8002 | 24.5653 | 21.7409 | 132.1169 | 0 | 0 | 127.7595
2697 | 64.6194 | 2.8405 | 1.7611 | 25.2728 | 15.6974 | 110.1912 | 0 | 0 | 105.5896
2698 | 38.9887 | 2.5348 | 1.7681 | 29.2038 | 18.8091 | 91.3045 | 200 | 0 | 287.0016
2699 | 28.6267 | 2.7446 | 1.3773 | 26.1535 | 13.8793 | 72.7813 | 0 | 0 | 68.6595
2700 | 0 | 3.0215 | 2.3299 | 26.3966 | 12.109 | 43.857 | 0 | 0 | 38.5056
2701 | 0 | 3.1185 | 2.3888 | 31.5957 | 15.8961 | 52.9991 | 0 | 0 | 47.4918
2702 | 0 | 2.9907 | 2.0295 | 27.8125 | 13.7662 | 46.5988 | 0 | 0 | 41.5787
2703 | 0 | 3.3244 | 2.3371 | 29.8869 | 14.8797 | 50.428 | 0 | 0 | 44.7666
2704 | 0 | 3.2927 | 2.2272 | 35.9029 | 17.3287 | 58.7516 | 0 | 0 | 53.2316
2705 | 0 | 2.8252 | 2.1199 | 25.1362 | 12.9166 | 42.9979 | 0 | 0 | 38.0528
2706 | 0 | 2.9181 | 1.5861 | 31.8586 | 11.1635 | 47.5263 | 0 | 0 | 43.0221
2707 | 0 | 2.8084 | 1.239 | 23.5811 | 1.8466 | 29.4751 | 0 | 0 | 25.4277
2708 | 0 | 2.7499 | 1.0185 | 27.8726 | 0 | 31.641 | 0 | 0 | 27.8726
2709 | 0 | 2.6255 | 1.0722 | 25.9174 | 0 | 29.6152 | 0 | 0 | 25.9174
2710 | 0 | 3.0908 | 1.1947 | 32.1845 | 0 | 36.47 | 0 | 0 | 32.1845
2711 | 0 | 2.5879 | 1.2542 | 33.6507 | 0 | 37.4928 | 0 | 0 | 33.6507
2712 | 0 | 3.2462 | 2.7569 | 27.2574 | 0 | 33.2605 | 0 | 0 | 27.2574
2713 | 0 | 3.0253 | 4.4314 | 27.9183 | 0 | 35.375 | 0 | 0 | 27.9183
2714 | 0 | 3.4257 | 4.2783 | 27.4783 | 0 | 35.1823 | 0 | 0 | 27.4783
2715 | 0 | 2.9383 | 4.9993 | 35.312 | 0 | 43.2495 | 0 | 0 | 35.312
2716 | 9.4281 | 3.5489 | 5.21 | 28.7054 | 0 | 46.8925 | 0 | 0 | 38.1336
2717 | 45.9168 | 3.4723 | 4.5524 | 29.995 | 0 | 83.9365 | 0 | 0 | 75.9118
2718 | 44.3307 | 3.2274 | 4.0906 | 25.1193 | 0 | 76.768 | 0 | 0 | 69.45
2719 | 22.9926 | 3.0576 | 3.8648 | 25.8781 | 0 | 55.7931 | 0 | 0 | 48.8707
2720 | 0.071913 | 2.7076 | 3.3735 | 27.6958 | 1.6198 | 35.4686 | 0 | 0 | 29.3875
2721 | 11.1088 | 2.9157 | 1.8708 | 28.2969 | 17.9376 | 62.1297 | 0 | 0 | 57.3433
2722 | 52.0868 | 2.5181 | 1.7681 | 30.5199 | 11.8708 | 98.7637 | 0 | 0 | 94.4774
2723 | 75.7399 | 2.3937 | 1.3773 | 28.5088 | 10.1867 | 118.2064 | 0 | 0 | 114.4355
2724 | 33.6144 | 3.5859 | 2.3299 | 29.0166 | 8.6721 | 77.2189 | 0 | 0 | 71.3031
2725 | 10.5337 | 2.7411 | 2.3888 | 21.8777 | 6.9575 | 44.4989 | 0 | 0 | 39.3689
2726 | 0 | 2.7037 | 2.0295 | 34.3659 | 20.0783 | 59.1773 | 0 | 0 | 54.4442
2727 | 0 | 2.6742 | 1.9886 | 30.281 | 11.3104 | 46.2542 | 0 | 0 | 41.5914
2728 | 0 | 2.7128 | 2.2272 | 29.2203 | 11.8243 | 45.9846 | 0 | 0 | 41.0446
2729 | 0 | 2.5095 | 2.1199 | 35.3723 | 11.8377 | 51.8394 | 0 | 0 | 47.21
2730 | 0 | 3.0571 | 1.5861 | 34.0393 | 7.2101 | 45.8927 | 0 | 0 | 41.2494
2731 | 0 | 3.0814 | 1.239 | 26.3266 | 27.8084 | 58.4554 | 0 | 0 | 54.135
2732 | 0 | 2.6381 | 1.0185 | 27.6688 | 0 | 31.3253 | 0 | 0 | 27.6688
2733 | 0 | 3.0765 | 1.0722 | 30.4731 | 0 | 34.6218 | 0 | 0 | 30.4731
2734 | 0 | 3.0298 | 1.1947 | 33.34 | 0 | 37.5644 | 0 | 0 | 33.34
2735 | 0 | 3.5307 | 1.2542 | 20.1008 | 0 | 24.8857 | 0 | 0 | 20.1008
2736 | 0 | 2.9965 | 2.7569 | 28.9348 | 0 | 34.6881 | 0 | 0 | 28.9348
2737 | 0 | 2.9181 | 4.3028 | 31.876 | 0 | 39.0968 | 0 | 0 | 31.876
2738 | 0 | 3.3784 | 4.2783 | 29.4347 | 0 | 37.0913 | 0 | 0 | 29.4347
2739 | 0 | 3.1879 | 5.2049 | 27.7845 | 0 | 36.1773 | 0 | 0 | 27.7845
2740 | 0 | 2.8923 | 5.7691 | 31.7987 | 0 | 40.4601 | 0 | 0 | 31.7987
2741 | 0 | 3.2049 | 5.8586 | 34.8994 | 0 | 43.9629 | 0 | 0 | 34.8994
2742 | 9.1244 | 2.8215 | 4.3853 | 29.1804 | 0 | 45.5116 | 0 | 0 | 38.3048
2743 | 34.4372 | 2.3537 | 5.03 | 30.5277 | 0 | 72.3486 | 0 | 0 | 64.9649
2744 | 15.3708 | 3.0251 | 5.139 | 27.8361 | 11.9301 | 63.3011 | 0 | 0 | 55.137
2745 | 0 | 2.9552 | 3.2918 | 36.8191 | 16.662 | 59.728 | 0 | 0 | 53.4811
2746 | 0 | 3.1731 | 2.8402 | 31.6258 | 12.9518 | 50.5909 | 0 | 0 | 44.5776
2747 | 0 | 2.8799 | 1.3773 | 30.1446 | 11.7595 | 46.1614 | 0 | 0 | 41.9041
2748 | 0 | 2.3629 | 2.3299 | 32.7718 | 10.7411 | 48.2057 | 0 | 0 | 43.5129
2749 | 0 | 2.9926 | 2.3888 | 22.5049 | 15.1185 | 43.0049 | 0 | 0 | 37.6235
2750 | 0 | 2.7278 | 2.3438 | 23.7787 | 16.6267 | 45.477 | 0 | 0 | 40.4054
2751 | 0 | 3.2328 | 2.1477 | 24.1984 | 22.6541 | 52.233 | 0 | 0 | 46.8524
2752 | 0 | 2.993 | 2.2272 | 26.899 | 22.638 | 54.7572 | 0 | 0 | 49.537
2753 | 0 | 2.5516 | 2.1199 | 24.5424 | 12.2224 | 41.4363 | 0 | 0 | 36.7648
2754 | 0 | 2.7909 | 1.5861 | 36.47 | 16.8816 | 57.7286 | 0 | 0 | 53.3516
2755 | 0 | 2.5933 | 1.239 | 30.7524 | 23.6608 | 58.2455 | 0 | 0 | 54.4131
2756 | 0 | 2.8187 | 1.0185 | 27.9035 | 0 | 31.7408 | 0 | 0 | 27.9035
2757 | 0 | 2.6182 | 1.0722 | 38.4676 | 0 | 42.158 | 0 | 0 | 38.4676
2758 | 0 | 3.1773 | 1.1947 | 30.9226 | 0 | 35.2946 | 0 | 0 | 30.9226
2759 | 0 | 2.891 | 2.1209 | 30.8572 | 0 | 35.8691 | 0 | 0 | 30.8572
2760 | 0 | 2.5177 | 3.1323 | 28.9299 | 0 | 34.5799 | 0 | 0 | 28.9299
2761 | 0 | 3.0968 | 5.7953 | 30.7212 | 0 | 39.6132 | 0 | 0 | 30.7212
2762 | 0 | 3.4641 | 4.852 | 31.8203 | 0 | 40.1365 | 0 | 0 | 31.8203
2763 | 0 | 2.8869 | 5.4791 | 34.8485 | 0 | 43.2145 | 0 | 200 | 234.8485
2764 | 3.1793 | 3.0689 | 5.21 | 29.3284 | 0 | 40.7866 | 0 | 0 | 32.5077
2765 | 25.6991 | 2.6333 | 4.3347 | 25.5447 | 0 | 58.2119 | 0 | 0 | 51.2439
2766 | 51.7862 | 2.831 | 4.3853 | 33.0249 | 0 | 92.0274 | 200 | 0 | 284.8111
2767 | 20.9514 | 3.3914 | 4.6188 | 19.1519 | 0 | 48.1134 | 0 | 0 | 40.1033
2768 | 0 | 2.9159 | 3.3056 | 37.4515 | 13.5235 | 57.1966 | 0 | 0 | 50.975
2769 | 0 | 2.8426 | 3.1565 | 25.4686 | 10.9686 | 42.4363 | 0 | 0 | 36.4372
2770 | 0.039946 | 3.1404 | 2.7093 | 33.9981 | 5.0963 | 44.9842 | 0 | 0 | 39.1344
2771 | 0.12313 | 3.0784 | 1.3773 | 31.796 | 13.199 | 49.5738 | 0 | 0 | 45.1181
2772 | 0 | 3.0658 | 2.3299 | 34.4773 | 1.7446 | 41.6176 | 0 | 0 | 36.2219
2773 | 0 | 3.4818 | 2.3888 | 31.291 | 10.5484 | 47.7101 | 0 | 0 | 41.8394
2774 | 0 | 2.9277 | 2.859 | 33.6816 | 11.6485 | 51.1168 | 0 | 0 | 45.3301
2775 | 0 | 2.8996 | 5.0827 | 34.8835 | 15.8436 | 58.7094 | 0 | 0 | 50.7271
2776 | 0 | 3.2206 | 2.8351 | 29.3685 | 12.0216 | 47.4457 | 0 | 0 | 41.39
2777 | 0 | 2.9034 | 2.1199 | 26.4097 | 1.1525 | 32.5855 | 0 | 0 | 27.5622
2778 | 0 | 2.9482 | 1.7087 | 27.2425 | 22.4284 | 54.3278 | 0 | 0 | 49.6709
2779 | 0 | 2.8595 | 1.5811 | 32.2242 | 17.7328 | 54.3975 | 0 | 0 | 49.957
2780 | 0 | 2.9565 | 2.7594 | 31.513 | 0 | 37.2289 | 0 | 0 | 31.513
2781 | 0 | 3.3993 | 2.4639 | 27.109 | 0 | 32.9723 | 0 | 0 | 27.109
2782 | 0 | 3.3126 | 2.739 | 29.5314 | 0 | 35.583 | 0 | 0 | 29.5314
2783 | 0 | 3.085 | 3.2475 | 28.9069 | 0 | 35.2394 | 0 | 0 | 28.9069
2784 | 0 | 2.8538 | 4.9418 | 28.3339 | 0 | 36.1295 | 0 | 0 | 28.3339
2785 | 0 | 2.9366 | 2.1636 | 24.8894 | 0 | 29.9896 | 0 | 0 | 24.8894
2786 | 0 | 3.1682 | 1.767 | 28.1113 | 0 | 33.0465 | 0 | 0 | 28.1113
2787 | 0 | 3.6597 | 2.6204 | 26.0904 | 0 | 32.3706 | 0 | 0 | 26.0904
2788 | 0 | 3.3933 | 4.3221 | 22.664 | 0 | 30.3794 | 0 | 0 | 22.664
2789 | 0 | 3.3297 | 4.0143 | 33.2894 | 0 | 40.6335 | 0 | 0 | 33.2894
2790 | 0 | 2.5174 | 3.8343 | 20.0539 | 0 | 26.4055 | 0 | 0 | 20.0539
2791 | 0 | 3.3135 | 3.0376 | 32.9126 | 0 | 39.2637 | 0 | 0 | 32.9126
2792 | 0 | 3.216 | 2.8189 | 30.7769 | 18.2397 | 55.0514 | 0 | 0 | 49.0166
2793 | 0 | 3.0391 | 2.2641 | 27.3511 | 24.3362 | 56.9904 | 0 | 0 | 51.6873
2794 | 0 | 2.3831 | 1.5534 | 37.2184 | 18.9178 | 60.0727 | 0 | 0 | 56.1362
2795 | 0 | 2.5929 | 1.8335 | 26.2189 | 3.3303 | 33.9755 | 0 | 0 | 29.5491
2796 | 0 | 2.9527 | 2.0907 | 31.3793 | 18.3615 | 54.7842 | 0 | 0 | 49.7408
2797 | 0 | 2.645 | 2.2196 | 31.5737 | 11.0985 | 47.5369 | 0 | 0 | 42.6723
2798 | 0 | 2.9329 | 2.2605 | 27.663 | 14.7212 | 47.5775 | 0 | 0 | 42.3841
2799 | 0 | 3.0244 | 2.1706 | 26.6152 | 6.5503 | 38.3606 | 0 | 0 | 33.1655
2800 | 0 | 2.5504 | 2.1677 | 28.9719 | 20.2324 | 53.9224 | 0 | 0 | 49.2043
2801 | 0 | 3.3159 | 2.1706 | 30.4616 | 16.707 | 52.6551 | 0 | 0 | 47.1686
2802 | 0 | 2.8933 | 1.9531 | 32.6185 | 11.3404 | 48.8052 | 0 | 0 | 43.9588
2803 | 0 | 2.7936 | 1.5255 | 31.1011 | 18.0693 | 53.4895 | 0 | 0 | 49.1704
2804 | 0 | 2.9332 | 1.1504 | 27.8229 | 0 | 31.9065 | 0 | 0 | 27.8229
2805 | 0 | 3.1986 | 1.1994 | 34.9627 | 0 | 39.3607 | 0 | 0 | 34.9627
2806 | 0 | 2.8646 | 1.0675 | 35.8089 | 0 | 39.7411 | 0 | 0 | 35.8089
2807 | 0 | 2.9964 | 1.3615 | 27.281 | 0 | 31.6389 | 0 | 0 | 27.281
2808 | 0 | 3.0188 | 1.7973 | 29.0352 | 0 | 33.8513 | 0 | 0 | 29.0352
2809 | 0 | 2.8386 | 2.1992 | 31.7842 | 0 | 36.8221 | 0 | 0 | 31.7842
2810 | 0 | 2.847 | 1.9945 | 31.8115 | 0 | 36.653 | 0 | 0 | 31.8115
2811 | 0 | 3.0347 | 3.6751 | 35.617 | 0 | 42.3269 | 0 | 0 | 35.617
2812 | 0 | 2.5511 | 3.4545 | 28.5386 | 0 | 34.5442 | 0 | 0 | 28.5386
2813 | 0 | 2.2568 | 3.7185 | 29.7924 | 0 | 35.7677 | 0 | 0 | 29.7924
2814 | 0 | 2.9617 | 2.8059 | 26.8432 | 0 | 32.6108 | 0 | 0 | 26.8432
2815 | 0 | 3.1014 | 4.1365 | 34.6043 | 0 | 41.8423 | 0 | 0 | 34.6043
2816 | 0 | 2.9368 | 1.9857 | 34.4062 | 27.8109 | 67.1395 | 0 | 0 | 62.217
2817 | 0 | 3.072 | 1.7436 | 33.6983 | 21.7349 | 60.2488 | 0 | 0 | 55.4332
2818 | 0 | 3.4399 | 1.9834 | 32.0173 | 25.9735 | 63.414 | 0 | 0 | 57.9908
2819 | 0 | 2.9185 | 2.2739 | 31.1 | 20.3283 | 56.6206 | 0 | 0 | 51.4282
2820 | 0 | 2.8617 | 2.4752 | 33.0437 | 12.7377 | 51.1182 | 0 | 0 | 45.7814
2821 | 0 | 2.3279 | 1.8702 | 34.4186 | 11.6305 | 50.2473 | 0 | 0 | 46.0492
2822 | 0 | 2.6539 | 2.2301 | 28.0485 | 16.3551 | 49.2877 | 0 | 0 | 44.4036
2823 | 0 | 2.8069 | 2.3118 | 22.8753 | 26.3423 | 54.3364 | 0 | 0 | 49.2176
2824 | 0 | 3.2243 | 1.9 | 28.9843 | 15.7276 | 49.8363 | 0 | 0 | 44.712
2825 | 0 | 3.4686 | 1.9367 | 31.0928 | 10.0617 | 46.5599 | 0 | 0 | 41.1546
2826 | 0 | 2.9933 | 1.5167 | 20.6789 | 15.602 | 40.7909 | 0 | 0 | 36.2809
2827 | 0 | 3.1429 | 1.4117 | 25.7468 | 11.5551 | 41.8564 | 0 | 0 | 37.3018
2828 | 0 | 2.962 | 2.7594 | 28.4767 | 0 | 34.1982 | 0 | 0 | 28.4767
2829 | 0 | 2.343 | 3.045 | 28.2576 | 0 | 33.6455 | 0 | 0 | 28.2576
2830 | 0 | 2.5506 | 3.934 | 23.8476 | 0 | 30.3322 | 0 | 0 | 23.8476
2831 | 0 | 2.8024 | 4.5485 | 29.2909 | 0 | 36.6418 | 0 | 0 | 29.2909
2832 | 0 | 3.2307 | 4.3399 | 29.1779 | 0 | 36.7485 | 0 | 0 | 29.1779
2833 | 0 | 2.6846 | 2.1636 | 25.6725 | 0 | 30.5207 | 200 | 0 | 225.6725
2834 | 0 | 2.9403 | 1.767 | 38.6293 | 0 | 43.3366 | 0 | 0 | 38.6293
2835 | 0 | 2.7652 | 2.6204 | 36.773 | 0 | 42.1586 | 0 | 0 | 36.773
2836 | 0 | 2.3168 | 4.3221 | 35.116 | 0 | 41.7549 | 0 | 0 | 35.116
2837 | 0 | 2.6696 | 4.5508 | 29.0689 | 0 | 36.2893 | 0 | 200 | 229.0689
2838 | 0 | 2.7569 | 4.707 | 30.8317 | 0 | 38.2955 | 0 | 0 | 30.8317
2839 | 0 | 3.0846 | 4.3968 | 19.5387 | 0 | 27.0201 | 0 | 0 | 19.5387
2840 | 0 | 3.3131 | 3.4198 | 30.8655 | 11.3534 | 48.9518 | 0 | 0 | 42.2189
2841 | 0 | 2.9914 | 2.6802 | 38.2922 | 14.4038 | 58.3676 | 0 | 0 | 52.696
2842 | 0 | 2.494 | 1.9083 | 29.3369 | 14.7515 | 48.4907 | 0 | 0 | 44.0884
2843 | 0 | 2.7572 | 1.8335 | 27.582 | 19.9729 | 52.1455 | 0 | 0 | 47.5549
2844 | 0 | 3.3821 | 2.0907 | 18.7566 | 13.3547 | 37.5842 | 0 | 0 | 32.1113
2845 | 0 | 3.276 | 2.2196 | 31.3819 | 11.4114 | 48.2889 | 0 | 0 | 42.7932
2846 | 0 | 2.5299 | 2.2605 | 24.03 | 21.4908 | 50.3112 | 0 | 0 | 45.5208
2847 | 0 | 2.933 | 2.1706 | 28.8391 | 4.6496 | 38.5924 | 0 | 0 | 33.4888
2848 | 0 | 2.9729 | 2.1677 | 27.7514 | 12.7732 | 45.6652 | 0 | 0 | 40.5246
2849 | 0 | 3.8357 | 2.1706 | 28.1581 | 9.9487 | 44.1132 | 0 | 0 | 38.1068
2850 | 0 | 2.7594 | 1.5861 | 33.7909 | 24.6761 | 62.8125 | 0 | 0 | 58.467
2851 | 0 | 2.9334 | 1.239 | 27.9157 | 15.8285 | 47.9166 | 0 | 0 | 43.7442
2852 | 0 | 2.9834 | 1.0185 | 34.8203 | 0 | 38.8222 | 0 | 0 | 34.8203
2853 | 0 | 2.3301 | 1.0722 | 33.822 | 0 | 37.2243 | 0 | 0 | 33.822
2854 | 0 | 3.2182 | 1.1947 | 28.356 | 0 | 32.7689 | 0 | 0 | 28.356
2855 | 0 | 3.0783 | 1.2542 | 28.7617 | 0 | 33.0942 | 0 | 0 | 28.7617
2856 | 0 | 2.7528 | 2.7569 | 24.5714 | 0 | 30.0811 | 0 | 0 | 24.5714
2857 | 0 | 2.7663 | 4.5288 | 27.0398 | 0 | 34.3349 | 0 | 0 | 27.0398
2858 | 0 | 2.7646 | 4.4422 | 39.3868 | 0 | 46.5936 | 0 | 0 | 39.3868
2859 | 0 | 2.4264 | 5.1364 | 33.3134 | 0 | 40.8761 | 0 | 0 | 33.3134
2860 | 5.5166 | 3.1689 | 5.0702 | 26.44 | 0 | 40.1957 | 0 | 0 | 31.9566
2861 | 20.5666 | 3.2118 | 4.5524 | 28.7764 | 0 | 57.1073 | 0 | 0 | 49.3431
2862 | 26.9152 | 2.9748 | 4.7537 | 20.0193 | 0 | 54.663 | 0 | 0 | 46.9345
2863 | 82.0575 | 3.2617 | 5.0986 | 25.092 | 0 | 115.5097 | 0 | 0 | 107.1494
2864 | 55.9399 | 2.8192 | 3.7809 | 24.0749 | 4.9213 | 91.5362 | 0 | 0 | 84.9361
2865 | 0 | 3.1288 | 3.3595 | 33.8028 | 8.0063 | 48.2974 | 0 | 0 | 41.8091
2866 | 0.12726 | 2.634 | 2.3166 | 25.482 | 20.4449 | 51.0048 | 0 | 0 | 46.0542
2867 | 10.635 | 2.7931 | 1.3773 | 31.7724 | 10.5427 | 57.1206 | 0 | 0 | 52.9502
2868 | 37.5752 | 2.9187 | 2.3299 | 25.4996 | 5.4335 | 73.7569 | 0 | 0 | 68.5083
2869 | 0 | 2.7387 | 2.3888 | 29.1733 | 18.3679 | 52.6687 | 0 | 0 | 47.5412
2870 | 0 | 3.1958 | 2.859 | 25.9065 | 12.4824 | 44.4436 | 0 | 0 | 38.3889
2871 | 0 | 2.7096 | 3.4732 | 22.7269 | 6.982 | 35.8916 | 0 | 0 | 29.7089
2872 | 0 | 2.7035 | 3.6334 | 28.1656 | 6.4528 | 40.9553 | 0 | 0 | 34.6184
2873 | 0 | 2.8807 | 3.3627 | 32.2845 | 24.2227 | 62.7506 | 0 | 0 | 56.5072
2874 | 0 | 2.7694 | 2.4685 | 36.1109 | 15.4933 | 56.8421 | 0 | 0 | 51.6042
2875 | 0 | 2.736 | 2.0128 | 26.905 | 12.8875 | 44.5414 | 0 | 0 | 39.7925
2876 | 0 | 2.551 | 2.3201 | 30.8053 | 0 | 35.6765 | 0 | 0 | 30.8053
2877 | 0 | 2.9134 | 2.8222 | 36.3017 | 0 | 42.0373 | 0 | 0 | 36.3017
2878 | 0 | 3.0156 | 3.397 | 25.1732 | 0 | 31.5858 | 0 | 0 | 25.1732
2879 | 0 | 3.0103 | 3.6526 | 35.3307 | 0 | 41.9936 | 0 | 0 | 35.3307
2880 | 0 | 2.5982 | 5.364 | 28.1138 | 0 | 36.076 | 0 | 0 | 28.1138
2881 | 0 | 1.3665 | 8.523 | 34.7291 | 0 | 44.6186 | 0 | 0 | 34.7291
2882 | 0 | 1.383 | 8.0485 | 32.3645 | 0 | 41.796 | 0 | 0 | 32.3645
2883 | 0 | 1.7606 | 8.0838 | 37.4725 | 0 | 47.3168 | 0 | 0 | 37.4725
2884 | 4.5949 | 1.6349 | 8.3549 | 31.004 | 0 | 45.5886 | 0 | 0 | 35.5988
2885 | 27.2901 | 1.776 | 8.1083 | 32.3265 | 0 | 69.5009 | 0 | 0 | 59.6167
2886 | 51.4699 | 1.7972 | 6.743 | 33.5724 | 0 | 93.5825 | 0 | 0 | 85.0423
2887 | 72.4445 | 1.7317 | 5.8526 | 25.7499 | 0 | 105.7787 | 0 | 0 | 98.1944
2888 | 0 | 1.8911 | 4.7315 | 32.6299 | 17.8597 | 57.1123 | 0 | 0 | 50.4896
2889 | 0 | 1.7911 | 4.1038 | 26.8642 | 7.452 | 40.2111 | 0 | 0 | 34.3162
2890 | 10.5724 | 1.442 | 3.2329 | 34.7622 | 13.2133 | 63.2228 | 0 | 0 | 58.5479
2891 | 32.088 | 1.753 | 1.3773 | 34.5767 | 12.417 | 82.212 | 0 | 0 | 79.0817
2892 | 5.5005 | 1.594 | 2.3299 | 32.5257 | 19.2309 | 61.181 | 0 | 0 | 57.2571
2893 | 0 | 1.7525 | 2.3888 | 31.2529 | 27.6581 | 63.0524 | 0 | 0 | 58.911
2894 | 0 | 2.1437 | 2.172 | 27.1572 | 20.6831 | 52.156 | 0 | 200 | 247.8403
2895 | 0 | 1.9543 | 5.4614 | 30.9628 | 8.201 | 46.5796 | 0 | 0 | 39.1638
2896 | 0 | 1.8883 | 6.1424 | 30.8317 | 9.4125 | 48.2749 | 0 | 0 | 40.2442
2897 | 0 | 1.7542 | 3.14 | 35.7989 | 15.7328 | 56.4258 | 0 | 0 | 51.5317
2898 | 0.013353 | 1.9339 | 2.5671 | 26.8788 | 10.0807 | 41.4738 | 0 | 0 | 36.9729
2899 | 23.7201 | 1.8896 | 2.0128 | 30.6255 | 3.9758 | 62.2237 | 0 | 0 | 58.3213
2900 | 84.2581 | 1.8015 | 2.5625 | 27.9823 | 0 | 116.6044 | 0 | 0 | 112.2404
2901 | 70.5216 | 1.95 | 2.983 | 22.8247 | 0 | 98.2793 | 0 | 0 | 93.3463
2902 | 35.9508 | 1.8021 | 3.8838 | 29.8215 | 0 | 71.4582 | 0 | 0 | 65.7723
2903 | 28.4626 | 2.0188 | 5.5069 | 37.842 | 0 | 73.8303 | 0 | 0 | 66.3046
2904 | 9.1326 | 1.6758 | 6.1756 | 35.075 | 0 | 52.0591 | 0 | 0 | 44.2076
2905 | 31.2822 | 1.7161 | 7.1591 | 21.4375 | 0 | 61.595 | 0 | 0 | 52.7197
2906 | 14.5717 | 1.475 | 5.1798 | 31.0843 | 0 | 52.3108 | 0 | 0 | 45.656
2907 | 0 | 1.8678 | 4.3138 | 30.3282 | 0 | 36.5098 | 0 | 0 | 30.3282
2908 | 0 | 1.5983 | 3.8822 | 28.0303 | 0 | 33.5109 | 0 | 0 | 28.0303
2909 | 11.7511 | 1.7309 | 2.8833 | 28.5823 | 0 | 44.9476 | 0 | 0 | 40.3334
2910 | 36.2358 | 1.769 | 3.0591 | 22.9374 | 0 | 64.0012 | 0 | 0 | 59.1732
2911 | 22.6955 | 1.7282 | 2.3568 | 31.4696 | 0 | 58.2501 | 0 | 0 | 54.1651
2912 | 31.9038 | 1.9909 | 1.8002 | 33.5654 | 18.0033 | 87.2637 | 0 | 0 | 83.4725
2913 | 70.9397 | 1.6453 | 1.7611 | 38.582 | 12.135 | 125.0632 | 0 | 0 | 121.6567
2914 | 59.8565 | 1.6859 | 1.7681 | 32.4984 | 17.1045 | 112.9135 | 0 | 0 | 109.4594
2915 | 2.7085 | 1.7344 | 1.3773 | 29.2013 | 13.4838 | 48.5054 | 0 | 0 | 45.3936
2916 | 0 | 1.669 | 2.3299 | 30.1992 | 11.2702 | 45.4683 | 0 | 0 | 41.4695
2917 | 0 | 1.6161 | 2.3888 | 28.5286 | 11.6443 | 44.1778 | 200 | 0 | 240.1729
2918 | 0 | 1.8993 | 2.0295 | 22.6815 | 9.0461 | 35.6563 | 0 | 0 | 31.7276
2919 | 0 | 1.7134 | 1.9886 | 29.9066 | 11.5456 | 45.1543 | 0 | 0 | 41.4522
2920 | 0 | 1.4094 | 2.2272 | 22.4322 | 11.5583 | 37.6272 | 0 | 0 | 33.9905
2921 | 0 | 2.051 | 2.1199 | 17.3389 | 15.6063 | 37.1162 | 0 | 0 | 32.9452
2922 | 0 | 1.799 | 1.5861 | 32.2513 | 15.5365 | 51.173 | 0 | 0 | 47.7878
2923 | 0 | 2.043 | 1.239 | 16.8835 | 16.205 | 36.3705 | 0 | 0 | 33.0885
2924 | 0.65153 | 1.7147 | 1.0185 | 36.7999 | 0 | 40.1847 | 0 | 0 | 37.4514
2925 | 21.1273 | 1.9008 | 1.6164 | 34.3665 | 0 | 59.011 | 0 | 0 | 55.4938
2926 | 63.9481 | 1.4668 | 3.5592 | 30.3156 | 0 | 99.2897 | 0 | 0 | 94.2637
2927 | 0 | 1.6614 | 5.3456 | 20.9654 | 0 | 27.9724 | 0 | 0 | 20.9654
2928 | 0 | 1.767 | 6.5814 | 30.0745 | 0 | 38.4229 | 0 | 0 | 30.0745
2929 | 5.9126 | 1.5794 | 5.9901 | 29.8422 | 0 | 43.3243 | 0 | 0 | 35.7548
2930 | 20.8459 | 1.7954 | 4.1144 | 36.2804 | 0 | 63.036 | 0 | 0 | 57.1262
2931 | 0.083318 | 1.6636 | 4.0397 | 39.8053 | 0 | 45.5919 | 0 | 0 | 39.8886
2932 | 0 | 1.605 | 4.2316 | 33.9634 | 0 | 39.8 | 0 | 0 | 33.9634
2933 | 0 | 1.5389 | 3.7541 | 32.6672 | 0 | 37.9602 | 0 | 0 | 32.6672
2934 | 0 | 1.6494 | 3.7959 | 32.7868 | 0 | 38.2321 | 0 | 0 | 32.7868
2935 | 0 | 1.7358 | 4.4131 | 35.8228 | 0 | 41.9717 | 0 | 0 | 35.8228
2936 | 0 | 1.5407 | 2.8982 | 32.8186 | 11.1734 | 48.431 | 0 | 0 | 43.992
2937 | 0 | 1.7762 | 2.2768 | 39.0868 | 19.9364 | 63.0762 | 0 | 0 | 59.0232
2938 | 0 | 1.7387 | 1.7681 | 34.7339 | 19.2083 | 57.449 | 0 | 0 | 53.9422
2939 | 0 | 1.8775 | 1.3773 | 27.6086 | 22.9848 | 53.8482 | 0 | 0 | 50.5934
2940 | 0 | 1.9025 | 2.3299 | 28.274 | 6.5891 | 39.0956 | 0 | 0 | 34.8632
2941 | 0 | 1.8713 | 2.3888 | 25.1795 | 10.8131 | 40.2527 | 0 | 0 | 35.9926
2942 | 0 | 1.7923 | 2.0295 | 23.5783 | 6.6064 | 34.0064 | 0 | 0 | 30.1847
2943 | 0 | 1.953 | 2.2424 | 33.6473 | 19.9615 | 57.8043 | 0 | 0 | 53.6088
2944 | 0 | 1.6948 | 3.2913 | 31.6933 | 9.5621 | 46.2414 | 0 | 0 | 41.2553
2945 | 0 | 1.8442 | 4.1422 | 30.1389 | 27.0931 | 63.2184 | 0 | 0 | 57.232
2946 | 1.2011 | 1.5871 | 4.5388 | 34.0593 | 9.5307 | 50.917 | 0 | 0 | 44.7911
2947 | 16.5153 | 1.8166 | 4.6151 | 32.1431 | 11.9791 | 67.0693 | 0 | 0 | 60.6375
2948 | 65.3706 | 1.4198 | 4.5824 | 34.9467 | 0 | 106.3194 | 0 | 0 | 100.3173
2949 | 83.0899 | 2.1066 | 5.3142 | 29.6889 | 0 | 120.1995 | 0 | 0 | 112.7788
2950 | 111.0055 | 1.9452 | 5.9124 | 30.8191 | 0 | 149.6822 | 0 | 0 | 141.8245
2951 | 75.7207 | 1.832 | 7.1192 | 36.0386 | 0 | 120.7105 | 0 | 200 | 311.7593
2952 | 11.7515 | 1.7992 | 7.7987 | 21.3255 | 0 | 42.6749 | 0 | 0 | 33.077
2953 | 0 | 1.8106 | 6.7695 | 28.869 | 0 | 37.449 | 0 | 0 | 28.869
2954 | 0 | 1.7987 | 4.0324 | 23.6218 | 0 | 29.4529 | 0 | 0 | 23.6218
2955 | 0 | 1.8399 | 3.2171 | 39.5183 | 0 | 44.5754 | 0 | 0 | 39.5183
2956 | 0 | 2.0539 | 3.0436 | 22.3698 | 0 | 27.4673 | 0 | 0 | 22.3698
2957 | 12.3742 | 1.3319 | 2.3028 | 34.802 | 0 | 50.8108 | 0 | 0 | 47.1762
2958 | 59.0216 | 1.7337 | 1.8545 | 31.4333 | 0 | 94.0431 | 0 | 0 | 90.4549
2959 | 73.1805 | 1.6955 | 1.8626 | 32.2475 | 0 | 108.9861 | 0 | 0 | 105.4279
2960 | 42.8625 | 1.5452 | 1.8002 | 28.9339 | 19.4144 | 94.5561 | 0 | 0 | 91.2107
2961 | 58.3787 | 1.5704 | 1.7611 | 27.453 | 8.9416 | 98.1048 | 0 | 0 | 94.7733
2962 | 39.7259 | 1.4473 | 1.7681 | 34.5217 | 0.87405 | 78.3371 | 0 | 0 | 75.1217
2963 | 53.5018 | 1.5788 | 1.3773 | 33.2108 | 11.0987 | 100.7674 | 0 | 0 | 97.8113
2964 | 0 | 1.8047 | 2.3299 | 25.7295 | 14.2243 | 44.0885 | 0 | 0 | 39.9538
2965 | 0 | 1.6116 | 2.3888 | 27.9323 | 14.3118 | 46.2445 | 0 | 0 | 42.2441
2966 | 0 | 1.6664 | 2.0295 | 41.6781 | 17.0275 | 62.4014 | 0 | 0 | 58.7056
2967 | 0 | 1.9097 | 1.9886 | 32.4004 | 22.1193 | 58.418 | 0 | 0 | 54.5197
2968 | 0 | 1.6958 | 2.2272 | 33.8363 | 10.6448 | 48.4041 | 0 | 0 | 44.4811
2969 | 0 | 1.8185 | 2.1199 | 32.9974 | 17.9419 | 54.8777 | 0 | 0 | 50.9393
2970 | 0 | 1.9465 | 1.9531 | 37.3031 | 15.281 | 56.4837 | 0 | 0 | 52.5841
2971 | 0 | 1.9199 | 1.5255 | 38.7843 | 5.0875 | 47.3171 | 0 | 0 | 43.8718
2972 | 0 | 1.7665 | 1.1504 | 31.1653 | 0 | 34.0822 | 0 | 0 | 31.1653
2973 | 0 | 1.9148 | 1.6357 | 23.1699 | 0 | 26.7204 | 0 | 0 | 23.1699
2974 | 0 | 1.7028 | 2.5654 | 30.0371 | 0 | 34.3053 | 0 | 0 | 30.0371
2975 | 0 | 1.8896 | 3.2445 | 29.6256 | 0 | 34.7597 | 0 | 0 | 29.6256
2976 | 0 | 1.8429 | 2.2112 | 30.519 | 0 | 34.5732 | 0 | 0 | 30.519
2977 | 0 | 1.8435 | 2.1992 | 34.9608 | 0 | 39.0036 | 0 | 0 | 34.9608
2978 | 0 | 1.6967 | 1.9945 | 31.6446 | 0 | 35.3358 | 0 | 0 | 31.6446
2979 | 0 | 2.0103 | 3.6751 | 23.73 | 0 | 29.4154 | 0 | 0 | 23.73
2980 | 0 | 1.6529 | 3.2685 | 27.9507 | 0 | 32.8721 | 0 | 0 | 27.9507
2981 | 0 | 1.9663 | 2.6595 | 36.7125 | 0 | 41.3383 | 0 | 0 | 36.7125
2982 | 0 | 1.8161 | 2.1561 | 31.1482 | 0 | 35.1203 | 0 | 0 | 31.1482
2983 | 0 | 1.4536 | 1.9466 | 27.025 | 0 | 30.4252 | 0 | 0 | 27.025
2984 | 0 | 1.8261 | 1.9857 | 31.469 | 14.7528 | 50.0336 | 0 | 0 | 46.2218
2985 | 0 | 1.6769 | 1.7436 | 32.2153 | 8.7986 | 44.4344 | 0 | 0 | 41.0139
2986 | 0 | 1.6024 | 1.9834 | 29.2557 | 7.9784 | 40.8199 | 0 | 0 | 37.2341
2987 | 0 | 1.6536 | 2.2739 | 22.9355 | 12.8593 | 39.7223 | 0 | 0 | 35.7948
2988 | 0 | 1.9625 | 2.4752 | 29.5261 | 15.3116 | 49.2753 | 0 | 0 | 44.8377
2989 | 0 | 2.0626 | 1.8702 | 37.2343 | 5.9967 | 47.1637 | 0 | 0 | 43.231
2990 | 0 | 1.7719 | 2.2301 | 30.4395 | 12.5655 | 47.0071 | 0 | 0 | 43.005
2991 | 0 | 1.6956 | 2.3118 | 28.7621 | 9.0903 | 41.8598 | 0 | 0 | 37.8524
2992 | 0 | 1.4454 | 1.9 | 26.9993 | 16.1668 | 46.5114 | 0 | 0 | 43.1661
2993 | 0 | 2.1248 | 1.9367 | 31.7572 | 6.5614 | 42.3801 | 0 | 0 | 38.3186
2994 | 0 | 1.7893 | 1.5167 | 31.7927 | 12.5147 | 47.6134 | 0 | 0 | 44.3074
2995 | 0 | 1.9022 | 1.4117 | 33.9903 | 11.9295 | 49.2337 | 0 | 0 | 45.9198
2996 | 0 | 1.7767 | 1.1486 | 29.2695 | 0 | 32.1948 | 0 | 0 | 29.2695
2997 | 0 | 1.7351 | 1.2344 | 34.2272 | 0 | 37.1967 | 0 | 0 | 34.2272
2998 | 8.0197 | 2.0227 | 1.3331 | 41.2366 | 0 | 52.6121 | 0 | 0 | 49.2563
2999 | 38.8481 | 1.605 | 1.3683 | 33.7338 | 0 | 75.5552 | 0 | 0 | 72.5819
3000 | 41.3943 | 1.8305 | 2.2059 | 27.8545 | 0 | 73.2852 | 0 | 0 | 69.2488
3001 | 0 | 2.0719 | 2.1636 | 23.9899 | 0 | 28.2254 | 0 | 0 | 23.9899
3002 | 0 | 1.6448 | 1.767 | 34.5008 | 0 | 37.9125 | 0 | 0 | 34.5008
3003 | 0 | 1.6753 | 2.6204 | 34.3204 | 0 | 38.6161 | 0 | 0 | 34.3204
3004 | 0 | 1.7815 | 2.6397 | 38.3073 | 0 | 42.7285 | 0 | 0 | 38.3073
3005 | 0 | 1.6035 | 2.3626 | 29.348 | 0 | 33.3141 | 0 | 0 | 29.348
3006 | 0 | 1.8317 | 1.8189 | 27.1474 | 0 | 30.798 | 0 | 0 | 27.1474
3007 | 0 | 1.8177 | 1.9431 | 29.4211 | 0 | 33.182 | 0 | 0 | 29.4211
3008 | 0 | 1.8905 | 1.9321 | 32.4278 | 8.5374 | 44.7878 | 0 | 0 | 40.9652
3009 | 0 | 1.9647 | 1.7582 | 34.1464 | 17.1485 | 55.0179 | 0 | 0 | 51.2949
3010 | 0 | 1.5534 | 1.4747 | 31.5448 | 10.7576 | 45.3305 | 0 | 0 | 42.3024
3011 | 0 | 1.8159 | 1.8335 | 25.9086 | 6.3779 | 35.9359 | 0 | 0 | 32.2865
3012 | 0 | 1.6421 | 2.0907 | 28.9724 | 22.0534 | 54.7587 | 0 | 0 | 51.0258
3013 | 0 | 1.7422 | 2.2196 | 22.9527 | 17.1442 | 44.0586 | 0 | 0 | 40.0968
3014 | 0 | 1.8812 | 2.2605 | 34.6386 | 20.4195 | 59.1998 | 0 | 0 | 55.0581
3015 | 0 | 1.7464 | 2.1706 | 30.2202 | 13.5593 | 47.6965 | 0 | 0 | 43.7795
3016 | 0 | 1.8499 | 2.1677 | 24.0519 | 19.4532 | 47.5227 | 0 | 0 | 43.505
3017 | 0 | 1.6781 | 2.1706 | 32.2471 | 12.8652 | 48.961 | 0 | 0 | 45.1122
3018 | 0 | 1.6846 | 1.5861 | 29.8913 | 13.6697 | 46.8317 | 0 | 0 | 43.561
3019 | 0 | 1.7468 | 1.239 | 29.8272 | 12.726 | 45.539 | 0 | 0 | 42.5532
3020 | 0 | 1.6499 | 1.0185 | 20.6664 | 0 | 23.3348 | 0 | 0 | 20.6664
3021 | 0 | 1.6923 | 1.0722 | 32.2939 | 0 | 35.0584 | 0 | 0 | 32.2939
3022 | 0 | 1.739 | 1.1947 | 35.2163 | 0 | 38.15 | 0 | 0 | 35.2163
3023 | 0 | 1.8408 | 1.7984 | 28.7523 | 0 | 32.3915 | 0 | 0 | 28.7523
3024 | 0 | 1.6581 | 2.7569 | 22.7348 | 0 | 27.1498 | 0 | 0 | 22.7348
3025 | 0 | 1.7339 | 4.3028 | 33.8677 | 0 | 39.9045 | 0 | 0 | 33.8677
3026 | 0 | 1.6313 | 3.0702 | 28.8998 | 0 | 33.6012 | 0 | 0 | 28.8998
3027 | 0 | 1.5483 | 2.3713 | 28.916 | 0 | 32.8355 | 0 | 0 | 28.916
3028 | 14.8204 | 1.4393 | 2.2727 | 24.6703 | 0 | 43.2027 | 0 | 0 | 39.4906
3029 | 74.1254 | 1.41 | 2.0277 | 31.5557 | 0 | 109.1189 | 0 | 0 | 105.6811
3030 | 64.7086 | 1.5937 | 1.8545 | 27.2178 | 0 | 95.3746 | 0 | 0 | 91.9264
3031 | 10.1312 | 1.5029 | 1.8626 | 29.6924 | 0 | 43.1892 | 200 | 0 | 239.8236
3032 | 0 | 1.7786 | 1.8002 | 28.8349 | 13.9811 | 46.3949 | 0 | 0 | 42.8161
3033 | 0.09118 | 2.0048 | 1.7611 | 26.2457 | 11.983 | 42.0858 | 0 | 0 | 38.3199
3034 | 20.509 | 1.5284 | 1.7681 | 26.8526 | 15.5862 | 66.2444 | 0 | 0 | 62.9478
3035 | 73.4665 | 1.9152 | 1.3773 | 29.2107 | 15.0774 | 121.0471 | 0 | 0 | 117.7546
3036 | 52.5256 | 2.1093 | 2.3299 | 35.0962 | 13.7939 | 105.8549 | 0 | 0 | 101.4157
3037 | 5.9044 | 1.8537 | 2.3888 | 24.2175 | 18.9708 | 53.3352 | 0 | 0 | 49.0927
3038 | 0 | 1.8512 | 2.0295 | 34.6514 | 10.5445 | 49.0766 | 0 | 0 | 45.1959
3039 | 0 | 1.9233 | 1.9886 | 22.255 | 14.8259 | 40.9927 | 0 | 0 | 37.0808
3040 | 0 | 1.9295 | 2.2272 | 24.1206 | 13.0499 | 41.3273 | 0 | 0 | 37.1706
3041 | 0 | 1.6619 | 2.1199 | 20.9515 | 7.1985 | 31.9318 | 0 | 0 | 28.15
3042 | 0 | 1.9282 | 1.5861 | 30.5106 | 18.4872 | 52.5122 | 0 | 0 | 48.9978
3043 | 0 | 1.5148 | 1.239 | 26.0664 | 14.7235 | 43.5437 | 0 | 0 | 40.7898
3044 | 0 | 1.3936 | 1.0185 | 25.1473 | 0 | 27.5594 | 0 | 0 | 25.1473
3045 | 0 | 1.7698 | 1.0722 | 26.441 | 0 | 29.2829 | 0 | 0 | 26.441
3046 | 0 | 1.8898 | 1.2061 | 40.0005 | 0 | 43.0964 | 0 | 0 | 40.0005
3047 | 0 | 1.9389 | 2.0402 | 29.6874 | 0 | 33.6665 | 0 | 200 | 229.6874
3048 | 0 | 1.5565 | 2.7569 | 26.2838 | 0 | 30.5972 | 0 | 0 | 26.2838
3049 | 0 | 1.3553 | 4.3028 | 33.5557 | 0 | 39.2137 | 0 | 0 | 33.5557
3050 | 0 | 1.9893 | 3.0702 | 33.1054 | 0 | 38.1649 | 0 | 0 | 33.1054
3051 | 0 | 1.6828 | 2.3713 | 28.838 | 0 | 32.8921 | 0 | 0 | 28.838
3052 | 5.1918 | 1.7613 | 2.2727 | 28.7912 | 0 | 38.017 | 0 | 0 | 33.983
3053 | 31.9778 | 1.5179 | 2.0277 | 28.3858 | 0 | 63.9092 | 0 | 0 | 60.3636
3054 | 53.5063 | 1.8809 | 1.8545 | 31.0408 | 0 | 88.2825 | 0 | 0 | 84.5471
3055 | 33.2755 | 1.8164 | 1.8626 | 21.9926 | 0 | 58.9471 | 0 | 0 | 55.2681
3056 | 64.8173 | 1.5034 | 1.8002 | 31.0215 | 5.755 | 104.8974 | 0 | 0 | 101.5939
3057 | 67.6712 | 1.4631 | 1.7611 | 34.7433 | 14.1005 | 119.7392 | 0 | 0 | 116.5149
3058 | 70.1856 | 1.7735 | 1.7681 | 26.7525 | 15.9059 | 116.3857 | 0 | 0 | 112.8441
3059 | 65.5987 | 1.9995 | 1.3773 | 26.3122 | 15.6979 | 110.9857 | 0 | 0 | 107.6088
3060 | 56.9992 | 1.7995 | 2.3299 | 32.3182 | 20.1289 | 113.5757 | 0 | 0 | 109.4463
3061 | 52.1498 | 1.5636 | 2.3888 | 34.0479 | 15.3184 | 105.4685 | 0 | 0 | 101.5161
3062 | 4.0519 | 1.8369 | 2.0295 | 32.9958 | 8.4034 | 49.3176 | 0 | 0 | 45.4511
3063 | 0 | 1.6034 | 1.9886 | 26.45 | 21.4086 | 51.4507 | 0 | 0 | 47.8587
3064 | 0 | 1.8245 | 2.2272 | 33.7501 | 12.3764 | 50.1783 | 0 | 0 | 46.1266
3065 | 0 | 1.6072 | 2.1199 | 28.4527 | 15.914 | 48.0938 | 0 | 0 | 44.3667
3066 | 0 | 1.6513 | 1.5861 | 26.9122 | 15.2806 | 45.4303 | 0 | 0 | 42.1928
3067 | 0 | 1.9651 | 1.239 | 33.334 | 23.1717 | 59.7099 | 0 | 0 | 56.5058
3068 | 0 | 1.7446 | 1.0185 | 31.1073 | 0 | 33.8704 | 0 | 0 | 31.1073
3069 | 0 | 1.8181 | 1.0722 | 38.5394 | 0 | 41.4297 | 0 | 0 | 38.5394
3070 | 0 | 1.7786 | 1.1947 | 23.0926 | 0 | 26.0658 | 0 | 0 | 23.0926
3071 | 0 | 1.8598 | 1.9596 | 27.8588 | 0 | 31.6782 | 0 | 0 | 27.8588
3072 | 0 | 1.6493 | 2.7569 | 27.4101 | 0 | 31.8164 | 0 | 0 | 27.4101
3073 | 0 | 1.5747 | 4.3028 | 34.387 | 0 | 40.2645 | 0 | 0 | 34.387
3074 | 0 | 1.9469 | 3.0702 | 35.4315 | 0 | 40.4486 | 0 | 0 | 35.4315
3075 | 0 | 1.7406 | 2.3713 | 29.9941 | 0 | 34.106 | 0 | 0 | 29.9941
3076 | 0 | 1.6531 | 2.2727 | 37.8367 | 0 | 41.7625 | 0 | 0 | 37.8367
3077 | 11.7969 | 1.6165 | 2.0277 | 30.1541 | 0 | 45.5952 | 0 | 0 | 41.951
3078 | 38.1318 | 1.7779 | 1.8545 | 25.907 | 0 | 67.6712 | 0 | 0 | 64.0388
3079 | 0 | 1.6235 | 1.8626 | 28.7638 | 0 | 32.2499 | 0 | 0 | 28.7638
3080 | 0 | 1.685 | 1.8002 | 30.5569 | 23.8755 | 57.9176 | 0 | 0 | 54.4324
3081 | 0 | 1.5601 | 1.7611 | 24.8222 | 22.6462 | 50.7896 | 0 | 0 | 47.4684
3082 | 0 | 1.9762 | 1.7681 | 33.3485 | 8.398 | 45.4908 | 0 | 0 | 41.7464
3083 | 0 | 1.8346 | 1.3773 | 41.1836 | 16.0299 | 60.4254 | 0 | 0 | 57.2135
3084 | 0 | 1.5515 | 2.3299 | 36.9949 | 14.9485 | 55.8247 | 0 | 0 | 51.9434
3085 | 0 | 1.7113 | 2.3888 | 33.4387 | 15.3706 | 52.9095 | 0 | 0 | 48.8094
3086 | 0 | 1.8208 | 2.0295 | 34.058 | 16.3838 | 54.2921 | 0 | 0 | 50.4418
3087 | 0 | 1.8079 | 1.9886 | 21.4912 | 7.6102 | 32.898 | 0 | 0 | 29.1015
3088 | 0 | 1.7912 | 2.2272 | 25.9032 | 16.4308 | 46.3524 | 0 | 0 | 42.334
3089 | 0 | 1.525 | 2.1199 | 29.3806 | 11.144 | 44.1695 | 0 | 0 | 40.5246
3090 | 0 | 1.6837 | 1.5167 | 27.4084 | 8.9672 | 39.5759 | 0 | 0 | 36.3756
3091 | 0 | 1.8486 | 1.4117 | 29.6451 | 16.5681 | 49.4735 | 0 | 0 | 46.2132
3092 | 0 | 1.6571 | 1.1486 | 23.6266 | 0 | 26.4323 | 0 | 0 | 23.6266
3093 | 0 | 1.6724 | 1.2344 | 26.3198 | 0 | 29.2266 | 0 | 0 | 26.3198
3094 | 0 | 1.5359 | 1.1264 | 34.5423 | 0 | 37.2046 | 0 | 0 | 34.5423
3095 | 0 | 1.642 | 1.1609 | 35.2714 | 0 | 38.0742 | 0 | 0 | 35.2714
3096 | 0 | 1.7398 | 1.1591 | 30.3634 | 0 | 33.2623 | 0 | 0 | 30.3634
3097 | 0 | 1.4346 | 2.1636 | 31.254 | 0 | 34.8522 | 0 | 0 | 31.254
3098 | 0 | 1.8089 | 1.767 | 22.678 | 0 | 26.2539 | 0 | 0 | 22.678
3099 | 0 | 1.9351 | 2.6204 | 29.542 | 0 | 34.0974 | 0 | 0 | 29.542
3100 | 0 | 1.7341 | 3.0389 | 25.5182 | 0 | 30.2912 | 0 | 0 | 25.5182
3101 | 0 | 1.4367 | 3.5267 | 32.19 | 0 | 37.1534 | 0 | 0 | 32.19
3102 | 0 | 2.0921 | 2.6343 | 28.6023 | 0 | 33.3287 | 0 | 0 | 28.6023
3103 | 0 | 1.9498 | 2.8745 | 35.8033 | 0 | 40.6276 | 0 | 0 | 35.8033
3104 | 0 | 1.5465 | 2.0979 | 26.8764 | 10.9999 | 41.5208 | 0 | 0 | 37.8764
3105 | 0 | 2.0323 | 1.7582 | 24.6668 | 20.4275 | 48.8848 | 0 | 0 | 45.0943
3106 | 0 | 1.5824 | 1.4747 | 29.0234 | 16.3214 | 48.4019 | 0 | 0 | 45.3448
3107 | 0 | 1.477 | 1.8335 | 34.5092 | 25.0441 | 62.8637 | 0 | 0 | 59.5533
3108 | 0 | 1.5529 | 2.0907 | 32.7792 | 15.5931 | 52.016 | 0 | 0 | 48.3723
3109 | 0 | 1.6465 | 2.2196 | 38.4274 | 17.4395 | 59.733 | 0 | 0 | 55.8668
3110 | 0 | 1.9989 | 2.2605 | 33.6179 | 4.2902 | 42.1675 | 0 | 0 | 37.9081
3111 | 0 | 1.722 | 2.1706 | 32.1381 | 16.271 | 52.3018 | 0 | 0 | 48.4091
3112 | 0 | 1.5379 | 2.1677 | 34.3355 | 11.7922 | 49.8333 | 0 | 0 | 46.1277
3113 | 0 | 1.9279 | 2.1706 | 29.7358 | 14.6443 | 48.4785 | 0 | 0 | 44.38
3114 | 0 | 1.6011 | 1.5861 | 35.3634 | 28.6207 | 67.1713 | 0 | 0 | 63.9841
3115 | 0 | 2.0631 | 1.239 | 29.1688 | 20.4012 | 52.8721 | 0 | 0 | 49.5699
3116 | 0 | 1.5493 | 2.3201 | 33.7142 | 0 | 37.5836 | 0 | 0 | 33.7142
3117 | 0 | 1.6289 | 3.1437 | 29.1689 | 0 | 33.9415 | 0 | 0 | 29.1689
3118 | 0 | 1.6955 | 4.1272 | 37.6114 | 0 | 43.4341 | 0 | 0 | 37.6114
3119 | 0 | 1.6025 | 5.3456 | 22.2857 | 0 | 29.2339 | 0 | 0 | 22.2857
3120 | 0 | 1.9043 | 5.6684 | 30.2751 | 0 | 37.8477 | 0 | 0 | 30.2751
3121 | 0 | 1.543 | 6.0875 | 32.299 | 0 | 39.9295 | 0 | 0 | 32.299
3122 | 0 | 1.7122 | 3.9504 | 24.7165 | 0 | 30.3792 | 0 | 0 | 24.7165
3123 | 0 | 1.7688 | 4.0397 | 28.9627 | 0 | 34.7712 | 0 | 0 | 28.9627
3124 | 0 | 1.6833 | 3.7424 | 27.4901 | 0 | 32.9159 | 0 | 0 | 27.4901
3125 | 0 | 1.6372 | 3.2462 | 28.6333 | 0 | 33.5167 | 0 | 0 | 28.6333
3126 | 0 | 1.7672 | 1.8545 | 24.4047 | 0 | 28.0264 | 0 | 0 | 24.4047
3127 | 0 | 1.8699 | 1.9456 | 33.8486 | 0 | 37.664 | 0 | 0 | 33.8486
3128 | 0 | 1.7759 | 1.8002 | 27.3897 | 18.2198 | 49.1856 | 0 | 0 | 45.6095
3129 | 0 | 1.7221 | 1.7611 | 36.3766 | 12.0509 | 51.9108 | 0 | 0 | 48.4276
3130 | 0 | 1.9302 | 1.7681 | 24.7046 | 9.9151 | 38.3181 | 0 | 0 | 34.6197
3131 | 0 | 1.7052 | 1.3773 | 29.6022 | 22.9015 | 55.5862 | 0 | 0 | 52.5037
3132 | 0 | 1.8956 | 2.3299 | 32.4266 | 18.0258 | 54.6779 | 0 | 0 | 50.4524
3133 | 0 | 1.75 | 2.3888 | 27.7816 | 13.7181 | 45.6385 | 0 | 0 | 41.4997
3134 | 0 | 2.0022 | 2.0295 | 29.7319 | 7.8437 | 41.6073 | 0 | 0 | 37.5756
3135 | 0 | 1.6492 | 1.9886 | 30.8496 | 16.3281 | 50.8156 | 0 | 200 | 247.1778
3136 | 0 | 1.59 | 2.2272 | 24.647 | 20.4038 | 48.868 | 0 | 0 | 45.0508
3137 | 0 | 1.8438 | 2.1199 | 35.8319 | 6.8766 | 46.6722 | 0 | 0 | 42.7086
3138 | 0 | 1.7948 | 1.9531 | 29.9442 | 12.0073 | 45.6993 | 0 | 0 | 41.9515
3139 | 0 | 1.4071 | 1.5255 | 27.4154 | 12.8839 | 43.2319 | 0 | 0 | 40.2993
3140 | 0 | 1.7178 | 1.1504 | 36.0371 | 0 | 38.9053 | 0 | 0 | 36.0371
3141 | 0 | 1.5933 | 1.1994 | 28.4702 | 0 | 31.2629 | 0 | 0 | 28.4702
3142 | 0 | 2.0087 | 1.0675 | 19.6979 | 0 | 22.7742 | 0 | 0 | 19.6979
3143 | 0 | 1.9264 | 1.3615 | 35.1541 | 0 | 38.442 | 0 | 0 | 35.1541
3144 | 0 | 1.8956 | 1.7973 | 34.0425 | 0 | 37.7354 | 0 | 0 | 34.0425
3145 | 0 | 1.7869 | 2.1992 | 29.2721 | 0 | 33.2582 | 0 | 0 | 29.2721
3146 | 0 | 1.965 | 1.9945 | 36.1635 | 0 | 40.123 | 200 | 0 | 236.1635
3147 | 0 | 1.6748 | 3.6751 | 34.8963 | 0 | 40.2463 | 0 | 0 | 34.8963
3148 | 0 | 1.5713 | 3.2685 | 34.6622 | 0 | 39.5021 | 0 | 0 | 34.6622
3149 | 0 | 1.8103 | 2.6595 | 41.4656 | 0 | 45.9354 | 0 | 0 | 41.4656
3150 | 0 | 1.9509 | 2.1561 | 31.7986 | 0 | 35.9056 | 0 | 0 | 31.7986
3151 | 0 | 1.3766 | 1.9466 | 26.4196 | 0 | 29.7428 | 0 | 0 | 26.4196
3152 | 0 | 1.9738 | 1.9857 | 29.6158 | 20.1046 | 53.68 | 0 | 0 | 49.7204
3153 | 0 | 1.6012 | 1.7436 | 29.3855 | 14.2951 | 47.0254 | 0 | 0 | 43.6806
3154 | 0 | 1.9325 | 1.9834 | 30.0653 | 11.7862 | 45.7674 | 0 | 0 | 41.8515
3155 | 0 | 1.6626 | 2.2739 | 35.136 | 18.9453 | 58.0178 | 0 | 0 | 54.0813
3156 | 0 | 1.6655 | 2.4752 | 34.0921 | 14.0666 | 52.2992 | 0 | 0 | 48.1586
3157 | 0 | 1.8107 | 1.8702 | 31.0982 | 16.8765 | 51.6557 | 0 | 0 | 47.9748
3158 | 0 | 1.4072 | 2.2301 | 27.1519 | 0.96747 | 31.7567 | 0 | 0 | 28.1194
3159 | 0 | 1.7874 | 2.3118 | 28.7708 | 13.7616 | 46.6316 | 0 | 0 | 42.5324
3160 | 0 | 1.9112 | 1.9 | 37.4158 | 29.5676 | 70.7945 | 0 | 0 | 66.9833
3161 | 0 | 2.0838 | 1.9367 | 30.2488 | 9.3664 | 43.6357 | 0 | 0 | 39.6152
3162 | 0 | 1.7109 | 1.5167 | 21.3392 | 12.1048 | 36.6716 | 0 | 0 | 33.444
3163 | 0 | 1.7826 | 1.4117 | 28.6051 | 17.0108 | 48.8102 | 0 | 0 | 45.6159
3164 | 0 | 1.6038 | 1.1486 | 18.8309 | 0 | 21.5833 | 0 | 0 | 18.8309
3165 | 0 | 1.918 | 1.2344 | 31.8212 | 0 | 34.9736 | 0 | 0 | 31.8212
3166 | 0 | 1.2069 | 1.1264 | 37.8884 | 0 | 40.2217 | 0 | 0 | 37.8884
3167 | 0 | 1.7815 | 1.1609 | 26.9283 | 0 | 29.8707 | 0 | 0 | 26.9283
3168 | 0 | 1.336 | 1.1591 | 31.9539 | 0 | 34.4491 | 0 | 0 | 31.9539
3169 | 0 | 1.7141 | 2.1636 | 26.09 | 0 | 29.9677 | 0 | 0 | 26.09
3170 | 0 | 1.8107 | 1.767 | 33.0964 | 0 | 36.6741 | 0 | 0 | 33.0964
3171 | 0 | 1.7312 | 2.6204 | 32.3257 | 0 | 36.6773 | 0 | 0 | 32.3257
3172 | 0 | 2.0772 | 2.6397 | 26.3403 | 0 | 31.0572 | 0 | 0 | 26.3403
3173 | 0 | 1.6678 | 2.3626 | 23.4858 | 0 | 27.5162 | 0 | 0 | 23.4858
3174 | 0 | 1.6741 | 1.8189 | 26.3001 | 0 | 29.7931 | 0 | 0 | 26.3001
3175 | 0 | 1.701 | 1.9431 | 19.1906 | 0 | 22.8348 | 0 | 0 | 19.1906
3176 | 0 | 1.8434 | 1.9321 | 33.4083 | 15.775 | 52.9588 | 0 | 0 | 49.1833
3177 | 0 | 1.8045 | 1.7582 | 34.1172 | 18.199 | 55.879 | 0 | 0 | 52.3162
3178 | 0 | 1.893 | 1.4747 | 31.3131 | 13.4035 | 48.0843 | 0 | 0 | 44.7166
3179 | 0 | 1.6245 | 1.8335 | 28.8274 | 16.0902 | 48.3756 | 0 | 0 | 44.9177
3180 | 0 | 1.5662 | 2.0907 | 32.4207 | 12.5403 | 48.6179 | 0 | 0 | 44.961
3181 | 0 | 2.0159 | 2.2196 | 30.2648 | 6.5533 | 41.0536 | 0 | 0 | 36.818
3182 | 0 | 1.5335 | 2.2605 | 31.9441 | 15.1295 | 50.8676 | 0 | 0 | 47.0736
3183 | 0 | 2.0051 | 2.1706 | 31.3321 | 6.1157 | 41.6236 | 0 | 0 | 37.4478
3184 | 0 | 1.8725 | 2.1677 | 24.41 | 9.8374 | 38.2877 | 0 | 0 | 34.2474
3185 | 0 | 1.745 | 2.1706 | 31.6486 | 13.9504 | 49.5146 | 0 | 0 | 45.5989
3186 | 0 | 1.7779 | 1.5861 | 20.8301 | 19.6197 | 43.8139 | 0 | 0 | 40.4498
3187 | 0 | 1.4832 | 1.239 | 31.0771 | 9.927 | 43.7264 | 0 | 0 | 41.0042
3188 | 0 | 1.7464 | 1.0185 | 37.5856 | 0 | 40.3506 | 0 | 0 | 37.5856
3189 | 0 | 1.6361 | 1.0722 | 29.9874 | 0 | 32.6957 | 0 | 0 | 29.9874
3190 | 0 | 1.7484 | 1.1947 | 39.0391 | 0 | 41.9822 | 0 | 0 | 39.0391
3191 | 0 | 2.0204 | 1.2542 | 29.3784 | 0 | 32.653 | 0 | 0 | 29.3784
3192 | 0 | 1.6309 | 2.7569 | 28.5255 | 0 | 32.9133 | 0 | 0 | 28.5255
3193 | 0 | 1.6521 | 4.3028 | 28.1665 | 0 | 34.1214 | 0 | 0 | 28.1665
3194 | 0 | 1.984 | 3.0702 | 36.3729 | 0 | 41.4271 | 0 | 0 | 36.3729
3195 | 2.8861 | 1.6792 | 2.3713 | 29.8517 | 0 | 36.7883 | 0 | 0 | 32.7378
3196 | 29.5806 | 1.6514 | 2.2727 | 30.3371 | 0 | 63.8418 | 0 | 0 | 59.9177
3197 | 90.9525 | 1.2143 | 2.0277 | 37.7233 | 0 | 131.9178 | 0 | 0 | 128.6758
3198 | 109.1823 | 1.9061 | 1.8545 | 31.5304 | 0 | 144.4733 | 0 | 0 | 140.7127
3199 | 95.4991 | 1.7699 | 1.8626 | 22.0577 | 0 | 121.1894 | 0 | 0 | 117.5569
3200 | 98.6745 | 1.7122 | 1.8002 | 30.5782 | 17.3715 | 150.1366 | 0 | 0 | 146.6242
3201 | 98.0809 | 1.792 | 1.7611 | 34.8587 | 17.2843 | 153.7771 | 0 | 0 | 150.224
3202 | 100.464 | 1.806 | 1.7681 | 26.017 | 5.493 | 135.5481 | 0 | 0 | 131.974
3203 | 90.9938 | 1.4739 | 1.3773 | 29.9741 | 15.7889 | 139.6079 | 0 | 0 | 136.7568
3204 | 63.3334 | 1.6996 | 2.3299 | 33.2175 | 9.8059 | 110.3864 | 0 | 0 | 106.3568
3205 | 0.090614 | 1.7224 | 2.3888 | 22.8634 | 10.9738 | 38.039 | 0 | 0 | 33.9278
3206 | 0 | 2.0439 | 2.0295 | 34.0804 | 12.5483 | 50.702 | 0 | 0 | 46.6286
3207 | 0 | 1.6647 | 1.9886 | 25.7111 | 19.0418 | 48.4062 | 0 | 0 | 44.7529
3208 | 0 | 2.0433 | 2.2272 | 30.1278 | 23.4039 | 57.8022 | 0 | 0 | 53.5317
3209 | 0 | 1.8658 | 2.1199 | 27.0959 | 20.4096 | 51.4912 | 0 | 0 | 47.5055
3210 | 0 | 1.815 | 1.5861 | 32.6918 | 15.5263 | 51.6193 | 0 | 0 | 48.2181
3211 | 0 | 1.7826 | 1.239 | 26.9084 | 17.0556 | 46.9857 | 0 | 0 | 43.964
3212 | 0 | 1.8771 | 1.0185 | 28.3414 | 0 | 31.237 | 0 | 0 | 28.3414
3213 | 0 | 1.7457 | 1.0722 | 29.3919 | 0 | 32.2099 | 0 | 0 | 29.3919
3214 | 0 | 1.6097 | 1.1947 | 39.1619 | 0 | 41.9663 | 0 | 0 | 39.1619
3215 | 0 | 1.5841 | 1.2542 | 31.5045 | 0 | 34.3427 | 0 | 0 | 31.5045
3216 | 0 | 1.7097 | 2.7569 | 32.6561 | 0 | 37.1227 | 0 | 0 | 32.6561
3217 | 0 | 1.4901 | 4.3028 | 31.8005 | 0 | 37.5933 | 0 | 0 | 31.8005
3218 | 0 | 1.6359 | 3.0702 | 29.3276 | 0 | 34.0337 | 0 | 0 | 29.3276
3219 | 0 | 1.716 | 2.3713 | 36.5272 | 0 | 40.6145 | 0 | 0 | 36.5272
3220 | 10.5737 | 1.5629 | 2.2727 | 34.8304 | 0 | 49.2397 | 0 | 0 | 45.4041
3221 | 38.003 | 1.7354 | 2.0277 | 24.6737 | 0 | 66.4399 | 0 | 0 | 62.6768
3222 | 25.9967 | 1.9916 | 1.8545 | 31.4738 | 0 | 61.3165 | 0 | 0 | 57.4704
3223 | 1.6729 | 1.686 | 1.8626 | 28.0253 | 0 | 33.2469 | 0 | 0 | 29.6982
3224 | 6.1182 | 1.9535 | 1.8002 | 31.2651 | 9.5809 | 50.718 | 0 | 0 | 46.9642
3225 | 3.0388 | 1.5442 | 1.7611 | 30.9612 | 21.0487 | 58.354 | 0 | 0 | 55.0486
3226 | 0 | 1.9342 | 1.7681 | 23.7565 | 13.4611 | 40.92 | 0 | 0 | 37.2176
3227 | 0 | 1.4114 | 1.3773 | 32.0146 | 9.7792 | 44.5824 | 0 | 0 | 41.7937
3228 | 0 | 1.6656 | 2.3299 | 28.5119 | 3.3179 | 35.8254 | 0 | 0 | 31.8298
3229 | 0 | 1.6767 | 2.3888 | 27.4486 | 7.0704 | 38.5846 | 0 | 0 | 34.5191
3230 | 0 | 1.6218 | 2.0295 | 31.336 | 13.9109 | 48.8982 | 0 | 0 | 45.2469
3231 | 0 | 2.0171 | 1.9886 | 31.5058 | 20.5239 | 56.0354 | 0 | 0 | 52.0297
3232 | 0 | 1.4468 | 2.2272 | 29.9292 | 10.9099 | 44.5132 | 0 | 0 | 40.8392
3233 | 0 | 1.7714 | 2.1199 | 27.7743 | 21.5534 | 53.2189 | 0 | 0 | 49.3277
3234 | 0 | 1.7374 | 1.5861 | 32.8835 | 11.5153 | 47.7224 | 0 | 0 | 44.3988
3235 | 0 | 1.9178 | 1.239 | 32.5183 | 10.8279 | 46.503 | 0 | 0 | 43.3462
3236 | 0 | 1.7529 | 1.0185 | 33.8248 | 0 | 36.5962 | 0 | 0 | 33.8248
3237 | 0 | 1.6201 | 1.0722 | 23.1677 | 0 | 25.86 | 0 | 0 | 23.1677
3238 | 0 | 1.6658 | 1.1947 | 29.8839 | 0 | 32.7443 | 0 | 0 | 29.8839
3239 | 0 | 1.7385 | 1.2542 | 30.6124 | 0 | 33.6051 | 0 | 200 | 230.6124
3240 | 0 | 1.5516 | 2.7569 | 37.8818 | 0 | 42.1904 | 0 | 0 | 37.8818
3241 | 0 | 1.6612 | 4.3028 | 32.8581 | 0 | 38.8221 | 0 | 0 | 32.8581
3242 | 0 | 1.8222 | 3.0702 | 26.7949 | 0 | 31.6873 | 0 | 0 | 26.7949
3243 | 0 | 1.8565 | 2.3713 | 30.9979 | 0 | 35.2258 | 0 | 0 | 30.9979
3244 | 0 | 1.8878 | 2.2727 | 28.6788 | 0 | 32.8393 | 0 | 0 | 28.6788
3245 | 0 | 2.2553 | 2.0277 | 31.281 | 0 | 35.564 | 0 | 0 | 31.281
3246 | 4.9577 | 1.7141 | 1.8545 | 37.7075 | 0 | 46.2338 | 0 | 0 | 42.6652
3247 | 26.4603 | 1.9971 | 1.8626 | 35.4326 | 0 | 65.7526 | 0 | 0 | 61.8929
3248 | 35.3469 | 1.9141 | 1.8002 | 17.9412 | 9.7862 | 66.7887 | 0 | 0 | 63.0743
3249 | 19.6266 | 1.4726 | 1.7611 | 32.8142 | 8.2668 | 63.9413 | 0 | 0 | 60.7076
3250 | 79.6694 | 1.653 | 1.7681 | 30.8497 | 24.8576 | 138.7978 | 0 | 0 | 135.3766
3251 | 65.3705 | 1.6849 | 1.3773 | 29.546 | 6.33 | 104.3087 | 0 | 0 | 101.2465
3252 | 24.5624 | 1.983 | 2.3299 | 27.5859 | 14.4702 | 70.9314 | 0 | 0 | 66.6185
3253 | 0 | 1.9822 | 2.3888 | 30.2189 | 14.1764 | 48.7664 | 0 | 0 | 44.3954
3254 | 0 | 1.5751 | 2.0295 | 23.8683 | 5.6088 | 33.0817 | 0 | 0 | 29.4771
3255 | 0 | 1.7098 | 1.9886 | 25.4059 | 26.7433 | 55.8477 | 0 | 0 | 52.1493
3256 | 0 | 1.6118 | 2.2272 | 30.6415 | 1.1517 | 35.6323 | 0 | 0 | 31.7932
3257 | 0 | 1.6319 | 2.1199 | 30.0801 | 7.4858 | 41.3177 | 0 | 0 | 37.5659
3258 | 0 | 1.4071 | 1.5861 | 25.3404 | 19.728 | 48.0616 | 0 | 0 | 45.0684
3259 | 0 | 1.5634 | 1.239 | 28.4354 | 18.5825 | 49.8203 | 0 | 0 | 47.0179
3260 | 0 | 1.6599 | 1.0185 | 40.1616 | 0 | 42.84 | 0 | 0 | 40.1616
3261 | 0 | 1.7319 | 1.0722 | 29.0694 | 0 | 31.8734 | 200 | 0 | 229.0694
3262 | 0 | 1.8521 | 1.1947 | 31.2023 | 0 | 34.2491 | 0 | 0 | 31.2023
3263 | 0.92423 | 2.0266 | 1.9596 | 27.4672 | 0 | 32.3776 | 0 | 0 | 28.3914
3264 | 23.4174 | 2.0812 | 2.7569 | 35.3598 | 0 | 63.6152 | 0 | 0 | 58.7772
3265 | 92.7239 | 1.8491 | 5.0159 | 26.2292 | 0 | 125.8181 | 0 | 0 | 118.9531
3266 | 53.6585 | 1.8347 | 4.3602 | 33.5396 | 0 | 93.393 | 0 | 0 | 87.1981
3267 | 4.5033 | 1.395 | 4.588 | 24.4997 | 0 | 34.9861 | 0 | 0 | 29.003
3268 | 0.81286 | 1.5153 | 4.1617 | 35.7214 | 0 | 42.2114 | 0 | 0 | 36.5343
3269 | 16.7511 | 2.083 | 3.609 | 26.1871 | 0 | 48.6302 | 0 | 0 | 42.9382
3270 | 50.3902 | 1.6465 | 2.4697 | 30.2727 | 0 | 84.779 | 0 | 0 | 80.6629
3271 | 52.0155 | 1.9474 | 3.1108 | 32.8624 | 0 | 89.9361 | 0 | 0 | 84.8779
3272 | 36.7019 | 1.7988 | 3.034 | 31.9561 | 18.4057 | 91.8966 | 0 | 0 | 87.0637
3273 | 58.4327 | 1.6731 | 2.0061 | 24.4558 | 14.5194 | 101.087 | 0 | 0 | 97.4079
3274 | 0 | 1.6266 | 2.0548 | 31.2095 | 11.6842 | 46.5751 | 0 | 0 | 42.8937
3275 | 0 | 2.0364 | 1.4167 | 29.4308 | 10.8099 | 43.6939 | 0 | 0 | 40.2407
3276 | 0 | 1.9172 | 2.3299 | 36.1326 | 10.5381 | 50.9178 | 0 | 0 | 46.6707
3277 | 0 | 1.6474 | 2.3888 | 25.9362 | 19.5834 | 49.5558 | 0 | 0 | 45.5196
3278 | 0 | 1.7504 | 2.0295 | 30.0861 | 9.7792 | 43.6451 | 0 | 0 | 39.8653
3279 | 0 | 1.5443 | 1.9886 | 28.8396 | 19.6209 | 51.9935 | 0 | 0 | 48.4605
3280 | 0 | 2.0008 | 2.2272 | 30.5331 | 18.764 | 53.5252 | 0 | 0 | 49.2971
3281 | 0 | 1.7045 | 2.1199 | 33.225 | 10.1138 | 47.1632 | 0 | 0 | 43.3388
3282 | 0 | 2.0082 | 1.5861 | 23.3792 | 7.6137 | 34.5872 | 0 | 0 | 30.9929
3283 | 0 | 1.6467 | 1.239 | 25.4949 | 23.4305 | 51.8111 | 0 | 0 | 48.9254
3284 | 5.1975 | 1.6408 | 1.0185 | 27.5951 | 0 | 35.4519 | 0 | 0 | 32.7926
3285 | 25.7184 | 1.8489 | 1.0722 | 27.4979 | 0 | 56.1374 | 0 | 0 | 53.2163
3286 | 64.4695 | 1.7546 | 1.3684 | 34.6568 | 0 | 102.2492 | 0 | 0 | 99.1263
3287 | 85.7875 | 1.9037 | 2.1209 | 24.5161 | 0 | 114.3282 | 0 | 0 | 110.3036
3288 | 73.8874 | 1.3976 | 2.7569 | 28.1103 | 0 | 106.1523 | 0 | 0 | 101.9978
3289 | 28.7692 | 2.0766 | 5.2107 | 30.6582 | 0 | 66.7148 | 0 | 0 | 59.4274
3290 | 0 | 1.8494 | 4.77 | 34.9719 | 0 | 41.5914 | 0 | 0 | 34.9719
3291 | 0 | 2.0075 | 5.2049 | 27.702 | 0 | 34.9144 | 0 | 0 | 27.702
3292 | 0 | 1.7648 | 5.1401 | 28.499 | 0 | 35.4039 | 0 | 0 | 28.499
3293 | 17.3535 | 1.6829 | 4.8427 | 24.2881 | 0 | 48.1672 | 0 | 0 | 41.6417
3294 | 80.5571 | 1.8806 | 4.0906 | 27.6651 | 0 | 114.1934 | 0 | 0 | 108.2222
3295 | 60.0174 | 1.6348 | 3.7963 | 35.2822 | 0 | 100.7306 | 0 | 0 | 95.2996
3296 | 41.849 | 1.8515 | 3.3056 | 27.5758 | 14.4693 | 89.0512 | 0 | 0 | 83.8941
3297 | 55.6489 | 1.4397 | 2.8181 | 30.5464 | 8.0214 | 98.4745 | 0 | 0 | 94.2167
3298 | 42.9064 | 1.6813 | 1.7681 | 28.4774 | 21.2059 | 96.0391 | 0 | 0 | 92.5897
3299 | 20.6997 | 1.9543 | 1.3773 | 26.8654 | 5.1284 | 56.0251 | 0 | 0 | 52.6935
3300 | 0 | 1.6395 | 2.3299 | 27.8594 | 19.8467 | 51.6756 | 0 | 0 | 47.7061
3301 | 0 | 1.9131 | 2.3888 | 34.283 | 13.1272 | 51.7121 | 0 | 0 | 47.4102
3302 | 0 | 1.4401 | 2.0295 | 29.1343 | 16.1516 | 48.7554 | 0 | 0 | 45.2859
3303 | 0 | 1.6835 | 1.9886 | 28.7777 | 0.57146 | 33.0213 | 0 | 0 | 29.3491
3304 | 0 | 1.6647 | 2.2272 | 32.3573 | 8.9248 | 45.1739 | 0 | 0 | 41.282
3305 | 0 | 1.8484 | 2.1199 | 29.134 | 12.2927 | 45.3949 | 0 | 0 | 41.4267
3306 | 0 | 1.4318 | 1.9531 | 20.8519 | 20.403 | 44.6398 | 0 | 0 | 41.2549
3307 | 0 | 1.6623 | 1.5255 | 31.2612 | 20.2743 | 54.7233 | 0 | 0 | 51.5355
3308 | 0 | 1.7193 | 1.1504 | 36.409 | 0 | 39.2787 | 0 | 0 | 36.409
3309 | 0 | 1.4804 | 1.1994 | 31.4456 | 0 | 34.1254 | 0 | 0 | 31.4456
3310 | 0 | 1.8562 | 1.0675 | 29.7903 | 0 | 32.714 | 0 | 0 | 29.7903
3311 | 0 | 1.7515 | 1.3615 | 25.2184 | 0 | 28.3314 | 0 | 0 | 25.2184
3312 | 0 | 1.9092 | 1.7973 | 29.6094 | 0 | 33.3158 | 0 | 0 | 29.6094
3313 | 0 | 1.7468 | 2.1992 | 26.4012 | 0 | 30.3472 | 0 | 0 | 26.4012
3314 | 0 | 1.8977 | 1.9945 | 28.4328 | 0 | 32.325 | 0 | 0 | 28.4328
3315 | 0 | 1.6669 | 3.6751 | 29.4942 | 0 | 34.8362 | 0 | 0 | 29.4942
3316 | 0 | 1.8205 | 4.9623 | 33.0559 | 0 | 39.8387 | 0 | 0 | 33.0559
3317 | 0 | 1.9371 | 5.2016 | 37.4552 | 0 | 44.594 | 0 | 0 | 37.4552
3318 | 0 | 1.7822 | 4.7788 | 36.0842 | 0 | 42.6451 | 0 | 200 | 236.0842
3319 | 0 | 1.5077 | 4.6741 | 31.5798 | 0 | 37.7617 | 0 | 0 | 31.5798
3320 | 0 | 1.8176 | 3.5906 | 27.8521 | 4.2035 | 37.4638 | 0 | 0 | 32.0556
3321 | 0 | 1.6773 | 3.5207 | 26.2598 | 12.1569 | 43.6147 | 0 | 0 | 38.4168
3322 | 0 | 1.733 | 1.9834 | 25.2236 | 7.4807 | 36.4206 | 0 | 0 | 32.7043
3323 | 0 | 1.9531 | 2.2739 | 31.44 | 10.8979 | 46.5649 | 0 | 0 | 42.3379
3324 | 0 | 1.7613 | 2.4752 | 32.7377 | 14.7922 | 51.7664 | 0 | 0 | 47.5299
3325 | 0 | 1.7382 | 1.8702 | 32.9545 | 15.0492 | 51.6122 | 0 | 0 | 48.0037
3326 | 0 | 1.8566 | 2.2301 | 31.777 | 13.3257 | 49.1895 | 0 | 0 | 45.1027
3327 | 0 | 1.8118 | 2.3118 | 30.3663 | 10.0312 | 44.5211 | 0 | 0 | 40.3975
3328 | 0 | 1.6801 | 2.3348 | 33.9138 | 10.5977 | 48.5264 | 0 | 0 | 44.5115
3329 | 0 | 1.5785 | 2.5535 | 30.8118 | 9.8642 | 44.8079 | 0 | 0 | 40.676
3330 | 0 | 1.8104 | 2.2788 | 33.8276 | 21.7274 | 59.6443 | 0 | 0 | 55.555
3331 | 0 | 1.774 | 2.2867 | 27.0512 | 6.8497 | 37.9616 | 0 | 0 | 33.9009
3332 | 0 | 1.8628 | 3.2731 | 34.7351 | 0 | 39.8711 | 0 | 0 | 34.7351
3333 | 0 | 1.8654 | 3.045 | 32.4057 | 0 | 37.3161 | 0 | 0 | 32.4057
3334 | 0 | 1.6323 | 3.7934 | 29.8794 | 0 | 35.3051 | 0 | 0 | 29.8794
3335 | 0 | 1.8505 | 4.1871 | 34.188 | 0 | 40.2256 | 0 | 0 | 34.188
3336 | 0 | 1.5319 | 3.7927 | 23.0481 | 0 | 28.3727 | 0 | 0 | 23.0481
3337 | 0 | 1.9508 | 2.1636 | 30.6216 | 0 | 34.7361 | 0 | 0 | 30.6216
3338 | 0 | 1.5948 | 1.767 | 32.3765 | 0 | 35.7383 | 0 | 0 | 32.3765
3339 | 0 | 1.6004 | 2.6204 | 39.7977 | 0 | 44.0185 | 0 | 0 | 39.7977
3340 | 0 | 1.6068 | 2.6397 | 37.0851 | 0 | 41.3316 | 0 | 0 | 37.0851
3341 | 0 | 1.7243 | 2.3626 | 29.8198 | 0 | 33.9067 | 0 | 0 | 29.8198
3342 | 0 | 1.4896 | 1.8189 | 35.7167 | 0 | 39.0252 | 0 | 0 | 35.7167
3343 | 0 | 1.7778 | 1.9431 | 32.5085 | 0 | 36.2295 | 0 | 0 | 32.5085
3344 | 0 | 1.4952 | 1.9321 | 25.2625 | 5.581 | 34.2707 | 0 | 0 | 30.8435
3345 | 0 | 1.935 | 1.7582 | 27.2138 | 12.8122 | 43.7192 | 0 | 0 | 40.026
3346 | 0 | 1.7177 | 1.4747 | 32.9117 | 9.758 | 45.8621 | 0 | 0 | 42.6697
3347 | 0 | 1.6472 | 1.8335 | 34.2637 | 22.2246 | 59.969 | 0 | 0 | 56.4883
3348 | 0 | 1.7555 | 2.0907 | 35.0734 | 27.7855 | 66.7052 | 0 | 0 | 62.8589
3349 | 0 | 1.7455 | 2.2196 | 29.9533 | 14.0268 | 47.9452 | 0 | 0 | 43.9801
3350 | 0 | 1.7358 | 2.2605 | 38.6341 | 12.1645 | 54.7948 | 0 | 0 | 50.7985
3351 | 0 | 1.5909 | 2.1706 | 30.3665 | 14.8226 | 48.9507 | 0 | 0 | 45.1892
3352 | 0 | 1.7105 | 2.1677 | 16.6669 | 8.362 | 28.9071 | 0 | 0 | 25.0289
3353 | 0 | 1.9073 | 2.1706 | 30.494 | 19.3725 | 53.9445 | 0 | 0 | 49.8665
3354 | 0 | 1.7189 | 1.5167 | 30.154 | 18.7327 | 52.1223 | 0 | 0 | 48.8867
3355 | 0 | 1.6825 | 1.4117 | 38.583 | 2.9186 | 44.5959 | 0 | 0 | 41.5016
3356 | 0 | 1.587 | 1.1486 | 36.6741 | 0 | 39.4097 | 0 | 0 | 36.6741
3357 | 0 | 1.5699 | 1.2344 | 28.9616 | 0 | 31.7658 | 0 | 0 | 28.9616
3358 | 0 | 1.4934 | 1.1264 | 33.7395 | 0 | 36.3593 | 0 | 0 | 33.7395
3359 | 0 | 1.8961 | 1.1609 | 26.6979 | 0 | 29.7549 | 0 | 0 | 26.6979
3360 | 0 | 1.8555 | 1.1591 | 26.6732 | 0 | 29.6879 | 0 | 0 | 26.6732
3361 | 0 | 1.834 | 2.1636 | 32.8984 | 0 | 36.896 | 0 | 0 | 32.8984
3362 | 0 | 1.9014 | 1.767 | 23.7404 | 0 | 27.4087 | 0 | 0 | 23.7404
3363 | 0 | 1.5023 | 2.6204 | 31.559 | 0 | 35.6817 | 0 | 0 | 31.559
3364 | 0 | 1.9122 | 2.6397 | 33.4525 | 0 | 38.0044 | 0 | 0 | 33.4525
3365 | 0 | 1.5884 | 2.3626 | 36.0945 | 0 | 40.0455 | 0 | 0 | 36.0945
3366 | 0 | 1.7045 | 1.8189 | 28.9339 | 0 | 32.4572 | 0 | 0 | 28.9339
3367 | 0 | 1.8118 | 1.9431 | 24.7975 | 0 | 28.5524 | 0 | 0 | 24.7975
3368 | 0 | 1.9713 | 1.9321 | 32.9181 | 9.645 | 46.4665 | 0 | 0 | 42.5631
3369 | 0 | 1.9554 | 1.7582 | 25.9168 | 17.5253 | 47.1557 | 0 | 0 | 43.4421
3370 | 0 | 1.8998 | 1.4747 | 31.8897 | 7.8679 | 43.1322 | 0 | 0 | 39.7577
3371 | 0 | 1.9301 | 1.8335 | 36.7481 | 15.9921 | 56.5038 | 0 | 0 | 52.7402
3372 | 0 | 1.661 | 2.0907 | 37.0256 | 13.3027 | 54.08 | 0 | 0 | 50.3283
3373 | 0 | 1.5811 | 2.2196 | 34.0023 | 13.6896 | 51.4927 | 0 | 0 | 47.6919
3374 | 0 | 1.9902 | 2.2605 | 31.392 | 3.2824 | 38.9251 | 0 | 0 | 34.6744
3375 | 0 | 1.8252 | 2.1706 | 33.9314 | 17.5164 | 55.4437 | 200 | 0 | 251.4478
3376 | 0 | 1.7407 | 2.1677 | 25.9389 | 9.5392 | 39.3865 | 0 | 0 | 35.4781
3377 | 0 | 1.8516 | 2.1706 | 30.3378 | 8.0704 | 42.4304 | 0 | 0 | 38.4082
3378 | 0 | 1.5977 | 1.5861 | 23.0219 | 19.9696 | 46.1754 | 0 | 0 | 42.9915
3379 | 0 | 1.6008 | 1.239 | 23.1668 | 12.534 | 38.5407 | 0 | 0 | 35.7009
3380 | 0 | 1.5668 | 1.0185 | 29.3203 | 0 | 31.9056 | 0 | 0 | 29.3203
3381 | 0 | 1.7012 | 1.0722 | 30.6894 | 0 | 33.4629 | 0 | 0 | 30.6894
3382 | 0 | 1.9163 | 1.1947 | 32.04 | 0 | 35.151 | 0 | 0 | 32.04
3383 | 0 | 1.2829 | 1.2542 | 29.9065 | 0 | 32.4436 | 0 | 0 | 29.9065
3384 | 0 | 1.6459 | 2.7569 | 30.9515 | 0 | 35.3543 | 0 | 0 | 30.9515
3385 | 0 | 1.9293 | 4.3028 | 29.2278 | 0 | 35.4599 | 0 | 0 | 29.2278
3386 | 0 | 1.6301 | 3.0702 | 30.8129 | 0 | 35.5131 | 0 | 0 | 30.8129
3387 | 0 | 2.0585 | 2.3713 | 26.1858 | 0 | 30.6156 | 0 | 0 | 26.1858
3388 | 6.3184 | 1.6749 | 2.2727 | 39.1256 | 0 | 49.3917 | 0 | 0 | 45.444
3389 | 36.0437 | 1.7649 | 2.0277 | 24.5329 | 0 | 64.3693 | 0 | 0 | 60.5766
3390 | 52.5929 | 1.7922 | 1.8545 | 28.2009 | 0 | 84.4405 | 0 | 0 | 80.7938
3391 | 25.373 | 1.6367 | 1.8626 | 24.8128 | 0 | 53.6852 | 0 | 0 | 50.1859
3392 | 0 | 1.2261 | 1.8002 | 38.0686 | 19.6038 | 60.6988 | 0 | 0 | 57.6724
3393 | 6.914 | 1.914 | 1.7611 | 35.5129 | 9.0329 | 55.135 | 0 | 0 | 51.4598
3394 | 41.4322 | 1.9392 | 1.7681 | 31.8801 | 25.3223 | 102.342 | 0 | 0 | 98.6346
3395 | 50.3477 | 1.7173 | 1.3773 | 25.2 | 6.3338 | 84.9762 | 0 | 0 | 81.8815
3396 | 22.7454 | 1.6134 | 2.3299 | 26.0101 | 10.1535 | 62.8524 | 0 | 0 | 58.9091
3397 | 0 | 2.2831 | 2.3888 | 32.7355 | 15.2543 | 52.6616 | 0 | 0 | 47.9897
3398 | 0 | 1.753 | 2.0295 | 28.1002 | 12.0194 | 43.902 | 0 | 0 | 40.1196
3399 | 0 | 1.761 | 1.9886 | 24.9891 | 15.325 | 44.0637 | 0 | 0 | 40.3141
3400 | 0 | 1.6562 | 2.2272 | 29.461 | 15.0805 | 48.4249 | 0 | 0 | 44.5415
3401 | 0 | 1.3854 | 2.1199 | 37.5736 | 25.5232 | 66.6022 | 0 | 0 | 63.0969
3402 | 0 | 1.9512 | 1.5861 | 32.3931 | 14.1873 | 50.1177 | 0 | 0 | 46.5804
3403 | 0 | 1.3937 | 1.239 | 30.727 | 19.609 | 52.9688 | 0 | 0 | 50.336
3404 | 0 | 1.6994 | 1.0185 | 26.7798 | 0 | 29.4977 | 0 | 0 | 26.7798
3405 | 0 | 1.4941 | 1.0722 | 27.5845 | 0 | 30.1508 | 0 | 0 | 27.5845
3406 | 0 | 1.9205 | 1.1947 | 32.4132 | 0 | 35.5284 | 0 | 0 | 32.4132
3407 | 0 | 1.9606 | 1.2542 | 35.1967 | 0 | 38.4115 | 0 | 0 | 35.1967
3408 | 0 | 1.8678 | 2.7569 | 29.8266 | 0 | 34.4513 | 0 | 0 | 29.8266
3409 | 0 | 1.5544 | 4.3028 | 25.5663 | 0 | 31.4235 | 0 | 0 | 25.5663
3410 | 0 | 1.6421 | 3.0702 | 30.5039 | 0 | 35.2161 | 0 | 0 | 30.5039
3411 | 0 | 1.6482 | 2.3713 | 27.158 | 0 | 31.1775 | 0 | 200 | 227.158
3412 | 10.3094 | 1.8187 | 2.2727 | 31.6455 | 0 | 46.0463 | 0 | 0 | 41.9549
3413 | 42.2031 | 1.7007 | 2.0277 | 32.619 | 0 | 78.5506 | 0 | 0 | 74.8221
3414 | 54.564 | 1.5031 | 1.8545 | 29.7613 | 0 | 87.6829 | 0 | 0 | 84.3253
3415 | 17.4491 | 1.7035 | 1.8626 | 23.2805 | 0 | 44.2958 | 0 | 0 | 40.7297
3416 | 2.4353 | 1.6734 | 1.8002 | 34.7561 | 23.9092 | 64.5742 | 0 | 0 | 61.1006
3417 | 14.3135 | 1.7615 | 1.7611 | 38.807 | 16.9249 | 73.568 | 0 | 0 | 70.0453
3418 | 32.7336 | 1.7047 | 1.7681 | 31.9574 | 15.0121 | 83.1759 | 0 | 0 | 79.7031
3419 | 11.587 | 1.7443 | 1.3773 | 31.911 | 14.472 | 61.0917 | 0 | 0 | 57.97
3420 | 35.1949 | 1.7091 | 2.3299 | 32.1038 | 14.377 | 85.7148 | 0 | 0 | 81.6758
3421 | 18.2022 | 1.7631 | 2.3888 | 27.1283 | 7.2751 | 56.7575 | 0 | 0 | 52.6056
3422 | 0 | 1.9734 | 2.0295 | 31.5303 | 6.7788 | 42.312 | 0 | 0 | 38.3091
3423 | 0 | 1.662 | 1.9886 | 33.1925 | 4.0203 | 40.8635 | 0 | 0 | 37.2129
3424 | 0 | 1.4168 | 2.2272 | 33.3424 | 13.9439 | 50.9303 | 0 | 0 | 47.2863
3425 | 0 | 1.5293 | 2.1199 | 33.9148 | 18.5123 | 56.0763 | 0 | 0 | 52.4271
3426 | 0 | 2.0192 | 1.5861 | 33.1907 | 18.7807 | 55.5767 | 0 | 0 | 51.9714
3427 | 0 | 1.5728 | 1.239 | 29.0421 | 10.3337 | 42.1877 | 0 | 0 | 39.3758
3428 | 0 | 1.7995 | 1.0185 | 33.1127 | 0 | 35.9308 | 0 | 0 | 33.1127
3429 | 0 | 1.5885 | 1.0722 | 34.2423 | 0 | 36.903 | 0 | 0 | 34.2423
3430 | 0 | 1.8877 | 1.1947 | 22.7174 | 0 | 25.7998 | 0 | 0 | 22.7174
3431 | 0 | 2.0219 | 1.2542 | 32.5334 | 0 | 35.8095 | 0 | 0 | 32.5334
3432 | 0 | 1.7801 | 2.7569 | 32.7497 | 0 | 37.2868 | 0 | 0 | 32.7497
3433 | 0 | 1.866 | 4.3028 | 23.0275 | 0 | 29.1963 | 0 | 0 | 23.0275
3434 | 0 | 1.7957 | 3.0702 | 33.8662 | 0 | 38.732 | 0 | 0 | 33.8662
3435 | 0 | 1.6568 | 2.3713 | 23.7753 | 0 | 27.8034 | 0 | 0 | 23.7753
3436 | 0 | 1.5802 | 2.2727 | 36.5353 | 0 | 40.3882 | 0 | 0 | 36.5353
3437 | 19.3403 | 1.7302 | 2.0277 | 28.8424 | 0 | 51.9406 | 0 | 0 | 48.1827
3438 | 55.222 | 1.8368 | 1.8545 | 31.073 | 0 | 89.9863 | 0 | 0 | 86.2951
3439 | 29.3603 | 1.866 | 1.8626 | 26.4762 | 0 | 59.5652 | 0 | 0 | 55.8365
3440 | 8.3454 | 1.6204 | 1.8002 | 37.8475 | 23.1064 | 72.7199 | 0 | 0 | 69.2993
3441 | 0 | 1.5305 | 1.7611 | 23.9334 | 6.7712 | 33.9963 | 0 | 0 | 30.7046
3442 | 6.7995 | 1.8186 | 1.7681 | 26.7847 | 18.9032 | 56.0741 | 0 | 0 | 52.4874
3443 | 37.4911 | 1.7086 | 1.3773 | 30.3388 | 10.8898 | 81.8056 | 0 | 0 | 78.7198
3444 | 59.2637 | 1.6011 | 2.3299 | 31.2068 | 18.7219 | 113.1234 | 0 | 0 | 109.1924
3445 | 0.37879 | 1.6704 | 2.3888 | 20.3445 | 2.1976 | 26.9801 | 0 | 0 | 22.9209
3446 | 0 | 1.8855 | 2.0295 | 27.949 | 10.8707 | 42.7347 | 0 | 0 | 38.8197
3447 | 0 | 1.7038 | 1.9886 | 33.1877 | 10.5352 | 47.4154 | 0 | 0 | 43.723
3448 | 0 | 1.8246 | 2.2272 | 27.2051 | 14.6937 | 45.9507 | 0 | 0 | 41.8988
3449 | 0 | 1.9111 | 2.1199 | 19.4714 | 9.2155 | 32.7179 | 0 | 0 | 28.6869
3450 | 0 | 1.7655 | 1.5861 | 30.9227 | 19.0301 | 53.3044 | 0 | 0 | 49.9528
3451 | 0 | 1.9123 | 1.239 | 35.2178 | 13.4618 | 51.831 | 0 | 0 | 48.6797
3452 | 0 | 1.8135 | 1.0185 | 27.8005 | 0 | 30.6325 | 0 | 0 | 27.8005
3453 | 0 | 1.7038 | 1.0722 | 34.2164 | 0 | 36.9924 | 0 | 0 | 34.2164
3454 | 0 | 1.865 | 1.1947 | 23.9287 | 0 | 26.9883 | 0 | 0 | 23.9287
3455 | 0 | 1.5442 | 1.2542 | 34.513 | 0 | 37.3113 | 0 | 0 | 34.513
3456 | 0 | 1.9296 | 2.7569 | 31.7143 | 0 | 36.4008 | 0 | 0 | 31.7143
3457 | 0 | 1.8996 | 4.3028 | 30.101 | 0 | 36.3034 | 0 | 0 | 30.101
3458 | 0 | 1.6705 | 3.0702 | 31.2331 | 0 | 35.9738 | 0 | 0 | 31.2331
3459 | 0 | 1.8223 | 2.3713 | 32.3385 | 0 | 36.5321 | 0 | 0 | 32.3385
3460 | 0 | 1.5486 | 2.2727 | 33.2009 | 0 | 37.0223 | 0 | 0 | 33.2009
3461 | 5.9329 | 1.7071 | 2.0277 | 26.8055 | 0 | 36.4732 | 0 | 0 | 32.7384
3462 | 20.6041 | 1.3085 | 1.8545 | 31.31 | 0 | 55.0771 | 0 | 0 | 51.9141
3463 | 0 | 1.7964 | 1.8626 | 25.3458 | 0 | 29.0048 | 0 | 0 | 25.3458
3464 | 0 | 2.0608 | 1.8002 | 35.7435 | 8.9456 | 48.5501 | 0 | 0 | 44.6891
3465 | 0 | 1.8319 | 1.7611 | 28.5246 | 12.8432 | 44.9608 | 0 | 0 | 41.3678
3466 | 0 | 1.7663 | 1.7681 | 31.0116 | 19.3629 | 53.909 | 0 | 0 | 50.3746
3467 | 0 | 1.7498 | 1.3773 | 28.6393 | 21.4519 | 53.2182 | 0 | 0 | 50.0911
3468 | 0 | 1.4765 | 2.3299 | 30.6505 | -2.2957 | 32.1613 | 0 | 0 | 28.3548
3469 | 0 | 1.8425 | 2.3888 | 30.9246 | 8.1197 | 43.2756 | 0 | 0 | 39.0443
3470 | 0 | 1.6994 | 2.0295 | 36.6856 | 11.5424 | 51.9569 | 0 | 0 | 48.228
3471 | 0 | 1.431 | 1.9886 | 36.0086 | 12.6707 | 52.099 | 0 | 0 | 48.6793
3472 | 0 | 1.8376 | 2.2272 | 27.7893 | 9.1633 | 41.0175 | 0 | 0 | 36.9527
3473 | 0 | 1.7362 | 2.1199 | 29.9392 | 6.1423 | 39.9376 | 0 | 0 | 36.0815
3474 | 0 | 2.1834 | 1.9531 | 30.25 | 8.529 | 42.9154 | 0 | 0 | 38.779
3475 | 0 | 1.5819 | 1.5255 | 36.3291 | 3.9964 | 43.4329 | 0 | 0 | 40.3255
3476 | 0 | 1.6791 | 1.1504 | 31.6481 | 0 | 34.4776 | 0 | 0 | 31.6481
3477 | 0 | 1.5328 | 1.1994 | 26.1659 | 0 | 28.8981 | 0 | 0 | 26.1659
3478 | 0 | 1.3282 | 1.0675 | 25.216 | 0 | 27.6118 | 0 | 0 | 25.216
3479 | 0 | 1.6529 | 1.3615 | 25.5734 | 0 | 28.5878 | 0 | 0 | 25.5734
3480 | 0 | 1.7408 | 1.7973 | 25.4696 | 0 | 29.0078 | 0 | 0 | 25.4696
3481 | 0 | 1.8174 | 2.1992 | 32.045 | 0 | 36.0616 | 0 | 0 | 32.045
3482 | 0 | 1.7893 | 1.9945 | 31.7061 | 0 | 35.49 | 0 | 0 | 31.7061
3483 | 0 | 1.5102 | 3.6751 | 38.6412 | 0 | 43.8265 | 0 | 0 | 38.6412
3484 | 0 | 1.8554 | 3.2685 | 28.5821 | 0 | 33.706 | 0 | 0 | 28.5821
3485 | 0 | 1.764 | 2.6595 | 30.9078 | 0 | 35.3313 | 0 | 0 | 30.9078
3486 | 0 | 1.5777 | 2.1561 | 25.3358 | 0 | 29.0695 | 0 | 0 | 25.3358
3487 | 0 | 1.8686 | 1.9466 | 24.2277 | 0 | 28.043 | 0 | 0 | 24.2277
3488 | 0 | 1.749 | 1.9857 | 29.2398 | 10.696 | 43.6705 | 0 | 0 | 39.9358
3489 | 0 | 2.1627 | 1.7436 | 23.3113 | 19.0668 | 46.2844 | 0 | 0 | 42.3781
3490 | 0 | 1.374 | 1.9834 | 32.4779 | -4.5975 | 31.2377 | 0 | 0 | 27.8804
3491 | 0 | 1.615 | 2.2739 | 38.3522 | 3.4204 | 45.6615 | 200 | 0 | 241.7726
3492 | 0 | 1.9321 | 2.4752 | 32.1632 | 9.423 | 45.9934 | 0 | 0 | 41.5862
3493 | 0 | 1.4908 | 1.8702 | 26.3025 | 16.0175 | 45.6809 | 0 | 0 | 42.3199
3494 | 0 | 1.4155 | 2.2301 | 33.7009 | 20.1087 | 57.4553 | 0 | 0 | 53.8096
3495 | 0 | 1.8496 | 2.3118 | 29.9928 | 16.9168 | 51.071 | 0 | 0 | 46.9096
3496 | 0 | 1.6599 | 1.9 | 30.71 | 7.1706 | 41.4406 | 0 | 0 | 37.8807
3497 | 0 | 1.63 | 1.9367 | 32.8737 | 6.6034 | 43.0438 | 0 | 0 | 39.4771
3498 | 0 | 1.5842 | 1.5167 | 20.5381 | 13.3595 | 36.9984 | 0 | 0 | 33.8975
3499 | 0 | 1.7791 | 1.4117 | 30.466 | 20.1763 | 53.8331 | 0 | 0 | 50.6423
3500 | 0 | 1.7782 | 1.1486 | 27.042 | 0 | 29.9688 | 0 | 0 | 27.042
3501 | 0 | 1.8081 | 1.2344 | 28.7612 | 0 | 31.8036 | 0 | 0 | 28.7612
3502 | 0 | 1.9447 | 1.1264 | 29.4056 | 0 | 32.4767 | 0 | 0 | 29.4056
3503 | 0 | 1.7716 | 1.1609 | 36.5164 | 0 | 39.4489 | 0 | 0 | 36.5164
3504 | 0 | 1.7288 | 1.1591 | 31.7437 | 0 | 34.6316 | 0 | 0 | 31.7437
3505 | 0 | 1.4866 | 2.1636 | 25.8722 | 0 | 29.5225 | 0 | 0 | 25.8722
3506 | 0 | 1.3877 | 1.767 | 19.5028 | 0 | 22.6575 | 0 | 0 | 19.5028
3507 | 0 | 1.5326 | 2.6204 | 32.8111 | 0 | 36.9641 | 0 | 0 | 32.8111
3508 | 0 | 2.0772 | 2.6397 | 25.2329 | 0 | 29.9498 | 0 | 0 | 25.2329
3509 | 0 | 1.6409 | 2.3626 | 37.4751 | 0 | 41.4786 | 0 | 0 | 37.4751
3510 | 0 | 1.89 | 1.8189 | 31.5778 | 0 | 35.2867 | 0 | 0 | 31.5778
3511 | 0 | 1.5215 | 1.9431 | 25.9243 | 0 | 29.3889 | 0 | 0 | 25.9243
3512 | 0 | 1.7383 | 1.9321 | 32.0874 | 5.5075 | 41.2653 | 0 | 0 | 37.595
3513 | 0 | 1.6479 | 1.7582 | 24.8166 | 8.3527 | 36.5754 | 0 | 0 | 33.1692
3514 | 0 | 1.9843 | 1.4747 | 29.6608 | 19.522 | 52.6418 | 0 | 200 | 249.1828
3515 | 0 | 1.4855 | 1.8335 | 27.9789 | 17.1649 | 48.4629 | 0 | 0 | 45.1439
3516 | 0 | 1.5782 | 2.0907 | 28.9186 | 6.7767 | 39.3642 | 0 | 0 | 35.6953
3517 | 0 | 1.8131 | 2.2196 | 26.6027 | 13.874 | 44.5093 | 0 | 0 | 40.4766
3518 | 0 | 1.9332 | 2.2605 | 32.9587 | 24.4748 | 61.6273 | 0 | 0 | 57.4336
3519 | 0 | 1.474 | 2.1706 | 28.732 | 14.8269 | 47.2035 | 0 | 0 | 43.5589
3520 | 0 | 1.5736 | 2.1677 | 21.0562 | 5.4233 | 30.2209 | 0 | 0 | 26.4795
3521 | 0 | 1.7714 | 2.1706 | 23.0004 | 20.7295 | 47.6719 | 0 | 0 | 43.7299
3522 | 0 | 1.5661 | 1.5861 | 28.373 | 15.015 | 46.5403 | 0 | 0 | 43.388
3523 | 0 | 1.7845 | 1.239 | 32.8504 | 8.5051 | 44.379 | 0 | 0 | 41.3555
3524 | 0 | 2.0506 | 1.0185 | 19.5089 | 0 | 22.578 | 0 | 0 | 19.5089
3525 | 0 | 1.5814 | 1.0722 | 33.3631 | 0 | 36.0167 | 0 | 0 | 33.3631
3526 | 0 | 1.8641 | 1.1947 | 23.3456 | 0 | 26.4044 | 0 | 0 | 23.3456
3527 | 0 | 2.0933 | 1.2542 | 33.7885 | 0 | 37.136 | 0 | 0 | 33.7885
3528 | 0 | 1.7919 | 2.7569 | 31.8329 | 0 | 36.3817 | 0 | 0 | 31.8329
3529 | 0 | 1.8433 | 4.3028 | 32.5621 | 0 | 38.7083 | 0 | 0 | 32.5621
3530 | 0 | 1.8135 | 3.0702 | 24.4048 | 0 | 29.2885 | 0 | 0 | 24.4048
3531 | 0.63329 | 1.7222 | 2.3713 | 27.2386 | 0 | 31.9654 | 0 | 0 | 27.8719
3532 | 14.4574 | 1.952 | 2.2727 | 29.4541 | 0 | 48.1362 | 0 | 0 | 43.9114
3533 | 67.1751 | 1.8254 | 2.0277 | 22.4553 | 0 | 93.4835 | 0 | 0 | 89.6304
3534 | 100.2942 | 1.4771 | 1.8545 | 22.7741 | 0 | 126.3999 | 0 | 0 | 123.0683
3535 | 83.3651 | 1.7166 | 1.8626 | 27.9628 | 0 | 114.9072 | 0 | 0 | 111.3279
3536 | 15.3303 | 1.6171 | 1.8002 | 33.0801 | 16.642 | 68.4697 | 0 | 0 | 65.0524
3537 | 0 | 1.8534 | 1.7611 | 22.8221 | 21.7265 | 48.1631 | 0 | 0 | 44.5486
3538 | 0 | 1.5712 | 1.7681 | 31.1409 | 14.7687 | 49.2488 | 0 | 0 | 45.9095
3539 | 0 | 1.6936 | 1.3773 | 22.5297 | 11.6371 | 37.2376 | 0 | 0 | 34.1668
3540 | 0 | 1.8442 | 2.3299 | 21.1268 | 13.476 | 38.7768 | 0 | 0 | 34.6028
3541 | 0 | 1.7397 | 2.3888 | 32.6469 | 25.3469 | 62.1224 | 0 | 0 | 57.9939
3542 | 0 | 1.6583 | 2.0295 | 37.2564 | 2.5951 | 43.5393 | 0 | 0 | 39.8515
3543 | 0 | 1.7626 | 1.9886 | 32.8718 | 10.1909 | 46.8139 | 0 | 0 | 43.0627
3544 | 0 | 1.662 | 2.2272 | 29.2669 | 14.4155 | 47.5716 | 0 | 0 | 43.6824
3545 | 0 | 1.7063 | 2.1199 | 23.0629 | 14.7683 | 41.6574 | 0 | 0 | 37.8312
3546 | 0 | 1.8974 | 1.5861 | 33.9719 | 7.3692 | 44.8246 | 0 | 0 | 41.3411
3547 | 0 | 1.6056 | 1.239 | 30.1697 | 8.7278 | 41.7421 | 0 | 0 | 38.8975
3548 | 0 | 1.6038 | 1.0185 | 29.3553 | 0 | 31.9777 | 0 | 0 | 29.3553
3549 | 0 | 1.8777 | 1.0722 | 27.2934 | 0 | 30.2433 | 0 | 0 | 27.2934
3550 | 0 | 1.6045 | 1.1947 | 38.7809 | 0 | 41.5801 | 0 | 0 | 38.7809
3551 | 0 | 1.7384 | 1.2542 | 27.3134 | 0 | 30.306 | 0 | 0 | 27.3134
3552 | 0 | 1.716 | 2.7569 | 28.9982 | 0 | 33.4711 | 0 | 0 | 28.9982
3553 | 0 | 1.5807 | 4.3028 | 24.7892 | 0 | 30.6726 | 0 | 0 | 24.7892
3554 | 0 | 1.6671 | 3.0702 | 25.8895 | 0 | 30.6268 | 0 | 0 | 25.8895
3555 | 0.2554 | 1.4906 | 2.3713 | 32.0221 | 0 | 36.1395 | 0 | 0 | 32.2775
3556 | 18.0586 | 1.8582 | 2.2727 | 25.8344 | 0 | 48.0239 | 0 | 0 | 43.8929
3557 | 66.3023 | 1.9486 | 2.0277 | 32.0406 | 0 | 102.3193 | 0 | 0 | 98.343
3558 | 16.4369 | 1.745 | 1.8545 | 25.4926 | 0 | 45.5289 | 0 | 0 | 41.9294
3559 | 0 | 2.0053 | 1.8626 | 35.2141 | 0 | 39.082 | 0 | 0 | 35.2141
3560 | 0 | 1.8397 | 1.8002 | 33.7787 | 12.0774 | 49.496 | 0 | 0 | 45.8561
3561 | 0.84291 | 1.4301 | 1.7611 | 32.9878 | 15.5692 | 52.5912 | 0 | 0 | 49.3999
3562 | 3.7879 | 1.9759 | 1.7681 | 29.8112 | 16.764 | 54.1071 | 0 | 0 | 50.3631
3563 | 1.9942 | 1.5589 | 1.3773 | 32.4607 | 20.4662 | 57.8573 | 0 | 0 | 54.9211
3564 | 0 | 1.8184 | 2.3299 | 25.2561 | 9.778 | 39.1823 | 0 | 0 | 35.0341
3565 | 0 | 1.3975 | 2.3888 | 21.1047 | 9.1221 | 34.0132 | 0 | 0 | 30.2268
3566 | 0 | 1.9579 | 2.0295 | 29.349 | 6.9342 | 40.2706 | 0 | 0 | 36.2832
3567 | 0 | 2.0172 | 1.9886 | 35.2181 | 10.005 | 49.2289 | 0 | 0 | 45.2231
3568 | 0 | 1.5586 | 2.2272 | 31.7702 | 10.1392 | 45.6953 | 0 | 0 | 41.9095
3569 | 0 | 1.5092 | 2.1199 | 32.2462 | 13.86 | 49.7353 | 0 | 0 | 46.1062
3570 | 0 | 1.8179 | 1.5861 | 27.4523 | 11.7131 | 42.5694 | 0 | 0 | 39.1654
3571 | 0 | 1.7888 | 1.239 | 28.9695 | 15.0008 | 46.9982 | 0 | 0 | 43.9703
3572 | 0 | 1.8426 | 1.0185 | 32.7437 | 0 | 35.6049 | 0 | 0 | 32.7437
3573 | 0 | 1.8402 | 1.0722 | 30.24 | 0 | 33.1523 | 0 | 0 | 30.24
3574 | 0 | 1.8805 | 1.1947 | 27.4799 | 0 | 30.5551 | 0 | 0 | 27.4799
3575 | 0 | 1.6499 | 1.2542 | 31.0566 | 0 | 33.9607 | 0 | 0 | 31.0566
3576 | 0 | 1.7301 | 2.7569 | 29.1846 | 0 | 33.6716 | 0 | 0 | 29.1846
3577 | 0 | 1.8646 | 4.3028 | 37.3406 | 0 | 43.508 | 0 | 0 | 37.3406
3578 | 0 | 1.8167 | 3.0702 | 27.8151 | 0 | 32.702 | 0 | 0 | 27.8151
3579 | 0 | 1.8442 | 2.3713 | 30.5539 | 0 | 34.7694 | 0 | 0 | 30.5539
3580 | 3.1729 | 2.0262 | 2.2727 | 29.555 | 0 | 37.0269 | 0 | 0 | 32.7279
3581 | 28.925 | 1.759 | 2.0277 | 35.432 | 0 | 68.1437 | 0 | 0 | 64.357
3582 | 74.653 | 1.6846 | 1.8545 | 25.2993 | 0 | 103.4914 | 0 | 0 | 99.9523
3583 | 31.4875 | 1.8602 | 1.8626 | 34.2625 | 0 | 69.4728 | 0 | 0 | 65.75
3584 | 11.4312 | 1.3726 | 1.8002 | 34.17 | 21.3349 | 70.1089 | 0 | 0 | 66.9361
3585 | 49.9013 | 1.7364 | 1.7611 | 35.3869 | 19.4201 | 108.2059 | 0 | 0 | 104.7083
3586 | 19.5548 | 1.9532 | 1.7681 | 28.9363 | 14.8998 | 67.1122 | 0 | 0 | 63.3909
3587 | 0 | 1.6151 | 1.3773 | 31.7931 | 14.8026 | 49.5881 | 0 | 0 | 46.5957
3588 | 0 | 1.9595 | 2.3299 | 38.3798 | 10.6662 | 53.3354 | 0 | 0 | 49.046
3589 | 0 | 1.6182 | 2.3888 | 31.3008 | 5.8822 | 41.1901 | 0 | 0 | 37.183
3590 | 0 | 1.5482 | 2.0295 | 34.7192 | 6.2319 | 44.5288 | 0 | 0 | 40.9511
3591 | 0 | 1.4396 | 1.9886 | 32.3923 | 21.3544 | 57.1749 | 0 | 0 | 53.7467
3592 | 0 | 1.7983 | 2.2272 | 32.2536 | 13.8677 | 50.1468 | 0 | 0 | 46.1212
3593 | 0 | 1.5792 | 2.1199 | 27.7992 | 6.7384 | 38.2367 | 0 | 0 | 34.5376
3594 | 0 | 1.6692 | 1.5861 | 24.2958 | 13.6189 | 41.17 | 0 | 0 | 37.9147
3595 | 0 | 1.6341 | 1.239 | 27.6651 | 13.1638 | 43.702 | 0 | 0 | 40.8289
3596 | 0 | 1.836 | 1.0185 | 36.1802 | 0 | 39.0347 | 0 | 0 | 36.1802
3597 | 0 | 1.5505 | 1.0722 | 33.1545 | 0 | 35.7772 | 0 | 0 | 33.1545
3598 | 0 | 1.5456 | 1.1947 | 32.9589 | 0 | 35.6992 | 0 | 0 | 32.9589
3599 | 0 | 1.7047 | 1.2542 | 25.182 | 0 | 28.141 | 0 | 0 | 25.182
3600 | 0 | 1.4936 | 2.7569 | 30.5857 | 0 | 34.8362 | 0 | 0 | 30.5857
3601 | 0 | 1.7878 | 4.3028 | 32.9188 | 0 | 39.0094 | 0 | 0 | 32.9188
3602 | 0 | 1.4842 | 3.0702 | 27.5558 | 0 | 32.1101 | 0 | 0 | 27.5558
3603 | 0 | 1.9538 | 2.3713 | 26.3904 | 0 | 30.7155 | 0 | 0 | 26.3904
3604 | 4.2544 | 1.9598 | 2.2727 | 34.7411 | 0 | 43.2281 | 0 | 0 | 38.9956
3605 | 35.3484 | 1.5456 | 2.0277 | 26.979 | 0 | 65.9007 | 0 | 0 | 62.3274
3606 | 86.4046 | 1.7322 | 1.8545 | 27.5846 | 0 | 117.5759 | 0 | 0 | 113.9892
3607 | 44.1638 | 1.853 | 1.8626 | 31.2081 | 0 | 79.0875 | 200 | 0 | 275.3719
3608 | 0.57792 | 1.4465 | 1.8002 | 27.5943 | 12.3967 | 43.8156 | 0 | 0 | 40.5689
3609 | 0 | 1.5035 | 1.7611 | 35.2319 | 11.5887 | 50.0852 | 0 | 0 | 46.8206
3610 | 0 | 1.8496 | 1.7681 | 24.5892 | 16.421 | 44.6279 | 0 | 0 | 41.0102
3611 | 0 | 1.6305 | 1.3773 | 24.4932 | 13.3 | 40.801 | 0 | 0 | 37.7932
3612 | 0 | 1.7639 | 2.3299 | 23.6226 | 18.0613 | 45.7777 | 0 | 0 | 41.6839
3613 | 0 | 1.8315 | 2.3888 | 32.2226 | 15.4934 | 51.9364 | 0 | 0 | 47.716
3614 | 0 | 1.6473 | 2.0295 | 34.6615 | 8.7649 | 47.1032 | 0 | 200 | 243.4264
3615 | 0 | 1.8736 | 1.9886 | 25.7026 | 13.4541 | 43.0189 | 0 | 0 | 39.1566
3616 | 0 | 1.8683 | 2.2272 | 31.3369 | 5.1451 | 40.5776 | 0 | 0 | 36.482
3617 | 0 | 1.7143 | 2.1199 | 28.6716 | 10.6443 | 43.1501 | 0 | 0 | 39.3159
3618 | 0 | 1.6548 | 1.5861 | 34.6047 | 9.3274 | 47.173 | 0 | 0 | 43.9321
3619 | 0 | 1.7696 | 1.239 | 35.3296 | 16.9286 | 55.2669 | 0 | 0 | 52.2583
3620 | 0 | 1.6284 | 1.0185 | 39.4351 | 0 | 42.082 | 0 | 0 | 39.4351
3621 | 0 | 1.6847 | 1.0722 | 21.0495 | 0 | 23.8064 | 0 | 0 | 21.0495
3622 | 0 | 1.7341 | 1.1947 | 36.1539 | 0 | 39.0827 | 0 | 0 | 36.1539
3623 | 0 | 1.9658 | 1.2542 | 33.9292 | 0 | 37.1492 | 0 | 0 | 33.9292
3624 | 0 | 2.123 | 2.7569 | 36.547 | 0 | 41.4269 | 0 | 0 | 36.547
3625 | 0 | 2.7975 | 4.3028 | 28.4102 | 0 | 35.5105 | 0 | 0 | 28.4102
3626 | 0 | 2.8114 | 3.0702 | 30.0504 | 0 | 35.9319 | 0 | 0 | 30.0504
3627 | 0 | 2.2536 | 2.3713 | 30.167 | 0 | 34.7919 | 0 | 0 | 30.167
3628 | 12.6713 | 2.3652 | 2.2727 | 23.8098 | 0 | 41.1189 | 0 | 0 | 36.481
3629 | 46.5044 | 2.6133 | 2.0277 | 21.6899 | 0 | 72.8353 | 0 | 0 | 68.1943
3630 | 29.2349 | 2.8502 | 1.8545 | 29.2384 | 0 | 63.178 | 0 | 0 | 58.4733
3631 | 0 | 2.5716 | 1.8626 | 29.4824 | 0 | 33.9167 | 0 | 0 | 29.4824
3632 | 0 | 2.5162 | 1.8002 | 22.4831 | 21.9707 | 48.7701 | 0 | 0 | 44.4537
3633 | 2.9069 | 2.4704 | 1.7611 | 32.2938 | 11.3271 | 50.7594 | 0 | 0 | 46.5278
3634 | 9.066 | 2.1328 | 1.7681 | 22.694 | 15.7239 | 51.3848 | 0 | 0 | 47.4838
3635 | 1.9864 | 2.5616 | 1.3773 | 23.8092 | 21.0224 | 50.7569 | 0 | 0 | 46.818
3636 | 0 | 2.6522 | 2.3299 | 21.512 | 8.1837 | 34.6779 | 0 | 0 | 29.6957
3637 | 0 | 2.4959 | 2.3888 | 33.5709 | 10.5508 | 49.0064 | 0 | 0 | 44.1217
3638 | 0 | 2.9721 | 2.0295 | 30.1291 | 11.6405 | 46.7711 | 0 | 0 | 41.7695
3639 | 0 | 2.7842 | 1.9886 | 33.6434 | 16.3368 | 54.7529 | 0 | 0 | 49.9801
3640 | 0 | 2.8447 | 2.2272 | 37.5306 | 11.8198 | 54.4223 | 0 | 0 | 49.3504
3641 | 0 | 2.7574 | 2.1199 | 32.8563 | 14.6154 | 52.3489 | 0 | 0 | 47.4717
3642 | 0 | 2.6371 | 1.9531 | 27.9732 | 11.404 | 43.9672 | 0 | 0 | 39.3771
3643 | 0 | 2.373 | 1.5255 | 29.6516 | 8.0789 | 41.6289 | 0 | 0 | 37.7305
3644 | 0 | 2.446 | 1.1504 | 24.7697 | 0 | 28.366 | 0 | 0 | 24.7697
3645 | 0 | 2.6346 | 1.1994 | 28.356 | 0 | 32.19 | 0 | 0 | 28.356
3646 | 0 | 2.5364 | 1.0675 | 23.4645 | 0 | 27.0684 | 0 | 0 | 23.4645
3647 | 0 | 2.4221 | 1.3615 | 26.5969 | 0 | 30.3805 | 0 | 0 | 26.5969
3648 | 0 | 2.6904 | 1.7973 | 28.734 | 0 | 33.2217 | 0 | 0 | 28.734
3649 | 0 | 2.3573 | 2.1992 | 34.99 | 0 | 39.5465 | 0 | 0 | 34.99
3650 | 0 | 2.3552 | 1.9945 | 28.1898 | 0 | 32.5395 | 0 | 0 | 28.1898
3651 | 0 | 2.6137 | 3.6751 | 41.1431 | 0 | 47.4319 | 0 | 0 | 41.1431
3652 | 0 | 2.4853 | 3.2685 | 19.8151 | 0 | 25.5689 | 0 | 0 | 19.8151
3653 | 0 | 2.4806 | 2.6595 | 19.7992 | 0 | 24.9392 | 0 | 0 | 19.7992
3654 | 0 | 2.2936 | 2.1561 | 30.8269 | 0 | 35.2765 | 0 | 0 | 30.8269
3655 | 0 | 2.8294 | 1.9466 | 33.2924 | 0 | 38.0685 | 0 | 0 | 33.2924
3656 | 0 | 2.9361 | 1.9857 | 27.1629 | 28.3821 | 60.4668 | 0 | 0 | 55.5449
3657 | 0 | 2.5856 | 1.7436 | 33.1294 | 19.808 | 57.2666 | 0 | 0 | 52.9374
3658 | 0 | 1.9247 | 1.9834 | 29.5524 | 16.4203 | 49.8809 | 0 | 0 | 45.9727
3659 | 0 | 2.2174 | 2.2739 | 28.6302 | 16.823 | 49.9444 | 0 | 0 | 45.4531
3660 | 0 | 2.2741 | 2.4752 | 30.0317 | 17.2859 | 52.0669 | 0 | 0 | 47.3176
3661 | 0 | 2.9901 | 1.8702 | 17.6062 | 3.8746 | 26.3411 | 0 | 0 | 21.4808
3662 | 0 | 2.7261 | 2.2301 | 25.8159 | 19.723 | 50.4951 | 0 | 0 | 45.5389
3663 | 0 | 2.5333 | 2.3118 | 30.6567 | 9.0873 | 44.5891 | 0 | 0 | 39.744
3664 | 0 | 2.8947 | 1.9 | 33.5663 | 19.3932 | 57.7543 | 0 | 0 | 52.9596
3665 | 0 | 2.4593 | 1.9367 | 27.3836 | 18.1863 | 49.9659 | 0 | 0 | 45.5699
3666 | 0 | 2.2205 | 1.5167 | 27.7837 | 13.019 | 44.5399 | 0 | 0 | 40.8027
3667 | 0 | 2.1606 | 1.4117 | 28.5798 | 19.0724 | 51.2245 | 0 | 0 | 47.6522
3668 | 0 | 2.5466 | 1.1486 | 25.7166 | 0 | 29.4117 | 0 | 0 | 25.7166
3669 | 0 | 2.681 | 1.2344 | 23.747 | 0 | 27.6624 | 0 | 0 | 23.747
3670 | 0 | 2.402 | 1.1264 | 23.3517 | 0 | 26.8802 | 0 | 0 | 23.3517
3671 | 0 | 2.5901 | 1.1609 | 26.1737 | 0 | 29.9247 | 0 | 0 | 26.1737
3672 | 0 | 2.1381 | 1.1591 | 29.798 | 0 | 33.0953 | 0 | 0 | 29.798
3673 | 0 | 2.0784 | 2.1636 | 27.4331 | 0 | 31.6752 | 0 | 0 | 27.4331
3674 | 0 | 2.7237 | 1.767 | 28.031 | 0 | 32.5216 | 0 | 0 | 28.031
3675 | 0 | 2.7077 | 2.6204 | 23.8687 | 0 | 29.1968 | 0 | 0 | 23.8687
3676 | 0 | 2.2067 | 2.6397 | 23.9385 | 0 | 28.7848 | 0 | 0 | 23.9385
3677 | 0 | 2.6378 | 2.3626 | 22.4551 | 0 | 27.4554 | 0 | 0 | 22.4551
3678 | 0 | 2.2077 | 1.8189 | 29.192 | 0 | 33.2186 | 0 | 0 | 29.192
3679 | 0 | 2.158 | 1.9431 | 26.5923 | 0 | 30.6934 | 0 | 0 | 26.5923
3680 | 0 | 3.055 | 1.9321 | 30.2511 | 19.1752 | 54.4133 | 0 | 0 | 49.4262
3681 | 0 | 2.1829 | 1.7582 | 34.4876 | 11.3034 | 49.732 | 0 | 0 | 45.791
3682 | 0 | 2.4288 | 1.4747 | 23.5734 | 17.0176 | 44.4945 | 0 | 0 | 40.591
3683 | 0 | 2.8141 | 1.8335 | 28.1041 | 0.57026 | 33.322 | 0 | 0 | 28.6744
3684 | 0 | 3.2837 | 2.0907 | 26.9412 | 21.2705 | 53.5861 | 0 | 0 | 48.2117
3685 | 0 | 2.6609 | 2.2196 | 27.3813 | 17.2048 | 49.4666 | 0 | 0 | 44.586
3686 | 0 | 2.3066 | 2.2605 | 23.5364 | 10.0145 | 38.118 | 0 | 0 | 33.551
3687 | 0 | 2.7702 | 2.1706 | 28.6388 | 10.7294 | 44.309 | 0 | 0 | 39.3682
3688 | 0 | 2.7078 | 2.1677 | 22.2456 | 6.288 | 33.4091 | 0 | 0 | 28.5336
3689 | 0 | 2.4647 | 2.1706 | 25.4256 | 13.847 | 43.9079 | 0 | 0 | 39.2726
3690 | 0 | 2.2785 | 1.5861 | 32.9258 | 10.1238 | 46.9142 | 0 | 0 | 43.0496
3691 | 0 | 2.8196 | 1.239 | 26.0245 | 2.7547 | 32.8378 | 200 | 0 | 228.7791
3692 | 0 | 2.644 | 1.0185 | 33.6075 | 0 | 37.2701 | 0 | 0 | 33.6075
3693 | 0 | 2.3609 | 1.0722 | 23.2956 | 0 | 26.7287 | 0 | 0 | 23.2956
3694 | 0 | 3.1072 | 1.1947 | 28.4988 | 0 | 32.8007 | 0 | 0 | 28.4988
3695 | 0 | 2.8431 | 1.2542 | 24.6176 | 0 | 28.7149 | 0 | 0 | 24.6176
3696 | 0 | 2.6525 | 2.7569 | 26.784 | 0 | 32.1934 | 0 | 0 | 26.784
3697 | 0 | 2.7055 | 4.3028 | 24.1695 | 0 | 31.1778 | 0 | 0 | 24.1695
3698 | 0 | 2.9344 | 3.0702 | 39.3794 | 0 | 45.384 | 0 | 0 | 39.3794
3699 | 11.3434 | 2.8171 | 2.3713 | 28.5428 | 0 | 45.0747 | 0 | 0 | 39.8862
3700 | 65.9043 | 2.5574 | 2.2727 | 24.1599 | 0 | 94.8943 | 0 | 0 | 90.0641
3701 | 91.3708 | 2.8843 | 2.0277 | 25.0848 | 0 | 121.3676 | 0 | 0 | 116.4556
3702 | 87.6537 | 2.4949 | 1.8545 | 29.8869 | 0 | 121.89 | 0 | 0 | 117.5406
3703 | 76.8999 | 2.7057 | 1.8626 | 22.6353 | 0 | 104.1036 | 0 | 0 | 99.5352
3704 | 75.3518 | 1.8158 | 1.8002 | 29.6393 | 26.517 | 135.124 | 0 | 0 | 131.508
3705 | 82.8889 | 2.5416 | 1.7611 | 28.2197 | 23.1465 | 138.5579 | 0 | 0 | 134.2551
3706 | 44.66 | 2.6642 | 1.7681 | 22.5695 | 15.9582 | 87.62 | 0 | 0 | 83.1877
3707 | 41.3899 | 2.7045 | 1.3773 | 18.1472 | 14.3659 | 77.9848 | 0 | 0 | 73.903
3708 | 64.3105 | 3.0052 | 2.3299 | 26.3565 | 8.4394 | 104.4415 | 0 | 0 | 99.1064
3709 | 52.059 | 2.5174 | 2.3888 | 26.9288 | 10.4288 | 94.3228 | 0 | 0 | 89.4166
3710 | 19.8699 | 3.0918 | 2.0295 | 20.4647 | 20.5139 | 65.9698 | 0 | 0 | 60.8485
3711 | 0 | 2.684 | 1.9886 | 26.8995 | 20.2224 | 51.7945 | 0 | 0 | 47.1219
3712 | 0 | 2.5076 | 2.2272 | 32.6126 | 22.0957 | 59.4431 | 0 | 0 | 54.7083
3713 | 0 | 2.4306 | 2.1199 | 27.818 | 14.3343 | 46.7027 | 0 | 0 | 42.1523
3714 | 0 | 2.439 | 1.5861 | 20.4034 | -0.10496 | 24.3236 | 0 | 0 | 20.2985
3715 | 0 | 2.8006 | 1.239 | 28.8987 | 6.5274 | 39.4658 | 0 | 0 | 35.4261
3716 | 0 | 2.8982 | 1.0185 | 37.2616 | 0 | 41.1784 | 0 | 0 | 37.2616
3717 | 0 | 2.9907 | 1.0722 | 28.5476 | 0 | 32.6105 | 0 | 0 | 28.5476
3718 | 0 | 2.253 | 1.1947 | 25.4204 | 0 | 28.8681 | 0 | 200 | 225.4204
3719 | 0 | 2.4482 | 1.2542 | 28.6618 | 0 | 32.3642 | 0 | 0 | 28.6618
3720 | 0 | 2.6123 | 2.7569 | 22.0222 | 0 | 27.3914 | 0 | 0 | 22.0222
3721 | 0 | 2.5254 | 4.3028 | 33.0071 | 0 | 39.8352 | 0 | 0 | 33.0071
3722 | 0 | 3.1161 | 3.0702 | 31.3048 | 0 | 37.4911 | 0 | 0 | 31.3048
3723 | 0 | 2.6821 | 2.3713 | 33.1471 | 0 | 38.2005 | 0 | 0 | 33.1471
3724 | 0 | 2.2225 | 2.2727 | 24.8334 | 0 | 29.3287 | 0 | 0 | 24.8334
3725 | 9.5491 | 2.7659 | 2.0277 | 32.7404 | 0 | 47.0832 | 0 | 0 | 42.2895
3726 | 43.649 | 2.6053 | 1.8545 | 26.3523 | 0 | 74.4611 | 0 | 0 | 70.0013
3727 | 74.855 | 3.0088 | 1.8626 | 31.3647 | 0 | 111.0912 | 0 | 0 | 106.2198
3728 | 101.1226 | 2.2627 | 1.8002 | 28.2811 | 10.9056 | 144.3723 | 0 | 0 | 140.3093
3729 | 71.4911 | 2.5082 | 1.7611 | 33.4112 | 13.1399 | 122.3115 | 0 | 0 | 118.0421
3730 | 69.5395 | 2.5284 | 1.7681 | 23.5628 | 12.4882 | 109.8871 | 0 | 0 | 105.5905
3731 | 72.2259 | 2.7105 | 1.3773 | 27.7586 | 9.2021 | 113.2744 | 0 | 0 | 109.1866
3732 | 70.2912 | 2.4085 | 2.3299 | 31.1998 | 6.0353 | 112.2648 | 0 | 0 | 107.5264
3733 | 61.8555 | 2.4769 | 2.3888 | 33.3208 | 4.9559 | 104.9979 | 0 | 0 | 100.1322
3734 | 5.2828 | 2.608 | 2.0295 | 26.8173 | 15.3517 | 52.0893 | 0 | 0 | 47.4518
3735 | 0 | 2.1546 | 1.9886 | 25.3532 | 14.4009 | 43.8974 | 0 | 0 | 39.7541
3736 | 0 | 2.3698 | 2.2272 | 25.4806 | 25.6169 | 55.6945 | 0 | 0 | 51.0975
3737 | 0 | 2.4712 | 2.1199 | 33.8905 | 9.7566 | 48.2382 | 0 | 0 | 43.6471
3738 | 0 | 2.6979 | 1.5861 | 17.8432 | 13.7268 | 35.8541 | 0 | 0 | 31.57
3739 | 0 | 2.6194 | 1.239 | 18.992 | 16.9278 | 39.7783 | 0 | 0 | 35.9198
3740 | 0 | 2.8457 | 1.0185 | 25.2131 | 0 | 29.0773 | 0 | 0 | 25.2131
3741 | 0 | 2.5113 | 1.0722 | 27.1905 | 0 | 30.7741 | 0 | 0 | 27.1905
3742 | 0 | 2.4655 | 1.1947 | 27.6369 | 0 | 31.2971 | 0 | 0 | 27.6369
3743 | 0 | 2.539 | 1.2542 | 23.7851 | 0 | 27.5783 | 0 | 0 | 23.7851
3744 | 0 | 2.4203 | 2.7569 | 28.2094 | 0 | 33.3866 | 0 | 0 | 28.2094
3745 | 0 | 2.4181 | 4.3028 | 27.3746 | 0 | 34.0955 | 0 | 0 | 27.3746
3746 | 0 | 2.6683 | 3.0702 | 26.3373 | 0 | 32.0758 | 0 | 0 | 26.3373
3747 | 0 | 2.5674 | 2.3713 | 29.0654 | 0 | 34.0041 | 0 | 0 | 29.0654
3748 | 0 | 2.7859 | 2.2727 | 21.1074 | 0 | 26.166 | 0 | 0 | 21.1074
3749 | 8.7572 | 2.9009 | 2.0277 | 26.122 | 0 | 39.8078 | 0 | 0 | 34.8792
3750 | 42.4855 | 2.8605 | 1.8545 | 35.4016 | 0 | 82.6021 | 0 | 0 | 77.8871
3751 | 70.1144 | 2.5109 | 1.8626 | 29.9058 | 0 | 104.3937 | 0 | 0 | 100.0202
3752 | 90.7966 | 2.7384 | 1.8002 | 21.4866 | 12.9185 | 129.7403 | 0 | 0 | 125.2017
3753 | 67.214 | 2.4418 | 1.7611 | 31.8004 | 25.1634 | 128.3807 | 0 | 0 | 124.1778
3754 | 22.7021 | 2.5747 | 1.7681 | 29.3773 | 14.7597 | 71.1819 | 0 | 0 | 66.8391
3755 | 5.0077 | 2.5601 | 1.3773 | 23.8613 | 17.9958 | 50.8021 | 0 | 0 | 46.8648
3756 | 16.5801 | 2.4738 | 2.3299 | 23.8776 | 21.3936 | 66.6549 | 0 | 0 | 61.8512
3757 | 4.0854 | 2.4586 | 2.3888 | 19.6095 | 10.1633 | 38.7056 | 0 | 0 | 33.8581
3758 | 0 | 2.3136 | 2.0295 | 23.0767 | 3.2654 | 30.6852 | 0 | 0 | 26.3421
3759 | 0 | 2.0929 | 1.9886 | 31.182 | -3.4114 | 31.8522 | 0 | 0 | 27.7706
3760 | 0 | 3.0364 | 2.2272 | 34.7545 | 19.8741 | 59.8922 | 0 | 0 | 54.6286
3761 | 0 | 2.7166 | 2.1199 | 25.9241 | 7.1148 | 37.8755 | 0 | 0 | 33.0389
3762 | 0 | 2.5503 | 1.5861 | 30.1714 | 20.4307 | 54.7386 | 0 | 0 | 50.6022
3763 | 0 | 2.8824 | 1.239 | 26.1644 | 25.2403 | 55.5261 | 0 | 0 | 51.4047
3764 | 0 | 2.5791 | 1.0185 | 30.5809 | 0 | 34.1785 | 0 | 0 | 30.5809
3765 | 0 | 2.0744 | 1.0722 | 31.9952 | 0 | 35.1418 | 0 | 0 | 31.9952
3766 | 0 | 2.2831 | 1.1947 | 28.3854 | 0 | 31.8632 | 0 | 0 | 28.3854
3767 | 0 | 2.4322 | 1.2542 | 30.0901 | 0 | 33.7765 | 0 | 0 | 30.0901
3768 | 0 | 2.6491 | 2.7569 | 25.4308 | 0 | 30.8369 | 200 | 0 | 225.4308
3769 | 0 | 2.9025 | 4.3028 | 23.2696 | 0 | 30.4749 | 0 | 0 | 23.2696
3770 | 0 | 2.3207 | 3.0702 | 24.7776 | 0 | 30.1685 | 0 | 0 | 24.7776
3771 | 2.2295 | 2.854 | 2.3713 | 28.8609 | 0 | 36.3157 | 0 | 0 | 31.0904
3772 | 22.4454 | 2.4521 | 2.2727 | 24.9985 | 0 | 52.1688 | 0 | 0 | 47.4439
3773 | 81.4914 | 2.7865 | 2.0277 | 25.7395 | 0 | 112.0451 | 0 | 0 | 107.2309
3774 | 74.6565 | 2.4752 | 1.8545 | 29.2563 | 0 | 108.2424 | 0 | 0 | 103.9127
3775 | 83.2966 | 2.3813 | 1.8626 | 29.1193 | 0 | 116.6597 | 0 | 0 | 112.4158
3776 | 96.3249 | 2.4864 | 1.8002 | 27.7197 | 12.099 | 140.4302 | 0 | 0 | 136.1435
3777 | 60.455 | 2.4001 | 1.7611 | 21.6175 | 9.1379 | 95.3717 | 0 | 0 | 91.2104
3778 | 63.9531 | 2.3585 | 1.7681 | 19.8604 | 9.6967 | 97.6368 | 0 | 0 | 93.5102
3779 | 70.3393 | 2.6278 | 1.3773 | 40.3712 | 11.4542 | 126.1698 | 0 | 0 | 122.1647
3780 | 59.6143 | 2.0955 | 2.3299 | 26.3797 | 14.7669 | 105.1863 | 0 | 0 | 100.7609
3781 | 0 | 2.4062 | 2.3888 | 28.2347 | 20.3429 | 53.3726 | 0 | 0 | 48.5776
3782 | 0 | 2.3391 | 2.0295 | 26.2982 | 17.3973 | 48.0641 | 0 | 0 | 43.6955
3783 | 0 | 2.7503 | 1.9886 | 34.2249 | 7.7892 | 46.753 | 0 | 0 | 42.0141
3784 | 0 | 2.63 | 2.2272 | 31.7818 | 7.8418 | 44.4809 | 0 | 0 | 39.6236
3785 | 0 | 2.4058 | 2.1199 | 28.7637 | 20.3172 | 53.6065 | 0 | 0 | 49.0809
3786 | 0 | 2.2424 | 1.5861 | 30.4718 | 29.8396 | 64.1399 | 0 | 0 | 60.3114
3787 | 0 | 2.3281 | 1.239 | 27.9637 | 6.6483 | 38.1791 | 0 | 0 | 34.6119
3788 | 0 | 2.8205 | 1.0185 | 27.8641 | 0 | 31.7032 | 0 | 0 | 27.8641
3789 | 0 | 2.5981 | 1.0722 | 33.0486 | 0 | 36.7189 | 0 | 0 | 33.0486
3790 | 0 | 2.5119 | 1.1947 | 32.3529 | 0 | 36.0596 | 0 | 0 | 32.3529
3791 | 0 | 2.4057 | 1.2542 | 26.9459 | 0 | 30.6058 | 0 | 0 | 26.9459
3792 | 0 | 2.708 | 2.7569 | 26.7567 | 0 | 32.2216 | 0 | 0 | 26.7567
3793 | 0 | 2.6292 | 4.3028 | 36.3011 | 0 | 43.2331 | 0 | 0 | 36.3011
3794 | 0 | 2.6708 | 3.0702 | 26.7721 | 0 | 32.5131 | 0 | 0 | 26.7721
3795 | 0 | 2.6036 | 2.3713 | 33.648 | 0 | 38.6229 | 0 | 0 | 33.648
3796 | 7.7178 | 3.2211 | 2.2727 | 25.2943 | 0 | 38.506 | 0 | 0 | 33.0121
3797 | 37.0557 | 2.6879 | 2.0277 | 29.9807 | 0 | 71.752 | 0 | 0 | 67.0364
3798 | 25.1199 | 2.4118 | 1.8545 | 34.3948 | 0 | 63.781 | 0 | 0 | 59.5147
3799 | 0 | 2.3489 | 1.8626 | 26.4023 | 0 | 30.6138 | 0 | 0 | 26.4023
3800 | 0 | 3.0693 | 1.8002 | 31.1224 | 12.9741 | 48.9661 | 0 | 0 | 44.0966
3801 | 0 | 2.6699 | 1.7611 | 31.383 | 12.7976 | 48.6117 | 0 | 0 | 44.1806
3802 | 4.2288 | 2.6187 | 1.7681 | 34.6402 | 12.9623 | 56.218 | 0 | 0 | 51.8312
3803 | 10.282 | 2.3977 | 1.3773 | 23.3465 | 18.0066 | 55.41 | 0 | 0 | 51.6351
3804 | 0 | 2.5048 | 2.3299 | 23.7326 | 12.888 | 41.4553 | 0 | 0 | 36.6206
3805 | 0 | 2.5925 | 2.3888 | 28.6216 | 17.706 | 51.309 | 0 | 0 | 46.3276
3806 | 0 | 2.3943 | 2.0295 | 30.5625 | 15.5278 | 50.5141 | 0 | 0 | 46.0903
3807 | 0 | 2.7526 | 1.9886 | 29.0925 | 24.9127 | 58.7464 | 0 | 0 | 54.0052
3808 | 0 | 2.733 | 2.2272 | 34.4223 | 9.5891 | 48.9717 | 0 | 0 | 44.0114
3809 | 0 | 2.494 | 2.1199 | 24.9094 | 17.0606 | 46.584 | 0 | 0 | 41.97
3810 | 0 | 2.6031 | 1.9531 | 28.1182 | 6.9743 | 39.6487 | 0 | 0 | 35.0925
3811 | 0 | 2.6851 | 1.5255 | 26.9752 | 22.5833 | 53.7691 | 0 | 0 | 49.5585
3812 | 0 | 2.4339 | 1.1504 | 29.6558 | 0 | 33.24 | 0 | 0 | 29.6558
3813 | 0 | 2.2323 | 1.1994 | 31.3391 | 0 | 34.7707 | 0 | 0 | 31.3391
3814 | 0 | 2.6859 | 1.0675 | 28.4209 | 0 | 32.1744 | 0 | 0 | 28.4209
3815 | 0 | 2.8676 | 1.3615 | 24.9064 | 0 | 29.1356 | 0 | 0 | 24.9064
3816 | 0 | 2.7716 | 1.7973 | 26.987 | 0 | 31.5559 | 0 | 0 | 26.987
3817 | 0 | 2.4995 | 2.1992 | 27.9988 | 0 | 32.6976 | 0 | 0 | 27.9988
3818 | 0 | 2.3214 | 1.9945 | 21.0422 | 0 | 25.358 | 0 | 200 | 221.0422
3819 | 0 | 2.7273 | 3.6751 | 17.4639 | 0 | 23.8663 | 0 | 0 | 17.4639
3820 | 0 | 2.5641 | 3.2685 | 26.3249 | 0 | 32.1575 | 0 | 0 | 26.3249
3821 | 0 | 2.3999 | 2.6595 | 23.5313 | 0 | 28.5907 | 0 | 0 | 23.5313
3822 | 0 | 2.3864 | 2.1561 | 32.0481 | 0 | 36.5906 | 0 | 0 | 32.0481
3823 | 0 | 2.3543 | 1.9466 | 21.8429 | 0 | 26.1438 | 0 | 0 | 21.8429
3824 | 0 | 2.6016 | 1.9857 | 26.1704 | 24.3784 | 55.1361 | 0 | 0 | 50.5488
3825 | 0 | 2.5269 | 1.7436 | 19.9922 | 16.5777 | 40.8406 | 0 | 0 | 36.57
3826 | 0 | 2.9713 | 1.9834 | 21.6128 | -0.25945 | 26.308 | 0 | 0 | 21.3533
3827 | 0 | 2.5867 | 2.2739 | 28.7586 | 11.8485 | 45.4678 | 0 | 0 | 40.6071
3828 | 0 | 2.787 | 2.4752 | 23.7227 | 4.4341 | 33.4189 | 0 | 0 | 28.1568
3829 | 0 | 2.6723 | 1.8702 | 21.4194 | 13.0024 | 38.9643 | 0 | 0 | 34.4218
3830 | 0 | 2.3273 | 2.2301 | 23.1314 | 15.5268 | 43.2156 | 0 | 0 | 38.6581
3831 | 0 | 2.1233 | 2.3118 | 28.5555 | 10.007 | 42.9975 | 0 | 0 | 38.5624
3832 | 0 | 2.7302 | 1.9 | 30.5657 | 15.728 | 50.9239 | 0 | 0 | 46.2937
3833 | 0 | 2.9423 | 1.9367 | 26.0279 | 5.1028 | 36.0097 | 0 | 0 | 31.1307
3834 | 0 | 2.34 | 1.5167 | 27.7773 | 22.7967 | 54.4307 | 0 | 0 | 50.574
3835 | 0 | 2.7711 | 1.4117 | 28.6206 | 13.2671 | 46.0705 | 0 | 0 | 41.8877
3836 | 0 | 2.3124 | 1.1486 | 29.5681 | 0 | 33.0291 | 0 | 0 | 29.5681
3837 | 0 | 2.3561 | 1.2344 | 31.4787 | 0 | 35.0693 | 0 | 0 | 31.4787
3838 | 0 | 2.9543 | 1.1264 | 27.5133 | 0 | 31.5941 | 0 | 0 | 27.5133
3839 | 0 | 2.4534 | 1.1609 | 29.1241 | 0 | 32.7384 | 0 | 0 | 29.1241
3840 | 0 | 2.6811 | 1.1591 | 33.6987 | 0 | 37.5389 | 0 | 0 | 33.6987
3841 | 0 | 2.7988 | 2.1636 | 33.1043 | 0 | 38.0668 | 0 | 0 | 33.1043
3842 | 0 | 2.6574 | 1.767 | 26.7437 | 0 | 31.1681 | 0 | 0 | 26.7437
3843 | 0 | 2.3882 | 2.6204 | 21.0322 | 0 | 26.0408 | 0 | 0 | 21.0322
3844 | 0 | 2.7805 | 2.6397 | 30.4131 | 0 | 35.8332 | 0 | 0 | 30.4131
3845 | 0 | 2.8224 | 2.3626 | 36.305 | 0 | 41.49 | 200 | 0 | 236.305
3846 | 0 | 3.035 | 1.8189 | 28.779 | 0 | 33.633 | 0 | 0 | 28.779
3847 | 0 | 2.1184 | 1.9431 | 27.4862 | 0 | 31.5477 | 0 | 0 | 27.4862
3848 | 0 | 2.4458 | 1.9321 | 20.9702 | 17.0368 | 42.3849 | 0 | 0 | 38.007
3849 | 0 | 2.8667 | 1.7582 | 23.9472 | 12.3558 | 40.9279 | 0 | 0 | 36.3029
3850 | 0 | 2.5826 | 1.4747 | 28.1783 | 10.843 | 43.0786 | 0 | 0 | 39.0213
3851 | 0 | 2.7883 | 1.8335 | 30.8178 | 27.1726 | 62.6122 | 0 | 0 | 57.9904
3852 | 0 | 2.3445 | 2.0907 | 24.1089 | 17.3585 | 45.9026 | 0 | 0 | 41.4674
3853 | 0 | 2.5248 | 2.2196 | 27.268 | 14.8637 | 46.8762 | 0 | 0 | 42.1317
3854 | 0 | 2.9515 | 2.2605 | 26.9367 | 17.4008 | 49.5495 | 0 | 0 | 44.3375
3855 | 0 | 2.4029 | 2.1706 | 26.2148 | 23.7823 | 54.5707 | 0 | 0 | 49.9971
3856 | 0 | 2.5289 | 2.1677 | 27.523 | 7.6113 | 39.831 | 0 | 0 | 35.1343
3857 | 0 | 2.5025 | 2.1706 | 31.9098 | 10.1398 | 46.7228 | 0 | 0 | 42.0496
3858 | 0 | 2.3971 | 1.5861 | 22.3757 | 17.8973 | 44.2563 | 0 | 0 | 40.273
3859 | 0 | 2.5375 | 1.239 | 31.6172 | 15.2365 | 50.6303 | 0 | 0 | 46.8537
3860 | 0 | 2.7173 | 1.0185 | 28.7741 | 0 | 32.51 | 0 | 0 | 28.7741
3861 | 0 | 2.7303 | 1.0722 | 27.3437 | 0 | 31.1463 | 0 | 0 | 27.3437
3862 | 0 | 2.5756 | 1.1947 | 24.375 | 0 | 28.1454 | 0 | 0 | 24.375
3863 | 0 | 2.3741 | 1.4759 | 29.9671 | 0 | 33.8171 | 0 | 0 | 29.9671
3864 | 0 | 2.3111 | 2.7569 | 34.4735 | 0 | 39.5414 | 0 | 0 | 34.4735
3865 | 0 | 2.8052 | 4.3028 | 33.5026 | 0 | 40.6106 | 0 | 0 | 33.5026
3866 | 0 | 1.7893 | 3.0702 | 25.8952 | 0 | 30.7547 | 0 | 0 | 25.8952
3867 | 0 | 2.2909 | 2.3713 | 27.5836 | 0 | 32.2458 | 0 | 0 | 27.5836
3868 | 8.7476 | 2.8434 | 2.2727 | 32.0587 | 0 | 45.9225 | 0 | 0 | 40.8063
3869 | 44.8303 | 2.1287 | 2.0277 | 35.107 | 0 | 84.0937 | 0 | 0 | 79.9373
3870 | 84.7837 | 2.5326 | 1.8545 | 31.594 | 0 | 120.7648 | 0 | 0 | 116.3777
3871 | 77.7708 | 2.7708 | 1.8626 | 29.5583 | 0 | 111.9626 | 0 | 0 | 107.3291
3872 | 61.6298 | 2.3261 | 1.8002 | 22.589 | 10.6919 | 99.037 | 0 | 0 | 94.9107
3873 | 9.1847 | 2.8859 | 1.7611 | 25.717 | 17.355 | 56.9038 | 0 | 0 | 52.2568
3874 | 14.6648 | 2.7083 | 1.7681 | 26.4985 | 10.665 | 56.3048 | 0 | 0 | 51.8283
3875 | 51.5895 | 3.1117 | 1.3773 | 33.1297 | 5.7001 | 94.9083 | 0 | 0 | 90.4193
3876 | 10.8484 | 2.5438 | 2.3299 | 30.192 | 6.6962 | 52.6102 | 0 | 0 | 47.7366
3877 | 20.5689 | 2.86 | 2.3888 | 33.5896 | 14.5281 | 73.9354 | 0 | 0 | 68.6866
3878 | 0 | 3.0287 | 2.0295 | 25.5289 | 17.513 | 48.1 | 0 | 0 | 43.0419
3879 | 0 | 2.4843 | 1.9886 | 29.8617 | 4.9017 | 39.2363 | 0 | 0 | 34.7634
3880 | 0 | 2.7859 | 2.2272 | 24.8886 | 12.559 | 42.4608 | 0 | 0 | 37.4477
3881 | 0 | 2.776 | 2.1199 | 38.0805 | 20.7312 | 63.7077 | 0 | 0 | 58.8117
3882 | 0 | 2.9192 | 1.5861 | 30.6174 | 8.1599 | 43.2826 | 0 | 0 | 38.7773
3883 | 6.6665 | 2.6339 | 1.239 | 25.1493 | 7.284 | 42.9728 | 0 | 0 | 39.0998
3884 | 44.5348 | 2.2769 | 1.0185 | 27.3454 | 0 | 75.1755 | 0 | 0 | 71.8801
3885 | 74.3 | 2.7063 | 1.0722 | 19.9698 | 0 | 98.0483 | 0 | 0 | 94.2698
3886 | 69.7832 | 3.0188 | 1.1947 | 25.6513 | 0 | 99.648 | 0 | 0 | 95.4344
3887 | 4.9866 | 2.4235 | 1.2542 | 22.8817 | 0 | 31.546 | 0 | 0 | 27.8682
3888 | 0 | 2.79 | 2.7569 | 28.7208 | 0 | 34.2677 | 0 | 0 | 28.7208
3889 | 0 | 2.27 | 4.3028 | 23.6741 | 0 | 30.247 | 0 | 0 | 23.6741
3890 | 0 | 2.3158 | 3.0702 | 21.9597 | 0 | 27.3457 | 0 | 0 | 21.9597
3891 | 0 | 2.7186 | 2.3713 | 27.9857 | 0 | 33.0757 | 0 | 0 | 27.9857
3892 | 0.32201 | 2.7616 | 2.3447 | 38.1503 | 0 | 43.5786 | 0 | 0 | 38.4724
3893 | 26.5905 | 2.4362 | 2.0277 | 25.4821 | 0 | 56.5365 | 0 | 0 | 52.0726
3894 | 92.7459 | 2.5241 | 1.8545 | 33.4829 | 0 | 130.6074 | 0 | 0 | 126.2288
3895 | 83.0602 | 2.2483 | 2.2883 | 29.4218 | 0 | 117.0186 | 0 | 0 | 112.4821
3896 | 31.4667 | 2.5595 | 1.8118 | 27.3604 | 6.8136 | 70.012 | 0 | 0 | 65.6407
3897 | 41.9891 | 2.6784 | 1.7611 | 31.3835 | 18.7444 | 96.5565 | 0 | 0 | 92.117
3898 | 33.9498 | 2.2766 | 1.7681 | 32.6441 | 18.9831 | 89.6218 | 0 | 0 | 85.5771
3899 | 0 | 2.2214 | 1.3773 | 20.6662 | 10.4369 | 34.7018 | 0 | 0 | 31.1031
3900 | 0 | 2.5091 | 2.3299 | 28.2322 | 7.5695 | 40.6406 | 0 | 0 | 35.8016
3901 | 0 | 2.9202 | 2.3888 | 29.1137 | 10.3748 | 44.7975 | 0 | 0 | 39.4885
3902 | 0 | 2.8989 | 2.0295 | 24.6715 | 19.2896 | 48.8895 | 0 | 0 | 43.9611
3903 | 0 | 2.3368 | 1.9886 | 32.4572 | 16.232 | 53.0147 | 0 | 0 | 48.6892
3904 | 0 | 2.4488 | 2.2272 | 26.9448 | 17.0595 | 48.6803 | 0 | 0 | 44.0043
3905 | 0.015174 | 2.3722 | 2.1199 | 22.2548 | 10.8725 | 37.6345 | 0 | 0 | 33.1424
3906 | 15.0264 | 2.6725 | 1.5861 | 32.5233 | 12.3456 | 64.154 | 0 | 0 | 59.8953
3907 | 55.6715 | 2.4845 | 1.239 | 31.8417 | 10.0249 | 101.2617 | 0 | 0 | 97.5381
3908 | 64.3251 | 2.6126 | 1.0185 | 22.4913 | 0 | 90.4475 | 0 | 0 | 86.8164
3909 | 70.3475 | 2.5387 | 1.0722 | 36.9278 | 0 | 110.8863 | 0 | 0 | 107.2753
3910 | 40.1103 | 2.7369 | 1.1947 | 30.4318 | 0 | 74.4736 | 0 | 0 | 70.5421
3911 | 36.0608 | 2.5632 | 1.2542 | 29.8673 | 0 | 69.7455 | 0 | 0 | 65.9281
3912 | 31.9063 | 2.6497 | 2.7569 | 28.0999 | 0 | 65.4127 | 0 | 0 | 60.0061
3913 | 93.1666 | 2.9393 | 4.3028 | 16.6517 | 0 | 117.0604 | 0 | 0 | 109.8183
3914 | 32.6587 | 2.7933 | 3.0702 | 24.6609 | 0 | 63.183 | 0 | 0 | 57.3196
3915 | 0 | 2.8383 | 2.3713 | 21.6144 | 0 | 26.824 | 0 | 0 | 21.6144
3916 | 0 | 2.7452 | 2.4146 | 27.978 | 0 | 33.1378 | 0 | 0 | 27.978
3917 | 14.4977 | 2.7807 | 2.0277 | 23.1356 | 0 | 42.4417 | 0 | 0 | 37.6333
3918 | 52.9624 | 2.8894 | 1.8545 | 24.6855 | 0 | 82.3918 | 0 | 200 | 277.6479
3919 | 62.379 | 2.9884 | 2.3568 | 23.3733 | 0 | 91.0976 | 0 | 0 | 85.7523
3920 | 21.4641 | 2.8841 | 1.8002 | 25.8383 | 24.0742 | 76.0609 | 0 | 0 | 71.3766
3921 | 51.9698 | 2.2373 | 1.7611 | 26.7599 | 7.7455 | 90.4737 | 0 | 0 | 86.4753
3922 | 74.1987 | 2.6005 | 1.7681 | 24.8172 | 10.7481 | 114.1326 | 200 | 0 | 309.764
3923 | 41.6343 | 2.4665 | 1.3773 | 26.8846 | 14.1479 | 86.5106 | 0 | 0 | 82.6668
3924 | 37.3456 | 2.6723 | 2.3299 | 25.0484 | 12.301 | 79.6972 | 0 | 0 | 74.695
3925 | 52.8253 | 2.571 | 2.3888 | 23.1925 | 17.9317 | 98.9093 | 0 | 0 | 93.9495
3926 | 42.4113 | 3.0171 | 2.0295 | 21.2316 | 15.0959 | 83.7854 | 0 | 0 | 78.7388
3927 | 0 | 2.6494 | 1.9886 | 24.9524 | 15.2083 | 44.7987 | 0 | 0 | 40.1606
3928 | 0 | 2.5902 | 2.2272 | 21.3352 | 20.9798 | 47.1324 | 0 | 0 | 42.3149
3929 | 0 | 2.3168 | 2.1199 | 30.6517 | 15.739 | 50.8275 | 0 | 0 | 46.3908
3930 | 12.5401 | 2.8666 | 1.5861 | 25.6941 | 7.8813 | 50.5683 | 0 | 0 | 46.1155
3931 | 51.1993 | 2.4013 | 1.239 | 22.3416 | 13.1353 | 90.3165 | 0 | 0 | 86.6762
3932 | 73.5444 | 2.8335 | 1.0185 | 33.6565 | 0 | 111.053 | 0 | 0 | 107.2009
3933 | 64.3003 | 2.7948 | 1.0722 | 26.5562 | 0 | 94.7236 | 0 | 0 | 90.8565
3934 | 46.0501 | 2.4628 | 1.1947 | 29.0671 | 0 | 78.7747 | 0 | 0 | 75.1172
3935 | 18.1939 | 2.317 | 1.2542 | 30.0606 | 0 | 51.8257 | 0 | 0 | 48.2545
3936 | 13.6973 | 2.6234 | 2.7569 | 26.7531 | 0 | 45.8307 | 0 | 0 | 40.4504
3937 | 59.8164 | 2.3354 | 4.3028 | 28.955 | 0 | 95.4097 | 0 | 0 | 88.7714
3938 | 36.5869 | 2.4559 | 3.0702 | 22.6108 | 0 | 64.7238 | 0 | 0 | 59.1978
3939 | 0 | 2.7731 | 2.3713 | 21.0403 | 0 | 26.1847 | 0 | 0 | 21.0403
3940 | 0 | 2.2915 | 2.2727 | 22.5944 | 0 | 27.1587 | 0 | 0 | 22.5944
3941 | 0 | 2.1623 | 2.0277 | 30.3718 | 0 | 34.5618 | 0 | 0 | 30.3718
3942 | 0 | 2.4432 | 1.8545 | 32.2804 | 0 | 36.5781 | 0 | 0 | 32.2804
3943 | 0 | 2.4272 | 1.8626 | 21.5424 | 0 | 25.8323 | 0 | 0 | 21.5424
3944 | 0 | 2.6109 | 1.8002 | 24.7093 | 26.1889 | 55.3094 | 0 | 0 | 50.8983
3945 | 0.66106 | 2.7158 | 1.7611 | 27.8368 | 4.7466 | 37.7214 | 0 | 0 | 33.2445
3946 | 15.4126 | 2.5179 | 1.7681 | 27.8752 | 4.1915 | 51.7653 | 0 | 0 | 47.4793
3947 | 51.7383 | 3.4076 | 1.3773 | 24.8381 | 15.5882 | 96.9495 | 0 | 0 | 92.1646
3948 | 10.1161 | 2.4877 | 2.3299 | 31.2122 | 3.2775 | 49.4234 | 0 | 0 | 44.6058
3949 | 0 | 2.8886 | 2.3888 | 19.4405 | 21.3153 | 46.0332 | 0 | 0 | 40.7558
3950 | 0 | 2.5337 | 2.0295 | 39.365 | 11.3249 | 55.2531 | 0 | 0 | 50.6899
3951 | 0 | 2.3296 | 1.9886 | 32.8207 | 10.1745 | 47.3134 | 0 | 0 | 42.9951
3952 | 0 | 2.5851 | 2.2272 | 30.3724 | 4.3479 | 39.5327 | 0 | 0 | 34.7204
3953 | 0 | 2.9731 | 2.1199 | 22.3785 | 22.8417 | 50.3132 | 0 | 0 | 45.2202
3954 | 0 | 2.3058 | 1.5861 | 25.6869 | 17.1342 | 46.713 | 0 | 0 | 42.8211
3955 | 0 | 2.5539 | 1.239 | 30.0979 | 4.8618 | 38.7527 | 0 | 0 | 34.9597
3956 | 0 | 2.3368 | 1.0185 | 28.8081 | 0 | 32.1634 | 0 | 0 | 28.8081
3957 | 0 | 2.0756 | 1.0722 | 31.6171 | 0 | 34.7649 | 0 | 0 | 31.6171
3958 | 8.518 | 2.7923 | 1.1947 | 26.5216 | 0 | 39.0267 | 0 | 0 | 35.0397
3959 | 45.6993 | 2.1296 | 1.2542 | 22.7873 | 0 | 71.8704 | 0 | 0 | 68.4867
3960 | 82.2847 | 2.3967 | 2.7569 | 23.374 | 0 | 110.8123 | 0 | 0 | 105.6587
3961 | 62.8293 | 2.4207 | 4.3028 | 31.9618 | 0 | 101.5146 | 0 | 0 | 94.7911
3962 | 13.6906 | 2.0611 | 3.0702 | 25.5979 | 0 | 44.4198 | 0 | 0 | 39.2885
3963 | 0 | 2.5996 | 2.3713 | 33.6361 | 0 | 38.607 | 0 | 0 | 33.6361
3964 | 0 | 2.6599 | 2.2727 | 30.3014 | 0 | 35.234 | 0 | 0 | 30.3014
3965 | 5.0628 | 2.385 | 2.0277 | 31.3206 | 0 | 40.7962 | 0 | 0 | 36.3834
3966 | 36.1539 | 2.5118 | 1.8545 | 29.8036 | 0 | 70.3238 | 0 | 0 | 65.9575
3967 | 88.663 | 2.5172 | 1.8626 | 27.6147 | 0 | 120.6575 | 0 | 0 | 116.2777
3968 | 89.1789 | 2.7705 | 1.8002 | 31.872 | 10.9086 | 136.5301 | 0 | 0 | 131.9595
3969 | 67.7738 | 2.2875 | 1.7611 | 29.9355 | 16.9215 | 118.6793 | 0 | 0 | 114.6307
3970 | 58.6905 | 2.9515 | 1.7681 | 38.9003 | 15.3166 | 117.627 | 0 | 0 | 112.9073
3971 | 74.9716 | 2.8335 | 1.3773 | 31.0066 | 11.7534 | 121.9425 | 0 | 0 | 117.7317
3972 | 61.1739 | 2.7741 | 2.3299 | 28.8933 | 14.0991 | 109.2703 | 0 | 0 | 104.1663
3973 | 82.7346 | 2.8425 | 2.3888 | 33.6735 | 20.0796 | 141.719 | 0 | 0 | 136.4877
3974 | 71.9346 | 2.5687 | 2.0295 | 38.8464 | 18.0713 | 133.4504 | 0 | 0 | 128.8522
3975 | 11.7923 | 2.4741 | 1.9886 | 28.3702 | 22.3033 | 66.9286 | 0 | 0 | 62.4658
3976 | 0 | 2.6867 | 2.2272 | 33.3353 | 10.7949 | 49.0441 | 0 | 0 | 44.1302
3977 | 0 | 2.4332 | 2.1199 | 21.8884 | 15.1821 | 41.6236 | 0 | 0 | 37.0705
3978 | 0 | 2.9839 | 1.9531 | 27.0543 | 14.1223 | 46.1136 | 0 | 0 | 41.1766
3979 | 0 | 2.495 | 1.5255 | 25.8291 | 8.7235 | 38.5731 | 0 | 0 | 34.5526
3980 | 0 | 2.2899 | 1.1504 | 24.1526 | 0 | 27.5929 | 0 | 0 | 24.1526
3981 | 0 | 2.5523 | 1.1994 | 22.5343 | 0 | 26.286 | 0 | 0 | 22.5343
3982 | 0 | 2.2369 | 1.0675 | 25.9216 | 0 | 29.2261 | 0 | 0 | 25.9216
3983 | 0 | 2.1522 | 1.3615 | 24.3711 | 0 | 27.8848 | 0 | 0 | 24.3711
3984 | 0 | 2.7572 | 1.7973 | 32.296 | 0 | 36.8505 | 0 | 0 | 32.296
3985 | 0 | 2.4172 | 2.1992 | 38.0922 | 0 | 42.7086 | 0 | 0 | 38.0922
3986 | 0 | 2.7946 | 1.9945 | 25.4865 | 0 | 30.2756 | 0 | 0 | 25.4865
3987 | 0 | 2.9435 | 3.6751 | 30.4873 | 0 | 37.106 | 0 | 0 | 30.4873
3988 | 2.0786 | 2.621 | 3.2685 | 33.8049 | 0 | 41.773 | 0 | 0 | 35.8835
3989 | 32.8718 | 2.9694 | 2.6595 | 37.6373 | 0 | 76.138 | 0 | 0 | 70.5091
3990 | 70.4878 | 2.7988 | 2.1561 | 22.4779 | 0 | 97.9205 | 0 | 0 | 92.9656
3991 | 87.7941 | 2.4703 | 1.9466 | 26.1943 | 0 | 118.4054 | 0 | 0 | 113.9884
3992 | 77.2414 | 2.7148 | 1.9857 | 27.9512 | 12.0957 | 121.9888 | 0 | 0 | 117.2883
3993 | 27.9683 | 1.9339 | 1.7436 | 20.9034 | 18.6131 | 71.1623 | 0 | 0 | 67.4848
3994 | 15.8442 | 2.5488 | 1.9834 | 27.2936 | 7.3085 | 54.9785 | 0 | 0 | 50.4463
3995 | 63.4559 | 2.8463 | 2.2739 | 27.9313 | 10.329 | 106.8364 | 0 | 0 | 101.7162
3996 | 89.0617 | 2.3852 | 2.4752 | 28.5519 | 20.4681 | 142.9421 | 0 | 0 | 138.0817
3997 | 76.7442 | 2.5941 | 1.8702 | 27.5715 | 15.021 | 123.8011 | 0 | 0 | 119.3368
3998 | 87.2495 | 2.5452 | 2.2301 | 21.5374 | 8.1779 | 121.7401 | 0 | 0 | 116.9648
3999 | 79.3586 | 2.8002 | 2.3118 | 34.4188 | 19.0992 | 137.9887 | 0 | 0 | 132.8766
4000 | 18.1333 | 2.2673 | 1.9 | 32.4356 | 17.68 | 72.4162 | 200 | 0 | 268.2489
4001 | 0 | 2.4676 | 1.9367 | 22.2489 | 17.0551 | 43.7083 | 0 | 0 | 39.304
4002 | 0 | 2.7418 | 1.5167 | 24.8658 | 13.2986 | 42.4229 | 0 | 0 | 38.1644
4003 | 0 | 3.18 | 1.4117 | 32.1215 | 10.5221 | 47.2353 | 0 | 0 | 42.6436
4004 | 0 | 2.4267 | 1.1486 | 30.109 | 0 | 33.6844 | 0 | 0 | 30.109
4005 | 0 | 3.0065 | 1.2344 | 28.7538 | 0 | 32.9947 | 0 | 0 | 28.7538
4006 | 0 | 2.5092 | 1.1264 | 29.8997 | 0 | 33.5353 | 0 | 0 | 29.8997
4007 | 0 | 2.5339 | 1.1609 | 25.2213 | 0 | 28.9161 | 0 | 0 | 25.2213
4008 | 0 | 2.8353 | 1.1591 | 32.2998 | 0 | 36.2942 | 0 | 0 | 32.2998
4009 | 0 | 2.7644 | 2.1636 | 25.2521 | 0 | 30.1801 | 0 | 0 | 25.2521
4010 | 0 | 2.3021 | 1.767 | 24.1092 | 0 | 28.1783 | 0 | 0 | 24.1092
4011 | 0 | 2.6116 | 2.6204 | 23.1315 | 0 | 28.3635 | 0 | 0 | 23.1315
4012 | 2.3693 | 2.9294 | 2.6397 | 22.9309 | 0 | 30.8693 | 0 | 0 | 25.3002
4013 | 30.4001 | 3.3168 | 2.3626 | 28.6477 | 0 | 64.7272 | 0 | 0 | 59.0478
4014 | 82.4024 | 2.8187 | 1.8189 | 30.3794 | 0 | 117.4194 | 0 | 0 | 112.7818
4015 | 93.0288 | 2.4809 | 1.9431 | 27.7559 | 0 | 125.2087 | 0 | 0 | 120.7847
4016 | 86.0639 | 2.4463 | 1.9321 | 29.0976 | 24.4529 | 143.9928 | 0 | 0 | 139.6144
4017 | 79.8625 | 2.7123 | 1.7582 | 28.6096 | 6.1719 | 119.1146 | 0 | 0 | 114.644
4018 | 82.7347 | 2.8626 | 1.4747 | 30.1214 | 21.4077 | 138.6011 | 0 | 0 | 134.2638
4019 | 86.1311 | 2.5667 | 1.8335 | 29.3921 | 13.1091 | 133.0324 | 0 | 0 | 128.6323
4020 | 84.9691 | 2.5428 | 2.0907 | 35.7716 | 11.3992 | 136.7735 | 0 | 200 | 332.14
4021 | 66.5998 | 2.293 | 2.2196 | 27.1801 | 13.9544 | 112.247 | 0 | 0 | 107.7343
4022 | 15.1476 | 2.6368 | 2.2605 | 24.013 | 12.7771 | 56.8349 | 0 | 0 | 51.9377
4023 | 0 | 2.9678 | 2.1706 | 33.2969 | 13.0726 | 51.508 | 0 | 0 | 46.3695
4024 | 0 | 2.4892 | 2.1677 | 34.6786 | 16.886 | 56.2216 | 0 | 0 | 51.5646
4025 | 0 | 2.8239 | 2.1706 | 22.2567 | 19.8926 | 47.1438 | 0 | 0 | 42.1493
4026 | 0 | 2.5126 | 1.5861 | 24.7334 | 15.1021 | 43.9343 | 0 | 0 | 39.8355
4027 | 0 | 2.5694 | 1.239 | 28.4544 | 24.5414 | 56.8042 | 0 | 0 | 52.9958
4028 | 0 | 2.2596 | 1.0185 | 27.833 | 0 | 31.1111 | 0 | 0 | 27.833
4029 | 0 | 2.3941 | 1.0722 | 33.6719 | 0 | 37.1382 | 0 | 0 | 33.6719
4030 | 0 | 2.6823 | 1.1947 | 24.8912 | 0 | 28.7682 | 0 | 0 | 24.8912
4031 | 0 | 2.3675 | 1.2542 | 35.7015 | 0 | 39.3232 | 0 | 0 | 35.7015
4032 | 0 | 3.0406 | 2.7569 | 25.8582 | 0 | 31.6557 | 0 | 0 | 25.8582
4033 | 0 | 2.5238 | 4.3028 | 33.2531 | 0 | 40.0797 | 0 | 0 | 33.2531
4034 | 0 | 2.724 | 3.0702 | 26.9946 | 0 | 32.7888 | 0 | 0 | 26.9946
4035 | 0 | 2.5636 | 2.3713 | 31.3916 | 0 | 36.3265 | 0 | 0 | 31.3916
4036 | 0 | 2.375 | 2.2727 | 29.7689 | 0 | 34.4166 | 0 | 0 | 29.7689
4037 | 9.0764 | 2.4487 | 2.0277 | 31.9183 | 0 | 45.4711 | 0 | 0 | 40.9946
4038 | 28.8546 | 3.0043 | 1.8545 | 34.2461 | 0 | 67.9596 | 0 | 0 | 63.1008
4039 | 10.4841 | 2.6289 | 1.8626 | 26.6873 | 0 | 41.663 | 0 | 0 | 37.1715
4040 | 10.5219 | 2.6942 | 1.8002 | 25.6507 | 11.3517 | 52.0187 | 0 | 0 | 47.5243
4041 | 44.1804 | 2.701 | 1.7611 | 30.8209 | 8.1912 | 87.6547 | 0 | 0 | 83.1925
4042 | 37.4073 | 2.4491 | 1.7681 | 35.8859 | 5.3775 | 82.888 | 0 | 0 | 78.6708
4043 | 0 | 2.5808 | 1.3773 | 27.1209 | 20.4527 | 51.5317 | 0 | 0 | 47.5736
4044 | 0 | 2.4055 | 2.3299 | 36.5478 | 11.1457 | 52.4289 | 0 | 0 | 47.6935
4045 | 0 | 2.6462 | 2.3888 | 34.7192 | 8.3551 | 48.1094 | 0 | 0 | 43.0743
4046 | 0 | 2.7133 | 2.0295 | 33.4673 | 19.9188 | 58.1288 | 0 | 0 | 53.3861
4047 | 0 | 2.3328 | 1.9886 | 26.2887 | 11.4366 | 42.0468 | 0 | 0 | 37.7253
4048 | 0 | 2.4906 | 2.2272 | 34.4272 | 17.272 | 56.417 | 0 | 0 | 51.6992
4049 | 0 | 2.8525 | 2.1199 | 30.3463 | 11.7772 | 47.0959 | 0 | 0 | 42.1235
4050 | 0 | 2.5711 | 1.5861 | 27.2622 | 9.7711 | 41.1906 | 0 | 0 | 37.0333
4051 | 0 | 2.5901 | 1.239 | 35.0373 | 15.2349 | 54.1013 | 0 | 0 | 50.2722
4052 | 0 | 2.4935 | 1.0185 | 35.7492 | 0 | 39.2613 | 0 | 0 | 35.7492
4053 | 0 | 2.7869 | 1.0722 | 20.3483 | 0 | 24.2074 | 0 | 0 | 20.3483
4054 | 0 | 2.6249 | 1.1947 | 36.4541 | 0 | 40.2737 | 0 | 0 | 36.4541
4055 | 0 | 2.5132 | 1.2542 | 29.8523 | 0 | 33.6196 | 0 | 0 | 29.8523
4056 | 0 | 2.8821 | 2.7569 | 27.752 | 0 | 33.3911 | 0 | 0 | 27.752
4057 | 0 | 2.5392 | 4.3028 | 27.8167 | 0 | 34.6587 | 0 | 0 | 27.8167
4058 | 0 | 2.7463 | 3.0702 | 17.5071 | 0 | 23.3236 | 0 | 0 | 17.5071
4059 | 0 | 2.6361 | 2.3713 | 25.5526 | 0 | 30.56 | 0 | 0 | 25.5526
4060 | 2.2871 | 2.2894 | 2.2727 | 23.4267 | 0 | 30.2759 | 0 | 0 | 25.7138
4061 | 18.0503 | 2.6236 | 2.0277 | 23.9234 | 0 | 46.6249 | 0 | 0 | 41.9737
4062 | 37.3483 | 2.9799 | 1.8545 | 30.2289 | 0 | 72.4115 | 0 | 0 | 67.5772
4063 | 22.2555 | 2.8687 | 1.8626 | 24.6441 | 0 | 51.631 | 0 | 0 | 46.8997
4064 | 2.4443 | 2.3919 | 1.8002 | 35.0877 | 19.5419 | 61.2659 | 0 | 0 | 57.0739
4065 | 24.7834 | 2.6491 | 1.7611 | 23.4912 | 21.2779 | 73.9627 | 0 | 0 | 69.5525
4066 | 67.5411 | 2.4659 | 1.7681 | 20.6175 | 10.6225 | 103.0151 | 0 | 0 | 98.7811
4067 | 34.9528 | 2.5771 | 1.3773 | 27.3844 | 11.1096 | 77.4011 | 0 | 0 | 73.4467
4068 | 0 | 2.2185 | 2.3299 | 28.0247 | 6.4476 | 39.0208 | 0 | 0 | 34.4723
4069 | 0 | 2.5565 | 2.3888 | 24.3069 | 20.8468 | 50.099 | 0 | 0 | 45.1536
4070 | 0 | 3.281 | 2.0295 | 23.5258 | 3.307 | 32.1432 | 0 | 0 | 26.8328
4071 | 0 | 2.9455 | 1.9886 | 38.4644 | 14.2566 | 57.6552 | 0 | 0 | 52.721
4072 | 0 | 2.2494 | 2.2272 | 21.6233 | 24.623 | 50.7229 | 0 | 0 | 46.2463
4073 | 0 | 2.621 | 2.1199 | 33.6897 | 10.5245 | 48.9551 | 0 | 0 | 44.2142
4074 | 0 | 2.5346 | 1.5861 | 28.3886 | 12.861 | 45.3703 | 0 | 0 | 41.2496
4075 | 0 | 2.9848 | 1.239 | 24.2896 | 16.6912 | 45.2046 | 0 | 0 | 40.9808
4076 | 0 | 2.3106 | 1.0185 | 33.8047 | 0 | 37.1338 | 200 | 0 | 233.8047
4077 | 0 | 2.6396 | 1.0722 | 31.0897 | 0 | 34.8015 | 0 | 0 | 31.0897
4078 | 0 | 2.2521 | 1.1947 | 34.4248 | 0 | 37.8716 | 0 | 0 | 34.4248
4079 | 0 | 2.9434 | 1.2542 | 30.5092 | 0 | 34.7069 | 0 | 0 | 30.5092
4080 | 0 | 2.5127 | 2.7569 | 30.3457 | 0 | 35.6153 | 0 | 0 | 30.3457
4081 | 0 | 2.6873 | 4.3028 | 28.8563 | 0 | 35.8464 | 0 | 0 | 28.8563
4082 | 0 | 2.8223 | 3.0702 | 33.2672 | 0 | 39.1597 | 0 | 0 | 33.2672
4083 | 0 | 2.4239 | 2.3713 | 22.6683 | 0 | 27.4634 | 0 | 0 | 22.6683
4084 | 0.45321 | 2.3718 | 2.2727 | 27.1543 | 0 | 32.252 | 0 | 0 | 27.6075
4085 | 16.8943 | 2.6952 | 2.0277 | 34.5013 | 0 | 56.1185 | 0 | 0 | 51.3956
4086 | 54.6891 | 2.5471 | 1.8545 | 35.0103 | 0 | 94.1009 | 0 | 0 | 89.6994
4087 | 57.782 | 2.546 | 1.8626 | 23.8919 | 0 | 86.0825 | 0 | 0 | 81.674
4088 | 7.8773 | 2.6607 | 1.8002 | 31.0321 | 24.2647 | 67.635 | 0 | 0 | 63.1741
4089 | 0 | 2.5442 | 1.7611 | 25.4586 | 15.6116 | 45.3755 | 0 | 0 | 41.0701
4090 | 0 | 2.6884 | 1.7681 | 24.1799 | 6.2721 | 34.9085 | 0 | 0 | 30.452
4091 | 0 | 2.8949 | 1.3773 | 28.6345 | 18.0866 | 50.9933 | 0 | 0 | 46.7211
4092 | 0 | 3.049 | 2.3299 | 26.7024 | 9.5894 | 41.6707 | 0 | 0 | 36.2918
4093 | 0 | 2.4714 | 2.3888 | 27.8291 | 19.4542 | 52.1436 | 0 | 0 | 47.2834
4094 | 0 | 2.6222 | 2.0295 | 26.2377 | 21.9293 | 52.8187 | 0 | 0 | 48.167
4095 | 0 | 2.6969 | 1.9886 | 26.3659 | 21.4594 | 52.5108 | 0 | 0 | 47.8253
4096 | 0 | 2.3668 | 2.2272 | 32.336 | 7.8392 | 44.7692 | 0 | 0 | 40.1752
4097 | 0 | 2.6115 | 2.1199 | 29.3485 | 1.967 | 36.047 | 0 | 0 | 31.3156
4098 | 0 | 2.6859 | 1.5861 | 24.8251 | 17.2068 | 46.3039 | 0 | 0 | 42.0318
4099 | 0 | 2.4651 | 1.239 | 33.5482 | 2.7181 | 39.9705 | 0 | 0 | 36.2664
4100 | 0 | 2.1632 | 1.0185 | 28.3278 | 0 | 31.5095 | 0 | 0 | 28.3278
4101 | 0 | 2.8973 | 1.0722 | 30.8401 | 0 | 34.8095 | 0 | 0 | 30.8401
4102 | 0 | 2.4752 | 1.1947 | 37.281 | 0 | 40.9509 | 0 | 0 | 37.281
4103 | 0 | 2.8819 | 1.2542 | 26.1955 | 0 | 30.3316 | 0 | 0 | 26.1955
4104 | 0 | 2.2668 | 2.7569 | 27.3786 | 0 | 32.4023 | 0 | 0 | 27.3786
4105 | 0 | 2.6397 | 4.3028 | 29.4147 | 0 | 36.3572 | 0 | 0 | 29.4147
4106 | 0 | 2.3027 | 3.0702 | 29.1685 | 0 | 34.5414 | 0 | 0 | 29.1685
4107 | 0 | 2.4599 | 2.3713 | 29.5078 | 0 | 34.339 | 0 | 0 | 29.5078
4108 | 0 | 3.3696 | 2.5544 | 30.0764 | 0 | 36.0003 | 0 | 0 | 30.0764
4109 | 15.3435 | 2.4315 | 2.0851 | 20.1939 | 0 | 40.054 | 0 | 0 | 35.5374
4110 | 66.8105 | 2.7976 | 1.8545 | 31.8987 | 0 | 103.3612 | 0 | 0 | 98.7091
4111 | 74.7287 | 2.3195 | 2.2883 | 29.3547 | 0 | 108.6912 | 0 | 0 | 104.0835
4112 | 74.5405 | 2.5585 | 2.4908 | 24.9363 | 11.0648 | 115.591 | 0 | 0 | 110.5417
4113 | 75.9944 | 2.7697 | 1.7611 | 27.9024 | 16.3888 | 124.8164 | 0 | 0 | 120.2855
4114 | 47.8402 | 2.4253 | 1.7681 | 23.8274 | 19.3075 | 95.1687 | 0 | 0 | 90.9752
4115 | 0 | 3.2035 | 1.3773 | 30.5325 | 11.3765 | 46.4897 | 0 | 0 | 41.9089
4116 | 0 | 2.506 | 2.3299 | 25.3426 | 8.6481 | 38.8266 | 0 | 0 | 33.9907
4117 | 0 | 2.6036 | 2.3888 | 23.4646 | 18.7486 | 47.2057 | 0 | 0 | 42.2132
4118 | 0 | 2.3854 | 2.0295 | 36.8001 | 4.9237 | 46.1386 | 0 | 0 | 41.7238
4119 | 0 | 2.7365 | 1.9886 | 28.3222 | 17.2083 | 50.2556 | 0 | 0 | 45.5305
4120 | 0 | 3.0759 | 2.2272 | 20.7921 | 7.0403 | 33.1355 | 0 | 200 | 227.8324
4121 | 0 | 2.4324 | 2.1199 | 28.4125 | 19.8905 | 52.8553 | 0 | 0 | 48.303
4122 | 0 | 2.4046 | 1.5861 | 37.0601 | 11.086 | 52.1369 | 0 | 0 | 48.1462
4123 | 0 | 2.2538 | 1.239 | 28.4314 | 3.3175 | 35.2417 | 0 | 0 | 31.7489
4124 | 0 | 2.5929 | 1.0185 | 26.8352 | 0 | 30.4466 | 0 | 0 | 26.8352
4125 | 0 | 2.3585 | 1.0722 | 31.5466 | 0 | 34.9772 | 0 | 0 | 31.5466
4126 | 0 | 2.4113 | 1.1947 | 28.4512 | 0 | 32.0572 | 0 | 0 | 28.4512
4127 | 0 | 2.3416 | 1.2542 | 23.7331 | 0 | 27.329 | 0 | 0 | 23.7331
4128 | 0 | 2.0901 | 2.7569 | 24.9372 | 0 | 29.7843 | 0 | 0 | 24.9372
4129 | 0 | 3.1578 | 4.3028 | 36.1872 | 0 | 43.6478 | 0 | 0 | 36.1872
4130 | 0 | 2.8322 | 3.0702 | 33.0471 | 0 | 38.9494 | 0 | 0 | 33.0471
4131 | 0 | 2.6817 | 3.2857 | 35.0225 | 0 | 40.9899 | 0 | 0 | 35.0225
4132 | 0 | 2.8605 | 3.4629 | 33.6426 | 0 | 39.966 | 0 | 0 | 33.6426
4133 | 0 | 2.3701 | 2.6656 | 33.1499 | 0 | 38.1857 | 0 | 0 | 33.1499
4134 | 0 | 2.3136 | 1.8545 | 27.4158 | 0 | 31.5839 | 0 | 0 | 27.4158
4135 | 0 | 2.4227 | 2.6996 | 28.1296 | 0 | 33.2518 | 0 | 0 | 28.1296
4136 | 0 | 2.6354 | 1.8002 | 22.2678 | 20.9538 | 47.6572 | 0 | 0 | 43.2216
4137 | 0 | 2.2602 | 1.7611 | 31.8381 | 10.5945 | 46.4539 | 0 | 0 | 42.4326
4138 | 0 | 2.7244 | 1.7681 | 25.1651 | 8.6352 | 38.2929 | 0 | 0 | 33.8003
4139 | 0 | 2.5801 | 1.3773 | 30.6086 | 13.3721 | 47.9381 | 0 | 0 | 43.9807
4140 | 0 | 2.4343 | 2.3299 | 27.8136 | 9.161 | 41.7389 | 0 | 0 | 36.9747
4141 | 0 | 2.3159 | 2.3888 | 26.0001 | 13.4807 | 44.1855 | 0 | 0 | 39.4808
4142 | 0 | 2.6083 | 2.0295 | 28.3122 | 13.43 | 46.3799 | 0 | 0 | 41.7422
4143 | 0 | 2.9701 | 1.9886 | 26.6608 | 5.3875 | 37.0071 | 0 | 0 | 32.0483
4144 | 0 | 2.1832 | 2.2272 | 23.6763 | 9.4916 | 37.5783 | 0 | 0 | 33.1679
4145 | 0 | 2.3571 | 2.1199 | 29.4267 | 11.3496 | 45.2533 | 0 | 0 | 40.7763
4146 | 0 | 2.9922 | 1.9531 | 22.8897 | 16.517 | 44.352 | 0 | 0 | 39.4067
4147 | 0 | 2.6254 | 1.5255 | 29.0162 | 13.3801 | 46.5471 | 0 | 0 | 42.3963
4148 | 0 | 2.7078 | 1.1504 | 30.518 | 0 | 34.3762 | 0 | 0 | 30.518
4149 | 0 | 2.0399 | 1.1994 | 24.3154 | 0 | 27.5546 | 0 | 0 | 24.3154
4150 | 0 | 2.826 | 1.0675 | 29.7448 | 0 | 33.6384 | 0 | 0 | 29.7448
4151 | 0 | 2.2923 | 1.3615 | 31.0277 | 0 | 34.6815 | 0 | 0 | 31.0277
4152 | 0 | 2.3885 | 1.7973 | 21.5355 | 0 | 25.7212 | 0 | 0 | 21.5355
4153 | 0 | 2.6925 | 2.1992 | 26.3507 | 0 | 31.2424 | 0 | 0 | 26.3507
4154 | 0 | 2.5746 | 1.9945 | 32.2044 | 0 | 36.7735 | 200 | 0 | 232.2044
4155 | 0 | 2.9115 | 3.6751 | 22.3246 | 0 | 28.9112 | 0 | 0 | 22.3246
4156 | 0 | 2.9584 | 3.2685 | 29.0848 | 0 | 35.3118 | 0 | 0 | 29.0848
4157 | 0 | 2.5307 | 2.6595 | 20.9887 | 0 | 26.1789 | 0 | 0 | 20.9887
4158 | 0 | 2.3605 | 2.1561 | 26.2524 | 0 | 30.769 | 0 | 0 | 26.2524
4159 | 0 | 2.6323 | 1.9466 | 27.4363 | 0 | 32.0153 | 0 | 0 | 27.4363
4160 | 0 | 2.4722 | 1.9857 | 24.923 | 21.1289 | 50.5099 | 0 | 0 | 46.052
4161 | 0 | 2.3654 | 1.7436 | 34.9767 | 12.0582 | 51.1439 | 0 | 0 | 47.0349
4162 | 0 | 3.065 | 1.9834 | 32.3418 | 4.0519 | 41.4421 | 0 | 0 | 36.3937
4163 | 0 | 2.0968 | 2.2739 | 31.0313 | 10.0233 | 45.4254 | 0 | 0 | 41.0546
4164 | 0 | 2.5676 | 2.4752 | 30.8552 | 10.9757 | 46.8736 | 0 | 0 | 41.8308
4165 | 0 | 2.3714 | 1.8702 | 21.9128 | 6.4497 | 32.6041 | 0 | 0 | 28.3624
4166 | 0 | 2.2513 | 2.2301 | 35.4918 | 14.4422 | 54.4155 | 0 | 0 | 49.934
4167 | 0 | 3.0042 | 2.3118 | 31.6378 | 14.4407 | 51.3945 | 0 | 0 | 46.0785
4168 | 0 | 2.6336 | 1.9 | 28.6291 | 22.4358 | 55.5985 | 0 | 0 | 51.0649
4169 | 0 | 2.9013 | 1.9367 | 27.5988 | 13.4369 | 45.8737 | 0 | 0 | 41.0357
4170 | 0 | 2.6393 | 1.5167 | 24.7024 | 16.9005 | 45.759 | 0 | 0 | 41.603
4171 | 0 | 2.5006 | 1.4117 | 34.7565 | 14.2482 | 52.917 | 0 | 0 | 49.0047
4172 | 0 | 2.3965 | 1.1486 | 29.9235 | 0 | 33.4686 | 0 | 0 | 29.9235
4173 | 0 | 2.5194 | 1.2344 | 22.9598 | 0 | 26.7136 | 0 | 0 | 22.9598
4174 | 0 | 2.6488 | 1.1264 | 30.5755 | 0 | 34.3508 | 0 | 0 | 30.5755
4175 | 0 | 2.6289 | 1.1609 | 31.8417 | 0 | 35.6315 | 0 | 0 | 31.8417
4176 | 0 | 2.3441 | 1.1591 | 27.7644 | 0 | 31.2676 | 0 | 0 | 27.7644
4177 | 0 | 2.7637 | 2.1636 | 27.6207 | 0 | 32.5481 | 0 | 0 | 27.6207
4178 | 0 | 2.6199 | 1.767 | 26.2927 | 0 | 30.6796 | 0 | 0 | 26.2927
4179 | 0 | 1.9137 | 2.6204 | 29.1545 | 0 | 33.6886 | 0 | 0 | 29.1545
4180 | 0 | 2.3238 | 2.8415 | 23.7802 | 0 | 28.9455 | 0 | 0 | 23.7802
4181 | 0 | 2.3737 | 3.039 | 21.1197 | 0 | 26.5324 | 0 | 0 | 21.1197
4182 | 0 | 3.0472 | 2.5798 | 32.815 | 0 | 38.442 | 0 | 0 | 32.815
4183 | 0 | 2.4278 | 2.222 | 26.96 | 0 | 31.6099 | 0 | 0 | 26.96
4184 | 0 | 3.0207 | 1.9321 | 28.6385 | 9.815 | 43.4061 | 0 | 0 | 38.4534
4185 | 0 | 2.6462 | 1.7582 | 24.1955 | 16.8602 | 45.4602 | 0 | 0 | 41.0558
4186 | 0 | 2.4889 | 1.4747 | 31.4847 | 17.4434 | 52.8917 | 0 | 0 | 48.928
4187 | 0 | 2.2513 | 1.8335 | 30.6143 | 12.9549 | 47.654 | 0 | 0 | 43.5692
4188 | 0 | 2.4216 | 2.0907 | 29.2187 | 13.3435 | 47.0745 | 0 | 0 | 42.5622
4189 | 0 | 2.496 | 2.2196 | 30.4108 | 13.8209 | 48.9474 | 0 | 0 | 44.2317
4190 | 0 | 2.7314 | 2.2605 | 25.7766 | 9.8562 | 40.6246 | 0 | 0 | 35.6328
4191 | 0 | 2.5168 | 2.1706 | 25.3912 | 16.1888 | 46.2675 | 0 | 0 | 41.58
4192 | 0 | 2.1828 | 2.1677 | 28.0044 | 17.6053 | 49.9602 | 0 | 0 | 45.6097
4193 | 0 | 2.6576 | 2.1706 | 35.0577 | 13.6498 | 53.5358 | 0 | 0 | 48.7075
4194 | 0 | 2.5365 | 1.5861 | 26.2899 | 8.611 | 39.0235 | 0 | 0 | 34.9009
4195 | 0 | 2.1935 | 1.239 | 35.3301 | 10.8735 | 49.6361 | 0 | 0 | 46.2036
4196 | 0 | 2.9419 | 1.0185 | 23.8786 | 0 | 27.8391 | 0 | 0 | 23.8786
4197 | 0 | 2.8455 | 1.0722 | 32.6627 | 0 | 36.5804 | 0 | 0 | 32.6627
4198 | 0 | 2.0848 | 1.1947 | 28.7602 | 0 | 32.0397 | 0 | 0 | 28.7602
4199 | 0 | 2.3916 | 1.2542 | 28.0302 | 0 | 31.676 | 0 | 0 | 28.0302
4200 | 0 | 3.1415 | 2.7569 | 23.1305 | 0 | 29.0289 | 0 | 0 | 23.1305
4201 | 0 | 2.6151 | 4.3028 | 29.9756 | 0 | 36.8935 | 0 | 0 | 29.9756
4202 | 0 | 2.4884 | 3.0702 | 21.7072 | 0 | 27.2657 | 0 | 0 | 21.7072
4203 | 11.1419 | 2.6264 | 2.3713 | 30.4522 | 0 | 46.5919 | 0 | 0 | 41.5941
4204 | 37.8528 | 2.6834 | 2.2727 | 26.2987 | 0 | 69.1077 | 0 | 0 | 64.1515
4205 | 62.9196 | 2.9111 | 2.0277 | 25.2506 | 0 | 93.109 | 0 | 0 | 88.1702
4206 | 69.5707 | 2.4083 | 1.8545 | 28.6357 | 0 | 102.4692 | 0 | 0 | 98.2064
4207 | 70.9987 | 2.6622 | 1.8626 | 31.8121 | 0 | 107.3357 | 0 | 0 | 102.8108
4208 | 52.2724 | 2.3628 | 1.8002 | 29.2614 | 12.3189 | 98.0157 | 0 | 0 | 93.8527
4209 | 19.6391 | 2.5423 | 1.7611 | 24.5341 | 18.0209 | 66.4975 | 0 | 0 | 62.1941
4210 | 32.3194 | 2.4882 | 1.7681 | 34.4308 | 16.6794 | 87.6859 | 0 | 0 | 83.4296
4211 | 56.6784 | 2.6021 | 1.3773 | 26.5544 | 5.0439 | 92.2562 | 0 | 0 | 88.2768
4212 | 58.4185 | 2.8072 | 2.3299 | 30.1609 | 16.519 | 110.2354 | 0 | 0 | 105.0984
4213 | 64.0621 | 2.2468 | 2.3888 | 28.9629 | 9.4819 | 107.1425 | 0 | 0 | 102.5069
4214 | 56.4562 | 3.0499 | 2.0295 | 23.034 | 12.8107 | 97.3803 | 0 | 0 | 92.3009
4215 | 36.1883 | 2.1428 | 1.9886 | 28.8765 | 11.4388 | 80.635 | 0 | 0 | 76.5036
4216 | 0 | 2.6522 | 2.2272 | 27.2311 | 15.6436 | 47.7541 | 0 | 0 | 42.8747
4217 | 0 | 2.5027 | 2.1199 | 33.3135 | 15.4316 | 53.3678 | 0 | 0 | 48.7452
4218 | 0 | 2.7219 | 1.5861 | 36.079 | 12.7667 | 53.1537 | 0 | 0 | 48.8457
4219 | 0 | 2.3854 | 1.239 | 19.0492 | 8.5917 | 31.2653 | 0 | 0 | 27.6409
4220 | 0 | 2.456 | 1.0185 | 30.2064 | 0 | 33.6809 | 0 | 0 | 30.2064
4221 | 0 | 2.1171 | 1.0722 | 16.457 | 0 | 19.6463 | 0 | 200 | 216.457
4222 | 0 | 2.306 | 1.1947 | 38.8241 | 0 | 42.3247 | 0 | 0 | 38.8241
4223 | 0 | 2.8255 | 1.2542 | 27.5555 | 0 | 31.6353 | 0 | 0 | 27.5555
4224 | 0 | 2.599 | 2.7569 | 22.7354 | 0 | 28.0912 | 0 | 0 | 22.7354
4225 | 0 | 3.1425 | 4.3028 | 31.3733 | 0 | 38.8186 | 0 | 0 | 31.3733
4226 | 0 | 2.6815 | 3.0702 | 28.0252 | 0 | 33.7768 | 0 | 0 | 28.0252
4227 | 0 | 2.3276 | 2.3713 | 30.1706 | 0 | 34.8695 | 0 | 0 | 30.1706
4228 | 0 | 3.0435 | 2.2727 | 28.4517 | 0 | 33.7679 | 0 | 0 | 28.4517
4229 | 13.6476 | 2.6522 | 2.0277 | 28.1359 | 0 | 46.4635 | 0 | 0 | 41.7836
4230 | 59.4231 | 2.6282 | 1.8545 | 26.6836 | 0 | 90.5894 | 0 | 0 | 86.1067
4231 | 81.7014 | 2.6817 | 1.8626 | 31.2029 | 0 | 117.4486 | 0 | 0 | 112.9043
4232 | 63.1966 | 2.3579 | 1.8002 | 26.8828 | 11.0187 | 105.2562 | 200 | 0 | 301.0981
4233 | 47.2893 | 2.723 | 1.7611 | 28.7836 | 21.3621 | 101.9192 | 0 | 0 | 97.4351
4234 | 57.4394 | 2.5072 | 1.7681 | 27.1866 | 9.3529 | 98.2543 | 0 | 0 | 93.9789
4235 | 67.8973 | 2.754 | 1.3773 | 20.518 | 14.1184 | 106.665 | 0 | 0 | 102.5337
4236 | 81.0399 | 2.5169 | 2.3299 | 32.2381 | 17.582 | 135.7067 | 0 | 0 | 130.8599
4237 | 55.3462 | 2.1587 | 2.3888 | 25.3073 | 17.7346 | 102.9356 | 0 | 0 | 98.3881
4238 | 0 | 2.3289 | 2.0295 | 32.1256 | 25.6414 | 62.1254 | 0 | 0 | 57.767
4239 | 0 | 2.5415 | 1.9886 | 30.2403 | 6.9805 | 41.7509 | 0 | 0 | 37.2208
4240 | 0 | 2.6933 | 2.2272 | 25.2985 | 6.5024 | 36.7215 | 0 | 0 | 31.8009
4241 | 0 | 2.5852 | 2.1199 | 32.9877 | 9.355 | 47.0478 | 0 | 0 | 42.3427
4242 | 0 | 2.2753 | 1.5861 | 31.5333 | 21.2689 | 56.6636 | 0 | 0 | 52.8022
4243 | 0 | 2.0201 | 1.239 | 34.421 | 15.4138 | 53.0939 | 0 | 0 | 49.8348
4244 | 0 | 2.2478 | 1.0185 | 31.7277 | 0 | 34.994 | 0 | 0 | 31.7277
4245 | 0 | 2.6023 | 1.0722 | 21.938 | 0 | 25.6125 | 0 | 0 | 21.938
4246 | 0 | 2.8473 | 1.1947 | 27.0798 | 0 | 31.1218 | 0 | 0 | 27.0798
4247 | 0 | 2.7138 | 1.3147 | 21.179 | 0 | 25.2075 | 0 | 0 | 21.179
4248 | 0 | 2.7813 | 2.7569 | 29.4693 | 0 | 35.0075 | 0 | 0 | 29.4693
4249 | 0 | 2.6791 | 4.3028 | 27.8638 | 0 | 34.8457 | 0 | 0 | 27.8638
4250 | 0 | 2.5348 | 3.0702 | 30.6409 | 0 | 36.2459 | 0 | 0 | 30.6409
4251 | 0 | 2.382 | 2.3713 | 28.425 | 0 | 33.1783 | 0 | 0 | 28.425
4252 | 0 | 2.4899 | 2.2727 | 28.6482 | 0 | 33.4109 | 0 | 0 | 28.6482
4253 | 8.8819 | 2.4615 | 2.0277 | 28.6772 | 0 | 42.0484 | 0 | 0 | 37.5591
4254 | 62.5378 | 2.2901 | 1.8545 | 27.9757 | 0 | 94.658 | 0 | 0 | 90.5135
4255 | 71.3594 | 2.663 | 1.8626 | 25.5212 | 0 | 101.4063 | 0 | 0 | 96.8806
4256 | 42.3472 | 2.3591 | 1.8002 | 23.4934 | 10.7862 | 80.7862 | 0 | 0 | 76.6269
4257 | 22.9115 | 2.1501 | 1.7611 | 15.7196 | 15.2332 | 57.7756 | 0 | 0 | 53.8644
4258 | 56.6401 | 2.3502 | 1.7681 | 27.1923 | 22.171 | 110.1218 | 0 | 0 | 106.0034
4259 | 73.689 | 2.3136 | 1.3773 | 20.1176 | 14.0057 | 111.5032 | 0 | 0 | 107.8123
4260 | 71.9561 | 2.9189 | 2.3299 | 35.8245 | 19.0728 | 132.1023 | 0 | 0 | 126.8535
4261 | 64.4014 | 2.5785 | 2.3888 | 20.3812 | 15.4565 | 105.2064 | 0 | 0 | 100.2391
4262 | 5.5607 | 2.7922 | 2.0295 | 24.8987 | 23.9855 | 59.2666 | 0 | 0 | 54.4449
4263 | 0 | 2.5072 | 1.9886 | 34.2479 | 17.9532 | 56.697 | 0 | 0 | 52.2011
4264 | 0 | 3.2112 | 2.2272 | 27.5451 | 16.4161 | 49.3997 | 0 | 0 | 43.9612
4265 | 0 | 2.7837 | 2.1199 | 23.5221 | 9.6585 | 38.0842 | 0 | 0 | 33.1806
4266 | 0 | 2.847 | 1.5861 | 19.1601 | 9.5108 | 33.104 | 0 | 0 | 28.6709
4267 | 0 | 2.382 | 1.239 | 35.6638 | 9.8099 | 49.0948 | 0 | 0 | 45.4737
4268 | 0 | 2.906 | 1.0185 | 27.0427 | 0 | 30.9672 | 0 | 0 | 27.0427
4269 | 0 | 2.5774 | 1.0722 | 29.4854 | 0 | 33.1349 | 0 | 0 | 29.4854
4270 | 0 | 2.4498 | 1.1947 | 24.8768 | 0 | 28.5213 | 0 | 0 | 24.8768
4271 | 0 | 2.3301 | 1.2542 | 30.1057 | 0 | 33.69 | 0 | 0 | 30.1057
4272 | 0 | 2.3752 | 2.7569 | 23.1979 | 0 | 28.33 | 0 | 0 | 23.1979
4273 | 0 | 2.5402 | 4.3028 | 29.5139 | 0 | 36.3569 | 0 | 0 | 29.5139
4274 | 0 | 2.7557 | 3.0702 | 28.5794 | 0 | 34.4053 | 0 | 0 | 28.5794
4275 | 0 | 2.9002 | 2.3713 | 30.1312 | 0 | 35.4026 | 0 | 0 | 30.1312
4276 | 0 | 2.7084 | 2.2727 | 31.5074 | 0 | 36.4886 | 0 | 0 | 31.5074
4277 | 4.875 | 2.4675 | 2.0277 | 23.6478 | 0 | 33.018 | 0 | 0 | 28.5228
4278 | 32.7894 | 2.562 | 1.8545 | 32.1547 | 0 | 69.3605 | 0 | 0 | 64.944
4279 | 75.2433 | 2.1855 | 1.8626 | 29.9561 | 0 | 109.2475 | 0 | 0 | 105.1994
4280 | 75.5857 | 2.4388 | 1.8002 | 26.11 | 13.5846 | 119.5193 | 0 | 0 | 115.2802
4281 | 73.085 | 2.6056 | 1.7611 | 20.0284 | 4.5815 | 102.0616 | 0 | 0 | 97.6949
4282 | 61.0093 | 2.2164 | 1.7681 | 32.6044 | 6.8518 | 104.45 | 0 | 0 | 100.4655
4283 | 57.5689 | 2.9835 | 1.3773 | 27.1788 | 7.4996 | 96.6081 | 0 | 0 | 92.2473
4284 | 53.3763 | 2.2391 | 2.3299 | 23.5632 | 11.6274 | 93.1358 | 0 | 0 | 88.5669
4285 | 84.7445 | 2.3846 | 2.3888 | 30.6176 | 18.398 | 138.5335 | 0 | 0 | 133.7601
4286 | 85.9538 | 2.3169 | 2.0295 | 28.0794 | 12.62 | 130.9995 | 0 | 0 | 126.6531
4287 | 73.116 | 2.5232 | 1.9886 | 32.7491 | 15.7693 | 126.1462 | 0 | 0 | 121.6344
4288 | 17.9019 | 2.7783 | 2.2272 | 27.86 | 10.0734 | 60.8408 | 0 | 0 | 55.8353
4289 | 0 | 2.7612 | 2.1199 | 34.25 | 16.5806 | 55.7117 | 0 | 0 | 50.8307
4290 | 0 | 1.9752 | 1.5861 | 23.7912 | 16.9848 | 44.3374 | 0 | 0 | 40.7761
4291 | 0 | 2.5796 | 1.239 | 30.0254 | 14.4537 | 48.2977 | 0 | 0 | 44.4791
4292 | 0 | 2.2745 | 1.0185 | 34.5489 | 0 | 37.842 | 0 | 0 | 34.5489
4293 | 0 | 2.5284 | 1.0722 | 26.6921 | 0 | 30.2927 | 0 | 0 | 26.6921
4294 | 0 | 2.5862 | 1.1947 | 22.5659 | 0 | 26.3468 | 0 | 0 | 22.5659
4295 | 0 | 2.5955 | 1.2542 | 25.7539 | 0 | 29.6036 | 0 | 0 | 25.7539
4296 | 0 | 2.6874 | 2.7569 | 19.5012 | 0 | 24.9455 | 0 | 0 | 19.5012
4297 | 0 | 2.4151 | 4.3028 | 25.6042 | 0 | 32.3221 | 0 | 0 | 25.6042
4298 | 0 | 2.822 | 3.0702 | 36.6349 | 0 | 42.527 | 0 | 0 | 36.6349
4299 | 0 | 2.7748 | 2.3713 | 20.3799 | 0 | 25.5261 | 0 | 0 | 20.3799
4300 | 0 | 2.8585 | 2.2727 | 30.9875 | 0 | 36.1188 | 0 | 0 | 30.9875
4301 | 13.8388 | 2.3576 | 2.0277 | 36.6323 | 0 | 54.8564 | 0 | 0 | 50.4711
4302 | 53.2697 | 2.4671 | 1.8545 | 25.0323 | 0 | 82.6236 | 0 | 0 | 78.302
4303 | 55.9014 | 2.509 | 1.8626 | 31.5634 | 0 | 91.8364 | 0 | 0 | 87.4648
4304 | 53.7689 | 2.5954 | 1.8002 | 28.4982 | 15.7094 | 102.3721 | 0 | 0 | 97.9765
4305 | 63.7763 | 2.9606 | 1.7611 | 30.5192 | 19.1954 | 118.2127 | 0 | 0 | 113.4909
4306 | 47.3264 | 2.5867 | 1.7681 | 29.27 | 5.32 | 86.2713 | 0 | 0 | 81.9165
4307 | 59.1653 | 2.5148 | 1.3773 | 27.7093 | 10.1737 | 100.9403 | 0 | 0 | 97.0482
4308 | 71.9734 | 2.883 | 2.3299 | 27.6186 | 24.7675 | 129.5723 | 0 | 0 | 124.3594
4309 | 53.8112 | 2.7896 | 2.3888 | 24.5951 | 13.9102 | 97.4949 | 0 | 0 | 92.3164
4310 | 7.7777 | 2.4135 | 2.0295 | 24.6202 | 13.163 | 50.0039 | 200 | 0 | 245.561
4311 | 0 | 2.4207 | 1.9886 | 28.2972 | 15.8803 | 48.5869 | 0 | 0 | 44.1775
4312 | 0 | 2.7906 | 2.2272 | 30.2499 | 16.4975 | 51.7652 | 0 | 0 | 46.7474
4313 | 0 | 2.3613 | 2.1199 | 26.2023 | 13.371 | 44.0545 | 0 | 0 | 39.5733
4314 | 0 | 2.8165 | 1.9531 | 30.8396 | -0.89985 | 34.7093 | 0 | 0 | 29.9397
4315 | 0 | 2.1336 | 1.5255 | 29.9898 | 21.7858 | 55.4348 | 0 | 0 | 51.7757
4316 | 0 | 2.655 | 1.1504 | 22.0391 | 0 | 25.8445 | 0 | 0 | 22.0391
4317 | 0 | 2.5219 | 1.1994 | 27.4249 | 0 | 31.1462 | 0 | 0 | 27.4249
4318 | 0 | 2.1766 | 1.0675 | 23.1426 | 0 | 26.3867 | 0 | 0 | 23.1426
4319 | 0 | 2.3392 | 1.3615 | 29.2458 | 0 | 32.9465 | 0 | 0 | 29.2458
4320 | 0 | 2.694 | 1.7973 | 31.2493 | 0 | 35.7406 | 0 | 0 | 31.2493
4321 | 0 | 2.145 | 2.1992 | 28.0501 | 0 | 32.3943 | 0 | 0 | 28.0501
4322 | 0 | 2.7502 | 1.9945 | 29.3584 | 0 | 34.1031 | 0 | 200 | 229.3584
4323 | 0 | 2.3833 | 3.6751 | 30.8697 | 0 | 36.9281 | 0 | 0 | 30.8697
4324 | 0 | 2.6756 | 3.2685 | 26.6693 | 0 | 32.6134 | 0 | 0 | 26.6693
4325 | 0 | 2.9681 | 2.6595 | 30.8964 | 0 | 36.524 | 0 | 0 | 30.8964
4326 | 0 | 2.3768 | 2.1561 | 15.7347 | 0 | 20.2676 | 0 | 0 | 15.7347
4327 | 0 | 2.1743 | 1.9466 | 26.8911 | 0 | 31.012 | 0 | 0 | 26.8911
4328 | 0 | 2.5222 | 1.9857 | 28.1498 | 20.8654 | 53.5231 | 0 | 0 | 49.0152
4329 | 0 | 2.5804 | 1.7436 | 18.5128 | 8.644 | 31.4809 | 0 | 0 | 27.1568
4330 | 0 | 2.3843 | 1.9834 | 33.6675 | 14.1018 | 52.137 | 0 | 0 | 47.7693
4331 | 0 | 2.4101 | 2.2739 | 32.7329 | 14.7887 | 52.2055 | 0 | 0 | 47.5215
4332 | 0 | 2.5617 | 2.4752 | 31.6508 | 14.5265 | 51.2141 | 0 | 0 | 46.1773
4333 | 0 | 2.6208 | 1.8702 | 35.8694 | 15.2222 | 55.5826 | 0 | 0 | 51.0915
4334 | 0 | 2.5406 | 2.2301 | 33.0115 | 11.0631 | 48.8453 | 0 | 0 | 44.0746
4335 | 0 | 2.1959 | 2.3118 | 29.6646 | 11.7262 | 45.8985 | 0 | 0 | 41.3908
4336 | 0 | 2.477 | 1.9 | 26.0239 | 5.9438 | 36.3447 | 0 | 0 | 31.9678
4337 | 0 | 2.6806 | 1.9367 | 30.4548 | 13.9785 | 49.0506 | 0 | 0 | 44.4332
4338 | 0 | 2.3101 | 1.5167 | 27.8886 | 18.6875 | 50.4028 | 0 | 0 | 46.576
4339 | 0 | 3.0673 | 1.4117 | 29.4974 | 8.7486 | 42.725 | 0 | 0 | 38.246
4340 | 0 | 2.6725 | 1.1486 | 21.8013 | 0 | 25.6224 | 0 | 0 | 21.8013
4341 | 0 | 2.9249 | 1.2344 | 30.534 | 0 | 34.6934 | 0 | 0 | 30.534
4342 | 0 | 2.635 | 1.1264 | 31.85 | 0 | 35.6115 | 0 | 0 | 31.85
4343 | 0 | 2.8278 | 1.1609 | 28.4316 | 0 | 32.4202 | 0 | 0 | 28.4316
4344 | 0 | 2.6927 | 1.1591 | 33.1516 | 0 | 37.0034 | 0 | 0 | 33.1516
4345 | 0 | 3.0699 | 2.1636 | 28.6264 | 0 | 33.86 | 0 | 0 | 28.6264
4346 | 0 | 2.1339 | 1.767 | 34.8612 | 0 | 38.7621 | 0 | 0 | 34.8612
4347 | 0 | 2.7243 | 2.6204 | 28.0311 | 0 | 33.3759 | 0 | 0 | 28.0311
4348 | 0 | 2.7001 | 2.6397 | 27.9065 | 0 | 33.2463 | 0 | 0 | 27.9065
4349 | 0 | 2.6374 | 2.3626 | 22.3091 | 0 | 27.3091 | 0 | 0 | 22.3091
4350 | 0 | 2.5266 | 1.8189 | 24.0556 | 0 | 28.4011 | 0 | 0 | 24.0556
4351 | 0 | 2.7361 | 1.9431 | 34.0983 | 0 | 38.7775 | 0 | 0 | 34.0983
4352 | 0 | 2.6039 | 1.9321 | 27.1864 | 23.3333 | 55.0556 | 0 | 0 | 50.5197
4353 | 0 | 3.0223 | 1.7582 | 25.7298 | 16.684 | 47.1944 | 0 | 0 | 42.4138
4354 | 0 | 2.9868 | 1.4747 | 25.6062 | 18.1585 | 48.2262 | 0 | 0 | 43.7647
4355 | 0 | 2.8808 | 1.8335 | 26.7491 | 13.1201 | 44.5835 | 0 | 0 | 39.8692
4356 | 0 | 2.5219 | 2.0907 | 25.8589 | 28.4641 | 58.9356 | 0 | 0 | 54.323
4357 | 0 | 3.4984 | 2.2196 | 27.3713 | 21.2046 | 54.2939 | 0 | 0 | 48.5759
4358 | 0 | 2.5647 | 2.2605 | 32.1528 | 5.4189 | 42.3969 | 0 | 0 | 37.5717
4359 | 0 | 3.2314 | 2.1706 | 34.227 | 17.9628 | 57.5918 | 0 | 0 | 52.1897
4360 | 0 | 3.0145 | 2.1677 | 21.9738 | 18.3076 | 45.4637 | 0 | 0 | 40.2814
4361 | 0 | 3.2722 | 2.1706 | 23.3605 | 8.7337 | 37.537 | 0 | 0 | 32.0941
4362 | 0 | 2.776 | 1.5861 | 30.6984 | 20.5536 | 55.614 | 0 | 0 | 51.2519
4363 | 0 | 3.0264 | 1.239 | 33.1753 | 17.7622 | 55.2029 | 0 | 0 | 50.9375
4364 | 0 | 3.1286 | 1.0185 | 26.1847 | 0 | 30.3318 | 0 | 0 | 26.1847
4365 | 0 | 3.2242 | 1.0722 | 28.8511 | 0 | 33.1476 | 0 | 0 | 28.8511
4366 | 0 | 2.9024 | 1.1947 | 34.6715 | 0 | 38.7685 | 0 | 0 | 34.6715
4367 | 0 | 2.7678 | 1.2542 | 32.3852 | 0 | 36.4072 | 0 | 0 | 32.3852
4368 | 0 | 2.69 | 2.7569 | 30.5701 | 0 | 36.0169 | 0 | 0 | 30.5701
4369 | 0 | 2.7397 | 4.3028 | 27.6681 | 0 | 34.7105 | 0 | 0 | 27.6681
4370 | 0 | 3.5886 | 3.0702 | 24.838 | 0 | 31.4968 | 0 | 0 | 24.838
4371 | 1.9141 | 2.8735 | 2.3713 | 30.6254 | 0 | 37.7843 | 0 | 0 | 32.5395
4372 | 26.3282 | 2.3687 | 2.2727 | 31.2224 | 0 | 62.192 | 0 | 0 | 57.5505
4373 | 79.8469 | 3.2157 | 2.0277 | 28.5246 | 0 | 113.6149 | 0 | 0 | 108.3715
4374 | 71.3443 | 2.8976 | 1.8545 | 18.7278 | 0 | 94.8243 | 0 | 0 | 90.0722
4375 | 75.3256 | 3.3656 | 1.8626 | 21.3155 | 0 | 101.8694 | 0 | 0 | 96.6411
4376 | 53.5261 | 3.0489 | 1.8002 | 31.1558 | 3.3549 | 92.886 | 0 | 0 | 88.0368
4377 | 11.6105 | 2.929 | 1.7611 | 30.7616 | 17.9785 | 65.0408 | 0 | 0 | 60.3506
4378 | 2.1539 | 2.9702 | 1.7681 | 23.0906 | 19.3863 | 49.3692 | 0 | 0 | 44.6309
4379 | 25.9571 | 3.0008 | 1.3773 | 36.414 | 15.1566 | 81.9058 | 0 | 0 | 77.5277
4380 | 54.6077 | 2.8913 | 2.3299 | 23.3893 | 10.7888 | 94.0069 | 0 | 0 | 88.7857
4381 | 1.7313 | 3.2807 | 2.3888 | 27.1154 | 17.0569 | 51.5732 | 0 | 0 | 45.9036
4382 | 0 | 3.1692 | 2.0295 | 24.8668 | 16.9559 | 47.0214 | 0 | 0 | 41.8227
4383 | 0 | 2.2875 | 1.9886 | 22.7284 | 14.1136 | 41.1182 | 200 | 0 | 236.842
4384 | 0 | 2.8244 | 2.2272 | 28.9225 | 16.3871 | 50.3612 | 0 | 0 | 45.3096
4385 | 0 | 3.4402 | 2.1199 | 29.8134 | 15.7654 | 51.1389 | 0 | 0 | 45.5788
4386 | 0 | 3.4845 | 1.5861 | 27.2537 | 15.5534 | 47.8777 | 0 | 0 | 42.8071
4387 | 6.9961 | 2.9 | 1.239 | 25.718 | 16.7326 | 53.5858 | 0 | 0 | 49.4468
4388 | 39.8428 | 2.9911 | 1.0185 | 33.5439 | 0 | 77.3963 | 0 | 0 | 73.3867
4389 | 67.8248 | 3.2076 | 1.0722 | 30.6961 | 0 | 102.8008 | 0 | 0 | 98.5209
4390 | 61.1503 | 3.1103 | 1.1947 | 22.7308 | 0 | 88.1861 | 0 | 0 | 83.8811
4391 | 5.8032 | 3.312 | 1.2542 | 33.0703 | 0 | 43.4397 | 0 | 0 | 38.8735
4392 | 0 | 3.0317 | 2.7569 | 26.217 | 0 | 32.0056 | 0 | 0 | 26.217
4393 | 0 | 3.2924 | 4.3028 | 29.241 | 0 | 36.8362 | 0 | 0 | 29.241
4394 | 0 | 3.0159 | 3.0702 | 30.8636 | 0 | 36.9497 | 0 | 0 | 30.8636
4395 | 0 | 2.7925 | 2.3713 | 28.0574 | 0 | 33.2212 | 0 | 0 | 28.0574
4396 | 2.41 | 2.6932 | 2.2727 | 23.3577 | 0 | 30.7336 | 0 | 0 | 25.7677
4397 | 24.6027 | 2.9079 | 2.0277 | 19.9508 | 0 | 49.4891 | 0 | 0 | 44.5534
4398 | 82.2719 | 3.0517 | 1.8545 | 21.5949 | 0 | 108.7729 | 0 | 0 | 103.8668
4399 | 74.8266 | 3.197 | 1.8626 | 33.2036 | 0 | 113.0899 | 0 | 0 | 108.0302
4400 | 90.2169 | 3.2539 | 1.8002 | 21.7118 | 12.8464 | 129.8292 | 0 | 0 | 124.7751
4401 | 71.2308 | 2.9889 | 1.7611 | 29.55 | 4.2527 | 109.7836 | 0 | 0 | 105.0336
4402 | 64.4601 | 2.5711 | 1.7681 | 24.5988 | 21.2229 | 114.621 | 0 | 0 | 110.2817
4403 | 89.6419 | 2.95 | 1.3773 | 30.8351 | 14.6683 | 139.4725 | 0 | 0 | 135.1453
4404 | 100.3303 | 3.2675 | 2.3299 | 27.1995 | 16.093 | 149.2202 | 0 | 0 | 143.6228
4405 | 81.4918 | 2.8362 | 2.3888 | 25.388 | 15.0971 | 127.2019 | 0 | 0 | 121.9768
4406 | 11.4528 | 2.8318 | 2.0295 | 24.409 | 17.7162 | 58.4393 | 0 | 0 | 53.578
4407 | 0 | 2.737 | 1.9886 | 24.127 | 22.3889 | 51.2415 | 0 | 0 | 46.5159
4408 | 0 | 2.7568 | 2.2272 | 27.2433 | 18.0385 | 50.2658 | 0 | 0 | 45.2818
4409 | 0 | 2.7758 | 2.1199 | 25.383 | 16.1314 | 46.4101 | 0 | 0 | 41.5143
4410 | 3.5816 | 2.7278 | 1.5861 | 34.6517 | 0.13829 | 42.6854 | 0 | 0 | 38.3715
4411 | 11.1298 | 3.2061 | 1.239 | 30.0543 | 13.3864 | 59.0157 | 0 | 0 | 54.5705
4412 | 0 | 2.8156 | 1.0185 | 29.8185 | 0 | 33.6525 | 0 | 0 | 29.8185
4413 | 15.5464 | 2.7636 | 1.0722 | 18.3233 | 0 | 37.7055 | 0 | 0 | 33.8698
4414 | 48.7934 | 2.6729 | 1.1947 | 25.7411 | 0 | 78.4021 | 0 | 0 | 74.5345
4415 | 30.015 | 3.3662 | 1.2542 | 29.8178 | 0 | 64.4532 | 0 | 0 | 59.8328
4416 | 22.5912 | 3.1899 | 2.7569 | 26.7246 | 0 | 55.2626 | 0 | 0 | 49.3157
4417 | 49.1808 | 2.5558 | 4.3028 | 28.695 | 0 | 84.7344 | 0 | 0 | 77.8758
4418 | 26.1616 | 3.0386 | 3.0702 | 17.7396 | 0 | 50.0099 | 0 | 0 | 43.9011
4419 | 0 | 2.7231 | 2.3713 | 30.9695 | 0 | 36.064 | 0 | 0 | 30.9695
4420 | 0 | 2.9929 | 2.2727 | 24.9729 | 0 | 30.2385 | 0 | 0 | 24.9729
4421 | 11.0506 | 2.5735 | 2.0277 | 27.9547 | 0 | 43.6065 | 0 | 0 | 39.0053
4422 | 68.8002 | 2.3867 | 1.8545 | 32.7748 | 0 | 105.8162 | 0 | 200 | 301.5751
4423 | 97.8392 | 2.8838 | 1.8626 | 29.9179 | 0 | 132.5035 | 0 | 0 | 127.7571
4424 | 65.2658 | 3.1182 | 1.8002 | 22.2463 | 5.1309 | 97.5614 | 0 | 0 | 92.643
4425 | 66.8638 | 3.0134 | 1.7611 | 28.7912 | 13.5079 | 113.9375 | 0 | 0 | 109.1629
4426 | 40.6397 | 3.3333 | 1.7681 | 25.3722 | 6.1944 | 77.3078 | 0 | 0 | 72.2063
4427 | 30.2645 | 2.9844 | 1.3773 | 22.5025 | 9.8483 | 66.9769 | 0 | 0 | 62.6153
4428 | 19.6324 | 3.1549 | 2.3299 | 23.1438 | 12.7587 | 61.0198 | 0 | 0 | 55.535
4429 | 0 | 2.9812 | 2.3888 | 33.9524 | 15.4607 | 54.7831 | 0 | 0 | 49.413
4430 | 0 | 2.5715 | 2.0295 | 24.8155 | 3.4556 | 32.8721 | 0 | 0 | 28.2711
4431 | 0 | 3.016 | 1.9886 | 26.8254 | 9.2657 | 41.0958 | 0 | 0 | 36.0911
4432 | 0 | 3.2994 | 2.2272 | 25.9739 | 16.7501 | 48.2507 | 0 | 0 | 42.724
4433 | 0 | 2.8019 | 2.1199 | 20.681 | 23.0624 | 48.6652 | 0 | 0 | 43.7434
4434 | 0 | 2.9697 | 1.5861 | 27.6574 | 12.4769 | 44.69 | 0 | 0 | 40.1342
4435 | 0.46801 | 3.2337 | 1.239 | 27.6749 | 21.5314 | 54.1471 | 0 | 0 | 49.6744
4436 | 19.247 | 2.7272 | 1.0185 | 22.5403 | 0 | 45.5331 | 0 | 0 | 41.7873
4437 | 73.1731 | 2.4775 | 1.0722 | 25.355 | 0 | 102.0777 | 0 | 0 | 98.528
4438 | 36.5974 | 2.9515 | 1.1947 | 24.5464 | 0 | 65.2901 | 0 | 0 | 61.1438
4439 | 27.724 | 2.5368 | 1.2542 | 29.3753 | 0 | 60.8903 | 0 | 0 | 57.0993
4440 | 12.5272 | 2.997 | 2.7569 | 27.7202 | 0 | 46.0013 | 0 | 0 | 40.2474
4441 | 6.4368 | 3.1696 | 4.3028 | 31.5397 | 0 | 45.4489 | 0 | 0 | 37.9765
4442 | 20.1456 | 2.3947 | 3.0702 | 26.663 | 0 | 52.2735 | 0 | 0 | 46.8086
4443 | 0 | 2.6802 | 2.3713 | 27.8158 | 0 | 32.8673 | 0 | 0 | 27.8158
4444 | 13.9569 | 2.8528 | 2.2727 | 25.8198 | 0 | 44.9023 | 0 | 0 | 39.7767
4445 | 58.7869 | 3.0732 | 2.0277 | 23.9845 | 0 | 87.8723 | 0 | 0 | 82.7714
4446 | 62.8161 | 2.8156 | 1.8545 | 26.2763 | 0 | 93.7625 | 0 | 0 | 89.0924
4447 | 42.3795 | 3.2721 | 1.8626 | 29.0443 | 0 | 76.5585 | 0 | 0 | 71.4238
4448 | 47.2381 | 2.696 | 1.8002 | 28.2978 | 10.4899 | 90.522 | 0 | 0 | 86.0258
4449 | 0.34475 | 3.5475 | 1.7611 | 28.3793 | 6.7693 | 40.802 | 0 | 0 | 35.4934
4450 | 14.9834 | 2.8793 | 1.7681 | 20.4401 | 15.2667 | 55.3375 | 0 | 0 | 50.6901
4451 | 55.4258 | 3.281 | 1.3773 | 23.8728 | 17.257 | 101.214 | 200 | 0 | 296.5557
4452 | 75.1265 | 2.5785 | 2.3299 | 27.9765 | 18.6596 | 126.6711 | 0 | 0 | 121.7626
4453 | 58.1637 | 3.3264 | 2.3888 | 28.0584 | 12.7137 | 104.651 | 0 | 0 | 98.9358
4454 | 42.8496 | 3.1549 | 2.0295 | 36.4518 | 15.7912 | 100.277 | 0 | 0 | 95.0926
4455 | 45.08 | 2.7112 | 1.9886 | 29.113 | 2.114 | 81.0068 | 0 | 0 | 76.307
4456 | 16.5623 | 3.429 | 2.2272 | 29.237 | 15.7544 | 67.2099 | 0 | 0 | 61.5537
4457 | 56.5653 | 2.9993 | 2.1199 | 25.9145 | 10.0861 | 97.6852 | 0 | 0 | 92.566
4458 | 82.8399 | 3.2359 | 1.5861 | 27.4596 | 11.2324 | 126.354 | 0 | 0 | 121.5319
4459 | 35.7473 | 2.4652 | 1.239 | 27.7256 | 9.1187 | 76.2959 | 0 | 0 | 72.5916
4460 | 0 | 3.3991 | 1.0185 | 25.6601 | 0 | 30.0777 | 0 | 0 | 25.6601
4461 | 3.1871 | 2.869 | 1.0722 | 30.337 | 0 | 37.4653 | 0 | 0 | 33.5241
4462 | 33.3341 | 3.3217 | 1.1947 | 30.8452 | 0 | 68.6956 | 0 | 0 | 64.1792
4463 | 58.0779 | 3.06 | 1.2542 | 25.7052 | 0 | 88.0973 | 0 | 0 | 83.7831
4464 | 5.2094 | 2.5467 | 2.7569 | 24.8468 | 0 | 35.3599 | 0 | 0 | 30.0563
4465 | 0 | 3.0751 | 4.3028 | 22.2761 | 0 | 29.6541 | 0 | 0 | 22.2761
4466 | 0 | 3.3509 | 3.0702 | 22.5288 | 0 | 28.9499 | 0 | 0 | 22.5288
4467 | 0 | 3.0561 | 2.3713 | 29.0898 | 0 | 34.5172 | 0 | 0 | 29.0898
4468 | 0 | 2.7958 | 2.2727 | 24.9835 | 0 | 30.052 | 0 | 0 | 24.9835
4469 | 15.4132 | 2.9261 | 2.0277 | 24.4483 | 0 | 44.8153 | 0 | 0 | 39.8615
4470 | 37.2179 | 2.7902 | 1.8545 | 29.1983 | 0 | 71.0609 | 0 | 0 | 66.4162
4471 | 6.3469 | 2.6106 | 1.8626 | 28.4321 | 0 | 39.2523 | 0 | 0 | 34.7791
4472 | 4.5992 | 2.4561 | 1.8002 | 30.2787 | 1.0773 | 40.2116 | 0 | 0 | 35.9553
4473 | 33.2125 | 2.9827 | 1.7611 | 26.4093 | 12.9448 | 77.3105 | 0 | 0 | 72.5666
4474 | 59.6927 | 2.8187 | 1.7681 | 24.9706 | 1.0291 | 90.2792 | 0 | 0 | 85.6924
4475 | 2.9003 | 3.0777 | 1.3773 | 32.3407 | -0.73835 | 38.9576 | 0 | 0 | 34.5027
4476 | 0 | 2.502 | 2.3299 | 26.163 | 12.2486 | 43.2436 | 0 | 0 | 38.4116
4477 | 0 | 3.3452 | 2.3888 | 27.0212 | 17.7796 | 50.5349 | 0 | 0 | 44.8008
4478 | 0 | 2.941 | 2.0295 | 23.4257 | 14.9674 | 43.3636 | 0 | 0 | 38.3931
4479 | 0 | 2.9675 | 1.9886 | 25.3803 | 23.8597 | 54.1963 | 0 | 0 | 49.2401
4480 | 0 | 2.8074 | 2.2272 | 24.6105 | 16.6163 | 46.2614 | 0 | 0 | 41.2268
4481 | 0 | 3.0688 | 2.1199 | 15.734 | 25.0735 | 45.9961 | 0 | 0 | 40.8075
4482 | 0 | 2.3713 | 1.9531 | 30.1716 | 17.2868 | 51.7828 | 0 | 0 | 47.4584
4483 | 0 | 3.2197 | 1.5255 | 21.5254 | 14.9778 | 41.2483 | 0 | 0 | 36.5032
4484 | 0 | 2.9224 | 1.1504 | 26.8087 | 0 | 30.8815 | 0 | 0 | 26.8087
4485 | 0 | 2.4597 | 1.1994 | 23.5494 | 0 | 27.2085 | 0 | 0 | 23.5494
4486 | 0 | 2.6554 | 1.0675 | 25.1584 | 0 | 28.8813 | 0 | 0 | 25.1584
4487 | 0 | 3.4099 | 1.3615 | 26.485 | 0 | 31.2565 | 0 | 0 | 26.485
4488 | 0 | 3.4269 | 1.7973 | 21.456 | 0 | 26.6802 | 0 | 0 | 21.456
4489 | 0 | 2.8005 | 2.1992 | 27.3453 | 0 | 32.345 | 0 | 0 | 27.3453
4490 | 0 | 3.1552 | 1.9945 | 27.3063 | 0 | 32.456 | 0 | 0 | 27.3063
4491 | 0 | 2.7905 | 3.6751 | 34.8906 | 0 | 41.3562 | 0 | 0 | 34.8906
4492 | 0 | 2.8419 | 3.2685 | 29.0103 | 0 | 35.1207 | 0 | 0 | 29.0103
4493 | 0 | 3.1746 | 2.6595 | 24.0802 | 0 | 29.9143 | 0 | 0 | 24.0802
4494 | 0 | 2.3586 | 2.1561 | 23.4372 | 0 | 27.9518 | 0 | 0 | 23.4372
4495 | 0 | 3.0801 | 1.9466 | 26.2293 | 0 | 31.256 | 0 | 0 | 26.2293
4496 | 0 | 2.837 | 1.9857 | 26.5366 | 9.2152 | 40.5745 | 0 | 0 | 35.7518
4497 | 0 | 2.8026 | 1.7436 | 24.0024 | 17.0039 | 45.5526 | 0 | 0 | 41.0064
4498 | 0 | 2.8829 | 1.9834 | 25.9574 | 17.0148 | 47.8386 | 0 | 0 | 42.9723
4499 | 0 | 3.0263 | 2.2739 | 30.1876 | 20.0525 | 55.5403 | 0 | 0 | 50.2401
4500 | 0 | 2.8159 | 2.4752 | 19.0691 | 8.6765 | 33.0367 | 0 | 0 | 27.7456
4501 | 0 | 3.1931 | 1.8702 | 26.1965 | 14.3547 | 45.6145 | 0 | 0 | 40.5512
4502 | 0 | 2.8825 | 2.2301 | 26.3632 | 21.2143 | 52.6901 | 0 | 0 | 47.5775
4503 | 0 | 3.1917 | 2.3118 | 34.2957 | 12.9756 | 52.7748 | 0 | 0 | 47.2713
4504 | 0 | 3.6472 | 1.9 | 27.1617 | 10.7856 | 43.4945 | 0 | 0 | 37.9473
4505 | 0 | 2.4505 | 1.9367 | 22.98 | -2.9201 | 24.4471 | 0 | 0 | 20.0599
4506 | 0 | 2.7319 | 1.5167 | 25.5168 | 15.9297 | 45.6951 | 0 | 0 | 41.4465
4507 | 0 | 2.9331 | 1.4117 | 26.4935 | 23.6181 | 54.4564 | 0 | 0 | 50.1116
4508 | 0 | 3.2708 | 1.1486 | 23.3173 | 0 | 27.7367 | 0 | 0 | 23.3173
4509 | 0 | 2.7379 | 1.2344 | 27.2687 | 0 | 31.2409 | 0 | 0 | 27.2687
4510 | 0 | 2.6271 | 1.1264 | 27.8964 | 0 | 31.65 | 0 | 0 | 27.8964
4511 | 0 | 2.2926 | 1.1609 | 24.101 | 0 | 27.5544 | 0 | 0 | 24.101
4512 | 0 | 2.9764 | 1.1591 | 20.3061 | 0 | 24.4417 | 0 | 0 | 20.3061
4513 | 0 | 3.0238 | 2.1636 | 27.6087 | 0 | 32.7962 | 0 | 0 | 27.6087
4514 | 0 | 2.7948 | 1.767 | 35.117 | 0 | 39.6788 | 0 | 0 | 35.117
4515 | 0 | 2.9638 | 2.6204 | 31.8897 | 0 | 37.4739 | 0 | 0 | 31.8897
4516 | 0 | 2.6704 | 2.6397 | 26.2423 | 0 | 31.5523 | 0 | 0 | 26.2423
4517 | 0 | 2.8892 | 2.3626 | 27.5277 | 0 | 32.7795 | 0 | 0 | 27.5277
4518 | 0 | 2.7128 | 1.8189 | 29.0599 | 0 | 33.5916 | 0 | 0 | 29.0599
4519 | 0 | 3.1474 | 1.9431 | 24.2116 | 0 | 29.3021 | 200 | 0 | 224.2116
4520 | 0 | 2.2355 | 1.9321 | 28.0984 | 10.8254 | 43.0914 | 0 | 0 | 38.9238
4521 | 0 | 2.5853 | 1.7582 | 24.8843 | 8.2307 | 37.4585 | 0 | 0 | 33.115
4522 | 0 | 2.9077 | 1.4747 | 25.5625 | 14.0909 | 44.0358 | 0 | 0 | 39.6534
4523 | 0 | 2.6967 | 1.8335 | 31.0089 | 18.1168 | 53.6559 | 0 | 0 | 49.1257
4524 | 0 | 2.9774 | 2.0907 | 31.1782 | 13.4455 | 49.6918 | 0 | 200 | 244.6237
4525 | 0 | 3.2205 | 2.2196 | 24.9474 | 5.6991 | 36.0866 | 0 | 0 | 30.6465
4526 | 0 | 2.665 | 2.2605 | 30.1465 | 9.0457 | 44.1177 | 0 | 0 | 39.1922
4527 | 0 | 3.1155 | 2.1706 | 30.9325 | 21.2879 | 57.5066 | 0 | 0 | 52.2204
4528 | 0 | 2.8479 | 2.1677 | 24.0314 | 17.5911 | 46.6382 | 0 | 0 | 41.6226
4529 | 0 | 2.9872 | 2.1706 | 24.9534 | 3.3364 | 33.4477 | 0 | 0 | 28.2898
4530 | 0 | 2.8036 | 1.5861 | 15.2041 | 13.5372 | 33.1311 | 0 | 0 | 28.7414
4531 | 0 | 2.4673 | 1.239 | 25.2679 | 15.9773 | 44.9515 | 0 | 0 | 41.2451
4532 | 0 | 3.2641 | 1.0185 | 19.4321 | 0 | 23.7147 | 0 | 0 | 19.4321
4533 | 0 | 2.6517 | 1.0722 | 30.7558 | 0 | 34.4797 | 0 | 0 | 30.7558
4534 | 0 | 3.0573 | 1.1947 | 29.9711 | 0 | 34.2231 | 0 | 0 | 29.9711
4535 | 0 | 2.7098 | 1.2542 | 27.6325 | 0 | 31.5965 | 0 | 0 | 27.6325
4536 | 0 | 2.2962 | 2.7569 | 17.7274 | 0 | 22.7805 | 0 | 0 | 17.7274
4537 | 0 | 2.401 | 4.3028 | 30.1682 | 0 | 36.8719 | 0 | 0 | 30.1682
4538 | 0 | 3.2089 | 3.0702 | 29.7873 | 0 | 36.0664 | 0 | 0 | 29.7873
4539 | 0 | 3.2592 | 2.3713 | 32.9086 | 0 | 38.5392 | 0 | 0 | 32.9086
4540 | 13.6556 | 2.9603 | 2.2727 | 25.7108 | 0 | 44.5994 | 0 | 0 | 39.3664
4541 | 46.666 | 2.671 | 2.0277 | 25.4026 | 0 | 76.7673 | 0 | 0 | 72.0686
4542 | 82.0891 | 2.481 | 1.8545 | 25.3875 | 0 | 111.8121 | 0 | 0 | 107.4766
4543 | 80.0357 | 3.2608 | 1.8626 | 29.265 | 0 | 114.4242 | 0 | 0 | 109.3008
4544 | 56.9821 | 2.6878 | 1.8002 | 29.8059 | 10.8196 | 102.0956 | 0 | 0 | 97.6076
4545 | 59.874 | 2.5324 | 1.7611 | 24.8773 | 22.8244 | 111.8693 | 0 | 0 | 107.5758
4546 | 3.3629 | 3.0424 | 1.7681 | 23.699 | 25.4095 | 57.2818 | 0 | 0 | 52.4713
4547 | 6.6609 | 2.7394 | 1.3773 | 31.5997 | 15.6634 | 58.0406 | 0 | 0 | 53.9239
4548 | 35.282 | 2.8923 | 2.3299 | 29.3936 | 4.082 | 73.9799 | 0 | 0 | 68.7576
4549 | 83.0872 | 2.7678 | 2.3888 | 32.8345 | 19.0528 | 140.1311 | 0 | 0 | 134.9745
4550 | 67.2836 | 3.108 | 2.0295 | 26.6611 | 14.3225 | 113.4048 | 0 | 0 | 108.2673
4551 | 25.5222 | 2.3829 | 1.9886 | 23.5441 | 20.2501 | 73.688 | 0 | 0 | 69.3164
4552 | 0 | 2.8691 | 2.2272 | 31.609 | 13.7926 | 50.4979 | 0 | 0 | 45.4016
4553 | 0 | 2.6169 | 2.1199 | 24.5438 | 9.0341 | 38.3147 | 0 | 0 | 33.5779
4554 | 0 | 3.0355 | 1.5861 | 32.0575 | 5.5243 | 42.2035 | 0 | 0 | 37.5818
4555 | 0 | 2.7587 | 1.239 | 25.2489 | 13.264 | 42.5105 | 0 | 0 | 38.5128
4556 | 0 | 3.0937 | 1.0185 | 25.3026 | 0 | 29.4149 | 0 | 0 | 25.3026
4557 | 0 | 2.8928 | 1.0722 | 34.1072 | 0 | 38.0722 | 0 | 0 | 34.1072
4558 | 0 | 2.9988 | 1.1947 | 30.0028 | 0 | 34.1964 | 0 | 0 | 30.0028
4559 | 0 | 2.7358 | 1.2542 | 29.3333 | 0 | 33.3233 | 0 | 0 | 29.3333
4560 | 0 | 2.8779 | 2.7569 | 31.6635 | 0 | 37.2984 | 0 | 0 | 31.6635
4561 | 0 | 2.5288 | 4.3028 | 32.1413 | 0 | 38.9729 | 0 | 0 | 32.1413
4562 | 0 | 2.7829 | 3.0702 | 26.1927 | 0 | 32.0457 | 0 | 0 | 26.1927
4563 | 0 | 2.8035 | 2.4632 | 27.1904 | 0 | 32.457 | 0 | 0 | 27.1904
4564 | 0 | 2.825 | 2.2727 | 34.5111 | 0 | 39.6088 | 0 | 0 | 34.5111
4565 | 0.10013 | 2.5596 | 2.0277 | 20.1026 | 0 | 24.79 | 0 | 0 | 20.2027
4566 | 8.5951 | 2.6815 | 1.8545 | 27.1873 | 0 | 40.3184 | 0 | 0 | 35.7824
4567 | 51.8611 | 3.1383 | 1.8626 | 37.0647 | 0 | 93.9267 | 0 | 0 | 88.9258
4568 | 88.6411 | 2.5909 | 1.8002 | 25.4659 | 23.5289 | 142.027 | 0 | 0 | 137.6358
4569 | 74.0333 | 3.3261 | 1.7611 | 26.2102 | 12.5478 | 117.8785 | 0 | 0 | 112.7913
4570 | 75.2196 | 2.9045 | 1.7681 | 28.8615 | 12.9572 | 121.711 | 0 | 0 | 117.0384
4571 | 37.4781 | 3.1108 | 1.3773 | 28.6077 | 15.313 | 85.8869 | 0 | 0 | 81.3988
4572 | 1.5726 | 2.0519 | 2.3299 | 21.5537 | 6.8299 | 34.3381 | 0 | 0 | 29.9563
4573 | 15.4673 | 2.8904 | 2.3888 | 19.4337 | 18.7384 | 58.9187 | 0 | 0 | 53.6394
4574 | 54.6942 | 2.9867 | 2.0295 | 27.5003 | 19.6911 | 106.9018 | 0 | 0 | 101.8857
4575 | 36.2096 | 2.7187 | 1.9886 | 32.9674 | 19.6267 | 93.5112 | 0 | 0 | 88.8038
4576 | 91.5393 | 2.6978 | 2.2272 | 28.0698 | 8.3122 | 132.8463 | 0 | 0 | 127.9213
4577 | 78.1711 | 3.2125 | 2.1199 | 30.7412 | 15.1712 | 129.4159 | 0 | 0 | 124.0835
4578 | 63.2982 | 3.347 | 1.5861 | 26.3585 | 9.8177 | 104.4074 | 0 | 0 | 99.4743
4579 | 18.0227 | 2.6281 | 1.239 | 29.5161 | 11.9158 | 63.3217 | 0 | 0 | 59.4546
4580 | 51.9872 | 2.8335 | 1.0185 | 16.1089 | 0 | 71.9481 | 0 | 0 | 68.0961
4581 | 17.5556 | 2.9144 | 1.0722 | 27.6197 | 0 | 49.162 | 0 | 0 | 45.1754
4582 | 0 | 2.6654 | 1.1947 | 23.0285 | 0 | 26.8887 | 0 | 0 | 23.0285
4583 | 0 | 2.9553 | 1.2542 | 32.5432 | 0 | 36.7526 | 0 | 0 | 32.5432
4584 | 0 | 2.9701 | 2.7569 | 28.8415 | 0 | 34.5685 | 0 | 0 | 28.8415
4585 | 3.1122 | 2.7964 | 4.3028 | 24.4197 | 0 | 34.6311 | 0 | 0 | 27.5319
4586 | 27.0243 | 2.8634 | 3.0702 | 29.3136 | 0 | 62.2715 | 0 | 0 | 56.3379
4587 | 69.5432 | 2.7676 | 2.3713 | 29.1636 | 0 | 103.8458 | 0 | 0 | 98.7068
4588 | 39.8825 | 3.037 | 2.2727 | 25.8441 | 0 | 71.0364 | 0 | 0 | 65.7266
4589 | 52.1507 | 2.3829 | 2.0277 | 23.7905 | 0 | 80.3518 | 0 | 0 | 75.9412
4590 | 70.5683 | 3.3239 | 1.8545 | 27.8157 | 0 | 103.5624 | 200 | 0 | 298.384
4591 | 72.3774 | 2.769 | 1.8626 | 23.5981 | 0 | 100.6072 | 0 | 0 | 95.9756
4592 | 92.334 | 3.2769 | 1.8002 | 23.6574 | 1.5132 | 122.5818 | 0 | 0 | 117.5047
4593 | 104.6911 | 2.7052 | 1.7611 | 24.8653 | 9.578 | 143.6007 | 0 | 0 | 139.1344
4594 | 103.2376 | 2.7256 | 1.7681 | 25.7407 | 12.2639 | 145.7359 | 0 | 0 | 141.2422
4595 | 103.4183 | 2.8047 | 1.3773 | 23.4519 | 20.7407 | 151.7929 | 0 | 0 | 147.6109
4596 | 97.5906 | 2.9471 | 2.3299 | 24.5473 | 21.9253 | 149.3402 | 0 | 0 | 144.0632
4597 | 104.2786 | 3.2031 | 2.3888 | 24.335 | 26.5894 | 160.7949 | 0 | 0 | 155.2031
4598 | 96.0169 | 3.0926 | 2.0295 | 31.2014 | 6.7353 | 139.0756 | 0 | 0 | 133.9536
4599 | 92.92 | 2.9796 | 1.9886 | 21.6428 | 10.2714 | 129.8024 | 0 | 0 | 124.8341
4600 | 84.9945 | 3.096 | 2.2272 | 21.5268 | 12.5597 | 124.4042 | 0 | 0 | 119.0809
4601 | 63.2212 | 2.7656 | 2.1199 | 25.8104 | -0.59752 | 93.3195 | 0 | 0 | 88.434
4602 | 0 | 3.454 | 1.5861 | 30.4568 | 4.7866 | 40.2835 | 0 | 0 | 35.2434
4603 | 0 | 2.5288 | 1.239 | 20.7302 | 24.8999 | 49.3979 | 0 | 0 | 45.6301
4604 | 0 | 2.9964 | 1.0185 | 36.3913 | 0 | 40.4062 | 0 | 0 | 36.3913
4605 | 0 | 3.4909 | 1.0722 | 25.0119 | 0 | 29.5749 | 0 | 0 | 25.0119
4606 | 20.6464 | 3.0743 | 1.1947 | 22.9315 | 0 | 47.8469 | 0 | 0 | 43.5779
4607 | 64.0617 | 3.3846 | 1.2542 | 24.7914 | 0 | 93.4919 | 0 | 0 | 88.8531
4608 | 83.3746 | 2.7898 | 2.7569 | 29.5758 | 0 | 118.4971 | 0 | 0 | 112.9503
4609 | 54.2619 | 2.4993 | 4.3028 | 23.0391 | 0 | 84.103 | 0 | 0 | 77.301
4610 | 0 | 2.7583 | 3.0702 | 29.7836 | 0 | 35.6121 | 0 | 0 | 29.7836
4611 | 0 | 3.2813 | 2.3713 | 26.3371 | 0 | 31.9897 | 0 | 0 | 26.3371
4612 | 0.39006 | 2.3063 | 2.2727 | 26.4726 | 0 | 31.4416 | 0 | 0 | 26.8626
4613 | 1.4318 | 3.0084 | 2.0277 | 23.5507 | 0 | 30.0186 | 0 | 0 | 24.9825
4614 | 0 | 2.115 | 1.8545 | 31.9997 | 0 | 35.9691 | 0 | 0 | 31.9997
4615 | 10.5331 | 2.9531 | 1.8626 | 29.9883 | 0 | 45.3371 | 0 | 0 | 40.5214
4616 | 61.0631 | 2.6845 | 1.8002 | 22.0538 | 14.8492 | 102.4508 | 0 | 0 | 97.9661
4617 | 87.2141 | 2.3955 | 1.7611 | 26.8987 | -1.4128 | 116.8566 | 0 | 0 | 112.7
4618 | 99.6781 | 2.3915 | 1.7681 | 24.8466 | 12.9319 | 141.6163 | 0 | 0 | 137.4566
4619 | 78.5427 | 3.1759 | 1.3773 | 27.8802 | 3.4892 | 114.4652 | 0 | 0 | 109.912
4620 | 98.11 | 3.157 | 2.3299 | 31.5524 | 12.1837 | 147.333 | 0 | 0 | 141.8461
4621 | 72.3033 | 3.2966 | 2.3888 | 22.867 | 3.3905 | 104.2463 | 0 | 0 | 98.5609
4622 | 19.9779 | 2.5433 | 2.0295 | 29.2511 | 14.7494 | 68.5511 | 0 | 0 | 63.9783
4623 | 14.2838 | 3.0789 | 1.9886 | 29.4632 | 19.1041 | 67.9186 | 0 | 0 | 62.8511
4624 | 52.3423 | 2.9902 | 2.2272 | 30.8011 | 22.233 | 110.5939 | 0 | 200 | 305.3764
4625 | 64.0761 | 2.4792 | 2.1199 | 28.4041 | 15.6529 | 112.7323 | 0 | 0 | 108.1332
4626 | 66.6196 | 2.7724 | 1.5861 | 24.3065 | 16.3953 | 111.68 | 0 | 0 | 107.3214
4627 | 43.7183 | 2.7288 | 1.239 | 31.1795 | 9.9834 | 88.8491 | 0 | 0 | 84.8813
4628 | 0 | 2.4705 | 1.0185 | 25.5788 | 0 | 29.0678 | 0 | 0 | 25.5788
4629 | 0 | 3.6051 | 1.0722 | 17.7226 | 0 | 22.3998 | 0 | 0 | 17.7226
4630 | 14.4101 | 2.8057 | 1.1947 | 37.3635 | 0 | 55.7739 | 0 | 0 | 51.7735
4631 | 47.1922 | 3.1871 | 1.2542 | 28.2606 | 0 | 79.8942 | 0 | 0 | 75.4528
4632 | 16.0076 | 2.9923 | 2.7569 | 28.1516 | 0 | 49.9085 | 0 | 0 | 44.1592
4633 | 0 | 3.1561 | 4.3028 | 34.3692 | 0 | 41.8281 | 0 | 0 | 34.3692
4634 | 2.4416 | 3.3065 | 3.0702 | 33.7292 | 0 | 42.5475 | 0 | 0 | 36.1708
4635 | 8.12 | 2.95 | 2.3713 | 19.6654 | 0 | 33.1068 | 0 | 0 | 27.7854
4636 | 1.5041 | 2.9506 | 2.2727 | 26.6959 | 0 | 33.4233 | 0 | 0 | 28.2
4637 | 0 | 2.6779 | 2.0277 | 18.8793 | 0 | 23.585 | 0 | 0 | 18.8793
4638 | 0 | 3.2033 | 1.8545 | 24.5264 | 0 | 29.5842 | 0 | 0 | 24.5264
4639 | 0 | 2.5837 | 1.8626 | 24.0674 | 0 | 28.5137 | 0 | 0 | 24.0674
4640 | 0.037247 | 2.6203 | 1.8002 | 30.9947 | 13.1562 | 48.6086 | 0 | 0 | 44.1882
4641 | 0.12484 | 2.7262 | 1.7611 | 26.1835 | 6.243 | 37.0387 | 0 | 0 | 32.5513
4642 | 11.9893 | 2.7643 | 1.7681 | 27.3598 | 11.4415 | 55.323 | 0 | 0 | 50.7906
4643 | 56.582 | 2.8757 | 1.3773 | 25.9002 | 8.5567 | 95.2919 | 0 | 0 | 91.0388
4644 | 56.9938 | 2.5597 | 2.3299 | 25.0158 | 12.6424 | 99.5416 | 0 | 0 | 94.652
4645 | 4.9868 | 2.7431 | 2.3888 | 18.5186 | 6.5154 | 35.1528 | 0 | 0 | 30.0209
4646 | 0 | 3.137 | 2.0295 | 29.1192 | 17.6112 | 51.8969 | 0 | 0 | 46.7304
4647 | 0 | 3.0243 | 1.9886 | 23.6691 | 14.7413 | 43.4233 | 0 | 0 | 38.4104
4648 | 0 | 3.1151 | 2.2272 | 17.8442 | 11.8924 | 35.0789 | 0 | 0 | 29.7366
4649 | 0 | 2.7707 | 2.1199 | 32.8868 | 15.2561 | 53.0335 | 0 | 0 | 48.1429
4650 | 0 | 2.9146 | 1.9531 | 22.529 | 16.5429 | 43.9396 | 0 | 0 | 39.0719
4651 | 0 | 2.819 | 1.5255 | 25.0707 | 10.8877 | 40.3029 | 0 | 0 | 35.9584
4652 | 4.2859 | 2.9701 | 1.1504 | 29.4411 | 0 | 37.8475 | 0 | 0 | 33.727
4653 | 34.1263 | 2.9048 | 1.1994 | 23.0147 | 0 | 61.2452 | 0 | 0 | 57.141
4654 | 73.5775 | 2.9621 | 1.0675 | 28.0855 | 0 | 105.6926 | 0 | 0 | 101.663
4655 | 36.0432 | 2.9167 | 1.3615 | 25.9898 | 0 | 66.3112 | 0 | 0 | 62.033
4656 | 0 | 2.9541 | 1.7973 | 26.1913 | 0 | 30.9426 | 0 | 0 | 26.1913
4657 | 0 | 2.938 | 2.1992 | 28.524 | 0 | 33.6612 | 0 | 0 | 28.524
4658 | 0 | 3.0395 | 1.9945 | 18.9235 | 0 | 23.9574 | 0 | 0 | 18.9235
4659 | 0 | 2.8269 | 3.6751 | 28.5838 | 0 | 35.0859 | 200 | 0 | 228.5838
4660 | 0 | 3.2987 | 3.2685 | 28.1392 | 0 | 34.7065 | 0 | 0 | 28.1392
4661 | 8.8284 | 2.5053 | 2.6595 | 25.5934 | 0 | 39.5866 | 0 | 0 | 34.4218
4662 | 38.8492 | 3.1194 | 2.1561 | 31.8832 | 0 | 76.0079 | 0 | 0 | 70.7324
4663 | 54.2445 | 2.6337 | 1.9466 | 22.1749 | 0 | 80.9998 | 0 | 0 | 76.4194
4664 | 5.8258 | 2.3215 | 1.9857 | 26.6589 | 23.5694 | 60.3613 | 0 | 0 | 56.0542
4665 | 5.7309 | 2.667 | 1.7436 | 25.4658 | 6.5725 | 42.1798 | 0 | 0 | 37.7691
4666 | 14.5217 | 3.1652 | 1.9834 | 30.7984 | 1.3752 | 51.8439 | 0 | 0 | 46.6953
4667 | 0 | 2.6137 | 2.2739 | 22.5296 | 19.6641 | 47.0812 | 0 | 0 | 42.1937
4668 | 0 | 2.4888 | 2.4752 | 27.9732 | 20.6905 | 53.6277 | 0 | 0 | 48.6637
4669 | 0 | 3.1417 | 1.8702 | 25.6335 | 17.875 | 48.5204 | 0 | 0 | 43.5085
4670 | 0 | 2.5849 | 2.2301 | 27.8876 | 17.5137 | 50.2163 | 0 | 0 | 45.4013
4671 | 0 | 2.8403 | 2.3118 | 30.3335 | 14.9406 | 50.4261 | 0 | 0 | 45.274
4672 | 0 | 3.3357 | 1.9 | 24.7579 | 12.8784 | 42.872 | 0 | 0 | 37.6363
4673 | 0 | 2.5277 | 1.9367 | 28.1511 | 7.6732 | 40.2888 | 0 | 0 | 35.8243
4674 | 0 | 2.3647 | 1.5167 | 27.4288 | 15.005 | 46.3153 | 0 | 0 | 42.4339
4675 | 0 | 2.7691 | 1.4117 | 28.2356 | 14.6064 | 47.0229 | 0 | 0 | 42.8421
4676 | 0 | 2.9158 | 1.1486 | 23.8915 | 0 | 27.9559 | 0 | 0 | 23.8915
4677 | 0 | 2.9193 | 1.2344 | 25.3396 | 0 | 29.4933 | 0 | 0 | 25.3396
4678 | 0 | 3.47 | 1.1264 | 14.1065 | 0 | 18.703 | 0 | 0 | 14.1065
4679 | 0 | 2.8544 | 1.1609 | 22.1088 | 0 | 26.124 | 0 | 0 | 22.1088
4680 | 0 | 2.7607 | 1.1591 | 25.1893 | 0 | 29.1091 | 0 | 0 | 25.1893
4681 | 0 | 3.2156 | 2.1636 | 22.3337 | 0 | 27.713 | 0 | 0 | 22.3337
4682 | 0 | 3.0856 | 1.767 | 29.5244 | 0 | 34.377 | 0 | 0 | 29.5244
4683 | 0 | 3.0025 | 2.6204 | 27.1882 | 0 | 32.8111 | 0 | 0 | 27.1882
4684 | 0 | 2.9438 | 2.6397 | 29.2559 | 0 | 34.8394 | 0 | 0 | 29.2559
4685 | 0 | 2.5568 | 2.3626 | 23.0164 | 0 | 27.9358 | 0 | 0 | 23.0164
4686 | 0 | 3.1795 | 1.8189 | 30.5812 | 0 | 35.5796 | 0 | 0 | 30.5812
4687 | 0 | 2.9671 | 1.9431 | 29.0708 | 0 | 33.981 | 0 | 0 | 29.0708
4688 | 0 | 3.0172 | 1.9321 | 29.7546 | 14.8882 | 49.592 | 0 | 0 | 44.6428
4689 | 0 | 3.0781 | 1.7582 | 23.748 | 13.4164 | 42.0008 | 0 | 0 | 37.1644
4690 | 0 | 2.2629 | 1.4747 | 29.2298 | 7.7309 | 40.6983 | 0 | 0 | 36.9607
4691 | 0 | 2.919 | 1.8335 | 26.2409 | 11.5559 | 42.5493 | 0 | 0 | 37.7968
4692 | 0 | 2.5119 | 2.0907 | 24.676 | 15.3182 | 44.5968 | 0 | 0 | 39.9941
4693 | 6.9466 | 2.5867 | 2.2196 | 27.1921 | 8.8587 | 47.8038 | 0 | 0 | 42.9975
4694 | 42.7523 | 2.4721 | 2.2605 | 28.6142 | 6.5117 | 82.6108 | 0 | 0 | 77.8782
4695 | 74.5143 | 2.6263 | 2.1706 | 25.1562 | 9.032 | 113.4993 | 0 | 0 | 108.7024
4696 | 39.8332 | 2.7879 | 2.1677 | 25.9155 | 12.7966 | 83.5009 | 0 | 0 | 78.5453
4697 | 0 | 2.3632 | 2.1706 | 29.3824 | 24.1407 | 58.057 | 0 | 0 | 53.5231
4698 | 0 | 3.1194 | 1.5861 | 25.0724 | 9.4824 | 39.2603 | 0 | 0 | 34.5548
4699 | 0 | 2.9053 | 1.239 | 35.5869 | 20.2423 | 59.9735 | 0 | 0 | 55.8292
4700 | 0 | 3.1313 | 1.0185 | 28.8598 | 0 | 33.0096 | 0 | 0 | 28.8598
4701 | 0 | 2.7554 | 1.0722 | 26.8624 | 0 | 30.69 | 0 | 0 | 26.8624
4702 | 0 | 2.5122 | 1.1947 | 30.7093 | 0 | 34.4162 | 0 | 0 | 30.7093
4703 | 0 | 2.5432 | 1.2542 | 26.0919 | 0 | 29.8894 | 0 | 0 | 26.0919
4704 | 0 | 2.9607 | 2.7569 | 15.6266 | 0 | 21.3442 | 0 | 0 | 15.6266
4705 | 0 | 2.7422 | 4.3028 | 22.8844 | 0 | 29.9294 | 0 | 0 | 22.8844
4706 | 0 | 2.5961 | 3.0702 | 23.4858 | 0 | 29.1521 | 0 | 0 | 23.4858
4707 | 0 | 2.925 | 2.3713 | 29.9283 | 0 | 35.2246 | 0 | 0 | 29.9283
4708 | 0.44731 | 3.2005 | 2.2727 | 34.9147 | 0 | 40.8352 | 0 | 0 | 35.362
4709 | 19.7429 | 3.1002 | 2.0277 | 25.0363 | 0 | 49.9071 | 0 | 0 | 44.7792
4710 | 76.2579 | 3.0383 | 1.8545 | 25.0159 | 0 | 106.1665 | 0 | 0 | 101.2738
4711 | 79.2633 | 2.9343 | 1.8626 | 31.6886 | 0 | 115.7488 | 0 | 0 | 110.9519
4712 | 65.5428 | 2.9768 | 1.8002 | 28.9286 | 11.8944 | 111.1429 | 0 | 0 | 106.3658
4713 | 43.257 | 2.8103 | 1.7611 | 27.4701 | 17.6185 | 92.9171 | 0 | 0 | 88.3456
4714 | 45.9313 | 3.4656 | 1.7681 | 27.1218 | -1.1796 | 77.1073 | 0 | 0 | 71.8736
4715 | 61.0021 | 2.8168 | 1.3773 | 33.8066 | 23.6902 | 122.693 | 0 | 0 | 118.4989
4716 | 67.5 | 3.1943 | 2.3299 | 33.8247 | 16.1141 | 122.9629 | 0 | 0 | 117.4387
4717 | 47.6441 | 2.9765 | 2.3888 | 20.9351 | 0.16867 | 74.1131 | 0 | 0 | 68.7479
4718 | 17.2307 | 3.0384 | 2.0295 | 26.8342 | 3.5663 | 52.6991 | 0 | 0 | 47.6313
4719 | 14.1095 | 3.0937 | 1.9886 | 30.4443 | 8.682 | 58.3182 | 0 | 0 | 53.2358
4720 | 0 | 2.5799 | 2.2272 | 24.1294 | 19.2553 | 48.1918 | 0 | 0 | 43.3847
4721 | 0 | 2.8216 | 2.1199 | 24.9905 | 8.5305 | 38.4624 | 0 | 0 | 33.5209
4722 | 0 | 3.4105 | 1.5861 | 28.9569 | 20.5278 | 54.4813 | 0 | 0 | 49.4846
4723 | 0 | 2.5505 | 1.239 | 22.4985 | 13.2687 | 39.5567 | 0 | 0 | 35.7671
4724 | 0 | 3.3822 | 1.0185 | 30.4011 | 0 | 34.8019 | 0 | 0 | 30.4011
4725 | 0 | 3.3234 | 1.0722 | 29.6932 | 0 | 34.0889 | 0 | 0 | 29.6932
4726 | 0 | 2.6849 | 1.1947 | 18.8458 | 0 | 22.7254 | 0 | 0 | 18.8458
4727 | 0 | 3.2826 | 1.2542 | 34.9186 | 0 | 39.4554 | 0 | 0 | 34.9186
4728 | 0 | 3.0007 | 2.7569 | 28.9361 | 0 | 34.6937 | 200 | 200 | 428.9361
4729 | 0 | 3.2367 | 4.3028 | 27.0097 | 0 | 34.5492 | 0 | 0 | 27.0097
4730 | 0 | 2.9303 | 3.0702 | 22.648 | 0 | 28.6484 | 0 | 0 | 22.648
4731 | 0 | 3.382 | 2.3713 | 28.6753 | 0 | 34.4287 | 0 | 0 | 28.6753
4732 | 0.51893 | 3.1656 | 2.2727 | 32.6115 | 0 | 38.5688 | 0 | 0 | 33.1305
4733 | 13.6172 | 2.8849 | 2.0277 | 26.1862 | 0 | 44.716 | 0 | 0 | 39.8033
4734 | 59.6689 | 2.4539 | 1.8545 | 26.5619 | 0 | 90.5392 | 0 | 0 | 86.2308
4735 | 56.126 | 3.1691 | 1.8626 | 22.6091 | 0 | 83.7668 | 0 | 0 | 78.7351
4736 | 29.9834 | 2.8677 | 1.8002 | 21.2917 | 15.8589 | 71.8018 | 0 | 0 | 67.134
4737 | 21.207 | 3.0147 | 1.7611 | 23.8296 | 16.7136 | 66.5259 | 0 | 0 | 61.7501
4738 | 39.9227 | 2.9492 | 1.7681 | 30.0723 | 2.7941 | 77.5065 | 0 | 0 | 72.7892
4739 | 66.4853 | 3.0194 | 1.3773 | 25.5728 | 16.5195 | 112.9743 | 0 | 0 | 108.5776
4740 | 71.5048 | 2.48 | 2.3299 | 28.2917 | 17.6877 | 122.294 | 0 | 0 | 117.4841
4741 | 49.3904 | 2.8767 | 2.3888 | 27.5683 | 23.582 | 105.8062 | 0 | 0 | 100.5406
4742 | 1.6783 | 2.7568 | 2.0295 | 20.5722 | 5.7858 | 32.8225 | 0 | 0 | 28.0363
4743 | 0 | 3.0612 | 1.9886 | 28.4295 | 21.3398 | 54.8192 | 0 | 0 | 49.7693
4744 | 0 | 2.478 | 2.2272 | 27.3412 | 17.784 | 49.8304 | 0 | 0 | 45.1252
4745 | 0 | 3.0821 | 2.1199 | 24.781 | 6.1999 | 36.1828 | 0 | 0 | 30.9808
4746 | 0 | 3.1791 | 1.5861 | 26.7444 | 17.9763 | 49.486 | 0 | 0 | 44.7207
4747 | 0 | 2.9633 | 1.239 | 27.7881 | 9.5441 | 41.5346 | 0 | 0 | 37.3323
4748 | 0 | 2.62 | 1.0185 | 25.6313 | 0 | 29.2698 | 0 | 0 | 25.6313
4749 | 0 | 3.0513 | 1.0722 | 30.8721 | 0 | 34.9956 | 0 | 0 | 30.8721
4750 | 0 | 2.1236 | 1.1947 | 27.3589 | 0 | 30.6772 | 0 | 0 | 27.3589
4751 | 0 | 2.7088 | 1.2542 | 30.8983 | 0 | 34.8613 | 0 | 0 | 30.8983
4752 | 0 | 2.9583 | 2.7569 | 22.3561 | 0 | 28.0713 | 0 | 0 | 22.3561
4753 | 0 | 2.4749 | 4.3028 | 29.8457 | 0 | 36.6234 | 0 | 0 | 29.8457
4754 | 0 | 2.9373 | 3.0702 | 30.9315 | 0 | 36.939 | 0 | 0 | 30.9315
4755 | 0 | 3.02 | 2.3713 | 30.8045 | 0 | 36.1958 | 0 | 0 | 30.8045
4756 | 12.8175 | 3.0006 | 2.2727 | 18.3265 | 0 | 36.4173 | 0 | 0 | 31.144
4757 | 54.3379 | 2.766 | 2.0277 | 30.8095 | 0 | 89.9412 | 0 | 0 | 85.1475
4758 | 78.8684 | 3.2067 | 1.8545 | 23.1137 | 0 | 107.0433 | 0 | 0 | 101.9821
4759 | 59.8147 | 2.9545 | 1.8626 | 25.6335 | 0 | 90.2653 | 0 | 0 | 85.4481
4760 | 23.1167 | 3.1855 | 1.8002 | 34.9048 | 21.1817 | 84.189 | 0 | 0 | 79.2032
4761 | 52.9372 | 3.0563 | 1.7611 | 26.2795 | 17.587 | 101.6211 | 0 | 0 | 96.8037
4762 | 43.3954 | 2.7932 | 1.7681 | 26.961 | 2.9939 | 77.9116 | 0 | 0 | 73.3503
4763 | 66.4854 | 2.9316 | 1.3773 | 32.5095 | 5.3659 | 108.6697 | 0 | 0 | 104.3608
4764 | 66.7388 | 2.7981 | 2.3299 | 22.7876 | 13.3668 | 108.0212 | 0 | 0 | 102.8932
4765 | 51.0106 | 2.776 | 2.3888 | 24.3031 | 22.9167 | 103.3952 | 0 | 0 | 98.2304
4766 | 39.4293 | 3.0816 | 2.0295 | 26.2598 | -0.89162 | 69.9086 | 0 | 0 | 64.7975
4767 | 52.4258 | 2.9692 | 1.9886 | 25.5951 | 13.5955 | 96.5743 | 0 | 0 | 91.6164
4768 | 44.8063 | 2.5437 | 2.2272 | 32.8596 | 11.7393 | 94.1761 | 0 | 0 | 89.4052
4769 | 63.5373 | 2.6351 | 2.1199 | 21.6598 | 17.6362 | 107.5883 | 0 | 0 | 102.8333
4770 | 70.1103 | 2.9889 | 1.5861 | 23.24 | 16.8274 | 114.7528 | 0 | 0 | 110.1777
4771 | 23.106 | 2.7694 | 1.239 | 24.1858 | 22.2492 | 73.5495 | 0 | 0 | 69.541
4772 | 22.1984 | 3.0482 | 1.0185 | 31.3985 | 0 | 57.6637 | 0 | 0 | 53.597
4773 | 82.0328 | 2.8167 | 1.0722 | 29.3254 | 0 | 115.2471 | 0 | 0 | 111.3582
4774 | 63.1261 | 2.8811 | 1.1947 | 29.268 | 0 | 96.4699 | 0 | 0 | 92.3942
4775 | 6.1701 | 3.1227 | 1.2542 | 21.1301 | 0 | 31.6771 | 0 | 0 | 27.3002
4776 | 0 | 2.7409 | 2.7569 | 31.5567 | 0 | 37.0545 | 0 | 0 | 31.5567
4777 | 0 | 2.7748 | 4.3028 | 25.0786 | 0 | 32.1563 | 0 | 0 | 25.0786
4778 | 0 | 2.7308 | 3.0702 | 32.2415 | 0 | 38.0425 | 0 | 0 | 32.2415
4779 | 0 | 3.0697 | 2.3713 | 31.8238 | 0 | 37.2648 | 0 | 0 | 31.8238
4780 | 8.7784 | 2.6112 | 2.2727 | 32.9287 | 0 | 46.591 | 0 | 0 | 41.7071
4781 | 36.0536 | 3.047 | 2.0277 | 31.3132 | 0 | 72.4415 | 0 | 0 | 67.3668
4782 | 42.7882 | 2.7283 | 1.8545 | 25.6315 | 0 | 73.0025 | 0 | 0 | 68.4197
4783 | 46.7552 | 3.1027 | 1.8626 | 27.2599 | 0 | 78.9805 | 0 | 0 | 74.0152
4784 | 59.5849 | 2.7471 | 1.8002 | 37.1906 | 13.9325 | 115.2553 | 0 | 0 | 110.708
4785 | 54.9881 | 3.0365 | 1.7611 | 32.6861 | 12.7218 | 105.1935 | 0 | 0 | 100.3959
4786 | 67.7445 | 2.4881 | 1.7681 | 22.4815 | 5.266 | 99.7482 | 0 | 0 | 95.492
4787 | 75.641 | 2.7017 | 1.3773 | 27.5348 | 10.3771 | 117.6318 | 0 | 0 | 113.5528
4788 | 68.3843 | 2.7184 | 2.3299 | 27.0543 | 11.7596 | 112.2465 | 0 | 0 | 107.1982
4789 | 67.6307 | 3.4335 | 2.3888 | 17.8641 | 21.4851 | 112.8021 | 0 | 0 | 106.9798
4790 | 74.6786 | 2.6493 | 2.0295 | 22.2316 | 13.2851 | 114.8741 | 0 | 0 | 110.1953
4791 | 59.6911 | 3.2512 | 1.9886 | 25.7609 | 14.3125 | 105.0043 | 0 | 0 | 99.7645
4792 | 43.4178 | 2.9842 | 2.2272 | 22.1758 | 21.6437 | 92.4487 | 0 | 0 | 87.2373
4793 | 27.4972 | 2.9932 | 2.1199 | 29.2768 | 6.3493 | 68.2364 | 0 | 0 | 63.1233
4794 | 25.1131 | 2.8165 | 1.5861 | 30.3807 | 11.5568 | 71.4532 | 0 | 0 | 67.0506
4795 | 0 | 2.9645 | 1.239 | 29.7728 | -4.4082 | 29.5682 | 0 | 0 | 25.3646
4796 | 0 | 2.785 | 1.0185 | 35.8571 | 0 | 39.6606 | 0 | 0 | 35.8571
4797 | 0 | 3.169 | 1.0722 | 24.3932 | 0 | 28.6343 | 200 | 0 | 224.3932
4798 | 0 | 2.7424 | 1.1947 | 19.4153 | 0 | 23.3524 | 0 | 0 | 19.4153
4799 | 0 | 3.117 | 1.2542 | 19.3406 | 0 | 23.7118 | 0 | 0 | 19.3406
4800 | 0 | 2.7927 | 2.7569 | 31.01 | 0 | 36.5597 | 0 | 0 | 31.01
4801 | 0 | 3.1311 | 4.3028 | 26.294 | 0 | 33.7279 | 0 | 0 | 26.294
4802 | 4.7102 | 3.1634 | 3.0702 | 32.5675 | 0 | 43.5112 | 0 | 0 | 37.2776
4803 | 30.8138 | 3.2178 | 2.3713 | 26.5468 | 0 | 62.9498 | 0 | 0 | 57.3606
4804 | 59.2332 | 2.458 | 2.2727 | 29.9827 | 0 | 93.9466 | 0 | 0 | 89.2159
4805 | 70.2171 | 2.9769 | 2.0277 | 29.9591 | 0 | 105.1808 | 0 | 0 | 100.1762
4806 | 47.2866 | 2.7716 | 1.8545 | 29.0598 | 0 | 80.9725 | 0 | 0 | 76.3464
4807 | 57.0155 | 3.4851 | 1.8626 | 24.6372 | 0 | 87.0004 | 0 | 0 | 81.6527
4808 | 61.7975 | 2.9536 | 1.8002 | 31.1108 | 9.942 | 107.6041 | 0 | 0 | 102.8503
4809 | 71.6265 | 2.9293 | 1.7611 | 24.8266 | 6.5449 | 107.6885 | 0 | 0 | 102.998
4810 | 66.9827 | 3.1021 | 1.7681 | 26.1773 | 21.9671 | 119.9974 | 0 | 0 | 115.1271
4811 | 44.815 | 3.5113 | 1.3773 | 22.2855 | 16.3125 | 88.3016 | 0 | 0 | 83.413
4812 | 51.5578 | 2.8644 | 2.3299 | 25.0378 | 6.6674 | 88.4573 | 0 | 0 | 83.2631
4813 | 35.9538 | 3.0277 | 2.3888 | 31.3372 | 14.3973 | 87.1048 | 0 | 0 | 81.6883
4814 | 14.1964 | 2.7037 | 2.0295 | 21.4924 | 14.9191 | 55.3411 | 0 | 0 | 50.6079
4815 | 3.4947 | 2.828 | 1.9886 | 28.9582 | 21.1399 | 58.4095 | 0 | 0 | 53.5929
4816 | 0 | 3.3397 | 2.2272 | 24.6797 | 18.5068 | 48.7534 | 0 | 0 | 43.1865
4817 | 0 | 3.0697 | 2.1199 | 29.2497 | 6.7254 | 41.1647 | 0 | 0 | 35.9751
4818 | 0 | 3.0389 | 1.9531 | 29.3968 | 13.1102 | 47.499 | 0 | 0 | 42.507
4819 | 0 | 2.892 | 1.5255 | 26.1881 | 13.6979 | 44.3035 | 0 | 0 | 39.8861
4820 | 0 | 3.1849 | 1.1504 | 28.4333 | 0 | 32.7686 | 0 | 0 | 28.4333
4821 | 0 | 2.6232 | 1.1994 | 26.8766 | 0 | 30.6991 | 0 | 0 | 26.8766
4822 | 0 | 3.2617 | 1.0675 | 16.9483 | 0 | 21.2775 | 0 | 0 | 16.9483
4823 | 0 | 2.9065 | 1.3615 | 23.1711 | 0 | 27.4391 | 0 | 0 | 23.1711
4824 | 0 | 2.7188 | 1.7973 | 28.9867 | 0 | 33.5029 | 0 | 0 | 28.9867
4825 | 0 | 3.1244 | 2.1992 | 31.8408 | 0 | 37.1644 | 0 | 0 | 31.8408
4826 | 0 | 2.7839 | 1.9945 | 25.8257 | 0 | 30.604 | 0 | 0 | 25.8257
4827 | 7.8952 | 2.6198 | 3.6751 | 21.461 | 0 | 35.651 | 0 | 200 | 229.3561
4828 | 37.3734 | 2.8677 | 3.2685 | 24.9546 | 0 | 68.4643 | 0 | 0 | 62.3281
4829 | 55.0303 | 2.95 | 2.6595 | 27.0054 | 0 | 87.6451 | 0 | 0 | 82.0357
4830 | 63.087 | 3.1212 | 2.1561 | 21.7782 | 0 | 90.1424 | 0 | 0 | 84.8652
4831 | 47.4781 | 2.608 | 1.9466 | 35.5588 | 0 | 87.5915 | 0 | 0 | 83.0369
4832 | 52.3419 | 2.8322 | 1.9857 | 28.0127 | 11.9643 | 97.1368 | 0 | 0 | 92.3189
4833 | 49.0311 | 2.7091 | 1.7436 | 23.7667 | 17.4989 | 94.7494 | 0 | 0 | 90.2966
4834 | 19.6373 | 2.7384 | 1.9834 | 30.0414 | 8.4127 | 62.8132 | 0 | 0 | 58.0914
4835 | 13.2477 | 3.0556 | 2.2739 | 30.7549 | 18.5372 | 67.8693 | 0 | 0 | 62.5398
4836 | 45.4908 | 3.0131 | 2.4752 | 23.0318 | 13.8027 | 87.8135 | 0 | 0 | 82.3252
4837 | 22.2097 | 2.935 | 1.8702 | 21.3685 | 3.7041 | 52.0875 | 0 | 0 | 47.2822
4838 | 0 | 3.025 | 2.2301 | 25.4199 | 5.9778 | 36.6528 | 0 | 0 | 31.3977
4839 | 0 | 3.0798 | 2.3118 | 32.1557 | 16.6608 | 54.2081 | 0 | 0 | 48.8165
4840 | 0 | 3.0972 | 1.9 | 31.6267 | 13.3416 | 49.9655 | 0 | 0 | 44.9683
4841 | 0 | 3.4428 | 1.9367 | 24.4203 | 16.2286 | 46.0284 | 0 | 0 | 40.6488
4842 | 0 | 2.9119 | 1.5167 | 30.2152 | 10.9444 | 45.5882 | 0 | 0 | 41.1596
4843 | 0 | 2.1862 | 1.4117 | 29.8502 | 20.1096 | 53.5577 | 0 | 0 | 49.9598
4844 | 0 | 3.1603 | 1.1486 | 23.7777 | 0 | 28.0867 | 0 | 0 | 23.7777
4845 | 0 | 2.637 | 1.2344 | 33.9495 | 0 | 37.8209 | 0 | 0 | 33.9495
4846 | 0 | 3.2891 | 1.1264 | 27.8331 | 0 | 32.2486 | 0 | 0 | 27.8331
4847 | 0 | 3.3559 | 1.1609 | 32.5373 | 0 | 37.0541 | 0 | 0 | 32.5373
4848 | 0 | 2.8583 | 1.1591 | 23.3942 | 0 | 27.4116 | 0 | 0 | 23.3942
4849 | 0 | 3.161 | 2.1636 | 27.294 | 0 | 32.6186 | 0 | 0 | 27.294
4850 | 0 | 3.24 | 1.767 | 28.8432 | 0 | 33.8502 | 0 | 0 | 28.8432
4851 | 0 | 2.3942 | 2.6204 | 19.4964 | 0 | 24.5111 | 0 | 0 | 19.4964
4852 | 0 | 3.1332 | 2.6397 | 28.9616 | 0 | 34.7345 | 0 | 0 | 28.9616
4853 | 14.6494 | 2.6548 | 2.3626 | 20.9447 | 0 | 40.6115 | 0 | 0 | 35.5941
4854 | 49.0645 | 2.6085 | 1.8189 | 30.3477 | 0 | 83.8396 | 0 | 0 | 79.4122
4855 | 55.9028 | 2.7532 | 1.9431 | 27.244 | 0 | 87.8431 | 0 | 0 | 83.1468
4856 | 70.9405 | 3.0634 | 1.9321 | 21.974 | 6.592 | 104.502 | 0 | 0 | 99.5065
4857 | 56.2957 | 3.0103 | 1.7582 | 24.8235 | 18.36 | 104.2476 | 0 | 0 | 99.4791
4858 | 17.1451 | 3.4079 | 1.4747 | 26.9371 | 16.7744 | 65.7391 | 0 | 0 | 60.8565
4859 | 0 | 3.131 | 1.8335 | 33.4929 | 12.3983 | 50.8556 | 0 | 0 | 45.8911
4860 | 0 | 2.7738 | 2.0907 | 27.6366 | 10.3256 | 42.8267 | 0 | 0 | 37.9622
4861 | 0 | 2.6641 | 2.2196 | 29.4685 | 28.5377 | 62.89 | 0 | 0 | 58.0062
4862 | 0 | 2.9918 | 2.2605 | 27.0121 | 7.0873 | 39.3516 | 0 | 0 | 34.0994
4863 | 0 | 2.9688 | 2.1706 | 25.6781 | 21.0323 | 51.8498 | 0 | 0 | 46.7104
4864 | 0 | 2.3542 | 2.1677 | 35.7771 | 17.3729 | 57.6719 | 0 | 0 | 53.15
4865 | 0 | 2.3964 | 2.1706 | 28.2417 | 15.5058 | 48.3145 | 200 | 0 | 243.7475
4866 | 0 | 2.6519 | 1.5861 | 27.8722 | 13.999 | 46.1093 | 0 | 0 | 41.8712
4867 | 0 | 2.7724 | 1.239 | 24.9645 | 20.7432 | 49.7191 | 0 | 0 | 45.7077
4868 | 0 | 3.5721 | 1.0185 | 22.6042 | 0 | 27.1949 | 0 | 0 | 22.6042
4869 | 0 | 2.96 | 1.0722 | 24.1959 | 0 | 28.2281 | 0 | 0 | 24.1959
4870 | 0 | 3.6177 | 1.1947 | 21.6397 | 0 | 26.4521 | 0 | 0 | 21.6397
4871 | 0 | 2.7861 | 1.2542 | 25.5077 | 0 | 29.548 | 0 | 0 | 25.5077
4872 | 0 | 2.486 | 2.7569 | 30.4587 | 0 | 35.7017 | 0 | 0 | 30.4587
4873 | 0 | 2.8654 | 4.3028 | 24.815 | 0 | 31.9832 | 0 | 0 | 24.815
4874 | 0 | 2.9105 | 3.0702 | 29.8956 | 0 | 35.8762 | 0 | 0 | 29.8956
4875 | 0 | 3.2797 | 2.3713 | 32.7859 | 0 | 38.4369 | 0 | 0 | 32.7859
4876 | 3.1509 | 2.8778 | 2.2727 | 24.0552 | 0 | 32.3566 | 0 | 0 | 27.2061
4877 | 29.6967 | 3.1975 | 2.0277 | 25.0842 | 0 | 60.0062 | 0 | 0 | 54.781
4878 | 73.7927 | 2.4255 | 1.8545 | 28.8749 | 0 | 106.9476 | 0 | 0 | 102.6676
4879 | 38.7841 | 3.1394 | 1.8626 | 23.9908 | 0 | 67.777 | 0 | 0 | 62.7749
4880 | 62.4268 | 3.1316 | 1.8002 | 32.4806 | 19.4859 | 119.3251 | 0 | 0 | 114.3933
4881 | 62.3051 | 2.4769 | 1.7611 | 21.638 | 4.984 | 93.1651 | 0 | 0 | 88.9271
4882 | 50.3146 | 2.8305 | 1.7681 | 24.6324 | 16.0639 | 95.6095 | 0 | 0 | 91.0109
4883 | 51.4255 | 2.8731 | 1.3773 | 28.6171 | 5.531 | 89.824 | 0 | 0 | 85.5736
4884 | 78.4559 | 2.7368 | 2.3299 | 26.0693 | 14.8114 | 124.4033 | 0 | 0 | 119.3366
4885 | 55.9554 | 2.9816 | 2.3888 | 34.2922 | 12.3172 | 107.9352 | 0 | 0 | 102.5647
4886 | 0 | 2.8222 | 2.0295 | 28.7448 | 13.9512 | 47.5477 | 0 | 0 | 42.696
4887 | 0 | 2.7892 | 1.9886 | 29.2886 | 13.0938 | 47.1603 | 0 | 0 | 42.3825
4888 | 0 | 2.962 | 2.2272 | 37.4242 | 10.3064 | 52.9198 | 0 | 0 | 47.7306
4889 | 0 | 3.2602 | 2.1199 | 36.7106 | 17.8945 | 59.9852 | 0 | 0 | 54.6051
4890 | 0 | 3.4571 | 1.5861 | 25.3483 | 15.2509 | 45.6425 | 0 | 0 | 40.5992
4891 | 0 | 2.6973 | 1.239 | 25.9889 | 17.1493 | 47.0745 | 0 | 0 | 43.1382
4892 | 0 | 2.6379 | 1.0185 | 33.8512 | 0 | 37.5076 | 0 | 0 | 33.8512
4893 | 0 | 2.9558 | 1.0722 | 25.8851 | 0 | 29.913 | 0 | 0 | 25.8851
4894 | 0 | 2.8604 | 1.1947 | 29.3082 | 0 | 33.3633 | 0 | 0 | 29.3082
4895 | 0 | 2.4582 | 1.2542 | 26.3795 | 0 | 30.0919 | 0 | 0 | 26.3795
4896 | 0 | 2.7848 | 2.7569 | 26.5829 | 0 | 32.1247 | 0 | 0 | 26.5829
4897 | 0 | 3.1096 | 4.3028 | 23.013 | 0 | 30.4254 | 0 | 0 | 23.013
4898 | 0 | 2.7226 | 3.0702 | 17.1591 | 0 | 22.9519 | 0 | 0 | 17.1591
4899 | 0 | 3.2494 | 2.3713 | 22.9771 | 0 | 28.5978 | 0 | 0 | 22.9771
4900 | 5.0424 | 3.2654 | 2.2727 | 26.4113 | 0 | 36.9919 | 0 | 0 | 31.4537
4901 | 25.528 | 2.2522 | 2.0277 | 25.6705 | 0 | 55.4784 | 0 | 0 | 51.1985
4902 | 65.7711 | 2.6301 | 1.8545 | 23.8955 | 0 | 94.1512 | 0 | 0 | 89.6666
4903 | 56.971 | 3.2818 | 1.8626 | 25.887 | 0 | 88.0024 | 0 | 0 | 82.858
4904 | 55.9771 | 3.1596 | 1.8002 | 19.3007 | 9.8983 | 90.1359 | 0 | 0 | 85.1761
4905 | 41.1918 | 2.8476 | 1.7611 | 28.0347 | 15.9232 | 89.7585 | 0 | 0 | 85.1497
4906 | 1.4901 | 2.965 | 1.7681 | 21.4859 | 19.0671 | 46.7763 | 0 | 0 | 42.0432
4907 | 6.124 | 3.4444 | 1.3773 | 26.6718 | 7.0139 | 44.6313 | 0 | 0 | 39.8097
4908 | 39.1007 | 3.0361 | 2.3299 | 27.9978 | 18.884 | 91.3485 | 0 | 0 | 85.9825
4909 | 52.5933 | 2.6592 | 2.3888 | 25.8288 | 15.5347 | 99.0048 | 0 | 0 | 93.9568
4910 | 0.53292 | 2.7902 | 2.0295 | 33.4105 | 14.0747 | 52.8378 | 0 | 0 | 48.0181
4911 | 0 | 2.8145 | 1.9886 | 26.2013 | 20.544 | 51.5484 | 0 | 0 | 46.7452
4912 | 0 | 3.4302 | 2.2272 | 23.7366 | 14.9621 | 44.3561 | 0 | 0 | 38.6987
4913 | 0 | 2.4514 | 2.1199 | 37.2497 | 6.9527 | 48.7737 | 0 | 0 | 44.2024
4914 | 0 | 2.7035 | 1.5861 | 41.2224 | 7.0315 | 52.5435 | 0 | 0 | 48.2539
4915 | 0 | 2.5627 | 1.239 | 29.1951 | 23.6261 | 56.6229 | 0 | 0 | 52.8212
4916 | 0 | 2.5689 | 1.0185 | 35.7832 | 0 | 39.3707 | 0 | 0 | 35.7832
4917 | 0 | 2.9007 | 1.0722 | 28.364 | 0 | 32.337 | 0 | 0 | 28.364
4918 | 0 | 2.7895 | 1.1947 | 25.3357 | 0 | 29.32 | 0 | 0 | 25.3357
4919 | 0 | 2.9374 | 1.2542 | 24.1539 | 0 | 28.3455 | 0 | 0 | 24.1539
4920 | 0 | 2.9977 | 2.7569 | 30.1692 | 0 | 35.9238 | 0 | 0 | 30.1692
4921 | 0 | 3.2627 | 4.3028 | 27.2978 | 0 | 34.8633 | 0 | 0 | 27.2978
4922 | 0 | 2.6537 | 3.0702 | 30.4625 | 0 | 36.1864 | 0 | 0 | 30.4625
4923 | 0 | 2.5966 | 2.3713 | 25.9078 | 0 | 30.8757 | 0 | 0 | 25.9078
4924 | 12.3878 | 2.5617 | 2.2727 | 29.7088 | 0 | 46.9311 | 0 | 0 | 42.0967
4925 | 37.9973 | 2.8502 | 2.0277 | 27.5862 | 0 | 70.4614 | 0 | 0 | 65.5835
4926 | 65.1737 | 2.5649 | 1.8545 | 31.7151 | 0 | 101.3081 | 0 | 0 | 96.8887
4927 | 72.4106 | 3.2587 | 1.8626 | 25.8855 | 0 | 103.4175 | 0 | 0 | 98.2961
4928 | 61.7313 | 2.3432 | 1.8002 | 28.7664 | 26.2163 | 120.8574 | 0 | 0 | 116.714
4929 | 24.245 | 3.2784 | 1.7611 | 25.8183 | 8.831 | 63.9338 | 0 | 200 | 258.8943
4930 | 23.1203 | 3.0507 | 1.7681 | 25.9663 | 13.4869 | 67.3924 | 0 | 0 | 62.5735
4931 | 22.9827 | 2.8949 | 1.3773 | 23.7935 | 11.4649 | 62.5133 | 0 | 0 | 58.2411
4932 | 15.536 | 2.9626 | 2.3299 | 26.3299 | 15.1739 | 62.3323 | 0 | 0 | 57.0397
4933 | 73.853 | 2.9186 | 2.3888 | 35.4764 | 11.4539 | 126.0908 | 0 | 0 | 120.7833
4934 | 66.1521 | 2.6362 | 2.0295 | 25.3282 | 14.7374 | 110.8834 | 200 | 0 | 306.2177
4935 | 25.4163 | 2.3758 | 1.9886 | 25.7399 | 20.3628 | 75.8834 | 0 | 0 | 71.519
4936 | 9.4617 | 2.7426 | 2.2272 | 25.4326 | 13.0149 | 52.879 | 0 | 0 | 47.9091
4937 | 42.226 | 2.9539 | 2.1199 | 30.3387 | 12.1791 | 89.8175 | 0 | 0 | 84.7438
4938 | 68.4603 | 3.1192 | 1.5861 | 26.0088 | 6.645 | 105.8195 | 0 | 0 | 101.1141
4939 | 46.6761 | 3.1401 | 1.239 | 28.8901 | 13.8664 | 93.8117 | 0 | 0 | 89.4325
4940 | 2.0443 | 2.8058 | 1.0185 | 25.6767 | 0 | 31.5453 | 0 | 0 | 27.721
4941 | 0 | 2.5504 | 1.0722 | 24.2278 | 0 | 27.8504 | 0 | 0 | 24.2278
4942 | 16.8131 | 2.6405 | 1.1947 | 33.6429 | 0 | 54.2911 | 0 | 0 | 50.4559
4943 | 69.4247 | 3.2912 | 1.2542 | 28.2323 | 0 | 102.2025 | 0 | 0 | 97.6571
4944 | 49.9563 | 3.029 | 2.7569 | 30.1601 | 0 | 85.9023 | 0 | 0 | 80.1164
4945 | 0 | 2.6509 | 4.3028 | 24.5452 | 0 | 31.4989 | 0 | 0 | 24.5452
4946 | 0 | 2.769 | 3.0702 | 27.3269 | 0 | 33.1661 | 0 | 0 | 27.3269
4947 | 0 | 2.8604 | 2.3713 | 25.7497 | 0 | 30.9814 | 0 | 0 | 25.7497
4948 | 6.4185 | 2.9047 | 2.2727 | 26.1778 | 0 | 37.7738 | 0 | 0 | 32.5963
4949 | 44.6037 | 2.6893 | 2.0277 | 26.2853 | 0 | 75.606 | 0 | 0 | 70.889
4950 | 59.0931 | 2.9254 | 1.8545 | 24.3584 | 0 | 88.2313 | 0 | 0 | 83.4514
4951 | 50.007 | 2.6418 | 1.8626 | 32.7776 | 0 | 87.2891 | 0 | 0 | 82.7846
4952 | 52.2461 | 3.1356 | 1.8002 | 28.0515 | 10.8871 | 96.1205 | 0 | 0 | 91.1847
4953 | 44.5593 | 3.2121 | 1.7611 | 27.663 | 26.0487 | 103.2443 | 0 | 0 | 98.2711
4954 | 6.7037 | 2.703 | 1.7681 | 32.5937 | 15.5655 | 59.3341 | 0 | 0 | 54.8629
4955 | 3.9335 | 2.7361 | 1.3773 | 31.0699 | 17.1384 | 56.2553 | 0 | 0 | 52.1418
4956 | 31.1693 | 2.6206 | 2.3299 | 25.4959 | 7.2863 | 68.9021 | 0 | 0 | 63.9515
4957 | 69.2346 | 2.8419 | 2.3888 | 27.1364 | 16.6567 | 118.2585 | 0 | 0 | 113.0278
4958 | 75.1432 | 3.0025 | 2.0295 | 27.9438 | 5.8225 | 113.9414 | 0 | 0 | 108.9094
4959 | 56.9506 | 2.8191 | 1.9886 | 23.1248 | 18.5466 | 103.4297 | 0 | 0 | 98.622
4960 | 64.6124 | 3.0658 | 2.2272 | 31.2945 | 12.5883 | 113.7882 | 0 | 0 | 108.4951
4961 | 61.3061 | 2.9136 | 2.1199 | 22.9885 | 13.0088 | 102.3369 | 0 | 0 | 97.3034
4962 | 34.0445 | 2.6421 | 1.5861 | 26.1492 | 5.6919 | 70.1139 | 0 | 0 | 65.8857
4963 | 30.1891 | 3.6241 | 1.239 | 27.6008 | 16.4622 | 79.1152 | 0 | 0 | 74.2521
4964 | 20.9875 | 3.3987 | 1.0185 | 27.7102 | 0 | 53.115 | 0 | 0 | 48.6977
4965 | 71.8287 | 3.1852 | 1.0722 | 30.9265 | 0 | 107.0126 | 0 | 0 | 102.7552
4966 | 75.3995 | 3.4936 | 1.1947 | 28.4722 | 0 | 108.5601 | 0 | 0 | 103.8718
4967 | 41.7081 | 3.3567 | 1.2542 | 34.26 | 0 | 80.579 | 0 | 0 | 75.9681
4968 | 0 | 2.8406 | 2.7569 | 20.1563 | 0 | 25.7538 | 0 | 0 | 20.1563
4969 | 0 | 3.3604 | 4.3028 | 25.9077 | 0 | 33.5709 | 0 | 0 | 25.9077
4970 | 0 | 3.1336 | 3.0702 | 28.3661 | 0 | 34.5699 | 0 | 0 | 28.3661
4971 | 0 | 2.4869 | 2.3713 | 26.8544 | 0 | 31.7126 | 0 | 0 | 26.8544
4972 | 0 | 3.2019 | 2.2727 | 25.4327 | 0 | 30.9074 | 0 | 0 | 25.4327
4973 | 0 | 2.7754 | 2.0277 | 19.4628 | 0 | 24.266 | 0 | 0 | 19.4628
4974 | 0 | 3.368 | 1.8545 | 28.8052 | 0 | 34.0277 | 0 | 0 | 28.8052
4975 | 0 | 3.688 | 1.8626 | 27.2613 | 0 | 32.812 | 0 | 0 | 27.2613
4976 | 0 | 2.5973 | 1.8002 | 28.0266 | 21.8516 | 54.2757 | 0 | 0 | 49.8782
4977 | 0 | 2.885 | 1.7611 | 27.436 | 11.6442 | 43.7263 | 0 | 0 | 39.0802
4978 | 0 | 3.349 | 1.7681 | 32.3602 | 8.1413 | 45.6185 | 0 | 0 | 40.5015
4979 | 0 | 3.0023 | 1.3773 | 25.177 | 23.0311 | 52.5877 | 0 | 0 | 48.2081
4980 | 0 | 2.8244 | 2.3299 | 28.9063 | 15.0745 | 49.1351 | 0 | 0 | 43.9809
4981 | 0 | 2.7728 | 2.3888 | 27.595 | 15.9368 | 48.6934 | 0 | 0 | 43.5318
4982 | 0 | 2.9625 | 2.0295 | 31.2684 | 17.249 | 53.5093 | 0 | 0 | 48.5174
4983 | 0 | 2.6306 | 1.9886 | 26.6363 | 11.5269 | 42.7824 | 0 | 0 | 38.1632
4984 | 0 | 2.7429 | 2.2272 | 25.1642 | 11.339 | 41.4733 | 0 | 0 | 36.5032
4985 | 0 | 2.9895 | 2.1199 | 22.6129 | 14.6163 | 42.3385 | 0 | 0 | 37.2292
4986 | 0 | 2.3715 | 1.9531 | 25.031 | 13.6589 | 43.0144 | 0 | 0 | 38.6898
4987 | 0 | 3.0959 | 1.5255 | 18.6729 | 14.826 | 38.1203 | 0 | 0 | 33.4989
4988 | 0 | 2.8335 | 1.1504 | 26.9608 | 0 | 30.9447 | 0 | 0 | 26.9608
4989 | 0 | 3.4624 | 1.1994 | 33.1057 | 0 | 37.7675 | 0 | 0 | 33.1057
4990 | 0 | 2.4091 | 1.0675 | 22.1474 | 0 | 25.6241 | 0 | 0 | 22.1474
4991 | 0 | 2.9404 | 1.3615 | 23.9476 | 0 | 28.2495 | 0 | 0 | 23.9476
4992 | 0 | 3.0025 | 1.7973 | 25.1323 | 0 | 29.932 | 0 | 0 | 25.1323
4993 | 0 | 2.5398 | 2.1992 | 27.2638 | 0 | 32.0029 | 0 | 0 | 27.2638
4994 | 0 | 2.9298 | 1.9945 | 26.19 | 0 | 31.1143 | 0 | 0 | 26.19
4995 | 0 | 3.0868 | 3.6751 | 28.653 | 0 | 35.4149 | 0 | 0 | 28.653
4996 | 0 | 2.6248 | 3.2685 | 25.8555 | 0 | 31.7488 | 0 | 0 | 25.8555
4997 | 0 | 3.2371 | 2.6595 | 25.7644 | 0 | 31.6609 | 0 | 0 | 25.7644
4998 | 0 | 2.9788 | 2.1561 | 27.7528 | 0 | 32.8876 | 0 | 0 | 27.7528
4999 | 0 | 2.7935 | 1.9466 | 19.2743 | 0 | 24.0145 | 0 | 0 | 19.2743
5000 | 0 | 2.7994 | 1.9857 | 33.4703 | 12.1947 | 50.4501 | 0 | 0 | 45.6649
5001 | 0 | 3.0372 | 1.7436 | 27.0591 | 8.5462 | 40.3862 | 0 | 0 | 35.6053
5002 | 0 | 2.9737 | 1.9834 | 31.6568 | 4.6227 | 41.2366 | 200 | 0 | 236.2795
5003 | 0 | 2.7307 | 2.2739 | 31.6601 | 22.8721 | 59.5369 | 0 | 0 | 54.5323
5004 | 0 | 3.1732 | 2.4752 | 31.0808 | 6.958 | 43.6872 | 0 | 0 | 38.0388
5005 | 0 | 2.7767 | 1.8702 | 32.6181 | 6.6834 | 43.9485 | 0 | 0 | 39.3015
5006 | 0 | 2.7691 | 2.2301 | 20.3565 | 11.9059 | 37.2616 | 0 | 0 | 32.2624
5007 | 0 | 3.2273 | 2.3118 | 24.8001 | 18.0425 | 48.3817 | 0 | 0 | 42.8425
5008 | 0 | 2.4762 | 1.9 | 35.7635 | 18.7605 | 58.9001 | 0 | 0 | 54.5239
5009 | 0 | 2.7949 | 1.9367 | 30.6394 | 12.2582 | 47.6293 | 0 | 0 | 42.8976
5010 | 0 | 3.0442 | 1.5167 | 24.282 | 12.4772 | 41.32 | 0 | 0 | 36.7592
5011 | 0 | 3.3602 | 1.4117 | 30.0656 | 6.6757 | 41.5132 | 0 | 0 | 36.7414
5012 | 0 | 3.0678 | 1.1486 | 25.3542 | 0 | 29.5706 | 0 | 0 | 25.3542
5013 | 0 | 2.8508 | 1.2344 | 28.909 | 0 | 32.9942 | 0 | 0 | 28.909
5014 | 0 | 2.518 | 1.1264 | 19.7809 | 0 | 23.4254 | 0 | 0 | 19.7809
5015 | 0 | 2.9073 | 1.1609 | 30.477 | 0 | 34.5452 | 0 | 0 | 30.477
5016 | 0 | 2.9218 | 1.1591 | 25.0535 | 0 | 29.1344 | 0 | 0 | 25.0535
5017 | 0 | 2.6341 | 2.1636 | 30.3669 | 0 | 35.1647 | 0 | 0 | 30.3669
5018 | 0 | 2.69 | 1.767 | 27.9131 | 0 | 32.37 | 0 | 0 | 27.9131
5019 | 0 | 2.6892 | 2.6204 | 22.1079 | 0 | 27.4175 | 0 | 0 | 22.1079
5020 | 0 | 3.0766 | 2.6397 | 28.1709 | 0 | 33.8871 | 0 | 0 | 28.1709
5021 | 0 | 2.8884 | 2.3626 | 24.4444 | 0 | 29.6954 | 0 | 0 | 24.4444
5022 | 0 | 3.1874 | 1.8189 | 24.7995 | 0 | 29.8058 | 0 | 0 | 24.7995
5023 | 0 | 2.9106 | 1.9431 | 20.6238 | 0 | 25.4775 | 0 | 0 | 20.6238
5024 | 0 | 2.7385 | 1.9321 | 23.7861 | 14.3953 | 42.8519 | 0 | 0 | 38.1814
5025 | 0 | 2.7577 | 1.7582 | 21.5747 | 17.7011 | 43.7917 | 0 | 0 | 39.2757
5026 | 0 | 2.0606 | 1.4747 | 19.0537 | 10.5623 | 33.1513 | 0 | 0 | 29.616
5027 | 0 | 2.5162 | 1.8335 | 24.0743 | 22.6004 | 51.0243 | 0 | 0 | 46.6746
5028 | 0 | 2.94 | 2.0907 | 29.7418 | 16.3155 | 51.0881 | 0 | 0 | 46.0573
5029 | 0 | 2.9824 | 2.2196 | 34.5424 | 22.1769 | 61.9214 | 0 | 0 | 56.7193
5030 | 0 | 2.8019 | 2.2605 | 23.2032 | 19.1234 | 47.389 | 0 | 0 | 42.3266
5031 | 0 | 2.5247 | 2.1706 | 30.1541 | 9.5663 | 44.4157 | 0 | 200 | 239.7204
5032 | 0 | 2.6912 | 2.1677 | 30.3289 | 10.9904 | 46.1782 | 0 | 0 | 41.3193
5033 | 0 | 2.7563 | 2.1706 | 30.1737 | 12.1304 | 47.2311 | 0 | 0 | 42.3041
5034 | 0 | 2.6814 | 1.5861 | 24.9906 | 19.8334 | 49.0916 | 0 | 0 | 44.824
5035 | 0 | 2.8633 | 1.239 | 28.5721 | 12.6229 | 45.2973 | 0 | 0 | 41.195
5036 | 0 | 2.6052 | 1.0185 | 29.3316 | 0 | 32.9553 | 0 | 0 | 29.3316
5037 | 0 | 2.8808 | 1.0722 | 25.6329 | 0 | 29.5858 | 0 | 0 | 25.6329
5038 | 0 | 3.0753 | 1.1947 | 29.5576 | 0 | 33.8276 | 0 | 0 | 29.5576
5039 | 0 | 3.0293 | 1.2542 | 24.4122 | 0 | 28.6957 | 0 | 0 | 24.4122
5040 | 0 | 2.8388 | 2.7569 | 26.2687 | 0 | 31.8643 | 0 | 0 | 26.2687
5041 | 0 | 2.6828 | 4.3028 | 28.5064 | 0 | 35.492 | 0 | 0 | 28.5064
5042 | 0 | 3.2631 | 3.0702 | 27.763 | 0 | 34.0963 | 0 | 0 | 27.763
5043 | 0 | 2.8485 | 2.3713 | 27.7184 | 0 | 32.9382 | 0 | 0 | 27.7184
5044 | 0 | 2.3992 | 2.2727 | 26.9217 | 0 | 31.5937 | 0 | 0 | 26.9217
5045 | 0 | 2.5302 | 2.0277 | 31.0599 | 0 | 35.6178 | 0 | 0 | 31.0599
5046 | 0 | 2.5958 | 1.8545 | 30.7109 | 0 | 35.1612 | 0 | 0 | 30.7109
5047 | 0 | 2.3996 | 1.8626 | 24.3122 | 0 | 28.5744 | 0 | 0 | 24.3122
5048 | 0 | 2.9336 | 1.8002 | 26.4778 | 11.8023 | 43.014 | 0 | 0 | 38.2802
5049 | 0 | 2.7942 | 1.7611 | 34.8708 | 11.4056 | 50.8318 | 0 | 0 | 46.2765
5050 | 0 | 2.8603 | 1.7681 | 24.5163 | 14.2945 | 43.4391 | 0 | 0 | 38.8107
5051 | 0 | 2.2096 | 1.3773 | 29.1702 | 17.8717 | 50.6287 | 0 | 0 | 47.0418
5052 | 0 | 2.663 | 2.3299 | 28.742 | 20.0686 | 53.8035 | 0 | 0 | 48.8106
5053 | 0 | 2.743 | 2.3888 | 24.1483 | 12.0504 | 41.3305 | 0 | 0 | 36.1987
5054 | 0 | 2.8779 | 2.0295 | 26.8817 | 11.0721 | 42.8611 | 0 | 0 | 37.9538
5055 | 0 | 2.7155 | 1.9886 | 34.3046 | 10.0495 | 49.0582 | 0 | 0 | 44.3541
5056 | 0 | 2.4554 | 2.2272 | 32.8269 | 13.4631 | 50.9726 | 0 | 0 | 46.29
5057 | 0 | 2.9275 | 2.1199 | 20.4271 | 18.5419 | 44.0163 | 0 | 0 | 38.969
5058 | 0 | 2.7471 | 1.5861 | 27.7543 | 18.2666 | 50.3541 | 0 | 0 | 46.0209
5059 | 0 | 2.5272 | 1.239 | 24.4849 | 6.9634 | 35.2145 | 0 | 0 | 31.4483
5060 | 0 | 2.5823 | 1.0185 | 30.0142 | 0 | 33.6151 | 0 | 0 | 30.0142
5061 | 0 | 2.9907 | 1.0722 | 33.3783 | 0 | 37.4412 | 0 | 0 | 33.3783
5062 | 0 | 2.9319 | 1.1947 | 21.014 | 0 | 25.1406 | 0 | 0 | 21.014
5063 | 0 | 2.8774 | 1.2542 | 30.9178 | 0 | 35.0494 | 0 | 0 | 30.9178
5064 | 0 | 2.8752 | 2.7569 | 26.4101 | 0 | 32.0423 | 0 | 0 | 26.4101
5065 | 0 | 2.9394 | 4.3028 | 34.269 | 0 | 41.5112 | 0 | 0 | 34.269
5066 | 0 | 2.65 | 3.0702 | 27.289 | 0 | 33.0092 | 0 | 0 | 27.289
5067 | 0 | 3.2664 | 2.3713 | 30.1052 | 0 | 35.7429 | 0 | 0 | 30.1052
5068 | 0 | 2.9837 | 2.2727 | 26.6414 | 0 | 31.8979 | 0 | 0 | 26.6414
5069 | 0 | 2.8871 | 2.0277 | 31.2288 | 0 | 36.1436 | 0 | 0 | 31.2288
5070 | 0 | 2.4916 | 1.8545 | 26.7389 | 0 | 31.085 | 0 | 0 | 26.7389
5071 | 0 | 2.4302 | 1.8626 | 19.2402 | 0 | 23.5331 | 0 | 0 | 19.2402
5072 | 0 | 2.9738 | 1.8002 | 25.2713 | 12.8066 | 42.8519 | 0 | 0 | 38.0779
5073 | 0 | 2.6312 | 1.7611 | 30.958 | 17.7432 | 53.0935 | 0 | 0 | 48.7011
5074 | 0 | 2.4328 | 1.7681 | 28.3496 | 4.7049 | 37.2554 | 200 | 0 | 233.0545
5075 | 0 | 2.4249 | 1.3773 | 20.1226 | 16.2815 | 40.2062 | 0 | 0 | 36.4041
5076 | 0 | 3.6706 | 2.3299 | 23.0735 | 19.3175 | 48.3915 | 0 | 0 | 42.3909
5077 | 0 | 2.8352 | 2.3888 | 29.2884 | 7.2443 | 41.7567 | 0 | 0 | 36.5327
5078 | 0 | 3.0127 | 2.0295 | 30.14 | 8.5685 | 43.7507 | 0 | 0 | 38.7085
5079 | 0 | 2.9911 | 1.9886 | 33.0152 | 13.3208 | 51.3158 | 0 | 0 | 46.336
5080 | 0 | 3.2884 | 2.2272 | 27.4437 | 8.2372 | 41.1966 | 0 | 0 | 35.6809
5081 | 0 | 3.3454 | 2.1199 | 19.4777 | 10.281 | 35.224 | 0 | 0 | 29.7587
5082 | 0 | 2.883 | 1.5861 | 29.2777 | 13.6696 | 47.4164 | 0 | 0 | 42.9473
5083 | 0 | 2.6746 | 1.239 | 19.557 | 14.4422 | 37.9129 | 0 | 0 | 33.9993
5084 | 0 | 2.6702 | 1.0185 | 25.5542 | 0 | 29.2429 | 0 | 0 | 25.5542
5085 | 0 | 2.5403 | 1.0722 | 21.8275 | 0 | 25.44 | 0 | 0 | 21.8275
5086 | 0 | 3.299 | 1.1947 | 26.2348 | 0 | 30.7285 | 0 | 0 | 26.2348
5087 | 0 | 3.2448 | 1.2542 | 22.8663 | 0 | 27.3653 | 0 | 0 | 22.8663
5088 | 0 | 2.4711 | 2.7569 | 27.4933 | 0 | 32.7213 | 0 | 0 | 27.4933
5089 | 0 | 3.4056 | 4.3028 | 3.309 | 0 | 11.0174 | 0 | 0 | 3.309
5090 | 0 | 2.5476 | 3.0702 | 4.407 | 0 | 10.0248 | 0 | 0 | 4.407
5091 | 0 | 2.8307 | 2.3713 | 4.1469 | 0 | 9.3489 | 0 | 0 | 4.1469
5092 | 0 | 3.2677 | 2.2727 | 4.5681 | 0 | 10.1085 | 0 | 0 | 4.5681
5093 | 0 | 3.2775 | 2.0277 | 3.5466 | 0 | 8.8518 | 0 | 0 | 3.5466
5094 | 0 | 3.2536 | 1.8545 | 4.9782 | 0 | 10.0863 | 0 | 0 | 4.9782
5095 | 0 | 2.5056 | 1.8626 | 4.17 | 0 | 8.5382 | 0 | 0 | 4.17
5096 | 0 | 2.9137 | 1.8002 | 4.4616 | 9.8818 | 19.0573 | 0 | 0 | 14.3434
5097 | 0 | 2.0666 | 1.7611 | 5.0607 | 11.5327 | 20.4212 | 0 | 0 | 16.5934
5098 | 0 | 2.4594 | 1.7681 | 4.8917 | 13.8434 | 22.9626 | 0 | 0 | 18.7351
5099 | 0 | 3.0171 | 1.3773 | 3.6668 | 21.6622 | 29.7234 | 0 | 0 | 25.329
5100 | 0 | 3.2153 | 2.3299 | 4.6434 | 20.328 | 30.5166 | 0 | 0 | 24.9714
5101 | 0 | 2.8294 | 2.3888 | 4.0383 | 15.86 | 25.1166 | 0 | 0 | 19.8983
5102 | 0 | 2.7976 | 2.0295 | 5.0079 | 15.0456 | 24.8806 | 0 | 0 | 20.0535
5103 | 0 | 2.7526 | 1.9886 | 3.6086 | 14.717 | 23.0668 | 0 | 0 | 18.3256
5104 | 0 | 3.5434 | 2.2272 | 4.1988 | 15.6195 | 25.5889 | 0 | 0 | 19.8183
5105 | 0 | 2.9071 | 2.1199 | 3.9509 | 17.7212 | 26.6991 | 0 | 0 | 21.6721
5106 | 0 | 2.7032 | 1.5861 | 3.6684 | 7.1316 | 15.0893 | 0 | 0 | 10.7999
5107 | 0 | 2.7355 | 1.239 | 4.5897 | 21.3878 | 29.9521 | 0 | 0 | 25.9775
5108 | 0 | 2.8461 | 1.0185 | 4.0538 | 0 | 7.9184 | 0 | 0 | 4.0538
5109 | 0 | 2.7534 | 1.0722 | 3.3646 | 0 | 7.1902 | 0 | 0 | 3.3646
5110 | 0 | 3.2082 | 1.1947 | 4.5363 | 0 | 8.9391 | 0 | 0 | 4.5363
5111 | 0 | 3.4037 | 1.2542 | 4.7637 | 0 | 9.4216 | 0 | 0 | 4.7637
5112 | 0 | 3.2976 | 2.7569 | 4.3999 | 0 | 10.4545 | 0 | 0 | 4.3999
5113 | 0 | 2.8011 | 4.3028 | 5.4957 | 0 | 12.5995 | 0 | 0 | 5.4957
5114 | 0 | 2.6544 | 3.0702 | 3.4441 | 0 | 9.1687 | 0 | 0 | 3.4441
5115 | 0 | 2.9649 | 2.3713 | 5.6476 | 0 | 10.9839 | 0 | 0 | 5.6476
5116 | 0 | 2.849 | 2.2727 | 4.7705 | 0 | 9.8922 | 0 | 0 | 4.7705
5117 | 0 | 2.9135 | 2.0277 | 4.3992 | 0 | 9.3404 | 0 | 0 | 4.3992
5118 | 0 | 3.0229 | 1.8545 | 3.9498 | 0 | 8.8272 | 0 | 0 | 3.9498
5119 | 1.7306 | 2.5752 | 1.8626 | 3.7526 | 0 | 9.921 | 0 | 0 | 5.4832
5120 | 7.0611 | 2.7776 | 1.8002 | 3.7211 | 16.6678 | 32.0278 | 0 | 0 | 27.4499
5121 | 8.8995 | 2.557 | 1.7611 | 4.2025 | 5.8669 | 23.2869 | 0 | 0 | 18.9688
5122 | 0.46695 | 2.9817 | 1.7681 | 5.0291 | 7.4782 | 17.7241 | 0 | 0 | 12.9742
5123 | 0 | 2.5312 | 1.3773 | 5.0454 | 14.7555 | 23.7094 | 0 | 0 | 19.8009
5124 | 0 | 2.4612 | 2.3299 | 3.8243 | 10.1183 | 18.7337 | 0 | 0 | 13.9426
5125 | 0 | 2.3058 | 2.3888 | 4.3653 | 10.6499 | 19.7097 | 0 | 0 | 15.0152
5126 | 0 | 2.709 | 2.0295 | 4.6945 | 8.6387 | 18.0718 | 0 | 0 | 13.3333
5127 | 0 | 2.9451 | 1.9886 | 2.802 | 12.0231 | 19.7588 | 0 | 0 | 14.8251
5128 | 0 | 3.2131 | 2.2272 | 4.2089 | 13.2464 | 22.8956 | 0 | 0 | 17.4553
5129 | 0 | 2.889 | 2.1199 | 4.5613 | 20.5191 | 30.0893 | 0 | 0 | 25.0804
5130 | 0 | 2.6494 | 1.5861 | 4.2686 | 13.1774 | 21.6816 | 0 | 0 | 17.4461
5131 | 0 | 2.7204 | 1.239 | 4.2124 | 11.9962 | 20.168 | 0 | 0 | 16.2086
5132 | 0 | 2.8126 | 1.0185 | 4.016 | 0 | 7.8472 | 0 | 0 | 4.016
5133 | 0 | 2.8183 | 1.0722 | 4.0217 | 0 | 7.9122 | 0 | 200 | 204.0217
5134 | 0 | 3.1191 | 1.1947 | 3.7537 | 0 | 8.0676 | 0 | 0 | 3.7537
5135 | 0 | 2.6068 | 1.2542 | 5.3119 | 0 | 9.1729 | 0 | 0 | 5.3119
5136 | 0 | 3.1085 | 2.7569 | 4.7562 | 0 | 10.6216 | 0 | 0 | 4.7562
5137 | 0 | 3.1308 | 4.3028 | 3.2435 | 0 | 10.6771 | 0 | 0 | 3.2435
5138 | 0 | 2.5667 | 3.0702 | 3.3771 | 0 | 9.014 | 0 | 0 | 3.3771
5139 | 0 | 2.4285 | 2.3713 | 4.7375 | 0 | 9.5373 | 0 | 0 | 4.7375
5140 | 0 | 2.5274 | 2.2727 | 3.4439 | 0 | 8.244 | 0 | 0 | 3.4439
5141 | 0 | 2.4174 | 2.0277 | 3.806 | 0 | 8.2511 | 0 | 0 | 3.806
5142 | 0 | 2.6496 | 1.8545 | 4.4213 | 0 | 8.9254 | 0 | 0 | 4.4213
5143 | 0.086766 | 2.7112 | 1.8626 | 4.3581 | 0 | 9.0186 | 0 | 0 | 4.4448
5144 | 0.28781 | 2.7404 | 1.8002 | 4.7945 | 13.0066 | 22.6296 | 200 | 0 | 218.0889
5145 | 0 | 2.9062 | 1.7611 | 3.8971 | 10.6338 | 19.1982 | 0 | 0 | 14.5309
5146 | 0 | 2.8993 | 1.7681 | 4.2103 | 10.3683 | 19.2461 | 0 | 0 | 14.5786
5147 | 0 | 2.7017 | 1.3773 | 3.8648 | 2.1416 | 10.0854 | 0 | 0 | 6.0064
5148 | 0 | 3.2497 | 2.3299 | 4.9348 | 7.8438 | 18.3581 | 0 | 0 | 12.7786
5149 | 0 | 2.7366 | 2.3888 | 4.1434 | 17.0476 | 26.3164 | 0 | 0 | 21.191
5150 | 0 | 3.3094 | 2.0295 | 4.0466 | 13.2391 | 22.6246 | 0 | 0 | 17.2857
5151 | 0 | 3.0885 | 1.9886 | 4.5962 | 4.0057 | 13.679 | 0 | 0 | 8.6019
5152 | 0 | 2.9311 | 2.2272 | 3.1162 | 17.199 | 25.4735 | 0 | 0 | 20.3152
5153 | 0 | 2.6736 | 2.1199 | 3.4451 | 12.5296 | 20.7682 | 0 | 0 | 15.9747
5154 | 0 | 2.5966 | 1.9531 | 3.5382 | 25.8415 | 33.9294 | 0 | 0 | 29.3797
5155 | 0 | 2.2721 | 1.5255 | 3.983 | 29.1794 | 36.9599 | 0 | 0 | 33.1624
5156 | 0 | 2.7013 | 1.1504 | 4.442 | 0 | 8.2936 | 0 | 0 | 4.442
5157 | 0 | 2.6016 | 1.1994 | 4.0183 | 0 | 7.8193 | 0 | 0 | 4.0183
5158 | 0 | 2.8184 | 1.0675 | 3.9473 | 0 | 7.8332 | 0 | 0 | 3.9473
5159 | 0 | 2.9084 | 1.3615 | 3.8725 | 0 | 8.1425 | 0 | 0 | 3.8725
5160 | 0 | 2.7039 | 1.7973 | 4.5483 | 0 | 9.0496 | 0 | 0 | 4.5483
5161 | 0 | 2.8029 | 2.1992 | 3.2168 | 0 | 8.2189 | 0 | 0 | 3.2168
5162 | 0 | 3.1804 | 1.9945 | 4.9938 | 0 | 10.1687 | 0 | 0 | 4.9938
5163 | 0 | 2.6997 | 3.6751 | 4.2061 | 0 | 10.5809 | 0 | 0 | 4.2061
5164 | 0 | 2.8466 | 3.2685 | 5.3555 | 0 | 11.4706 | 0 | 0 | 5.3555
5165 | 0 | 3.068 | 2.6595 | 4.5025 | 0 | 10.23 | 0 | 0 | 4.5025
5166 | 0 | 3.276 | 2.1561 | 4.4113 | 0 | 9.8434 | 0 | 0 | 4.4113
5167 | 0 | 2.9355 | 1.9466 | 4.2903 | 0 | 9.1725 | 0 | 0 | 4.2903
5168 | 0 | 2.8697 | 1.9857 | 3.3835 | 18.8083 | 27.0472 | 0 | 0 | 22.1918
5169 | 0 | 2.8176 | 1.7436 | 4.0699 | 15.8747 | 24.5058 | 0 | 0 | 19.9445
5170 | 0 | 2.7673 | 1.9834 | 4.3666 | 14.2459 | 23.3632 | 0 | 0 | 18.6125
5171 | 0 | 2.6976 | 2.2739 | 3.7528 | 18.7066 | 27.4309 | 0 | 0 | 22.4594
5172 | 0 | 2.6176 | 2.4752 | 3.2667 | 8.0414 | 16.4008 | 0 | 0 | 11.3081
5173 | 0 | 3.1297 | 1.8702 | 3.9528 | 12.1645 | 21.1173 | 0 | 0 | 16.1174
5174 | 0 | 2.3852 | 2.2301 | 3.5126 | 8.1553 | 16.2833 | 0 | 0 | 11.6679
5175 | 0 | 3.1858 | 2.3118 | 5.246 | 23.1908 | 33.9343 | 0 | 0 | 28.4367
5176 | 0 | 2.3901 | 1.9 | 3.9321 | 10.0161 | 18.2383 | 0 | 0 | 13.9482
5177 | 0 | 3.0534 | 1.9367 | 5.0351 | 20.0046 | 30.0299 | 0 | 0 | 25.0397
5178 | 0 | 3.2253 | 1.5167 | 4.0641 | 15.571 | 24.3771 | 0 | 0 | 19.6351
5179 | 0 | 2.9977 | 1.4117 | 3.4463 | 18.6791 | 26.5348 | 0 | 0 | 22.1254
5180 | 0 | 2.7319 | 1.1486 | 4.6044 | 0 | 8.4849 | 0 | 0 | 4.6044
5181 | 0 | 3.1277 | 1.2344 | 4.6401 | 0 | 9.0022 | 0 | 0 | 4.6401
5182 | 0 | 2.4423 | 1.1264 | 3.1952 | 0 | 6.7639 | 0 | 0 | 3.1952
5183 | 0 | 3.5598 | 1.1609 | 4.9198 | 0 | 9.6404 | 0 | 0 | 4.9198
5184 | 0 | 3.2021 | 1.1591 | 3.9217 | 0 | 8.283 | 0 | 0 | 3.9217
5185 | 0 | 2.9089 | 2.1636 | 4.0493 | 0 | 9.1218 | 0 | 0 | 4.0493
5186 | 0 | 2.5013 | 1.767 | 3.7332 | 0 | 8.0015 | 0 | 0 | 3.7332
5187 | 0 | 2.835 | 2.6204 | 4.5513 | 0 | 10.0067 | 0 | 0 | 4.5513
5188 | 0 | 3.0908 | 2.6397 | 3.8037 | 0 | 9.5342 | 0 | 0 | 3.8037
5189 | 0 | 3.1752 | 2.3626 | 3.8794 | 0 | 9.4171 | 0 | 0 | 3.8794
5190 | 0 | 3.2113 | 1.8189 | 4.5495 | 0 | 9.5797 | 0 | 0 | 4.5495
5191 | 0 | 2.4945 | 1.9431 | 4.8702 | 0 | 9.3078 | 0 | 0 | 4.8702
5192 | 0 | 2.9058 | 1.9321 | 4.0685 | 14.9491 | 23.8554 | 0 | 0 | 19.0176
5193 | 0 | 2.7511 | 1.7582 | 4.2629 | 17.2193 | 25.9915 | 0 | 0 | 21.4822
5194 | 0 | 2.4857 | 1.4747 | 3.7722 | 17.4931 | 25.2256 | 0 | 0 | 21.2653
5195 | 0 | 2.7538 | 1.8335 | 4.0188 | 21.6981 | 30.3042 | 0 | 0 | 25.7169
5196 | 0 | 2.9712 | 2.0907 | 3.6849 | 11.4803 | 20.2271 | 0 | 0 | 15.1652
5197 | 0 | 2.5481 | 2.2196 | 4.8377 | 11.6084 | 21.2139 | 0 | 0 | 16.4461
5198 | 0 | 2.7929 | 2.2605 | 3.7185 | 15.2839 | 24.0557 | 0 | 0 | 19.0024
5199 | 0 | 2.902 | 2.1706 | 4.5216 | 11.6708 | 21.2651 | 0 | 0 | 16.1924
5200 | 0 | 2.7824 | 2.1677 | 3.8526 | 12.9952 | 21.7979 | 0 | 0 | 16.8477
5201 | 0 | 2.9146 | 2.1706 | 4.5722 | 8.4759 | 18.1334 | 0 | 0 | 13.0481
5202 | 0 | 2.8082 | 1.5861 | 5.3419 | 17.0594 | 26.7956 | 0 | 0 | 22.4012
5203 | 0 | 2.8302 | 1.239 | 3.9635 | 11.538 | 19.5707 | 0 | 0 | 15.5015
5204 | 0 | 2.7596 | 1.0185 | 3.504 | 0 | 7.2821 | 0 | 0 | 3.504
5205 | 0 | 2.1162 | 1.0722 | 4.7134 | 0 | 7.9018 | 0 | 0 | 4.7134
5206 | 0 | 3.2897 | 1.1947 | 4.6366 | 0 | 9.121 | 0 | 0 | 4.6366
5207 | 0 | 2.2408 | 1.2542 | 3.9079 | 0 | 7.4029 | 0 | 0 | 3.9079
5208 | 0 | 2.7993 | 2.7569 | 3.2093 | 0 | 8.7655 | 0 | 0 | 3.2093
5209 | 0 | 2.9189 | 4.3028 | 3.9984 | 0 | 11.2201 | 0 | 0 | 3.9984
5210 | 0 | 2.5184 | 3.0702 | 4.3218 | 0 | 9.9104 | 0 | 0 | 4.3218
5211 | 0 | 3.0789 | 2.3713 | 4.2901 | 0 | 9.7404 | 0 | 0 | 4.2901
5212 | 0 | 3.2997 | 2.2727 | 3.964 | 0 | 9.5364 | 0 | 0 | 3.964
5213 | 0 | 2.4834 | 2.0277 | 3.7351 | 0 | 8.2463 | 0 | 0 | 3.7351
5214 | 0 | 2.6916 | 1.8545 | 4.3585 | 0 | 8.9045 | 0 | 0 | 4.3585
5215 | 0 | 2.2938 | 1.8626 | 3.7435 | 0 | 7.8999 | 200 | 0 | 203.7435
5216 | 0 | 3.5348 | 1.8002 | 4.5717 | 20.3565 | 30.2632 | 0 | 0 | 24.9281
5217 | 0 | 2.9953 | 1.7611 | 4.3816 | 11.1324 | 20.2704 | 0 | 0 | 15.514
5218 | 0 | 2.7137 | 1.7681 | 3.2764 | 29.3128 | 37.0711 | 0 | 0 | 32.5893
5219 | 0 | 2.7132 | 1.3773 | 3.6769 | 20.1209 | 27.8883 | 0 | 0 | 23.7978
5220 | 0 | 2.3135 | 2.3299 | 3.8237 | 14.014 | 22.4811 | 0 | 0 | 17.8377
5221 | 1.9389 | 2.6444 | 2.3888 | 3.5158 | 26.2281 | 36.716 | 0 | 0 | 31.6828
5222 | 27.6669 | 2.5509 | 2.0295 | 5.7614 | 10.5796 | 48.5882 | 0 | 0 | 44.0079
5223 | 69.2859 | 2.8663 | 1.9886 | 3.8273 | 11.3124 | 89.2805 | 0 | 0 | 84.4255
5224 | 62.4035 | 2.8878 | 2.2272 | 2.9607 | 8.6706 | 79.1498 | 0 | 0 | 74.0348
5225 | 31.5097 | 2.6014 | 2.1199 | 3.8518 | 16.6354 | 56.7182 | 0 | 0 | 51.9969
5226 | 0 | 3.1963 | 1.5861 | 3.5398 | 13.1626 | 21.4848 | 0 | 0 | 16.7024
5227 | 0 | 3.2178 | 1.239 | 3.9915 | 13.2966 | 21.7449 | 0 | 0 | 17.2881
5228 | 0 | 2.7838 | 1.0185 | 5.2194 | 0 | 9.0217 | 0 | 0 | 5.2194
5229 | 0 | 2.7424 | 1.0722 | 3.8651 | 0 | 7.6797 | 0 | 0 | 3.8651
5230 | 0 | 3.0172 | 1.1947 | 4.3625 | 0 | 8.5745 | 0 | 0 | 4.3625
5231 | 0 | 2.9337 | 1.2542 | 4.4168 | 0 | 8.6047 | 0 | 0 | 4.4168
5232 | 0 | 2.98 | 2.7569 | 3.8606 | 0 | 9.5976 | 0 | 0 | 3.8606
5233 | 0 | 3.0997 | 4.3028 | 4.6657 | 0 | 12.0681 | 0 | 0 | 4.6657
5234 | 0 | 2.8351 | 3.0702 | 5.3897 | 0 | 11.295 | 0 | 200 | 205.3897
5235 | 0 | 2.4621 | 2.3713 | 4.6973 | 0 | 9.5308 | 0 | 0 | 4.6973
5236 | 1.5613 | 2.6888 | 2.2727 | 3.9381 | 0 | 10.4609 | 0 | 0 | 5.4994
5237 | 21.2521 | 2.4634 | 2.0277 | 4.1934 | 0 | 29.9366 | 0 | 0 | 25.4455
5238 | 78.3415 | 2.6743 | 1.8545 | 3.763 | 0 | 86.6332 | 0 | 0 | 82.1044
5239 | 42.0042 | 3.0921 | 1.8626 | 4.026 | 0 | 50.985 | 0 | 0 | 46.0302
5240 | 24.845 | 2.8989 | 1.8002 | 4.7457 | 13.1814 | 47.4711 | 0 | 0 | 42.772
5241 | 22.6744 | 2.7899 | 1.7611 | 3.7983 | 17.8671 | 48.8908 | 0 | 0 | 44.3397
5242 | 38.0906 | 2.4946 | 1.7681 | 3.7502 | 19.3697 | 65.4732 | 0 | 0 | 61.2105
5243 | 49.4801 | 2.8147 | 1.3773 | 4.0195 | 19.3807 | 77.0723 | 0 | 0 | 72.8803
5244 | 57.5816 | 3.0021 | 2.3299 | 3.6722 | 7.8677 | 74.4536 | 0 | 0 | 69.1216
5245 | 61.1699 | 2.8431 | 2.3888 | 3.4112 | 9.3454 | 79.1584 | 0 | 0 | 73.9265
5246 | 70.8779 | 2.5497 | 2.0295 | 4.5707 | 8.0792 | 88.107 | 0 | 0 | 83.5278
5247 | 61.4994 | 2.7193 | 1.9886 | 3.8008 | 20.7015 | 90.7096 | 0 | 0 | 86.0017
5248 | 79.0531 | 2.7796 | 2.2272 | 3.3867 | 13.4165 | 100.8631 | 0 | 0 | 95.8563
5249 | 73.7595 | 3.1221 | 2.1199 | 5.1072 | 18.8785 | 102.9872 | 0 | 0 | 97.7452
5250 | 63.4208 | 3.0254 | 1.5861 | 4.2582 | 9.8834 | 82.1739 | 0 | 0 | 77.5624
5251 | 64.1023 | 3.1701 | 1.239 | 4.538 | 11.7975 | 84.847 | 0 | 0 | 80.4379
5252 | 49.1681 | 2.9554 | 1.0185 | 4.5578 | 0 | 57.6998 | 0 | 0 | 53.7259
5253 | 34.3578 | 2.894 | 1.0722 | 4.6694 | 0 | 42.9934 | 0 | 0 | 39.0273
5254 | 40.5253 | 2.8078 | 1.1947 | 4.1583 | 0 | 48.686 | 0 | 0 | 44.6835
5255 | 32.8203 | 2.9986 | 1.2542 | 4.1344 | 0 | 41.2074 | 0 | 0 | 36.9546
5256 | 0 | 2.4445 | 2.7569 | 3.785 | 0 | 8.9865 | 0 | 0 | 3.785
5257 | 0 | 3.0066 | 4.3028 | 3.1618 | 0 | 10.4712 | 0 | 0 | 3.1618
5258 | 7.3287 | 2.4916 | 3.0702 | 4.3692 | 0 | 17.2597 | 0 | 0 | 11.6979
5259 | 27.6521 | 2.4728 | 2.3713 | 2.926 | 0 | 35.4222 | 0 | 0 | 30.5781
5260 | 18.4426 | 3.0438 | 2.2727 | 5.3127 | 0 | 29.0718 | 0 | 0 | 23.7552
5261 | 16.9928 | 2.5265 | 2.0277 | 4.9401 | 0 | 26.4871 | 0 | 0 | 21.9329
5262 | 51.0761 | 2.4665 | 1.8545 | 4.8879 | 0 | 60.2849 | 0 | 0 | 55.9639
5263 | 44.4464 | 2.6251 | 1.8626 | 4.0032 | 0 | 52.9374 | 0 | 0 | 48.4496
5264 | 42.3359 | 2.4472 | 1.8002 | 5.0074 | 10.327 | 61.9178 | 0 | 0 | 57.6704
5265 | 44.7877 | 2.8398 | 1.7611 | 3.8652 | 12.3813 | 65.6352 | 0 | 0 | 61.0342
5266 | 46.2551 | 2.9215 | 1.7681 | 4.1485 | 15.3853 | 70.4786 | 0 | 0 | 65.789
5267 | 17.7088 | 2.3824 | 1.3773 | 4.6732 | 16.2506 | 42.3923 | 0 | 0 | 38.6326
5268 | 0 | 2.9663 | 2.3299 | 4.3337 | 14.4911 | 24.121 | 0 | 0 | 18.8248
5269 | 0 | 2.7098 | 2.3888 | 3.8789 | 12.6344 | 21.6119 | 0 | 0 | 16.5133
5270 | 0 | 3.2476 | 2.0295 | 4.0635 | 16.0743 | 25.4149 | 0 | 0 | 20.1378
5271 | 0 | 2.4748 | 1.9886 | 4.5821 | 15.1476 | 24.1931 | 0 | 0 | 19.7297
5272 | 0 | 2.5865 | 2.2272 | 3.5565 | 8.4958 | 16.866 | 0 | 0 | 12.0523
5273 | 0 | 3.1228 | 2.1199 | 4.7265 | 17.8492 | 27.8185 | 0 | 0 | 22.5758
5274 | 0 | 3.0085 | 1.5861 | 5.1022 | 15.4484 | 25.1453 | 0 | 0 | 20.5507
5275 | 0 | 3.145 | 1.239 | 4.1549 | 22.3672 | 30.9062 | 0 | 0 | 26.5221
5276 | 0 | 2.0108 | 1.0185 | 2.8824 | 0 | 5.9117 | 0 | 0 | 2.8824
5277 | 0 | 3.0214 | 1.0722 | 3.5458 | 0 | 7.6395 | 0 | 0 | 3.5458
5278 | 0 | 2.6012 | 1.1947 | 5.1589 | 0 | 8.9549 | 0 | 0 | 5.1589
5279 | 0 | 2.6011 | 1.2542 | 3.3998 | 0 | 7.2551 | 0 | 0 | 3.3998
5280 | 0 | 3.2207 | 2.7569 | 3.9845 | 0 | 9.9621 | 0 | 0 | 3.9845
5281 | 0 | 3.0655 | 4.3028 | 5.3986 | 0 | 12.7669 | 0 | 0 | 5.3986
5282 | 0 | 2.4738 | 3.0702 | 4.7574 | 0 | 10.3014 | 0 | 0 | 4.7574
5283 | 0 | 2.7511 | 2.3713 | 4.3014 | 0 | 9.4239 | 0 | 0 | 4.3014
5284 | 0 | 3.2012 | 2.2727 | 3.432 | 0 | 8.906 | 0 | 0 | 3.432
5285 | 0 | 3.2971 | 2.0277 | 4.3552 | 0 | 9.68 | 0 | 0 | 4.3552
5286 | 0 | 2.6793 | 1.8545 | 4.0823 | 0 | 8.6161 | 200 | 0 | 204.0823
5287 | 0 | 3.0219 | 1.8626 | 3.8266 | 0 | 8.7111 | 0 | 0 | 3.8266
5288 | 0 | 2.6878 | 1.8002 | 4.0418 | 16.224 | 24.7537 | 0 | 0 | 20.2658
5289 | 0 | 3.4236 | 1.7611 | 5.1471 | 9.9145 | 20.2464 | 0 | 0 | 15.0616
5290 | 0 | 2.6817 | 1.7681 | 4.9278 | 26.4774 | 35.8551 | 0 | 0 | 31.4052
5291 | 0 | 3.2892 | 1.3773 | 4.0715 | 19.1838 | 27.9218 | 0 | 0 | 23.2553
5292 | 0 | 2.8767 | 2.3299 | 4.7024 | 14.2165 | 24.1256 | 0 | 0 | 18.9189
5293 | 0 | 2.4846 | 2.3888 | 3.9688 | 22.0483 | 30.8905 | 0 | 0 | 26.017
5294 | 0 | 2.7095 | 2.0295 | 4.5089 | 8.0024 | 17.2503 | 0 | 0 | 12.5113
5295 | 0 | 2.6562 | 1.9886 | 5.6141 | 13.7518 | 24.0107 | 0 | 0 | 19.3659
5296 | 0 | 2.9464 | 2.2272 | 5.0783 | 14.8424 | 25.0944 | 0 | 0 | 19.9207
5297 | 0 | 2.6794 | 2.1199 | 4.434 | 8.0024 | 17.2357 | 0 | 0 | 12.4364
5298 | 0 | 2.9538 | 1.5861 | 4.0775 | 12.4082 | 21.0256 | 0 | 0 | 16.4857
5299 | 0 | 3.2002 | 1.239 | 4.0451 | 10.8927 | 19.377 | 0 | 0 | 14.9378
5300 | 0 | 2.5076 | 1.0185 | 3.8404 | 0 | 7.3665 | 0 | 0 | 3.8404
5301 | 0 | 2.9475 | 1.0722 | 4.0587 | 0 | 8.0784 | 0 | 0 | 4.0587
5302 | 0 | 2.6414 | 1.1947 | 4.8724 | 0 | 8.7085 | 0 | 0 | 4.8724
5303 | 0 | 3.2767 | 1.2542 | 3.1686 | 0 | 7.6995 | 0 | 0 | 3.1686
5304 | 0 | 3.4204 | 2.7569 | 3.6423 | 0 | 9.8196 | 0 | 0 | 3.6423
5305 | 0 | 3.0613 | 4.3028 | 4.821 | 0 | 12.1851 | 0 | 0 | 4.821
5306 | 0 | 2.7484 | 3.0702 | 2.8492 | 0 | 8.6678 | 0 | 0 | 2.8492
5307 | 0 | 3.3846 | 2.3713 | 4.2589 | 0 | 10.0148 | 0 | 0 | 4.2589
5308 | 0 | 2.1958 | 2.2727 | 3.5316 | 0 | 8.0001 | 0 | 0 | 3.5316
5309 | 0 | 3.2528 | 2.0277 | 4.2727 | 0 | 9.5533 | 0 | 0 | 4.2727
5310 | 0 | 2.7511 | 1.8545 | 4.6593 | 0 | 9.2648 | 0 | 0 | 4.6593
5311 | 0 | 3.1709 | 1.8626 | 3.3748 | 0 | 8.4083 | 0 | 0 | 3.3748
5312 | 0 | 2.7504 | 1.8002 | 1.7386 | 9.9405 | 16.2297 | 0 | 0 | 11.6792
5313 | 14.3719 | 2.7367 | 1.7611 | 3.9221 | 13.9381 | 36.73 | 0 | 0 | 32.2322
5314 | 53.1647 | 2.8088 | 1.7681 | 4.4703 | 16.5793 | 78.7913 | 0 | 0 | 74.2144
5315 | 43.2934 | 2.7922 | 1.3773 | 3.3097 | 11.1492 | 61.9218 | 0 | 0 | 57.7523
5316 | 68.1319 | 2.8531 | 2.3299 | 4.3229 | 18.3545 | 95.9923 | 0 | 0 | 90.8093
5317 | 74.5597 | 3.1841 | 2.3888 | 4.7282 | 15.9761 | 100.837 | 0 | 0 | 95.2641
5318 | 56.6786 | 3.0605 | 2.0295 | 3.2454 | 19.9156 | 84.9296 | 0 | 0 | 79.8396
5319 | 71.6313 | 2.635 | 1.9886 | 3.5642 | 10.1842 | 90.0033 | 0 | 0 | 85.3797
5320 | 49.4619 | 2.7824 | 2.2272 | 3.8224 | 20.7092 | 79.0032 | 0 | 0 | 73.9935
5321 | 0 | 2.3026 | 2.1199 | 4.447 | 2.9038 | 11.7734 | 0 | 0 | 7.3509
5322 | 0 | 2.2923 | 1.9531 | 5.0795 | 17.6175 | 26.9424 | 0 | 0 | 22.697
5323 | 0 | 3.0086 | 1.5255 | 3.5063 | 6.8073 | 14.8476 | 0 | 0 | 10.3136
5324 | 0 | 3.0206 | 1.1504 | 2.8268 | 0 | 6.9978 | 0 | 0 | 2.8268
5325 | 0 | 2.9366 | 1.1994 | 4.8085 | 0 | 8.9445 | 0 | 0 | 4.8085
5326 | 0 | 2.4138 | 1.0675 | 3.1215 | 0 | 6.6028 | 0 | 0 | 3.1215
5327 | 0 | 3.0316 | 1.3615 | 2.5487 | 0 | 6.9418 | 0 | 0 | 2.5487
5328 | 0 | 2.4558 | 1.7973 | 4.4086 | 0 | 8.6617 | 0 | 0 | 4.4086
5329 | 0 | 2.4756 | 2.1992 | 3.6217 | 0 | 8.2965 | 0 | 0 | 3.6217
5330 | 0 | 2.8719 | 1.9945 | 4.7704 | 0 | 9.6368 | 0 | 0 | 4.7704
5331 | 0 | 2.9207 | 3.6751 | 2.4673 | 0 | 9.0631 | 0 | 0 | 2.4673
5332 | 0 | 3.3186 | 3.2685 | 2.8548 | 0 | 9.4419 | 0 | 0 | 2.8548
5333 | 0 | 2.97 | 2.6595 | 4.932 | 0 | 10.5615 | 0 | 0 | 4.932
5334 | 0 | 2.8107 | 2.1561 | 4.3664 | 0 | 9.3332 | 0 | 200 | 204.3664
5335 | 0 | 2.565 | 1.9466 | 3.0525 | 0 | 7.5641 | 0 | 0 | 3.0525
5336 | 0 | 2.8649 | 1.9857 | 3.2513 | 15.246 | 23.3479 | 0 | 0 | 18.4973
5337 | 0 | 2.9747 | 1.7436 | 3.1928 | 15.4528 | 23.3641 | 0 | 0 | 18.6457
5338 | 0 | 2.8242 | 1.9834 | 4.568 | 9.5872 | 18.9627 | 0 | 0 | 14.1551
5339 | 0 | 2.7332 | 2.2739 | 3.6005 | 9.2288 | 17.8364 | 0 | 0 | 12.8293
5340 | 0 | 3.0997 | 2.4752 | 4.2452 | 15.7013 | 25.5214 | 0 | 0 | 19.9466
5341 | 0 | 2.9899 | 1.8702 | 3.6461 | 4.5467 | 13.053 | 0 | 0 | 8.1928
5342 | 0 | 2.6078 | 2.2301 | 4.6057 | 18.9677 | 28.4114 | 0 | 0 | 23.5734
5343 | 0 | 2.3899 | 2.3118 | 3.861 | 13.6515 | 22.2141 | 0 | 0 | 17.5124
5344 | 0 | 2.895 | 1.9 | 4.5909 | 6.7763 | 16.1622 | 0 | 0 | 11.3672
5345 | 0 | 2.3964 | 1.9367 | 3.6579 | 11.1393 | 19.1303 | 0 | 0 | 14.7971
5346 | 0 | 2.7895 | 1.5167 | 5.0627 | 8.7835 | 18.1524 | 0 | 0 | 13.8462
5347 | 0 | 2.7909 | 1.4117 | 4.437 | 21.7999 | 30.4395 | 0 | 0 | 26.2369
5348 | 0 | 2.7915 | 1.1486 | 3.7456 | 0 | 7.6858 | 0 | 0 | 3.7456
5349 | 0 | 2.3699 | 1.2344 | 4.2206 | 0 | 7.8249 | 0 | 0 | 4.2206
5350 | 0 | 2.5344 | 1.1264 | 4.4342 | 0 | 8.095 | 0 | 0 | 4.4342
5351 | 0 | 3.206 | 1.1609 | 4.4328 | 0 | 8.7997 | 0 | 0 | 4.4328
5352 | 0 | 2.9335 | 1.1591 | 4.0356 | 0 | 8.1282 | 0 | 0 | 4.0356
5353 | 0 | 2.5162 | 2.1636 | 3.9051 | 0 | 8.585 | 0 | 0 | 3.9051
5354 | 0 | 2.908 | 1.767 | 4.9918 | 0 | 9.6667 | 0 | 0 | 4.9918
5355 | 0 | 2.9525 | 2.6204 | 3.3135 | 0 | 8.8864 | 0 | 0 | 3.3135
5356 | 0 | 2.6448 | 2.6397 | 4.0884 | 0 | 9.3728 | 0 | 0 | 4.0884
5357 | 0 | 2.7708 | 2.3626 | 3.8123 | 0 | 8.9457 | 200 | 0 | 203.8123
5358 | 0 | 2.551 | 1.8189 | 3.7652 | 0 | 8.1351 | 0 | 0 | 3.7652
5359 | 0 | 3.089 | 1.9431 | 4.4041 | 0 | 9.4362 | 0 | 0 | 4.4041
5360 | 0 | 2.5394 | 1.9321 | 4.5661 | 19.1097 | 28.1473 | 0 | 0 | 23.6758
5361 | 0 | 2.652 | 1.7582 | 4.6776 | 9.1089 | 18.1967 | 0 | 0 | 13.7865
5362 | 0 | 2.7396 | 1.4747 | 3.3521 | 13.1172 | 20.6836 | 0 | 0 | 16.4693
5363 | 0 | 2.7555 | 1.8335 | 4.128 | 18.4688 | 27.1858 | 0 | 0 | 22.5969
5364 | 0 | 2.7135 | 2.0907 | 2.8025 | 14.208 | 21.8148 | 0 | 0 | 17.0106
5365 | 0 | 2.4378 | 2.2196 | 4.3874 | 22.299 | 31.3439 | 0 | 0 | 26.6865
5366 | 0 | 2.5434 | 2.2605 | 3.9405 | 7.6503 | 16.3948 | 0 | 0 | 11.5909
5367 | 0 | 3.1775 | 2.1706 | 3.6522 | 18.3775 | 27.3779 | 0 | 0 | 22.0297
5368 | 0 | 2.8472 | 2.1677 | 3.7533 | 12.0741 | 20.8423 | 0 | 0 | 15.8273
5369 | 0 | 2.7977 | 2.1706 | 3.7915 | 14.7147 | 23.4746 | 0 | 0 | 18.5062
5370 | 1.4678 | 2.4684 | 1.5861 | 4.4588 | 22.2382 | 32.2193 | 0 | 0 | 28.1648
5371 | 13.4499 | 3.3188 | 1.239 | 4.2104 | 11.5148 | 33.7329 | 0 | 0 | 29.1751
5372 | 45.2787 | 2.5502 | 1.0185 | 5.0933 | 0 | 53.9406 | 0 | 0 | 50.3719
5373 | 4.4982 | 2.7196 | 1.0722 | 5.5986 | 0 | 13.8886 | 0 | 0 | 10.0968
5374 | 14.9213 | 2.9273 | 1.1947 | 3.815 | 0 | 22.8583 | 0 | 0 | 18.7363
5375 | 0.039182 | 2.7266 | 1.2542 | 4.2636 | 0 | 8.2836 | 0 | 0 | 4.3027
5376 | 0 | 2.7817 | 2.7569 | 4.3039 | 0 | 9.8425 | 0 | 0 | 4.3039
5377 | 0 | 2.6314 | 4.3028 | 4.0016 | 0 | 10.9359 | 0 | 0 | 4.0016
5378 | 0 | 2.6602 | 3.0702 | 4.5238 | 0 | 10.2541 | 0 | 0 | 4.5238
5379 | 0 | 2.9488 | 2.3713 | 5.9065 | 0 | 11.2267 | 0 | 0 | 5.9065
5380 | 0.57752 | 2.8537 | 2.2727 | 4.5232 | 0 | 10.2272 | 0 | 0 | 5.1007
5381 | 8.9096 | 2.6845 | 2.0277 | 3.7634 | 0 | 17.3852 | 0 | 0 | 12.6731
5382 | 21.5814 | 2.8906 | 1.8545 | 2.7297 | 0 | 29.0562 | 0 | 0 | 24.3111
5383 | 2.7059 | 3.1282 | 1.8626 | 2.8451 | 0 | 10.5419 | 0 | 0 | 5.551
5384 | 0 | 2.6878 | 1.8002 | 4.6918 | 20.628 | 29.8078 | 0 | 0 | 25.3198
5385 | 0 | 2.5953 | 1.7611 | 3.9263 | 10.0474 | 18.3301 | 0 | 0 | 13.9737
5386 | 0 | 2.3862 | 1.7681 | 4.7735 | 13.251 | 22.1789 | 0 | 0 | 18.0246
5387 | 0 | 2.7921 | 1.3773 | 4.3859 | -2.3696 | 6.1858 | 0 | 0 | 2.0164
5388 | 0 | 2.6625 | 2.3299 | 3.2243 | 12.2794 | 20.496 | 0 | 0 | 15.5037
5389 | 0 | 2.7061 | 2.3888 | 4.1864 | 13.1181 | 22.3995 | 0 | 0 | 17.3045
5390 | 0 | 2.721 | 2.0295 | 4.0366 | 14.4058 | 23.1928 | 0 | 0 | 18.4424
5391 | 0 | 2.7283 | 1.9886 | 3.8503 | 12.3708 | 20.938 | 0 | 0 | 16.2211
5392 | 0 | 3.0845 | 2.2272 | 3.407 | 18.4294 | 27.1481 | 0 | 0 | 21.8364
5393 | 0 | 2.8317 | 2.1199 | 3.1536 | 12.777 | 20.8821 | 0 | 0 | 15.9306
5394 | 0 | 2.7497 | 1.5861 | 4.0908 | 21.1833 | 29.6099 | 0 | 0 | 25.274
5395 | 0 | 2.5134 | 1.239 | 4.3658 | 18.6859 | 26.8042 | 0 | 0 | 23.0517
5396 | 0 | 3.006 | 1.0185 | 4.7385 | 0 | 8.763 | 0 | 0 | 4.7385
5397 | 0 | 2.9112 | 1.0722 | 4.2462 | 0 | 8.2297 | 0 | 0 | 4.2462
5398 | 0 | 2.2545 | 1.1947 | 4.2044 | 0 | 7.6536 | 0 | 0 | 4.2044
5399 | 0 | 2.9683 | 1.2542 | 4.916 | 0 | 9.1385 | 0 | 0 | 4.916
5400 | 0 | 2.6439 | 2.7569 | 3.6328 | 0 | 9.0336 | 0 | 0 | 3.6328
5401 | 0 | 2.7681 | 4.3028 | 5.0846 | 0 | 12.1554 | 0 | 0 | 5.0846
5402 | 0 | 2.4461 | 3.0702 | 3.8708 | 0 | 9.3871 | 0 | 0 | 3.8708
5403 | 0 | 2.9576 | 2.3713 | 3.6867 | 0 | 9.0155 | 0 | 0 | 3.6867
5404 | 0 | 3.1488 | 2.2727 | 3.2501 | 0 | 8.6716 | 0 | 0 | 3.2501
5405 | 0 | 2.8155 | 2.0277 | 4.1474 | 0 | 8.9906 | 0 | 0 | 4.1474
5406 | 0 | 2.8556 | 1.8545 | 4.4283 | 0 | 9.1383 | 0 | 0 | 4.4283
5407 | 0 | 2.6807 | 1.8626 | 3.5461 | 0 | 8.0895 | 0 | 0 | 3.5461
5408 | 0 | 3.1577 | 1.8002 | 3.4509 | 15.1706 | 23.5795 | 0 | 0 | 18.6215
5409 | 0 | 2.7352 | 1.7611 | 4.5444 | 10.2835 | 19.3243 | 0 | 0 | 14.828
5410 | 0 | 2.6543 | 1.7681 | 3.9891 | 6.1493 | 14.5608 | 0 | 0 | 10.1384
5411 | 0 | 2.8309 | 1.3773 | 4.4412 | 13.687 | 22.3364 | 0 | 0 | 18.1283
5412 | 0 | 2.7386 | 2.3299 | 4.8148 | 17.2782 | 27.1615 | 0 | 0 | 22.093
5413 | 0 | 2.5115 | 2.3888 | 3.9774 | 13.3218 | 22.1996 | 0 | 0 | 17.2992
5414 | 0 | 2.982 | 2.0295 | 4.1217 | 15.3824 | 24.5156 | 0 | 0 | 19.5041
5415 | 0 | 2.9639 | 1.9886 | 4.5463 | 5.5871 | 15.086 | 0 | 0 | 10.1335
5416 | 0 | 2.3478 | 2.2272 | 3.4951 | 28.7438 | 36.814 | 0 | 0 | 32.239
5417 | 0 | 3.0087 | 2.1199 | 4.6848 | 6.8696 | 16.6829 | 0 | 0 | 11.5543
5418 | 0 | 2.7016 | 1.5861 | 3.5749 | 8.3214 | 16.184 | 0 | 0 | 11.8964
5419 | 0 | 2.3868 | 1.239 | 4.2694 | 17.4358 | 25.3311 | 0 | 0 | 21.7053
5420 | 0 | 2.6187 | 1.0185 | 3.5441 | 0 | 7.1813 | 0 | 0 | 3.5441
5421 | 0 | 3.1047 | 1.0722 | 3.5682 | 0 | 7.7451 | 0 | 0 | 3.5682
5422 | 0 | 2.8281 | 1.1947 | 2.9512 | 0 | 6.9741 | 0 | 0 | 2.9512
5423 | 0 | 2.7108 | 1.2542 | 3.9332 | 0 | 7.8982 | 0 | 0 | 3.9332
5424 | 0 | 3.0016 | 2.7569 | 4.2025 | 0 | 9.961 | 0 | 0 | 4.2025
5425 | 0 | 2.7747 | 4.3028 | 3.7886 | 0 | 10.8661 | 0 | 0 | 3.7886
5426 | 0 | 2.6281 | 3.0702 | 4.6619 | 0 | 10.3601 | 0 | 0 | 4.6619
5427 | 0 | 2.5588 | 2.3713 | 4.3457 | 0 | 9.2758 | 0 | 0 | 4.3457
5428 | 8.9259 | 2.4131 | 2.2727 | 3.9293 | 0 | 17.541 | 0 | 0 | 12.8552
5429 | 37.1035 | 2.3014 | 2.0277 | 4.3404 | 0 | 45.7731 | 200 | 0 | 241.4439
5430 | 48.152 | 2.5589 | 1.8545 | 3.2605 | 0 | 55.8258 | 0 | 0 | 51.4125
5431 | 22.6528 | 2.3148 | 1.8626 | 4.348 | 0 | 31.1781 | 0 | 0 | 27.0007
5432 | 0 | 2.8153 | 1.8002 | 4.6121 | 13.3953 | 22.6229 | 0 | 0 | 18.0074
5433 | 0 | 2.8345 | 1.7611 | 4.889 | 20.5401 | 30.0248 | 0 | 0 | 25.4292
5434 | 3.8267 | 3.0403 | 1.7681 | 3.9 | 23.2242 | 35.7593 | 0 | 0 | 30.9509
5435 | 10.0718 | 2.6783 | 1.3773 | 2.9709 | 15.4099 | 32.5082 | 0 | 0 | 28.4526
5436 | 0.16992 | 2.8628 | 2.3299 | 3.4747 | 21.4729 | 30.3102 | 0 | 200 | 225.1175
5437 | 0 | 2.6606 | 2.3888 | 4.4323 | 12.2862 | 21.768 | 0 | 0 | 16.7186
5438 | 0 | 2.9435 | 2.0295 | 4.8261 | 17.7787 | 27.5778 | 0 | 0 | 22.6048
5439 | 0 | 2.9902 | 1.9886 | 3.949 | 10.0741 | 19.0019 | 0 | 0 | 14.0231
5440 | 0 | 3.12 | 2.2272 | 3.4498 | 5.4976 | 14.2946 | 0 | 0 | 8.9474
5441 | 0 | 2.5412 | 2.1199 | 4.7525 | 23.6041 | 33.0177 | 0 | 0 | 28.3566
5442 | 0 | 2.9369 | 1.5861 | 4.2687 | 4.4541 | 13.2459 | 0 | 0 | 8.7228
5443 | 0 | 3.1441 | 1.239 | 3.9199 | -0.17093 | 8.1322 | 0 | 0 | 3.749
5444 | 0 | 3.0393 | 1.0185 | 3.8408 | 0 | 7.8987 | 0 | 0 | 3.8408
5445 | 0 | 2.9819 | 1.0722 | 4.1874 | 0 | 8.2414 | 0 | 0 | 4.1874
5446 | 0 | 3.1645 | 1.1947 | 4.1317 | 0 | 8.4909 | 0 | 0 | 4.1317
5447 | 0 | 2.5975 | 1.2542 | 3.2851 | 0 | 7.1368 | 0 | 0 | 3.2851
5448 | 0 | 3.1195 | 2.7569 | 3.41 | 0 | 9.2864 | 0 | 0 | 3.41
5449 | 0 | 2.858 | 4.3028 | 4.048 | 0 | 11.2088 | 0 | 0 | 4.048
5450 | 0 | 3.0365 | 3.0702 | 4.0055 | 0 | 10.1121 | 0 | 0 | 4.0055
5451 | 0 | 2.6813 | 2.3713 | 3.4407 | 0 | 8.4933 | 0 | 0 | 3.4407
5452 | 6.8211 | 3.2501 | 2.2727 | 4.7546 | 0 | 17.0985 | 0 | 0 | 11.5756
5453 | 25.7397 | 2.8878 | 2.0277 | 4.0307 | 0 | 34.6859 | 0 | 0 | 29.7704
5454 | 30.5085 | 2.7906 | 1.8545 | 3.6433 | 0 | 38.7968 | 0 | 0 | 34.1518
5455 | 13.4756 | 2.5809 | 1.8626 | 4.015 | 0 | 21.934 | 0 | 0 | 17.4905
5456 | 0 | 3.0075 | 1.8002 | 3.9898 | 4.9766 | 13.7741 | 0 | 0 | 8.9663
5457 | 0 | 2.9675 | 1.7611 | 3.2658 | 12.0233 | 20.0177 | 0 | 0 | 15.2891
5458 | 0 | 2.8733 | 1.7681 | 4.6607 | 26.8034 | 36.1055 | 0 | 0 | 31.4641
5459 | 0 | 2.2108 | 1.3773 | 4.4246 | 6.8184 | 14.831 | 0 | 0 | 11.2429
5460 | 0 | 2.3317 | 2.3299 | 4.0989 | 4.5065 | 13.267 | 0 | 0 | 8.6055
5461 | 0 | 2.8088 | 2.3888 | 3.6164 | 15.0364 | 23.8504 | 0 | 0 | 18.6528
5462 | 0 | 2.6065 | 2.0295 | 5.209 | 13.5351 | 23.3801 | 0 | 0 | 18.7441
5463 | 0 | 2.9533 | 1.9886 | 4.5587 | 4.0334 | 13.534 | 0 | 0 | 8.5921
5464 | 0 | 2.9226 | 2.2272 | 4.0232 | 12.6379 | 21.811 | 0 | 0 | 16.6611
5465 | 0 | 2.9126 | 2.1199 | 4.1891 | 13.8988 | 23.1205 | 0 | 0 | 18.0879
5466 | 0 | 2.7307 | 1.5861 | 4.9431 | 16.1612 | 25.4212 | 0 | 0 | 21.1043
5467 | 0 | 2.969 | 1.239 | 3.427 | 16.967 | 24.602 | 0 | 0 | 20.3939
5468 | 0 | 3.1643 | 1.0185 | 3.9894 | 0 | 8.1722 | 0 | 0 | 3.9894
5469 | 0 | 2.8086 | 1.0722 | 3.907 | 0 | 7.7878 | 0 | 0 | 3.907
5470 | 0 | 2.413 | 1.1947 | 3.0934 | 0 | 6.7011 | 0 | 0 | 3.0934
5471 | 0 | 2.7336 | 1.2542 | 4.4748 | 0 | 8.4627 | 0 | 0 | 4.4748
5472 | 0 | 2.686 | 2.7569 | 3.8519 | 0 | 9.2948 | 0 | 0 | 3.8519
5473 | 0 | 3.0442 | 4.3028 | 3.8562 | 0 | 11.2033 | 0 | 0 | 3.8562
5474 | 0 | 2.6686 | 3.0702 | 5.0559 | 0 | 10.7947 | 0 | 0 | 5.0559
5475 | 0 | 2.6494 | 2.3713 | 5.4341 | 0 | 10.4549 | 0 | 0 | 5.4341
5476 | 0 | 2.8363 | 2.2727 | 4.1842 | 0 | 9.2932 | 0 | 0 | 4.1842
5477 | 0 | 3.008 | 2.0277 | 4.1254 | 0 | 9.1611 | 0 | 0 | 4.1254
5478 | 0 | 2.7735 | 1.8545 | 4.0026 | 0 | 8.6306 | 0 | 0 | 4.0026
5479 | 0 | 3.2207 | 1.8626 | 3.9947 | 0 | 9.078 | 0 | 0 | 3.9947
5480 | 0 | 2.6791 | 1.8002 | 2.7064 | 11.0307 | 18.2165 | 0 | 0 | 13.7371
5481 | 0 | 2.8697 | 1.7611 | 3.498 | 18.6648 | 26.7936 | 0 | 0 | 22.1627
5482 | 0 | 2.7166 | 1.7681 | 3.707 | 10.5915 | 18.7833 | 0 | 0 | 14.2985
5483 | 0 | 3.1265 | 1.3773 | 3.5475 | 22.3352 | 30.3865 | 0 | 0 | 25.8827
5484 | 0 | 2.8711 | 2.3299 | 4.7007 | 9.382 | 19.2837 | 0 | 0 | 14.0827
5485 | 0 | 2.646 | 2.3888 | 4.8112 | 20.765 | 30.6111 | 0 | 0 | 25.5762
5486 | 0 | 3.031 | 2.0295 | 4.673 | 26.2496 | 35.9831 | 0 | 0 | 30.9227
5487 | 0 | 2.5134 | 1.9886 | 5.053 | 22.1304 | 31.6854 | 0 | 0 | 27.1833
5488 | 0 | 2.4881 | 2.2272 | 3.4179 | 8.3275 | 16.4607 | 0 | 0 | 11.7454
5489 | 0 | 2.436 | 2.1199 | 4.2479 | 2.7779 | 11.5817 | 0 | 0 | 7.0257
5490 | 0 | 3.1987 | 1.9531 | 4.4558 | 14.491 | 24.0985 | 0 | 0 | 18.9468
5491 | 0 | 2.8137 | 1.5255 | 4.2587 | 11.7598 | 20.3576 | 0 | 0 | 16.0184
5492 | 0 | 2.7675 | 1.1504 | 4.1681 | 0 | 8.0859 | 0 | 0 | 4.1681
5493 | 0 | 2.8869 | 1.1994 | 5.0408 | 0 | 9.127 | 0 | 0 | 5.0408
5494 | 0 | 2.7877 | 1.0675 | 4.9699 | 0 | 8.8252 | 0 | 0 | 4.9699
5495 | 0 | 3.2339 | 1.3615 | 3.1474 | 0 | 7.7429 | 0 | 0 | 3.1474
5496 | 0 | 2.8706 | 1.7973 | 4.4642 | 0 | 9.1321 | 0 | 0 | 4.4642
5497 | 0 | 2.5822 | 2.1992 | 3.2772 | 0 | 8.0586 | 0 | 0 | 3.2772
5498 | 0 | 2.6404 | 1.9945 | 3.4809 | 0 | 8.1158 | 0 | 0 | 3.4809
5499 | 0 | 2.7548 | 3.6751 | 3.8764 | 0 | 10.3062 | 0 | 0 | 3.8764
5500 | 0 | 2.8722 | 3.2685 | 4.4257 | 0 | 10.5664 | 200 | 0 | 204.4257
5501 | 0 | 2.9606 | 2.6595 | 3.0976 | 0 | 8.7177 | 0 | 0 | 3.0976
5502 | 0 | 2.6031 | 2.1561 | 2.9315 | 0 | 7.6907 | 0 | 0 | 2.9315
5503 | 0 | 2.567 | 1.9466 | 3.9784 | 0 | 8.492 | 0 | 0 | 3.9784
5504 | 0 | 2.6173 | 1.9857 | 3.9474 | 15.0207 | 23.5711 | 0 | 0 | 18.9681
5505 | 0 | 2.9761 | 1.7436 | 4.5416 | 17.9721 | 27.2334 | 0 | 0 | 22.5137
5506 | 0 | 2.7278 | 1.9834 | 3.6921 | 11.8476 | 20.2508 | 0 | 0 | 15.5397
5507 | 0 | 3.2838 | 2.2739 | 3.7766 | 13.613 | 22.9473 | 0 | 0 | 17.3896
5508 | 0 | 3.1488 | 2.4752 | 4.0024 | 17.3517 | 26.9781 | 0 | 0 | 21.3542
5509 | 0 | 3.0681 | 1.8702 | 4.6861 | 6.1968 | 15.8213 | 0 | 0 | 10.8829
5510 | 0 | 2.8633 | 2.2301 | 3.9336 | 8.1435 | 17.1705 | 0 | 0 | 12.0771
5511 | 0 | 3.0047 | 2.3118 | 3.7702 | 20.1814 | 29.2682 | 0 | 0 | 23.9516
5512 | 0 | 2.2515 | 1.9 | 3.7912 | 11.8001 | 19.7427 | 0 | 0 | 15.5913
5513 | 0 | 2.8501 | 1.9367 | 4.3697 | 10.8567 | 20.0133 | 0 | 0 | 15.2265
5514 | 0 | 3.1282 | 1.5167 | 3.6378 | 20.5517 | 28.8344 | 0 | 0 | 24.1894
5515 | 0 | 3.735 | 1.4117 | 3.4658 | 3.9697 | 12.5821 | 0 | 0 | 7.4355
5516 | 0 | 2.8821 | 1.1486 | 3.7767 | 0 | 7.8074 | 0 | 0 | 3.7767
5517 | 0 | 3.0144 | 1.2344 | 2.9982 | 0 | 7.247 | 0 | 0 | 2.9982
5518 | 0 | 3.0819 | 1.1264 | 3.9276 | 0 | 8.136 | 0 | 0 | 3.9276
5519 | 0 | 2.8897 | 1.1609 | 3.7609 | 0 | 7.8115 | 0 | 0 | 3.7609
5520 | 0 | 2.31 | 1.1591 | 3.9346 | 0 | 7.4037 | 0 | 0 | 3.9346
5521 | 0 | 2.5501 | 2.1636 | 4.2358 | 0 | 8.9496 | 0 | 0 | 4.2358
5522 | 0 | 2.9345 | 1.767 | 4.1914 | 0 | 8.8929 | 0 | 0 | 4.1914
5523 | 0 | 3.0538 | 2.6204 | 4.2477 | 0 | 9.9219 | 0 | 0 | 4.2477
5524 | 0 | 2.4093 | 2.6397 | 3.4398 | 0 | 8.4888 | 0 | 0 | 3.4398
5525 | 0 | 2.4133 | 2.3626 | 5.1438 | 0 | 9.9197 | 0 | 0 | 5.1438
5526 | 0 | 2.7993 | 1.8189 | 4.1831 | 0 | 8.8012 | 0 | 0 | 4.1831
5527 | 0 | 2.7485 | 1.9431 | 4.3158 | 0 | 9.0074 | 0 | 0 | 4.3158
5528 | 0 | 2.7453 | 1.9321 | 3.5794 | 6.4043 | 14.661 | 0 | 0 | 9.9836
5529 | 0 | 2.8722 | 1.7582 | 3.8906 | 15.2632 | 23.7842 | 0 | 0 | 19.1538
5530 | 0 | 2.7746 | 1.4747 | 3.5968 | 11.4202 | 19.2663 | 0 | 0 | 15.017
5531 | 0 | 2.9838 | 1.8335 | 4.633 | 20.5741 | 30.0244 | 0 | 0 | 25.2072
5532 | 0 | 2.3551 | 2.0907 | 4.5474 | 12.4411 | 21.4344 | 0 | 0 | 16.9886
5533 | 0 | 2.7076 | 2.2196 | 4.0734 | 19.4734 | 28.4741 | 0 | 0 | 23.5468
5534 | 0 | 2.4658 | 2.2605 | 4.75 | 17.3601 | 26.8364 | 0 | 0 | 22.1101
5535 | 0 | 2.9966 | 2.1706 | 4.6238 | 14.953 | 24.7441 | 0 | 0 | 19.5768
5536 | 0 | 2.9115 | 2.1677 | 4.396 | 5.7313 | 15.2065 | 0 | 0 | 10.1273
5537 | 0 | 3.0349 | 2.1706 | 3.3021 | 4.78 | 13.2876 | 0 | 0 | 8.082
5538 | 0 | 2.5846 | 1.5861 | 3.6586 | 14.6805 | 22.5099 | 0 | 0 | 18.3391
5539 | 0 | 2.5222 | 1.239 | 3.8553 | 4.0995 | 11.7162 | 0 | 200 | 207.9549
5540 | 0 | 2.6751 | 1.0185 | 5.2842 | 0 | 8.9778 | 0 | 0 | 5.2842
5541 | 0 | 2.4557 | 1.0722 | 3.7637 | 0 | 7.2916 | 0 | 0 | 3.7637
5542 | 0 | 2.3101 | 1.1947 | 4.712 | 0 | 8.2168 | 0 | 0 | 4.712
5543 | 0 | 2.3308 | 1.2542 | 4.6349 | 0 | 8.2199 | 0 | 0 | 4.6349
5544 | 0 | 2.9298 | 2.7569 | 4.1212 | 0 | 9.8079 | 0 | 0 | 4.1212
5545 | 0 | 2.493 | 4.3028 | 3.3583 | 0 | 10.1541 | 0 | 0 | 3.3583
5546 | 0 | 2.976 | 3.0702 | 4.1581 | 0 | 10.2043 | 0 | 0 | 4.1581
5547 | 0 | 2.9143 | 2.3713 | 4.5925 | 0 | 9.8781 | 0 | 0 | 4.5925
5548 | 0 | 2.7152 | 2.2727 | 4.0695 | 0 | 9.0575 | 0 | 0 | 4.0695
5549 | 0 | 2.6511 | 2.0277 | 3.9075 | 0 | 8.5863 | 0 | 0 | 3.9075
5550 | 0 | 2.7913 | 1.8545 | 3.1963 | 0 | 7.8421 | 0 | 0 | 3.1963
5551 | 0 | 2.5794 | 1.8626 | 4.9293 | 0 | 9.3713 | 0 | 0 | 4.9293
5552 | 0 | 2.7558 | 1.8002 | 4.2365 | 25.4808 | 34.2733 | 0 | 0 | 29.7173
5553 | 0 | 2.7019 | 1.7611 | 5.3145 | 13.9892 | 23.7667 | 0 | 0 | 19.3037
5554 | 0 | 2.9681 | 1.7681 | 4.4266 | 12.2497 | 21.4125 | 0 | 0 | 16.6762
5555 | 0 | 2.8863 | 1.3773 | 3.6265 | 24.6151 | 32.5053 | 0 | 0 | 28.2417
5556 | 0 | 3.2717 | 2.3299 | 3.5166 | 15.5991 | 24.7173 | 0 | 0 | 19.1156
5557 | 0 | 2.4429 | 2.3888 | 3.6642 | 5.9457 | 14.4417 | 0 | 0 | 9.6099
5558 | 0 | 3.0118 | 2.0295 | 4.0654 | 11.0193 | 20.126 | 0 | 0 | 15.0847
5559 | 0 | 2.9316 | 1.9886 | 5.062 | 11.3095 | 21.2917 | 0 | 0 | 16.3715
5560 | 0 | 2.561 | 2.2272 | 4.3636 | 15.7271 | 24.8789 | 0 | 0 | 20.0907
5561 | 0 | 3.2742 | 2.1199 | 4.332 | 9.7029 | 19.4291 | 0 | 0 | 14.0349
5562 | 0 | 3.3262 | 1.5861 | 3.9298 | 9.4203 | 18.2624 | 0 | 0 | 13.3501
5563 | 0 | 2.5802 | 1.239 | 4.6033 | 2.0068 | 10.4293 | 0 | 0 | 6.61
5564 | 0 | 2.6681 | 1.0185 | 4.009 | 0 | 7.6956 | 0 | 0 | 4.009
5565 | 0 | 2.3045 | 1.0722 | 4.1591 | 0 | 7.5358 | 0 | 0 | 4.1591
5566 | 0 | 3.1663 | 1.1947 | 4.3408 | 0 | 8.7018 | 0 | 0 | 4.3408
5567 | 0 | 2.7989 | 1.2542 | 2.8921 | 0 | 6.9452 | 0 | 0 | 2.8921
5568 | 0 | 2.892 | 2.7569 | 4.8388 | 0 | 10.4877 | 0 | 0 | 4.8388
5569 | 0 | 2.4218 | 4.3028 | 120.2373 | 0 | 126.9619 | 0 | 0 | 120.2373
5570 | 0 | 2.6175 | 3.0702 | 118.2414 | 0 | 123.9291 | 0 | 0 | 118.2414
5571 | 0 | 2.9946 | 2.3713 | 100.8689 | 0 | 106.2347 | 0 | 0 | 100.8689
5572 | 7.3735 | 2.7882 | 2.2727 | 66.4296 | 0 | 78.864 | 200 | 0 | 273.803
5573 | 38.3208 | 2.8211 | 2.0277 | 103.2298 | 0 | 146.3995 | 0 | 0 | 141.5506
5574 | 58.7355 | 3.082 | 1.8545 | 119.3299 | 0 | 183.0019 | 0 | 0 | 178.0654
5575 | 6.2452 | 2.4758 | 1.8626 | 117.6414 | 0 | 128.2251 | 0 | 0 | 123.8866
5576 | 0 | 2.8137 | 1.8002 | 106.8814 | 12.3328 | 123.8282 | 0 | 0 | 119.2142
5577 | 0 | 2.8462 | 1.7611 | 131.5703 | 12.7964 | 148.9741 | 0 | 0 | 144.3667
5578 | 22.5807 | 2.6755 | 1.7681 | 110.9861 | 18.8691 | 156.8796 | 0 | 0 | 152.4359
5579 | 83.4979 | 3.0839 | 1.3773 | 110.795 | 13.4491 | 212.2031 | 0 | 0 | 207.7419
5580 | 62.0774 | 3.2951 | 2.3299 | 102.4854 | 11.8344 | 182.0222 | 0 | 0 | 176.3972
5581 | 16.3694 | 3.0189 | 2.3888 | 114.8852 | -3.2567 | 133.4056 | 0 | 0 | 127.9979
5582 | 0 | 2.2998 | 2.0295 | 108.3785 | 14.7679 | 127.4757 | 0 | 0 | 123.1464
5583 | 0 | 3.0086 | 1.9886 | 87.2089 | 11.1981 | 103.4042 | 0 | 0 | 98.407
5584 | 0 | 2.8868 | 2.2272 | 130.8111 | -0.12799 | 135.7971 | 0 | 0 | 130.6831
5585 | 0 | 2.7506 | 2.1199 | 85.5365 | 8.2082 | 98.6151 | 0 | 0 | 93.7446
5586 | 0 | 3.5561 | 1.5861 | 96.8599 | 11.4278 | 113.4299 | 0 | 0 | 108.2877
5587 | 0 | 3.1012 | 1.239 | 106.3618 | 32.4225 | 143.1246 | 0 | 0 | 138.7843
5588 | 0 | 2.5767 | 1.0185 | 102.8114 | 0 | 106.4067 | 0 | 0 | 102.8114
5589 | 0 | 2.4939 | 1.0722 | 108.5141 | 0 | 112.0802 | 0 | 0 | 108.5141
5590 | 0 | 2.9526 | 1.1947 | 111.8189 | 0 | 115.9662 | 0 | 0 | 111.8189
5591 | 0 | 3.0733 | 1.2542 | 129.8578 | 0 | 134.1854 | 0 | 0 | 129.8578
5592 | 0 | 2.9498 | 2.7569 | 113.4462 | 0 | 119.1529 | 0 | 0 | 113.4462
5593 | 0 | 2.9128 | 4.3028 | 110.7778 | 0 | 117.9935 | 0 | 0 | 110.7778
5594 | 0 | 3.2913 | 3.0702 | 136.626 | 0 | 142.9874 | 0 | 0 | 136.626
5595 | 0 | 2.7737 | 2.3713 | 113.1534 | 0 | 118.2985 | 0 | 0 | 113.1534
5596 | 0 | 3.2846 | 2.2727 | 121.5329 | 0 | 127.0903 | 0 | 0 | 121.5329
5597 | 0 | 2.9496 | 2.0277 | 95.502 | 0 | 100.4793 | 0 | 0 | 95.502
5598 | 0 | 2.8199 | 1.8545 | 100.0825 | 0 | 104.7569 | 0 | 0 | 100.0825
5599 | 9.1806 | 2.3238 | 1.8626 | 116.201 | 0 | 129.568 | 0 | 0 | 125.3816
5600 | 43.4284 | 3.2245 | 1.8002 | 138.6321 | 13.7592 | 200.8443 | 0 | 0 | 195.8197
5601 | 74.8874 | 3.0882 | 1.7611 | 90.3139 | 7.9862 | 178.0369 | 0 | 0 | 173.1875
5602 | 81.4498 | 2.8939 | 1.7681 | 141.9653 | 7.7625 | 235.8397 | 0 | 0 | 231.1776
5603 | 62.3076 | 3.2854 | 1.3773 | 110.0995 | 10.8813 | 187.9511 | 0 | 0 | 183.2884
5604 | 56.2915 | 2.711 | 2.3299 | 124.2255 | 15.6127 | 201.1707 | 0 | 0 | 196.1298
5605 | 22.3269 | 2.9298 | 2.3888 | 91.997 | 21.5966 | 141.2392 | 0 | 0 | 135.9206
5606 | 0.36786 | 2.6936 | 2.0295 | 144.8156 | 15.2462 | 165.1526 | 0 | 0 | 160.4296
5607 | 9.6696 | 2.5102 | 1.9886 | 110.4654 | 16.8469 | 141.4808 | 0 | 0 | 136.9819
5608 | 46.4847 | 3.2432 | 2.2272 | 104.0509 | 14.2536 | 170.2597 | 0 | 0 | 164.7892
5609 | 82.82 | 2.8698 | 2.1199 | 131.7822 | 14.823 | 234.415 | 0 | 0 | 229.4253
5610 | 67.5089 | 3.0794 | 1.5861 | 78.3882 | 5.6808 | 156.2434 | 0 | 0 | 151.5779
5611 | 58.8453 | 3.018 | 1.239 | 101.3853 | 18.3286 | 182.8162 | 0 | 0 | 178.5592
5612 | 8.9071 | 3.0092 | 1.0185 | 77.3163 | 0 | 90.2511 | 0 | 0 | 86.2234
5613 | 0 | 3.0711 | 1.0722 | 100.3353 | 0 | 104.4786 | 0 | 0 | 100.3353
5614 | 0 | 2.5701 | 1.1947 | 132.9506 | 0 | 136.7154 | 0 | 0 | 132.9506
5615 | 7.0639 | 2.666 | 1.2542 | 110.174 | 0 | 121.1581 | 0 | 0 | 117.2379
5616 | 41.7369 | 3.1597 | 2.7569 | 110.6289 | 0 | 158.2823 | 0 | 0 | 152.3658
5617 | 75.8829 | 3.1087 | 4.3028 | 108.252 | 0 | 191.5465 | 0 | 0 | 184.135
5618 | 85.8822 | 2.9926 | 3.0702 | 115.3412 | 0 | 207.2862 | 0 | 0 | 201.2234
5619 | 62.043 | 2.73 | 2.3713 | 108.6122 | 0 | 175.7564 | 0 | 0 | 170.6551
5620 | 0 | 2.6331 | 2.2727 | 124.5587 | 0 | 129.4646 | 0 | 0 | 124.5587
5621 | 0 | 3.3547 | 2.0277 | 111.4723 | 0 | 116.8547 | 0 | 0 | 111.4723
5622 | 0 | 2.2516 | 1.8545 | 104.2565 | 0 | 108.3626 | 0 | 0 | 104.2565
5623 | 0 | 2.7494 | 1.8626 | 82.4279 | 0 | 87.04 | 0 | 0 | 82.4279
5624 | 8.7657 | 2.8956 | 1.8002 | 124.0256 | 26.3399 | 163.827 | 0 | 0 | 159.1312
5625 | 51.956 | 2.9599 | 1.7611 | 107.1446 | 12.0794 | 175.901 | 0 | 0 | 171.18
5626 | 62.0173 | 2.8827 | 1.7681 | 112.8805 | 10.0154 | 189.564 | 0 | 0 | 184.9131
5627 | 46.6662 | 2.7897 | 1.3773 | 85.4595 | 20.1971 | 156.4898 | 0 | 0 | 152.3228
5628 | 0 | 2.8967 | 2.3299 | 101.3537 | 20.5646 | 127.1449 | 0 | 0 | 121.9183
5629 | 0 | 3.2546 | 2.3888 | 114.5686 | 7.8834 | 128.0954 | 0 | 0 | 122.452
5630 | 0 | 2.3487 | 2.0295 | 125.9876 | 4.5458 | 134.9116 | 0 | 0 | 130.5334
5631 | 0 | 2.5958 | 1.9886 | 113.6363 | 7.7443 | 125.9651 | 0 | 0 | 121.3806
5632 | 4.4003 | 2.6253 | 2.2272 | 109.6009 | 16.0175 | 134.8712 | 0 | 0 | 130.0187
5633 | 31.7504 | 3.4232 | 2.1199 | 118.0875 | 15.4851 | 170.866 | 0 | 0 | 165.3229
5634 | 69.8299 | 2.7276 | 1.5861 | 107.9514 | 9.2352 | 191.3303 | 0 | 0 | 187.0165
5635 | 48.82 | 2.5405 | 1.239 | 103.3677 | 18.5351 | 174.5023 | 0 | 0 | 170.7228
5636 | 0 | 3.118 | 1.0185 | 91.1627 | 0 | 95.2992 | 0 | 0 | 91.1627
5637 | 0 | 2.8836 | 1.0722 | 89.0725 | 0 | 93.0283 | 0 | 0 | 89.0725
5638 | 11.9687 | 3.0199 | 1.1947 | 117.6351 | 0 | 133.8185 | 0 | 0 | 129.6038
5639 | 58.6958 | 2.8559 | 1.2542 | 114.9421 | 0 | 177.7481 | 0 | 0 | 173.638
5640 | 77.1061 | 2.753 | 2.7569 | 130.48 | 0 | 213.096 | 0 | 200 | 407.5861
5641 | 37.3985 | 2.8395 | 4.3028 | 35.1309 | 0 | 79.6717 | 200 | 0 | 272.5294
5642 | 0 | 2.5671 | 3.0702 | 26.7862 | 0 | 32.4234 | 0 | 0 | 26.7862
5643 | 0 | 2.9292 | 2.3713 | 28.083 | 0 | 33.3835 | 0 | 0 | 28.083
5644 | 0 | 2.9746 | 2.2727 | 36.9304 | 0 | 42.1777 | 0 | 0 | 36.9304
5645 | 9.2729 | 2.7021 | 2.0277 | 29.2286 | 0 | 43.2313 | 0 | 0 | 38.5015
5646 | 45.2624 | 2.6233 | 1.8545 | 24.1623 | 0 | 73.9025 | 0 | 0 | 69.4247
5647 | 53.6628 | 3.0918 | 1.8626 | 24.1905 | 0 | 82.8078 | 0 | 0 | 77.8533
5648 | 60.4171 | 2.8007 | 1.8002 | 32.2008 | 10.4806 | 107.6995 | 0 | 0 | 103.0986
5649 | 50.5079 | 2.5302 | 1.7611 | 36.2617 | 8.4148 | 99.4756 | 0 | 0 | 95.1843
5650 | 69.0465 | 2.8966 | 1.7681 | 28.1036 | 7.4209 | 109.2358 | 0 | 0 | 104.571
5651 | 55.7392 | 2.7425 | 1.3773 | 26.2665 | 11.9233 | 98.0487 | 0 | 0 | 93.929
5652 | 48.8523 | 2.603 | 2.3299 | 33.5652 | 17.4894 | 104.8399 | 0 | 0 | 99.907
5653 | 26.8749 | 2.8723 | 2.3888 | 33.7753 | 14.6364 | 80.5477 | 0 | 0 | 75.2866
5654 | 0 | 3.265 | 2.0295 | 28.3191 | 28.3955 | 62.009 | 0 | 0 | 56.7146
5655 | 0 | 3.1041 | 1.9886 | 33.5748 | 30.02 | 68.6876 | 0 | 0 | 63.5949
5656 | 0 | 2.6414 | 2.2272 | 34.3763 | 16.329 | 55.5739 | 0 | 0 | 50.7053
5657 | 0 | 2.8485 | 2.1199 | 31.3277 | 13.3594 | 49.6555 | 0 | 0 | 44.6871
5658 | 0 | 2.2059 | 1.9531 | 20.0687 | 17.9017 | 42.1293 | 0 | 0 | 37.9704
5659 | 0 | 2.8724 | 1.5255 | 28.3254 | 20.852 | 53.5753 | 0 | 0 | 49.1774
5660 | 0 | 3.4346 | 1.1504 | 30.9011 | 0 | 35.4861 | 0 | 0 | 30.9011
5661 | 0 | 3.1753 | 1.1994 | 25.2941 | 0 | 29.6687 | 0 | 0 | 25.2941
5662 | 0 | 2.8031 | 1.0675 | 25.7738 | 0 | 29.6444 | 0 | 0 | 25.7738
5663 | 0 | 2.5687 | 1.3615 | 33.1687 | 0 | 37.0989 | 0 | 0 | 33.1687
5664 | 0 | 2.5189 | 1.7973 | 21.0229 | 0 | 25.3391 | 0 | 0 | 21.0229
5665 | 0 | 3.1305 | 2.1992 | 38.6784 | 0 | 44.0081 | 0 | 0 | 38.6784
5666 | 0 | 2.9243 | 1.9945 | 31.8176 | 0 | 36.7363 | 0 | 0 | 31.8176
5667 | 0 | 3.1658 | 3.6751 | 23.0724 | 0 | 29.9133 | 0 | 0 | 23.0724
5668 | 0 | 2.8853 | 3.2685 | 33.267 | 0 | 39.4208 | 0 | 0 | 33.267
5669 | 0 | 3.0501 | 2.6595 | 33.2362 | 0 | 38.9458 | 0 | 0 | 33.2362
5670 | 0 | 2.912 | 2.1561 | 29.5515 | 0 | 34.6196 | 0 | 0 | 29.5515
5671 | 0 | 3.0387 | 1.9466 | 29.6809 | 0 | 34.6663 | 0 | 0 | 29.6809
5672 | 0 | 3.0727 | 1.9857 | 25.4146 | 15.4871 | 45.9601 | 0 | 0 | 40.9017
5673 | 0 | 2.8839 | 1.7436 | 28.4729 | 22.1869 | 55.2873 | 0 | 0 | 50.6598
5674 | 0 | 3.1858 | 1.9834 | 32.3823 | 17.8705 | 55.422 | 0 | 0 | 50.2528
5675 | 0 | 2.8458 | 2.2739 | 28.2478 | 12.9501 | 46.3176 | 0 | 0 | 41.1979
5676 | 0 | 2.9015 | 2.4752 | 30.7117 | 17.8951 | 53.9835 | 0 | 0 | 48.6069
5677 | 0 | 2.7237 | 1.8702 | 38.0051 | 20.1608 | 62.7598 | 0 | 0 | 58.1659
5678 | 0 | 2.6425 | 2.2301 | 32.3348 | 16.8754 | 54.0828 | 0 | 0 | 49.2101
5679 | 0 | 2.9649 | 2.3118 | 27.0656 | 13.1469 | 45.4892 | 0 | 0 | 40.2125
5680 | 0 | 2.7538 | 1.9 | 29.7039 | 8.8755 | 43.2332 | 0 | 0 | 38.5794
5681 | 0 | 2.6275 | 1.9367 | 28.4728 | 12.6627 | 45.6997 | 0 | 0 | 41.1354
5682 | 0 | 2.6842 | 1.5167 | 20.9806 | 2.7879 | 27.9694 | 0 | 0 | 23.7685
5683 | 0 | 2.7152 | 1.4117 | 27.856 | 7.9429 | 39.9258 | 0 | 0 | 35.7989
5684 | 0 | 2.4787 | 1.1486 | 22.7759 | 0 | 26.4032 | 0 | 0 | 22.7759
5685 | 0 | 2.9663 | 1.2344 | 23.9717 | 0 | 28.1724 | 0 | 0 | 23.9717
5686 | 0 | 2.6918 | 1.7549 | 27.3339 | 0 | 31.7805 | 0 | 0 | 27.3339
5687 | 0 | 2.8921 | 1.8742 | 29.5632 | 0 | 34.3295 | 0 | 0 | 29.5632
5688 | 0 | 3.1387 | 2.7531 | 28.3918 | 0 | 34.2836 | 0 | 0 | 28.3918
5689 | 0 | 2.688 | 2.1636 | 31.8252 | 0 | 36.6768 | 0 | 0 | 31.8252
5690 | 0 | 2.4268 | 1.767 | 21.0581 | 0 | 25.2519 | 0 | 0 | 21.0581
5691 | 0 | 2.5624 | 2.6204 | 22.2769 | 0 | 27.4597 | 0 | 0 | 22.2769
5692 | 0 | 2.9427 | 2.6397 | 27.24 | 0 | 32.8223 | 0 | 0 | 27.24
5693 | 0 | 3.1906 | 2.3626 | 32.8566 | 0 | 38.4097 | 0 | 0 | 32.8566
5694 | 0 | 2.8613 | 1.8189 | 29.557 | 0 | 34.2372 | 0 | 0 | 29.557
5695 | 0 | 2.878 | 1.9431 | 32.0684 | 0 | 36.8895 | 0 | 0 | 32.0684
5696 | 0 | 2.7019 | 1.9321 | 23.074 | 20.1088 | 47.8168 | 0 | 0 | 43.1828
5697 | 0 | 3.263 | 1.7582 | 28.6472 | 10.7377 | 44.4062 | 0 | 0 | 39.3849
5698 | 0 | 2.508 | 1.4747 | 41.4313 | 13.0449 | 58.4589 | 0 | 0 | 54.4761
5699 | 0 | 2.5104 | 1.8335 | 23.1075 | 8.0036 | 35.455 | 0 | 0 | 31.1111
5700 | 0 | 3.1459 | 2.0907 | 34.3287 | 20.1082 | 59.6735 | 0 | 0 | 54.4369
5701 | 0 | 2.5598 | 2.2196 | 27.766 | 22.0831 | 54.6286 | 0 | 0 | 49.8491
5702 | 0 | 2.5462 | 2.2605 | 30.1093 | 13.2822 | 48.1981 | 0 | 0 | 43.3915
5703 | 0 | 2.9166 | 2.1706 | 28.5937 | 11.3934 | 45.0743 | 0 | 0 | 39.9871
5704 | 0 | 2.8748 | 2.1677 | 27.4411 | 16.2758 | 48.7594 | 0 | 0 | 43.7169
5705 | 0 | 2.7664 | 2.1706 | 25.7847 | 13.0122 | 43.7339 | 0 | 0 | 38.7969
5706 | 0 | 2.7176 | 1.5861 | 26.949 | 7.8609 | 39.1136 | 0 | 0 | 34.8099
5707 | 0 | 2.6084 | 1.239 | 31.3562 | 14.507 | 49.7107 | 0 | 0 | 45.8633
5708 | 0 | 2.8722 | 1.0185 | 25.5981 | 0 | 29.4888 | 0 | 0 | 25.5981
5709 | 0 | 2.9635 | 1.0722 | 31.6064 | 0 | 35.6421 | 0 | 0 | 31.6064
5710 | 0 | 2.5803 | 1.1947 | 30.4714 | 0 | 34.2464 | 0 | 0 | 30.4714
5711 | 0 | 2.6199 | 1.2542 | 27.6507 | 0 | 31.5248 | 0 | 0 | 27.6507
5712 | 0 | 2.5476 | 2.7569 | 29.4414 | 0 | 34.7459 | 200 | 0 | 229.4414
5713 | 0 | 2.6787 | 4.3028 | 31.124 | 0 | 38.1055 | 0 | 0 | 31.124
5714 | 3.5979 | 2.7786 | 3.0702 | 24.52 | 0 | 33.9666 | 0 | 0 | 28.1178
5715 | 34.6848 | 2.5833 | 2.3713 | 31.6076 | 0 | 71.2471 | 0 | 0 | 66.2924
5716 | 113.1211 | 3.0625 | 2.2727 | 33.2201 | 0 | 151.6764 | 0 | 0 | 146.3412
5717 | 104.4695 | 2.8638 | 2.0277 | 22.1014 | 0 | 131.4624 | 0 | 0 | 126.5709
5718 | 60.5797 | 3.0072 | 1.8545 | 27.5418 | 0 | 92.9832 | 0 | 0 | 88.1216
5719 | 67.9326 | 2.4518 | 1.8626 | 29.1531 | 0 | 101.4001 | 0 | 0 | 97.0856
5720 | 33.1076 | 2.8198 | 1.8002 | 28.6166 | 16.0948 | 82.4391 | 0 | 0 | 77.819
5721 | 45.0768 | 3.028 | 1.7611 | 25.8197 | 22.9649 | 98.6506 | 0 | 0 | 93.8614
5722 | 51.9069 | 2.9701 | 1.7681 | 36.2469 | 10.1827 | 103.0747 | 0 | 0 | 98.3364
5723 | 81.8245 | 3.0926 | 1.3773 | 36.1951 | 11.521 | 134.0105 | 0 | 0 | 129.5405
5724 | 73.0646 | 2.4287 | 2.3299 | 23.7063 | 11.6404 | 113.17 | 0 | 0 | 108.4114
5725 | 20.5063 | 2.9493 | 2.3888 | 24.3937 | 15.4352 | 65.6733 | 0 | 0 | 60.3352
5726 | 0 | 2.2698 | 2.0295 | 30.919 | 22.5338 | 57.7521 | 0 | 0 | 53.4528
5727 | 0 | 2.8079 | 1.9886 | 35.4073 | 6.7799 | 46.9837 | 0 | 0 | 42.1872
5728 | 0 | 2.3788 | 2.2272 | 21.9228 | 10.347 | 36.8758 | 0 | 0 | 32.2698
5729 | 0 | 3.2498 | 2.1199 | 25.9117 | 19.3632 | 50.6445 | 0 | 0 | 45.2748
5730 | 0 | 2.5557 | 1.5861 | 29.0875 | 7.5579 | 40.7873 | 0 | 0 | 36.6454
5731 | 0 | 3.0735 | 1.239 | 24.4883 | 19.3911 | 48.1919 | 0 | 0 | 43.8794
5732 | 2.3936 | 2.3739 | 1.0185 | 26.746 | 0 | 32.532 | 0 | 0 | 29.1396
5733 | 22.9108 | 2.9745 | 1.0722 | 24.341 | 0 | 51.2985 | 0 | 0 | 47.2518
5734 | 68.9612 | 2.834 | 1.1947 | 22.0578 | 0 | 95.0477 | 0 | 0 | 91.019
5735 | 46.077 | 2.8328 | 1.2542 | 28.6938 | 0 | 78.8578 | 0 | 0 | 74.7708
5736 | 19.9615 | 2.6652 | 2.7569 | 26.8442 | 0 | 52.2278 | 0 | 0 | 46.8058
5737 | 67.9904 | 2.7307 | 4.3028 | 27.7844 | 0 | 102.8083 | 0 | 0 | 95.7748
5738 | 46.5454 | 3.0115 | 3.0702 | 35.6904 | 0 | 88.3174 | 0 | 0 | 82.2358
5739 | 65.3833 | 2.4471 | 2.3713 | 34.0604 | 0 | 104.2621 | 0 | 200 | 299.4437
5740 | 22.6055 | 2.7065 | 2.2727 | 26.2588 | 0 | 53.8435 | 0 | 0 | 48.8643
5741 | 15.8023 | 2.8929 | 2.0277 | 26.2446 | 0 | 46.9675 | 0 | 0 | 42.0469
5742 | 65.2267 | 3.1167 | 1.8545 | 27.813 | 0 | 98.0109 | 0 | 0 | 93.0397
5743 | 78.9264 | 2.4637 | 1.8626 | 24.9362 | 0 | 108.1889 | 0 | 0 | 103.8626
5744 | 67.2547 | 3.0672 | 1.8002 | 20.5859 | 17.2207 | 109.9286 | 0 | 0 | 105.0613
5745 | 55.2481 | 3.0135 | 1.7611 | 29.5705 | 18.1751 | 107.7683 | 0 | 0 | 102.9937
5746 | 49.8935 | 2.7588 | 1.7681 | 28.5074 | 13.0835 | 96.0114 | 0 | 0 | 91.4844
5747 | 50.6248 | 2.21 | 1.3773 | 33.6255 | 15.6718 | 103.5093 | 0 | 0 | 99.922
5748 | 67.869 | 2.9515 | 2.3299 | 23.7269 | 20.5168 | 117.3941 | 0 | 0 | 112.1127
5749 | 47.4837 | 3.1404 | 2.3888 | 32.8736 | 9.0996 | 94.9861 | 0 | 0 | 89.4569
5750 | 40.9259 | 2.6922 | 2.0295 | 29.0746 | 11.3408 | 86.063 | 0 | 0 | 81.3413
5751 | 35.595 | 2.4227 | 1.9886 | 32.3492 | 14.2731 | 86.6287 | 0 | 0 | 82.2173
5752 | 0 | 3.1442 | 2.2272 | 25.7335 | 27.2345 | 58.3395 | 0 | 0 | 52.968
5753 | 0 | 2.9245 | 2.1199 | 29.3029 | 22.6297 | 56.9771 | 0 | 0 | 51.9326
5754 | 0 | 2.5901 | 1.5861 | 31.2576 | 10.848 | 46.2818 | 0 | 0 | 42.1056
5755 | 0 | 2.91 | 1.239 | 30.7572 | 12.8653 | 47.7715 | 0 | 0 | 43.6225
5756 | 3.6969 | 2.8125 | 1.0185 | 29.1534 | 0 | 36.6812 | 0 | 0 | 32.8503
5757 | 28.7774 | 2.9082 | 1.0722 | 24.4173 | 0 | 57.1751 | 0 | 0 | 53.1947
5758 | 44.584 | 3.2383 | 1.1947 | 31.212 | 0 | 80.2291 | 0 | 0 | 75.796
5759 | 21.9381 | 2.8794 | 1.2542 | 27.6826 | 0 | 53.7543 | 0 | 0 | 49.6206
5760 | 22.9233 | 3.3421 | 2.7569 | 29.0154 | 0 | 58.0377 | 0 | 0 | 51.9387
5761 | 34.9701 | 2.7414 | 4.3028 | 29.5941 | 0 | 71.6085 | 0 | 0 | 64.5643
5762 | 23.543 | 2.9116 | 3.0702 | 31.993 | 0 | 61.5178 | 0 | 0 | 55.536
5763 | 51.8417 | 3.2616 | 2.3713 | 29.7667 | 0 | 87.2414 | 0 | 0 | 81.6085
5764 | 61.0864 | 2.4357 | 2.2727 | 29.5623 | 0 | 95.3571 | 0 | 0 | 90.6486
5765 | 53.552 | 2.6122 | 2.0277 | 27.4157 | 0 | 85.6076 | 0 | 0 | 80.9677
5766 | 62.5262 | 3.0711 | 1.8545 | 29.9548 | 0 | 97.4067 | 0 | 0 | 92.4811
5767 | 51.7635 | 2.7033 | 1.8626 | 23.8967 | 0 | 80.2262 | 0 | 0 | 75.6602
5768 | 66.3838 | 2.7873 | 1.8002 | 28.7858 | 9.5387 | 109.2958 | 0 | 0 | 104.7083
5769 | 68.0472 | 2.9699 | 1.7611 | 26.6346 | 9.788 | 109.2009 | 0 | 0 | 104.4698
5770 | 72.6156 | 2.7558 | 1.7681 | 29.0095 | 26.8065 | 132.9555 | 0 | 0 | 128.4315
5771 | 64.5056 | 2.7987 | 1.3773 | 31.3739 | 26.3553 | 126.4108 | 0 | 0 | 122.2348
5772 | 55.082 | 2.9959 | 2.3299 | 39.1962 | 4.0963 | 103.7004 | 0 | 0 | 98.3746
5773 | 62.8942 | 2.5727 | 2.3888 | 27.8999 | 19.1706 | 114.9262 | 0 | 0 | 109.9647
5774 | 68.7776 | 2.4067 | 2.0295 | 29.9973 | 10.6839 | 113.895 | 0 | 0 | 109.4587
5775 | 67.0281 | 3.3156 | 1.9886 | 21.2021 | 11.0213 | 104.5558 | 0 | 0 | 99.2515
5776 | 68.2385 | 2.6287 | 2.2272 | 38.2274 | 18.0672 | 129.3891 | 0 | 0 | 124.5331
5777 | 54.6818 | 2.4515 | 2.1199 | 32.0694 | 6.4419 | 97.7645 | 0 | 0 | 93.1932
5778 | 12.282 | 2.2146 | 1.5861 | 35.2827 | 16.4346 | 67.8 | 0 | 0 | 63.9992
5779 | 6.8363 | 2.7185 | 1.239 | 30.2301 | 11.1316 | 52.1555 | 0 | 0 | 48.198
5780 | 32.6905 | 2.6981 | 1.0185 | 26.8608 | 0 | 63.2679 | 0 | 0 | 59.5513
5781 | 40.8219 | 2.75 | 1.0722 | 31.9479 | 0 | 76.5919 | 0 | 0 | 72.7697
5782 | 66.4284 | 2.8827 | 1.1947 | 29.6489 | 0 | 100.1547 | 0 | 0 | 96.0773
5783 | 49.1092 | 3.0093 | 1.2542 | 25.2773 | 0 | 78.65 | 200 | 0 | 274.3865
5784 | 9.3485 | 2.8083 | 2.7569 | 23.7478 | 0 | 38.6615 | 0 | 0 | 33.0963
5785 | 6.9063 | 2.7902 | 4.3028 | 28.413 | 0 | 42.4123 | 0 | 0 | 35.3193
5786 | 30.0756 | 2.7087 | 3.0702 | 29.0349 | 0 | 64.8893 | 0 | 0 | 59.1105
5787 | 41.2582 | 3.0843 | 2.3713 | 29.9689 | 0 | 76.6828 | 0 | 0 | 71.2272
5788 | 15.7985 | 3.0374 | 2.2727 | 21.9936 | 0 | 43.1022 | 0 | 0 | 37.7921
5789 | 56.5521 | 3.2389 | 2.0277 | 19.184 | 0 | 81.0027 | 0 | 0 | 75.7361
5790 | 72.7645 | 3.5118 | 1.8545 | 26.5534 | 0 | 104.6841 | 0 | 0 | 99.3179
5791 | 75.4621 | 2.9595 | 1.8626 | 17.367 | 0 | 97.6513 | 0 | 0 | 92.8291
5792 | 60.2543 | 3.5774 | 1.8002 | 29.9548 | 8.5117 | 104.0985 | 0 | 0 | 98.7208
5793 | 12.7403 | 2.7874 | 1.7611 | 32.5863 | 21.9632 | 71.8383 | 0 | 0 | 67.2898
5794 | 19.4313 | 3.1797 | 1.7681 | 31.3519 | 13.5088 | 69.2398 | 0 | 0 | 64.292
5795 | 37.6333 | 3.1477 | 1.3773 | 26.9692 | 21.6316 | 90.7591 | 0 | 0 | 86.2341
5796 | 0 | 2.6128 | 2.3299 | 28.0987 | 9.255 | 42.2965 | 0 | 0 | 37.3537
5797 | 0.015036 | 2.568 | 2.3888 | 22.9238 | 21.9671 | 49.8628 | 0 | 0 | 44.906
5798 | 3.094 | 2.7853 | 2.0295 | 32.6864 | 17.2954 | 57.8906 | 0 | 0 | 53.0758
5799 | 11.5833 | 2.814 | 1.9886 | 30.5507 | 7.0037 | 53.9403 | 0 | 0 | 49.1376
5800 | 0 | 2.5455 | 2.2272 | 26.1173 | 13.9891 | 44.8792 | 0 | 0 | 40.1064
5801 | 0 | 3.103 | 2.1199 | 25.4877 | 12.739 | 43.4496 | 0 | 0 | 38.2267
5802 | 0 | 2.863 | 1.5861 | 25.0003 | 6.0182 | 35.4676 | 0 | 0 | 31.0185
5803 | 0 | 3.0195 | 1.239 | 23.2254 | 15.5947 | 43.0786 | 0 | 0 | 38.8201
5804 | 0 | 2.9822 | 1.0185 | 33.7256 | 0 | 37.7263 | 0 | 0 | 33.7256
5805 | 0 | 3.0944 | 1.3753 | 29.0581 | 0 | 33.5277 | 0 | 0 | 29.0581
5806 | 0 | 3.345 | 1.9364 | 27.2414 | 0 | 32.5227 | 0 | 0 | 27.2414
5807 | 0 | 2.5684 | 3.1689 | 39.1998 | 0 | 44.9371 | 0 | 0 | 39.1998
5808 | 0 | 2.6996 | 4.5525 | 29.1381 | 0 | 36.3902 | 0 | 0 | 29.1381
5809 | 0 | 3.0826 | 5.7953 | 28.2341 | 0 | 37.112 | 0 | 0 | 28.2341
5810 | 0 | 2.5186 | 3.0702 | 27.9364 | 0 | 33.5252 | 0 | 0 | 27.9364
5811 | 0 | 2.5901 | 2.3713 | 26.0601 | 0 | 31.0215 | 0 | 0 | 26.0601
5812 | 4.6281 | 3.0279 | 2.2727 | 33.4787 | 0 | 43.4075 | 0 | 0 | 38.1069
5813 | 28.5445 | 2.5119 | 2.0277 | 34.2645 | 0 | 67.3486 | 0 | 0 | 62.809
5814 | 64.7773 | 2.9088 | 1.8545 | 34.6024 | 0 | 104.1429 | 0 | 0 | 99.3796
5815 | 56.5617 | 2.8605 | 1.8626 | 23.7517 | 0 | 85.0365 | 0 | 0 | 80.3134
5816 | 65.6271 | 3.1621 | 1.8002 | 31.2538 | 19.1994 | 121.0426 | 0 | 0 | 116.0804
5817 | 43.4381 | 2.9799 | 1.7611 | 29.2873 | 18.7552 | 96.2216 | 0 | 0 | 91.4806
5818 | 44.0746 | 2.7914 | 1.7681 | 28.9673 | 13.0341 | 90.6356 | 0 | 0 | 86.076
5819 | 0.073577 | 2.1763 | 1.3773 | 27.9977 | 20.4509 | 52.0758 | 0 | 0 | 48.5222
5820 | 0 | 2.8088 | 2.3299 | 20.2146 | 13.782 | 39.1353 | 0 | 0 | 33.9966
5821 | 0 | 2.901 | 2.3888 | 23.2216 | 14.9059 | 43.4173 | 0 | 0 | 38.1275
5822 | 0 | 2.8776 | 2.0295 | 31.8784 | 14.1187 | 50.9041 | 0 | 0 | 45.997
5823 | 0 | 2.4885 | 1.9886 | 30.1565 | 7.3638 | 41.9975 | 0 | 0 | 37.5203
5824 | 0 | 2.2745 | 2.2272 | 26.3378 | 13.1828 | 44.0223 | 0 | 0 | 39.5206
5825 | 0 | 3.0151 | 2.1199 | 30.6815 | 12.9248 | 48.7414 | 0 | 0 | 43.6064
5826 | 0 | 2.4834 | 1.9531 | 25.9591 | 8.3086 | 38.7041 | 0 | 0 | 34.2676
5827 | 0 | 2.7899 | 1.5255 | 24.6987 | 11.2282 | 40.2422 | 0 | 0 | 35.9268
5828 | 0 | 2.6386 | 1.1504 | 26.7169 | 0 | 30.5059 | 0 | 0 | 26.7169
5829 | 0 | 2.8976 | 1.2405 | 29.2197 | 0 | 33.3578 | 0 | 0 | 29.2197
5830 | 0 | 2.7347 | 2.2707 | 23.5334 | 0 | 28.5388 | 0 | 0 | 23.5334
5831 | 0 | 3.0592 | 2.572 | 32.2444 | 0 | 37.8756 | 0 | 0 | 32.2444
5832 | 0 | 3.3937 | 3.0058 | 27.2669 | 0 | 33.6664 | 0 | 0 | 27.2669
5833 | 0 | 3.5658 | 2.1992 | 35.6877 | 0 | 41.4527 | 0 | 0 | 35.6877
5834 | 0 | 2.9454 | 1.9945 | 37.3207 | 0 | 42.2606 | 0 | 0 | 37.3207
5835 | 0 | 3.0703 | 3.6751 | 33.2894 | 0 | 40.0348 | 0 | 200 | 233.2894
5836 | 0 | 3.1341 | 3.2685 | 23.7272 | 0 | 30.1298 | 0 | 0 | 23.7272
5837 | 0 | 3.6156 | 2.6595 | 31.1954 | 0 | 37.4705 | 0 | 0 | 31.1954
5838 | 0 | 3.4109 | 2.1561 | 34.4809 | 0 | 40.0478 | 0 | 0 | 34.4809
5839 | 0 | 2.9186 | 1.9466 | 35.5468 | 0 | 40.412 | 0 | 0 | 35.5468
5840 | 0 | 2.8719 | 1.9857 | 32.8659 | 21.0189 | 58.7425 | 0 | 0 | 53.8848
5841 | 0 | 3.7868 | 1.7436 | 22.9783 | 20.6724 | 49.1812 | 0 | 0 | 43.6508
5842 | 0 | 3.5317 | 1.9834 | 32.8031 | 14.5379 | 52.856 | 0 | 0 | 47.3409
5843 | 0 | 3.3504 | 2.2739 | 28.6294 | 15.9101 | 50.1638 | 0 | 0 | 44.5395
5844 | 0 | 2.703 | 2.4752 | 28.5421 | 13.8246 | 47.5448 | 0 | 0 | 42.3667
5845 | 0 | 3.3563 | 1.8702 | 28.2883 | 17.3443 | 50.8592 | 0 | 0 | 45.6326
5846 | 0 | 2.647 | 2.2301 | 33.2 | 12.2139 | 50.2911 | 0 | 0 | 45.414
5847 | 0 | 3.1378 | 2.3118 | 28.3053 | 9.1997 | 42.9546 | 0 | 0 | 37.505
5848 | 0 | 2.6396 | 1.9 | 37.2427 | 16.0507 | 57.8329 | 0 | 0 | 53.2934
5849 | 0 | 3.0125 | 1.9367 | 34.8032 | 14.1294 | 53.8819 | 0 | 0 | 48.9326
5850 | 0 | 3.1865 | 1.5167 | 35.9995 | 18.8378 | 59.5405 | 0 | 0 | 54.8373
5851 | 0 | 3.1216 | 1.4117 | 30.6854 | 17.6082 | 52.827 | 200 | 0 | 248.2936
5852 | 0 | 3.1059 | 1.1486 | 27.4699 | 0 | 31.7244 | 0 | 0 | 27.4699
5853 | 0 | 2.4768 | 1.2344 | 28.1355 | 0 | 31.8467 | 0 | 0 | 28.1355
5854 | 0 | 2.9925 | 1.1264 | 30.9459 | 0 | 35.0648 | 0 | 0 | 30.9459
5855 | 0 | 2.9108 | 1.1609 | 32.237 | 0 | 36.3086 | 0 | 0 | 32.237
5856 | 0 | 3.4015 | 1.1591 | 23.0765 | 0 | 27.6372 | 0 | 0 | 23.0765
5857 | 0 | 3.1423 | 2.1636 | 29.5448 | 0 | 34.8507 | 0 | 0 | 29.5448
5858 | 0 | 3.1862 | 1.767 | 32.7035 | 0 | 37.6566 | 0 | 0 | 32.7035
5859 | 0 | 3.0925 | 2.6204 | 36.4747 | 0 | 42.1876 | 0 | 0 | 36.4747
5860 | 0 | 2.9549 | 2.6397 | 28.0253 | 0 | 33.6199 | 0 | 0 | 28.0253
5861 | 0 | 3.1137 | 2.3626 | 29.4191 | 0 | 34.8953 | 0 | 0 | 29.4191
5862 | 0 | 2.7556 | 1.8189 | 23.5911 | 0 | 28.1656 | 0 | 0 | 23.5911
5863 | 0 | 2.8318 | 1.9431 | 33.2374 | 0 | 38.0123 | 0 | 0 | 33.2374
5864 | 0 | 3.1359 | 1.9321 | 34.7187 | 12.3247 | 52.1113 | 0 | 0 | 47.0433
5865 | 0 | 3.0909 | 1.7582 | 26.8469 | 11.5752 | 43.2712 | 0 | 0 | 38.4221
5866 | 0 | 2.5064 | 1.4747 | 40.4127 | 13.7729 | 58.1667 | 0 | 0 | 54.1857
5867 | 0 | 3.0284 | 1.8335 | 28.5625 | 10.3829 | 43.8073 | 0 | 0 | 38.9454
5868 | 0 | 3.0934 | 2.0907 | 27.8696 | 11.9351 | 44.9889 | 0 | 0 | 39.8047
5869 | 0 | 2.6573 | 2.2196 | 33.6719 | 7.3418 | 45.8906 | 0 | 0 | 41.0136
5870 | 0 | 3.0365 | 2.2605 | 35.8129 | 12.4033 | 53.5132 | 0 | 0 | 48.2162
5871 | 0 | 3.3504 | 2.1706 | 28.181 | 7.7019 | 41.4039 | 0 | 0 | 35.8829
5872 | 0 | 2.6356 | 2.1677 | 27.8973 | 4.9032 | 37.6039 | 0 | 0 | 32.8006
5873 | 0 | 3.0966 | 2.1706 | 29.4083 | 16.8138 | 51.4895 | 0 | 0 | 46.2222
5874 | 0 | 2.799 | 1.5861 | 30.499 | 21.4331 | 56.3173 | 0 | 0 | 51.9321
5875 | 0 | 3.276 | 1.239 | 30.0466 | 12.8714 | 47.4331 | 0 | 0 | 42.918
5876 | 0 | 3.1814 | 1.0185 | 23.9279 | 0 | 28.1279 | 0 | 0 | 23.9279
5877 | 0 | 3.947 | 1.0722 | 27.0376 | 0 | 32.0568 | 0 | 0 | 27.0376
5878 | 0 | 2.5866 | 1.1947 | 34.3735 | 0 | 38.1548 | 0 | 0 | 34.3735
5879 | 0 | 2.9698 | 1.2542 | 27.5506 | 0 | 31.7747 | 0 | 0 | 27.5506
5880 | 0 | 3.2235 | 2.7569 | 28.7229 | 0 | 34.7034 | 0 | 0 | 28.7229
5881 | 0 | 2.5891 | 4.3028 | 30.4055 | 0 | 37.2974 | 0 | 0 | 30.4055
5882 | 0 | 3.1429 | 3.0702 | 31.2793 | 0 | 37.4923 | 0 | 0 | 31.2793
5883 | 0 | 3.2055 | 2.3713 | 28.1927 | 0 | 33.7696 | 0 | 0 | 28.1927
5884 | 7.418 | 2.4427 | 2.2727 | 30.2152 | 0 | 42.3486 | 0 | 0 | 37.6331
5885 | 35.9419 | 3.2878 | 2.0277 | 27.3186 | 0 | 68.5759 | 0 | 0 | 63.2604
5886 | 68.8316 | 2.8644 | 1.8545 | 31.8174 | 0 | 105.3678 | 0 | 0 | 100.6489
5887 | 73.3776 | 3.011 | 1.8626 | 32.2516 | 0 | 110.5027 | 0 | 0 | 105.6292
5888 | 72.0394 | 3.2078 | 1.8002 | 38.9453 | 22.6018 | 138.5945 | 0 | 0 | 133.5865
5889 | 68.1168 | 3.5285 | 1.7611 | 35.2291 | 16.3113 | 124.9469 | 0 | 0 | 119.6572
5890 | 11.6756 | 3.2338 | 1.7681 | 30.2242 | 12.3002 | 59.2019 | 0 | 0 | 54.2
5891 | 13.6476 | 3.057 | 1.3773 | 31.1045 | 17.3055 | 66.492 | 0 | 0 | 62.0577
5892 | 28.43 | 3.0649 | 2.3299 | 27.3553 | 9.5451 | 70.7251 | 0 | 0 | 65.3304
5893 | 37.3071 | 3.0406 | 2.3888 | 34.4194 | 20.304 | 97.4601 | 0 | 0 | 92.0306
5894 | 0 | 2.8821 | 2.0295 | 34.0407 | 9.4879 | 48.4402 | 0 | 0 | 43.5286
5895 | 0 | 3.3214 | 1.9886 | 28.7732 | 24.0666 | 58.1499 | 0 | 0 | 52.8398
5896 | 0 | 3.1446 | 2.2272 | 19.7027 | 5.7734 | 30.848 | 0 | 0 | 25.4761
5897 | 0 | 3.093 | 2.1199 | 24.6042 | 14.3503 | 44.1674 | 0 | 0 | 38.9545
5898 | 0 | 2.5957 | 1.5861 | 27.1948 | 13.7315 | 45.1082 | 0 | 0 | 40.9264
5899 | 0 | 3.4761 | 1.239 | 25.3072 | 3.1699 | 33.1923 | 0 | 0 | 28.4771
5900 | 0 | 2.8008 | 1.0185 | 37.1704 | 0 | 40.9897 | 0 | 0 | 37.1704
5901 | 0 | 3.268 | 1.0722 | 29.4107 | 0 | 33.7509 | 0 | 0 | 29.4107
5902 | 0 | 3.4312 | 1.1947 | 26.295 | 0 | 30.921 | 0 | 0 | 26.295
5903 | 0 | 3.0381 | 1.2542 | 33.9137 | 0 | 38.206 | 0 | 0 | 33.9137
5904 | 0 | 2.8813 | 2.7569 | 21.8439 | 0 | 27.4821 | 0 | 0 | 21.8439
5905 | 0 | 3.2632 | 4.3028 | 32.2349 | 0 | 39.8009 | 0 | 0 | 32.2349
5906 | 0 | 2.8605 | 3.0702 | 35.0647 | 0 | 40.9953 | 0 | 0 | 35.0647
5907 | 0 | 3.2528 | 2.3713 | 32.8435 | 0 | 38.4677 | 0 | 0 | 32.8435
5908 | 0 | 2.8822 | 2.2727 | 41.5665 | 0 | 46.7215 | 0 | 0 | 41.5665
5909 | 2.4228 | 3.0251 | 2.0277 | 28.6105 | 0 | 36.0861 | 0 | 0 | 31.0333
5910 | 12.5205 | 3.4082 | 1.8545 | 30.6682 | 0 | 48.4514 | 0 | 0 | 43.1887
5911 | 20.8462 | 3.1649 | 1.8626 | 29.8608 | 0 | 55.7346 | 0 | 0 | 50.707
5912 | 0 | 2.7885 | 1.8002 | 28.4254 | 4.8946 | 37.9088 | 0 | 0 | 33.32
5913 | 0 | 3.1704 | 1.7611 | 27.3632 | 14.3245 | 46.6193 | 0 | 0 | 41.6878
5914 | 9.0853 | 3.2591 | 1.7681 | 31.2134 | 15.9715 | 61.2974 | 0 | 0 | 56.2701
5915 | 65.244 | 3.886 | 1.3773 | 29.0561 | 19.0048 | 118.5682 | 0 | 0 | 113.3049
5916 | 60.5835 | 3.5692 | 2.3299 | 32.6277 | 15.9651 | 115.0754 | 200 | 0 | 309.1763
5917 | 47.5674 | 2.8427 | 2.3888 | 34.1546 | 20.3575 | 107.311 | 0 | 0 | 102.0795
5918 | 6.4086 | 3.3042 | 2.0295 | 34.6366 | 11.485 | 57.8639 | 0 | 0 | 52.5302
5919 | 0 | 3.3574 | 1.9886 | 36.651 | -0.44069 | 41.5563 | 0 | 0 | 36.2103
5920 | 0 | 2.9497 | 2.2272 | 35.1409 | 15.6952 | 56.013 | 0 | 0 | 50.8361
5921 | 0 | 2.6052 | 2.1199 | 29.6004 | 13.9435 | 48.2691 | 0 | 0 | 43.5439
5922 | 0 | 2.8454 | 1.5861 | 26.6418 | 11.0233 | 42.0966 | 0 | 0 | 37.6651
5923 | 0 | 2.8692 | 1.239 | 29.5444 | 17.1729 | 50.8255 | 0 | 0 | 46.7173
5924 | 0 | 3.0583 | 1.0185 | 30.9866 | 0 | 35.0634 | 0 | 0 | 30.9866
5925 | 0 | 2.9268 | 1.0722 | 33.2608 | 0 | 37.2598 | 0 | 0 | 33.2608
5926 | 0 | 3.6046 | 1.1947 | 32.7342 | 0 | 37.5335 | 0 | 0 | 32.7342
5927 | 0 | 3.021 | 1.2542 | 22.8008 | 0 | 27.076 | 0 | 0 | 22.8008
5928 | 0 | 3.1637 | 2.7569 | 31.5561 | 0 | 37.4767 | 0 | 0 | 31.5561
5929 | 0 | 3.3863 | 4.3028 | 24.1971 | 0 | 31.8863 | 0 | 0 | 24.1971
5930 | 0 | 3.0736 | 3.0702 | 31.6068 | 0 | 37.7506 | 0 | 0 | 31.6068
5931 | 0 | 3.0077 | 2.3713 | 35.0568 | 0 | 40.4358 | 0 | 0 | 35.0568
5932 | 0 | 3.2025 | 2.2727 | 35.3842 | 0 | 40.8594 | 0 | 0 | 35.3842
5933 | 0.12717 | 2.7217 | 2.0277 | 27.8414 | 0 | 32.718 | 0 | 0 | 27.9686
5934 | 15.8153 | 2.527 | 1.8545 | 35.6468 | 0 | 55.8435 | 0 | 0 | 51.4621
5935 | 64.2586 | 2.7829 | 1.8626 | 31.8144 | 0 | 100.7186 | 0 | 0 | 96.0731
5936 | 50.7101 | 3.321 | 1.8002 | 29.2982 | 11.2121 | 96.3416 | 0 | 0 | 91.2204
5937 | 70.6985 | 3.6654 | 1.7611 | 26.8063 | 16.1088 | 119.0402 | 0 | 200 | 313.6136
5938 | 63.9811 | 3.0413 | 1.7681 | 29.538 | 16.2572 | 114.5856 | 0 | 0 | 109.7762
5939 | 71.1938 | 3.6356 | 1.3773 | 32.0202 | 18.47 | 126.6969 | 0 | 0 | 121.684
5940 | 32.5002 | 2.43 | 2.3299 | 24.8927 | 5.7557 | 67.9085 | 0 | 0 | 63.1486
5941 | 5.2351 | 3.4082 | 2.3888 | 32.3952 | 13.1129 | 56.5402 | 0 | 0 | 50.7432
5942 | 0 | 3.1188 | 2.0295 | 30.2138 | 10.8295 | 46.1916 | 0 | 0 | 41.0433
5943 | 0 | 3.05 | 1.9886 | 25.2869 | 20.0247 | 50.3502 | 0 | 0 | 45.3116
5944 | 0 | 3.1412 | 2.2272 | 28.3914 | 13.3885 | 47.1483 | 0 | 0 | 41.7798
5945 | 7.1297 | 3.7372 | 2.1199 | 27.6644 | 13.1315 | 53.7826 | 0 | 0 | 47.9255
5946 | 38.1523 | 3.4491 | 1.5861 | 28.2624 | 14.9062 | 86.3561 | 0 | 0 | 81.3208
5947 | 79.7486 | 3.3058 | 1.239 | 25.1584 | 9.0282 | 118.4801 | 0 | 0 | 113.9353
5948 | 65.6326 | 2.9293 | 1.0185 | 34.9854 | 0 | 104.5658 | 0 | 0 | 100.618
5949 | 41.9281 | 2.8119 | 1.0722 | 36.2526 | 0 | 82.0648 | 0 | 0 | 78.1807
5950 | 0 | 3.0805 | 1.1947 | 27.9641 | 0 | 32.2393 | 0 | 0 | 27.9641
5951 | 0 | 2.4177 | 1.2542 | 33.3732 | 0 | 37.0451 | 0 | 0 | 33.3732
5952 | 0 | 3.0344 | 2.7569 | 36.6569 | 0 | 42.4482 | 0 | 0 | 36.6569
5953 | 0 | 3.2995 | 4.3028 | 27.1019 | 0 | 34.7042 | 0 | 0 | 27.1019
5954 | 0 | 3.5169 | 3.0702 | 27.0179 | 0 | 33.605 | 0 | 0 | 27.0179
5955 | 0 | 2.4091 | 2.3713 | 33.8573 | 0 | 38.6377 | 0 | 0 | 33.8573
5956 | 0 | 3.4304 | 2.2727 | 29.2999 | 0 | 35.003 | 0 | 0 | 29.2999
5957 | 0.37939 | 2.5404 | 2.0277 | 36.6275 | 0 | 41.575 | 0 | 0 | 37.0069
5958 | 21.0949 | 3.0378 | 1.8545 | 31.7042 | 0 | 57.6914 | 0 | 0 | 52.7991
5959 | 60.6208 | 3.6405 | 1.8626 | 31.392 | 0 | 97.5159 | 0 | 0 | 92.0128
5960 | 60.2706 | 3.5544 | 1.8002 | 44.2338 | 10.1423 | 120.0014 | 0 | 0 | 114.6468
5961 | 48.3715 | 2.8572 | 1.7611 | 31.9111 | 13.9526 | 98.8536 | 0 | 0 | 94.2352
5962 | 55.7743 | 2.9185 | 1.7681 | 27.8126 | 4.8102 | 93.0837 | 0 | 0 | 88.3971
5963 | 65.8436 | 3.3297 | 1.3773 | 29.1369 | 9.7159 | 109.4033 | 0 | 0 | 104.6963
5964 | 78.199 | 3.222 | 2.3299 | 23.9437 | 24.8057 | 132.5002 | 0 | 0 | 126.9483
5965 | 38.3401 | 2.8885 | 2.3888 | 27.3916 | 16.0023 | 87.0112 | 0 | 0 | 81.734
5966 | 0 | 3.1478 | 2.0295 | 29.3989 | 18.3951 | 52.9713 | 0 | 0 | 47.794
5967 | 0 | 3.2107 | 1.9886 | 35.485 | 10.9988 | 51.6832 | 0 | 0 | 46.4839
5968 | 0 | 2.8135 | 2.2272 | 36.6117 | 25.5282 | 67.1806 | 0 | 0 | 62.1399
5969 | 0 | 2.5709 | 2.1199 | 29.6903 | 14.9526 | 49.3337 | 0 | 0 | 44.6428
5970 | 0 | 2.6622 | 1.5861 | 32.9084 | 13.5027 | 50.6594 | 0 | 0 | 46.4111
5971 | 2.3629 | 3.1013 | 1.239 | 28.1495 | 18.1778 | 53.0307 | 0 | 0 | 48.6903
5972 | 21.4696 | 3.1414 | 1.0185 | 30.3695 | 0 | 55.9991 | 0 | 0 | 51.8391
5973 | 48.3311 | 2.9574 | 1.0722 | 35.0544 | 0 | 87.4152 | 0 | 0 | 83.3856
5974 | 28.2034 | 3.329 | 1.1947 | 34.4626 | 0 | 67.1897 | 0 | 0 | 62.666
5975 | 14.8987 | 2.9569 | 1.2542 | 30.1264 | 0 | 49.2362 | 0 | 0 | 45.0251
5976 | 19.7786 | 2.929 | 2.7569 | 25.8925 | 0 | 51.3569 | 0 | 0 | 45.671
5977 | 66.9736 | 2.9845 | 4.3028 | 36.6582 | 0 | 110.9191 | 0 | 0 | 103.6318
5978 | 68.2128 | 3.1292 | 3.0702 | 32.4203 | 0 | 106.8325 | 0 | 0 | 100.6332
5979 | 55.375 | 3.1693 | 2.6003 | 27.9747 | 0 | 89.1193 | 0 | 0 | 83.3498
5980 | 10.7856 | 3.6725 | 2.2748 | 26.1122 | 0 | 42.8451 | 0 | 0 | 36.8978
5981 | 0 | 3.1696 | 2.0277 | 22.3547 | 0 | 27.552 | 200 | 0 | 222.3547
5982 | 0 | 2.5146 | 2.3223 | 18.1048 | 0 | 22.9417 | 0 | 0 | 18.1048
5983 | 0 | 2.911 | 1.8626 | 29.6176 | 0 | 34.3913 | 0 | 0 | 29.6176
5984 | 0 | 2.8219 | 1.8002 | 27.1167 | 6.859 | 38.5979 | 0 | 0 | 33.9757
5985 | 0 | 3.1135 | 1.7611 | 36.3603 | 10.3826 | 51.6176 | 0 | 0 | 46.743
5986 | 12.5014 | 3.1211 | 1.7681 | 33.8212 | 8.2321 | 59.4441 | 0 | 0 | 54.5548
5987 | 62.3261 | 3.1414 | 1.3773 | 33.2263 | 13.5732 | 113.6443 | 0 | 0 | 109.1256
5988 | 49.8809 | 3.0901 | 2.3299 | 34.2261 | 10.6313 | 100.1583 | 0 | 0 | 94.7383
5989 | 25.0463 | 2.2224 | 2.3888 | 25.8371 | 9.288 | 64.7828 | 0 | 0 | 60.1715
5990 | 0 | 3.0608 | 2.0295 | 30.6571 | 15.2954 | 51.0428 | 0 | 0 | 45.9525
5991 | 0 | 3.2676 | 1.9886 | 36.3052 | 0.96261 | 42.5241 | 0 | 0 | 37.2679
5992 | 0 | 2.8858 | 2.2272 | 30.3695 | 14.4384 | 49.9209 | 0 | 0 | 44.8079
5993 | 0 | 2.5224 | 2.1199 | 31.3555 | 26.0247 | 62.0225 | 0 | 0 | 57.3802
5994 | 0 | 3.27 | 1.9531 | 30.1332 | 13.3812 | 48.7373 | 0 | 0 | 43.5143
5995 | 0 | 3.1432 | 1.5255 | 27.634 | 8.0019 | 40.3046 | 0 | 0 | 35.6359
5996 | 0 | 2.453 | 1.1504 | 30.3391 | 0 | 33.9425 | 0 | 0 | 30.3391
5997 | 0 | 2.7307 | 1.1994 | 36.9735 | 0 | 40.9036 | 0 | 0 | 36.9735
5998 | 0 | 3.2566 | 1.0675 | 31.836 | 0 | 36.1601 | 0 | 0 | 31.836
5999 | 0 | 3.0373 | 1.3615 | 30.1338 | 0 | 34.5326 | 0 | 0 | 30.1338
6000 | 0 | 2.8793 | 1.7973 | 29.4535 | 0 | 34.1301 | 0 | 0 | 29.4535
6001 | 0 | 3.6395 | 2.1992 | 33.0276 | 0 | 38.8664 | 0 | 0 | 33.0276
6002 | 0 | 2.8399 | 1.9945 | 34.7718 | 0 | 39.6062 | 0 | 0 | 34.7718
6003 | 0 | 2.9263 | 3.6751 | 33.9844 | 0 | 40.5858 | 0 | 0 | 33.9844
6004 | 8.8773 | 3.3144 | 3.2685 | 32.6159 | 0 | 48.0762 | 0 | 0 | 41.4933
6005 | 41.5141 | 3.4912 | 2.6595 | 35.4302 | 0 | 83.095 | 0 | 0 | 76.9443
6006 | 51.6834 | 3.0586 | 2.1561 | 27.4066 | 0 | 84.3047 | 0 | 0 | 79.0901
6007 | 5.9884 | 3.6598 | 1.9466 | 20.6395 | 0 | 32.2343 | 0 | 0 | 26.6278
6008 | 0 | 3.4263 | 1.9857 | 31.6194 | 21.5489 | 58.5803 | 0 | 0 | 53.1683
6009 | 0 | 2.7929 | 1.7436 | 20.7181 | 21.6083 | 46.8629 | 0 | 0 | 42.3263
6010 | 0 | 3.4724 | 1.9834 | 30.621 | 11.0231 | 47.0999 | 0 | 0 | 41.6441
6011 | 0 | 2.4013 | 2.2739 | 27.0165 | 13.4889 | 45.1806 | 0 | 0 | 40.5054
6012 | 0 | 2.6865 | 2.4752 | 30.9186 | 13.0002 | 49.0804 | 0 | 0 | 43.9187
6013 | 0 | 3.2941 | 1.8702 | 31.2842 | 3.8767 | 40.3253 | 0 | 0 | 35.161
6014 | 0 | 2.8201 | 2.2301 | 23.1277 | 9.6999 | 37.8779 | 0 | 0 | 32.8276
6015 | 0 | 3.4063 | 2.3118 | 29.9663 | 13.0702 | 48.7546 | 0 | 0 | 43.0364
6016 | 0 | 2.6023 | 1.9 | 28.0917 | 16.9397 | 49.5338 | 0 | 0 | 45.0315
6017 | 0 | 3.3294 | 1.9367 | 30.8636 | 8.8835 | 45.0133 | 0 | 0 | 39.7472
6018 | 0 | 2.923 | 1.5167 | 36.2847 | 12.4167 | 53.1411 | 0 | 0 | 48.7014
6019 | 0 | 3.0743 | 1.4117 | 30.2004 | 10.4329 | 45.1193 | 0 | 0 | 40.6332
6020 | 0 | 3.0516 | 1.1486 | 25.4853 | 0 | 29.6855 | 0 | 0 | 25.4853
6021 | 0 | 3.073 | 1.2344 | 29.7855 | 0 | 34.093 | 0 | 0 | 29.7855
6022 | 0 | 2.4263 | 1.1264 | 28.2073 | 0 | 31.7601 | 0 | 0 | 28.2073
6023 | 0 | 2.9917 | 1.1609 | 28.3608 | 0 | 32.5134 | 0 | 0 | 28.3608
6024 | 0 | 2.7845 | 1.1591 | 22.2734 | 0 | 26.2169 | 0 | 0 | 22.2734
6025 | 0 | 3.0963 | 2.1636 | 24.4389 | 0 | 29.6989 | 0 | 0 | 24.4389
6026 | 0 | 3.1429 | 1.767 | 31.4192 | 0 | 36.3291 | 0 | 0 | 31.4192
6027 | 0 | 3.7269 | 2.6204 | 27.9679 | 0 | 34.3152 | 0 | 0 | 27.9679
6028 | 0 | 2.824 | 2.6397 | 25.9253 | 0 | 31.389 | 0 | 0 | 25.9253
6029 | 0 | 2.9649 | 2.3626 | 27.5069 | 0 | 32.8344 | 0 | 0 | 27.5069
6030 | 0 | 3.1661 | 1.8189 | 27.4751 | 0 | 32.4601 | 0 | 0 | 27.4751
6031 | 0 | 3.2789 | 1.9431 | 25.0736 | 0 | 30.2956 | 0 | 0 | 25.0736
6032 | 0 | 3.4068 | 1.9321 | 27.5137 | 15.5688 | 48.4213 | 0 | 0 | 43.0825
6033 | 0 | 3.7031 | 1.7582 | 31.9024 | 6.9294 | 44.2932 | 0 | 0 | 38.8319
6034 | 0 | 3.0873 | 1.4747 | 29.0449 | 19.1057 | 52.7127 | 0 | 0 | 48.1507
6035 | 0 | 3.1463 | 1.8335 | 27.4238 | 17.153 | 49.5565 | 0 | 0 | 44.5767
6036 | 0 | 3.1345 | 2.0907 | 31.1491 | 12.2019 | 48.5762 | 0 | 0 | 43.3509
6037 | 0 | 2.5282 | 2.2196 | 24.8944 | 15.4753 | 45.1176 | 0 | 0 | 40.3698
6038 | 0 | 3.4369 | 2.2605 | 26.9741 | 9.8311 | 42.5026 | 0 | 0 | 36.8052
6039 | 0 | 3.7528 | 2.1706 | 31.0808 | 16.7899 | 53.7941 | 0 | 200 | 247.8707
6040 | 0 | 2.8008 | 2.1677 | 32.4692 | 18.2757 | 55.7134 | 0 | 0 | 50.7449
6041 | 0 | 3.1578 | 2.1706 | 38.4603 | 12.0871 | 55.8759 | 0 | 0 | 50.5474
6042 | 0 | 2.5 | 1.5861 | 35.6717 | 5.8822 | 45.6401 | 0 | 0 | 41.5539
6043 | 0 | 3.3662 | 1.239 | 33.9836 | 13.3106 | 51.8994 | 0 | 0 | 47.2942
6044 | 0 | 3.1432 | 1.0185 | 33.8017 | 0 | 37.9634 | 0 | 0 | 33.8017
6045 | 0 | 2.681 | 1.0722 | 35.1031 | 0 | 38.8564 | 0 | 0 | 35.1031
6046 | 0 | 2.5887 | 1.1947 | 18.801 | 0 | 22.5845 | 0 | 0 | 18.801
6047 | 0 | 2.9946 | 1.2542 | 30.0904 | 0 | 34.3392 | 200 | 0 | 230.0904
6048 | 0 | 3.098 | 2.7569 | 40.3639 | 0 | 46.2189 | 0 | 0 | 40.3639
6049 | 0 | 3.1888 | 4.3028 | 27.0531 | 0 | 34.5447 | 0 | 0 | 27.0531
6050 | 0.18886 | 3.6905 | 3.0702 | 27.9991 | 0 | 34.9486 | 0 | 0 | 28.1879
6051 | 21.6115 | 2.9968 | 2.3713 | 35.638 | 0 | 62.6177 | 0 | 0 | 57.2495
6052 | 81.5475 | 2.8362 | 2.2727 | 26.3891 | 0 | 113.0455 | 0 | 0 | 107.9366
6053 | 74.3048 | 3.0738 | 2.0277 | 30.2783 | 0 | 109.6846 | 0 | 0 | 104.5831
6054 | 96.6529 | 3.1099 | 1.8545 | 28.7476 | 0 | 130.3649 | 0 | 0 | 125.4005
6055 | 73.4276 | 2.6609 | 1.8626 | 28.4706 | 0 | 106.4218 | 0 | 0 | 101.8982
6056 | 82.6397 | 3.0094 | 1.8002 | 32.1674 | 12.5572 | 132.174 | 0 | 0 | 127.3644
6057 | 80.3214 | 2.7817 | 1.7611 | 22.9224 | 23.0873 | 130.874 | 0 | 0 | 126.3312
6058 | 90.6194 | 3.089 | 1.7681 | 30.1815 | 5.0268 | 130.6849 | 0 | 0 | 125.8278
6059 | 67.0417 | 3.1314 | 1.3773 | 37.1396 | 23.3754 | 132.0653 | 0 | 0 | 127.5567
6060 | 72.9489 | 3.3752 | 2.3299 | 26.458 | 16.6709 | 121.783 | 0 | 0 | 116.0779
6061 | 83.1987 | 3.0271 | 2.3888 | 34.1806 | 12.0779 | 134.8732 | 0 | 0 | 129.4573
6062 | 74.6894 | 3.4053 | 2.0295 | 23.7937 | 18.2012 | 122.1192 | 0 | 0 | 116.6844
6063 | 54.4168 | 2.5792 | 1.9886 | 32.3947 | 15.1739 | 106.5532 | 0 | 0 | 101.9853
6064 | 56.7285 | 3.0342 | 2.2272 | 31.9305 | 8.0029 | 101.9233 | 0 | 0 | 96.6619
6065 | 17.1065 | 2.9291 | 2.1199 | 33.166 | 16.682 | 72.0035 | 0 | 0 | 66.9544
6066 | 0 | 3.5084 | 1.5861 | 33.8846 | 21.6207 | 60.5998 | 0 | 0 | 55.5053
6067 | 0 | 3.5189 | 1.239 | 19.8267 | 16.7578 | 41.3424 | 0 | 0 | 36.5845
6068 | 0 | 3.065 | 1.0185 | 26.0848 | 0 | 30.1683 | 0 | 0 | 26.0848
6069 | 0 | 2.7342 | 1.0722 | 39.6017 | 0 | 43.4081 | 0 | 0 | 39.6017
6070 | 0 | 3.0922 | 1.1947 | 32.5522 | 0 | 36.8392 | 0 | 0 | 32.5522
6071 | 0 | 2.9437 | 1.2542 | 38.093 | 0 | 42.2909 | 0 | 0 | 38.093
6072 | 0 | 3.2305 | 2.7569 | 28.4697 | 0 | 34.4571 | 0 | 0 | 28.4697
6073 | 0 | 2.5369 | 4.3028 | 27.7328 | 0 | 34.5725 | 0 | 0 | 27.7328
6074 | 0 | 2.7078 | 3.0702 | 25.3581 | 0 | 31.1361 | 0 | 0 | 25.3581
6075 | 0 | 2.9222 | 2.3713 | 31.2932 | 0 | 36.5867 | 0 | 0 | 31.2932
6076 | 0 | 2.9902 | 2.2727 | 37.851 | 0 | 43.1139 | 0 | 0 | 37.851
6077 | 12.7369 | 2.6614 | 2.0277 | 34.2936 | 0 | 51.7197 | 0 | 0 | 47.0305
6078 | 55.6457 | 3.3527 | 1.8545 | 25.0204 | 0 | 85.8733 | 0 | 0 | 80.6661
6079 | 83.3573 | 3.0808 | 1.8626 | 29.0774 | 0 | 117.378 | 0 | 0 | 112.4346
6080 | 75.9361 | 4.0531 | 1.8002 | 30.1514 | 19.9419 | 131.8828 | 0 | 0 | 126.0295
6081 | 68.3046 | 3.0472 | 1.7611 | 30.2104 | 6.4824 | 109.8057 | 0 | 0 | 104.9974
6082 | 79.3397 | 3.2549 | 1.7681 | 26.9149 | 12.4264 | 123.7041 | 0 | 0 | 118.681
6083 | 82.1422 | 3.1778 | 1.3773 | 32.9805 | 9.9399 | 129.6176 | 0 | 0 | 125.0626
6084 | 57.6655 | 3.3031 | 2.3299 | 30.0883 | 21.7688 | 115.1556 | 0 | 0 | 109.5226
6085 | 18.3265 | 3.0036 | 2.3888 | 31.1991 | 5.3253 | 60.2433 | 0 | 0 | 54.8509
6086 | 65.1638 | 3.2437 | 2.0295 | 23.2122 | 15.4544 | 109.1035 | 0 | 0 | 103.8303
6087 | 36.9915 | 2.7902 | 1.9886 | 30.6933 | 14.8493 | 87.3129 | 0 | 0 | 82.534
6088 | 0 | 2.7576 | 2.2272 | 24.636 | 9.914 | 39.5349 | 0 | 0 | 34.55
6089 | 0 | 3.2399 | 2.1199 | 28.4292 | 7.6905 | 41.4795 | 0 | 0 | 36.1198
6090 | 0 | 2.8606 | 1.5861 | 29.2969 | 9.5753 | 43.3189 | 0 | 0 | 38.8722
6091 | 0 | 3.3997 | 1.239 | 28.6936 | 25.9574 | 59.2897 | 0 | 0 | 54.651
6092 | 0 | 3.2063 | 1.0185 | 32.4209 | 0 | 36.6457 | 0 | 0 | 32.4209
6093 | 0 | 2.8061 | 1.0722 | 36.9022 | 0 | 40.7806 | 0 | 0 | 36.9022
6094 | 0 | 2.9233 | 1.1947 | 29.3108 | 0 | 33.4288 | 0 | 0 | 29.3108
6095 | 0 | 3.0235 | 1.2542 | 26.6976 | 0 | 30.9753 | 0 | 0 | 26.6976
6096 | 0 | 3.3314 | 2.7569 | 30.3122 | 0 | 36.4005 | 0 | 0 | 30.3122
6097 | 0 | 3.1679 | 4.3028 | 34.2312 | 0 | 41.702 | 0 | 0 | 34.2312
6098 | 0.1665 | 3.2067 | 3.0702 | 35.1835 | 0 | 41.6269 | 0 | 0 | 35.35
6099 | 16.2996 | 2.4334 | 2.7373 | 23.7382 | 0 | 45.2085 | 0 | 0 | 40.0378
6100 | 72.4245 | 2.7936 | 3.4629 | 33.3388 | 0 | 112.0197 | 0 | 0 | 105.7633
6101 | 83.5389 | 2.9982 | 2.593 | 31.9376 | 0 | 121.0677 | 0 | 0 | 115.4765
6102 | 70.5983 | 2.6033 | 2.0276 | 28.7062 | 0 | 103.9354 | 0 | 0 | 99.3045
6103 | 77.8061 | 2.7845 | 2.3568 | 27.1581 | 0 | 110.1056 | 0 | 0 | 104.9643
6104 | 70.9794 | 3.0417 | 2.2871 | 26.4536 | 20.3836 | 123.1454 | 0 | 0 | 117.8166
6105 | 85.8493 | 3.0433 | 1.7611 | 34.2371 | 11.0963 | 135.9872 | 0 | 0 | 131.1827
6106 | 65.3421 | 3.3832 | 1.7681 | 29.9809 | 17.7182 | 118.1924 | 0 | 0 | 113.0411
6107 | 44.3428 | 2.7254 | 1.3773 | 25.0119 | 19.6062 | 93.0636 | 0 | 0 | 88.9609
6108 | 57.1306 | 2.8034 | 2.3299 | 32.2735 | 14.0822 | 108.6196 | 0 | 0 | 103.4863
6109 | 49.7533 | 3.2626 | 2.3888 | 35.993 | 11.4014 | 102.7991 | 0 | 0 | 97.1477
6110 | 40.9411 | 3.5177 | 2.0295 | 34.1077 | 24.1475 | 104.7435 | 0 | 0 | 99.1964
6111 | 60.8852 | 3.1896 | 1.9886 | 30.2826 | 19.5579 | 115.9039 | 0 | 0 | 110.7257
6112 | 42.1482 | 3.1984 | 2.2272 | 30.516 | 24.7968 | 102.8867 | 200 | 0 | 297.461
6113 | 0 | 3.1505 | 2.1199 | 31.4674 | 23.2287 | 59.9664 | 0 | 0 | 54.696
6114 | 0 | 3.0466 | 1.5861 | 31.6695 | 11.9754 | 48.2776 | 0 | 0 | 43.6449
6115 | 0 | 3.4351 | 1.239 | 27.7733 | 4.842 | 37.2895 | 0 | 0 | 32.6153
6116 | 0 | 3.3058 | 1.0185 | 27.937 | 0 | 32.2614 | 0 | 0 | 27.937
6117 | 0 | 3.1789 | 1.0722 | 35.3408 | 0 | 39.5919 | 0 | 0 | 35.3408
6118 | 0 | 3.1319 | 1.6118 | 25.9154 | 0 | 30.6592 | 0 | 0 | 25.9154
6119 | 0 | 3.7903 | 2.927 | 22.8777 | 0 | 29.5951 | 0 | 0 | 22.8777
6120 | 0 | 3.1272 | 4.8568 | 30.5046 | 0 | 38.4887 | 0 | 0 | 30.5046
6121 | 0 | 3.1282 | 7.4514 | 25.1085 | 0 | 35.6881 | 0 | 0 | 25.1085
6122 | 0 | 2.929 | 3.9504 | 32.8404 | 0 | 39.7199 | 0 | 0 | 32.8404
6123 | 0.77063 | 3.4404 | 2.4632 | 32.3882 | 0 | 39.0624 | 0 | 0 | 33.1589
6124 | 21.8673 | 3.2465 | 2.2727 | 23.6397 | 0 | 51.0262 | 0 | 0 | 45.507
6125 | 89.0631 | 2.9792 | 2.0277 | 27.731 | 0 | 121.8011 | 0 | 0 | 116.7942
6126 | 67.764 | 3.4193 | 1.8545 | 29.4689 | 0 | 102.5067 | 0 | 0 | 97.2329
6127 | 70.3511 | 3.8017 | 1.8626 | 32.6596 | 0 | 108.675 | 0 | 0 | 103.0107
6128 | 61.1071 | 3.6027 | 1.8002 | 26.1296 | 7.704 | 100.3437 | 0 | 0 | 94.9408
6129 | 68.6763 | 2.529 | 1.7611 | 32.4021 | 19.4837 | 124.8522 | 0 | 0 | 120.5621
6130 | 70.2227 | 2.9177 | 1.7681 | 44.948 | 17.9071 | 137.7637 | 0 | 0 | 133.0778
6131 | 83.1659 | 3.4578 | 1.3773 | 30.4169 | 13.9116 | 132.3295 | 0 | 0 | 127.4944
6132 | 78.8372 | 3.2129 | 2.3299 | 34.4713 | 14.9535 | 133.8048 | 0 | 0 | 128.262
6133 | 84.5106 | 3.0667 | 2.3888 | 22.3443 | 10.9691 | 123.2795 | 0 | 0 | 117.824
6134 | 68.2306 | 3.1646 | 2.0295 | 29.7526 | 14.4724 | 117.6496 | 0 | 200 | 312.4555
6135 | 46.9866 | 3.1844 | 1.9886 | 37.8389 | 19.779 | 109.7776 | 0 | 0 | 104.6045
6136 | 0 | 3.2013 | 2.2272 | 31.0465 | 19.8742 | 56.3493 | 0 | 0 | 50.9207
6137 | 0 | 2.5288 | 2.1199 | 31.1063 | 7.4327 | 43.1877 | 0 | 0 | 38.539
6138 | 0 | 3.0339 | 2.1727 | 23.4268 | 13.4458 | 42.0793 | 0 | 0 | 36.8726
6139 | 0 | 2.9888 | 2.0995 | 25.6258 | 23.6088 | 54.3229 | 0 | 0 | 49.2346
6140 | 0 | 3.2481 | 2.4009 | 31.0698 | 0 | 36.7189 | 0 | 0 | 31.0698
6141 | 0 | 3.3454 | 3.3045 | 29.9334 | 0 | 36.5833 | 0 | 0 | 29.9334
6142 | 0 | 3.4384 | 3.7215 | 33.2091 | 0 | 40.369 | 0 | 0 | 33.2091
6143 | 0 | 3.3289 | 5.0231 | 26.9362 | 0 | 35.2882 | 0 | 0 | 26.9362
6144 | 0 | 2.8812 | 7.3929 | 30.2856 | 0 | 40.5598 | 0 | 0 | 30.2856
6145 | 0 | 2.8348 | 8.1333 | 23.1214 | 0 | 34.0895 | 0 | 0 | 23.1214
6146 | 0 | 2.9758 | 4.852 | 30.3581 | 0 | 38.1858 | 0 | 0 | 30.3581
6147 | 0 | 2.6116 | 2.943 | 30.484 | 0 | 36.0385 | 0 | 0 | 30.484
6148 | 0 | 3.2043 | 2.2727 | 34.4877 | 0 | 39.9647 | 0 | 0 | 34.4877
6149 | 0 | 2.6855 | 2.0277 | 27.4982 | 0 | 32.2114 | 0 | 0 | 27.4982
6150 | 15.9048 | 2.7639 | 1.8545 | 36.1495 | 0 | 56.6727 | 0 | 0 | 52.0543
6151 | 71.069 | 3.1748 | 1.8626 | 29.2714 | 0 | 105.3779 | 0 | 0 | 100.3404
6152 | 72.6479 | 2.5757 | 1.8002 | 25.7278 | 8.4258 | 111.1774 | 0 | 0 | 106.8015
6153 | 66.0604 | 3.3886 | 1.7611 | 31.2072 | 13.0286 | 115.446 | 0 | 0 | 110.2962
6154 | 40.6832 | 3.3417 | 1.7681 | 34.1079 | 15.7567 | 95.6576 | 0 | 0 | 90.5478
6155 | 7.951 | 2.9618 | 1.3773 | 31.1274 | 11.7083 | 55.1258 | 0 | 0 | 50.7867
6156 | 5.6369 | 3.2398 | 2.3299 | 31.365 | 11.9284 | 54.5001 | 0 | 0 | 48.9304
6157 | 5.5154 | 2.8836 | 2.3888 | 27.7765 | 13.2271 | 51.7915 | 0 | 0 | 46.519
6158 | 0 | 3.3732 | 2.0295 | 26.7365 | 16.1223 | 48.2614 | 0 | 0 | 42.8588
6159 | 0 | 4.0199 | 1.9886 | 25.2786 | 14.7558 | 46.043 | 0 | 0 | 40.0344
6160 | 0 | 3.3264 | 2.2272 | 36.5778 | 19.7647 | 61.8962 | 0 | 0 | 56.3426
6161 | 0 | 2.8395 | 2.1199 | 30.0097 | 9.6063 | 44.5753 | 0 | 0 | 39.616
6162 | 0 | 3.183 | 1.9531 | 25.4035 | 13.9 | 44.4396 | 0 | 0 | 39.3035
6163 | 0 | 2.9208 | 1.5255 | 34.066 | 14.9854 | 53.4977 | 0 | 0 | 49.0514
6164 | 0 | 3.1706 | 1.1504 | 40.3423 | 0 | 44.6633 | 0 | 0 | 40.3423
6165 | 0 | 3.0559 | 1.1994 | 23.6297 | 0 | 27.885 | 0 | 0 | 23.6297
6166 | 0 | 3.1158 | 1.0675 | 26.8717 | 0 | 31.055 | 0 | 0 | 26.8717
6167 | 0 | 3.0151 | 1.3615 | 35.7584 | 0 | 40.1351 | 0 | 0 | 35.7584
6168 | 0 | 3.0008 | 1.7973 | 29.9652 | 0 | 34.7633 | 0 | 0 | 29.9652
6169 | 0 | 2.961 | 2.1992 | 31.8259 | 0 | 36.9862 | 0 | 0 | 31.8259
6170 | 0 | 2.8134 | 1.9945 | 35.8531 | 0 | 40.6609 | 0 | 0 | 35.8531
6171 | 0 | 3.6156 | 3.6751 | 31.2971 | 0 | 38.5878 | 0 | 0 | 31.2971
6172 | 0 | 3.3876 | 3.2685 | 30.2419 | 0 | 36.8979 | 0 | 0 | 30.2419
6173 | 0 | 3.395 | 2.6595 | 25.0304 | 0 | 31.0849 | 0 | 0 | 25.0304
6174 | 0 | 3.3392 | 2.1561 | 28.2945 | 0 | 33.7898 | 0 | 0 | 28.2945
6175 | 0 | 3.0227 | 1.9466 | 31.4236 | 0 | 36.3929 | 0 | 0 | 31.4236
6176 | 0 | 2.9776 | 1.9857 | 31.5658 | 12.4743 | 49.0034 | 200 | 0 | 244.0401
6177 | 0 | 3.4352 | 1.7436 | 28.0176 | 3.0059 | 36.2024 | 0 | 0 | 31.0235
6178 | 0 | 3.1374 | 1.9834 | 30.6287 | 17.0254 | 52.7749 | 0 | 0 | 47.6541
6179 | 0 | 2.5385 | 2.2739 | 28.0899 | 11.2587 | 44.161 | 0 | 0 | 39.3486
6180 | 0 | 3.2804 | 2.4752 | 39.8527 | 14.9241 | 60.5323 | 0 | 0 | 54.7768
6181 | 0 | 3.0304 | 1.8702 | 29.0976 | 20.5203 | 54.5185 | 0 | 0 | 49.6179
6182 | 0 | 3.2796 | 2.2301 | 28.8789 | 15.1308 | 49.5194 | 0 | 0 | 44.0097
6183 | 0 | 3.3029 | 2.3118 | 27.4807 | 22.5398 | 55.6353 | 0 | 0 | 50.0206
6184 | 0 | 3.711 | 1.9 | 32.6218 | 16.5149 | 54.7477 | 0 | 0 | 49.1367
6185 | 0 | 2.8849 | 1.9367 | 34.1567 | 12.9339 | 51.9122 | 0 | 0 | 47.0906
6186 | 0 | 2.801 | 1.5167 | 38.3535 | 7.3448 | 50.016 | 0 | 0 | 45.6983
6187 | 0 | 3.0786 | 1.4117 | 32.1272 | 4.0357 | 40.6532 | 0 | 0 | 36.1629
6188 | 0 | 3.1461 | 1.1486 | 38.8882 | 0 | 43.1829 | 0 | 0 | 38.8882
6189 | 0 | 3.067 | 1.2344 | 32.1143 | 0 | 36.4157 | 0 | 0 | 32.1143
6190 | 0 | 2.8651 | 1.1264 | 27.5407 | 0 | 31.5323 | 0 | 0 | 27.5407
6191 | 0 | 2.7937 | 1.1609 | 32.0408 | 0 | 35.9954 | 0 | 0 | 32.0408
6192 | 0 | 3.3054 | 1.4398 | 28.4469 | 0 | 33.1921 | 0 | 0 | 28.4469
6193 | 0 | 3.3253 | 2.1636 | 26.3775 | 0 | 31.8665 | 0 | 0 | 26.3775
6194 | 0 | 2.9175 | 1.767 | 36.9797 | 0 | 41.6641 | 0 | 0 | 36.9797
6195 | 0 | 3.1572 | 2.6204 | 28.3755 | 0 | 34.1531 | 0 | 0 | 28.3755
6196 | 1.4388 | 2.574 | 2.6397 | 35.1185 | 0 | 41.771 | 0 | 0 | 36.5574
6197 | 24.9123 | 2.7087 | 2.3626 | 33.6392 | 0 | 63.6228 | 0 | 0 | 58.5515
6198 | 62.5661 | 2.7891 | 1.8189 | 25.2044 | 0 | 92.3785 | 0 | 0 | 87.7705
6199 | 5.817 | 2.863 | 1.9431 | 32.419 | 0 | 43.0422 | 0 | 0 | 38.236
6200 | 0 | 3.3168 | 1.9321 | 29.5041 | 21.5457 | 56.2986 | 0 | 0 | 51.0497
6201 | 0 | 3.3419 | 1.7582 | 34.0433 | 16.9476 | 56.0911 | 0 | 0 | 50.9909
6202 | 0 | 2.827 | 1.4747 | 33.5041 | -3.7886 | 34.0172 | 0 | 0 | 29.7155
6203 | 0 | 3.3521 | 1.8335 | 33.1034 | 9.2734 | 47.5624 | 0 | 0 | 42.3769
6204 | 0 | 2.9542 | 2.0907 | 28.4246 | 15.4643 | 48.9339 | 0 | 0 | 43.889
6205 | 0 | 2.9649 | 2.2196 | 21.7356 | 10.0879 | 37.008 | 0 | 0 | 31.8235
6206 | 0 | 2.6991 | 2.2605 | 25.1156 | 22.3055 | 52.3807 | 0 | 0 | 47.4211
6207 | 0 | 2.7765 | 2.1706 | 27.9075 | 17.5036 | 50.3582 | 0 | 0 | 45.4111
6208 | 0 | 3.1419 | 2.1677 | 28.5752 | 14.5216 | 48.4065 | 0 | 0 | 43.0969
6209 | 0 | 2.796 | 2.1706 | 31.368 | 17.7666 | 54.1012 | 0 | 0 | 49.1346
6210 | 0 | 2.8768 | 1.5861 | 24.9594 | 17.099 | 46.5213 | 0 | 0 | 42.0584
6211 | 0 | 3.8984 | 1.239 | 30.9233 | 5.049 | 41.1098 | 0 | 0 | 35.9723
6212 | 0 | 2.7314 | 1.0185 | 23.0732 | 0 | 26.8231 | 0 | 0 | 23.0732
6213 | 0 | 3.2162 | 1.0722 | 29.0544 | 0 | 33.3427 | 0 | 0 | 29.0544
6214 | 0 | 2.6626 | 1.1947 | 30.1647 | 0 | 34.022 | 0 | 0 | 30.1647
6215 | 0 | 2.966 | 1.2542 | 33.9269 | 0 | 38.1471 | 0 | 0 | 33.9269
6216 | 0 | 2.7844 | 2.7569 | 31.0714 | 0 | 36.6127 | 0 | 0 | 31.0714
6217 | 0 | 3.2198 | 4.3028 | 33.5038 | 0 | 41.0264 | 0 | 0 | 33.5038
6218 | 0 | 3.3828 | 3.0702 | 31.4954 | 0 | 37.9484 | 0 | 0 | 31.4954
6219 | 0 | 3.3569 | 2.3713 | 28.3746 | 0 | 34.1028 | 0 | 0 | 28.3746
6220 | 11.435 | 2.9795 | 2.2727 | 31.3749 | 0 | 48.0621 | 0 | 0 | 42.8099
6221 | 55.5134 | 2.8749 | 2.0277 | 30.4717 | 0 | 90.8877 | 0 | 0 | 85.9851
6222 | 81.0332 | 3.5562 | 1.8545 | 28.7898 | 0 | 115.2337 | 0 | 0 | 109.823
6223 | 69.441 | 2.8297 | 1.8626 | 42.2985 | 0 | 116.4318 | 0 | 0 | 111.7395
6224 | 68.0692 | 3.8473 | 1.8002 | 35.038 | 18.877 | 127.6317 | 0 | 200 | 321.9842
6225 | 48.1389 | 3.4126 | 1.7611 | 26.7832 | 23.3628 | 103.4586 | 0 | 0 | 98.2849
6226 | 13.9103 | 3.3304 | 1.7681 | 30.34 | 9.2951 | 58.6439 | 0 | 0 | 53.5454
6227 | 9.5892 | 3.2516 | 1.3773 | 37.9178 | 14.6128 | 66.7486 | 0 | 0 | 62.1197
6228 | 47.3321 | 2.7116 | 2.3299 | 33.5567 | 16.4071 | 102.3374 | 0 | 0 | 97.2959
6229 | 60.8874 | 3.4754 | 2.3888 | 30.7977 | 17.5978 | 115.1471 | 0 | 0 | 109.2829
6230 | 8.2835 | 3.2325 | 2.0295 | 22.2021 | 15.8339 | 51.5814 | 0 | 0 | 46.3194
6231 | 0 | 3.2255 | 1.9886 | 35.6195 | 17.231 | 58.0647 | 0 | 0 | 52.8506
6232 | 0 | 3.0458 | 2.2272 | 29.0987 | 28.4259 | 62.7976 | 0 | 0 | 57.5246
6233 | 0 | 2.653 | 2.1199 | 29.7377 | 5.8794 | 40.3901 | 0 | 0 | 35.6171
6234 | 0 | 3.1065 | 1.5861 | 30.7862 | 7.911 | 43.3899 | 0 | 0 | 38.6972
6235 | 0 | 2.8512 | 1.239 | 30.5398 | 9.7146 | 44.3447 | 0 | 0 | 40.2544
6236 | 0 | 3.0433 | 1.0185 | 27.6779 | 0 | 31.7397 | 0 | 0 | 27.6779
6237 | 0 | 2.6531 | 1.0722 | 24.6802 | 0 | 28.4056 | 0 | 0 | 24.6802
6238 | 0 | 3.4594 | 1.1947 | 30.3023 | 0 | 34.9564 | 0 | 0 | 30.3023
6239 | 0 | 2.8508 | 1.2542 | 26.5732 | 0 | 30.6782 | 0 | 0 | 26.5732
6240 | 0 | 3.5578 | 2.7569 | 26.8489 | 0 | 33.1636 | 200 | 0 | 226.8489
6241 | 0 | 3.6833 | 4.3028 | 32.6413 | 0 | 40.6273 | 0 | 0 | 32.6413
6242 | 0 | 2.7478 | 3.0702 | 23.6857 | 0 | 29.5037 | 0 | 0 | 23.6857
6243 | 0 | 3.2075 | 2.3713 | 37.8372 | 0 | 43.416 | 0 | 0 | 37.8372
6244 | 1.6515 | 2.8055 | 2.2727 | 31.0601 | 0 | 37.7898 | 0 | 0 | 32.7116
6245 | 17.9366 | 2.9222 | 2.0277 | 27.4918 | 0 | 50.3784 | 0 | 0 | 45.4285
6246 | 53.4477 | 2.9122 | 1.8545 | 31.3991 | 0 | 89.6135 | 0 | 0 | 84.8469
6247 | 54.252 | 3.3817 | 1.8626 | 29.2167 | 0 | 88.713 | 0 | 0 | 83.4687
6248 | 60.5731 | 3.3707 | 1.8002 | 35.2652 | 18.1044 | 119.1137 | 0 | 0 | 113.9427
6249 | 48.5908 | 2.6693 | 1.7611 | 24.48 | 17.4171 | 94.9183 | 0 | 0 | 90.4879
6250 | 0.64467 | 3.316 | 1.7681 | 31.0866 | 8.703 | 45.5185 | 0 | 0 | 40.4343
6251 | 8.2246 | 3.0007 | 1.3773 | 27.5422 | -0.34718 | 39.7975 | 0 | 0 | 35.4196
6252 | 47.8051 | 2.7269 | 2.3299 | 28.8696 | 13.8881 | 95.6196 | 0 | 0 | 90.5628
6253 | 73.2824 | 3.4528 | 2.3888 | 34.8562 | 0.88745 | 114.8676 | 0 | 0 | 109.0261
6254 | 39.2612 | 3.3912 | 2.0295 | 32.1796 | 13.8312 | 90.6926 | 0 | 0 | 85.272
6255 | 0 | 2.8983 | 1.9886 | 31.9355 | 12.565 | 49.3874 | 0 | 0 | 44.5005
6256 | 0 | 2.9079 | 2.2272 | 37.3942 | 3.9527 | 46.4821 | 0 | 0 | 41.3469
6257 | 0 | 3.096 | 2.1199 | 35.1514 | 17.9649 | 58.3321 | 0 | 0 | 53.1162
6258 | 0 | 3.3209 | 1.5861 | 28.608 | 9.6573 | 43.1723 | 0 | 0 | 38.2653
6259 | 0 | 2.852 | 1.239 | 29.0468 | 10.5306 | 43.6684 | 0 | 0 | 39.5774
6260 | 0 | 3.0843 | 1.0185 | 36.7949 | 0 | 40.8977 | 0 | 0 | 36.7949
6261 | 0 | 3.144 | 1.0722 | 36.8393 | 0 | 41.0555 | 0 | 0 | 36.8393
6262 | 0 | 3.6588 | 1.1947 | 31.119 | 0 | 35.9725 | 0 | 0 | 31.119
6263 | 0 | 3.5192 | 1.2542 | 32.1728 | 0 | 36.9462 | 0 | 0 | 32.1728
6264 | 0 | 3.0833 | 2.7569 | 27.5216 | 0 | 33.3619 | 0 | 0 | 27.5216
6265 | 0 | 2.6398 | 4.3028 | 32.2637 | 0 | 39.2064 | 0 | 0 | 32.2637
6266 | 0 | 3.6435 | 3.0702 | 29.1257 | 0 | 35.8394 | 0 | 0 | 29.1257
6267 | 0 | 3.2236 | 2.3713 | 25.0153 | 0 | 30.6103 | 0 | 0 | 25.0153
6268 | 1.421 | 2.5101 | 2.2727 | 28.4398 | 0 | 34.6436 | 0 | 0 | 29.8607
6269 | 21.4661 | 3.1137 | 2.0277 | 34.1648 | 0 | 60.7723 | 0 | 0 | 55.6309
6270 | 45.1861 | 3.6266 | 1.8545 | 35.9918 | 0 | 86.659 | 0 | 0 | 81.178
6271 | 8.3503 | 3.018 | 1.8626 | 34.0673 | 0 | 47.2983 | 0 | 0 | 42.4177
6272 | 24.7727 | 2.9298 | 1.8002 | 36.4319 | -1.0562 | 64.8785 | 0 | 0 | 60.1485
6273 | 8.0102 | 3.3858 | 1.7611 | 33.6249 | 11.9669 | 58.749 | 0 | 0 | 53.6021
6274 | 17.008 | 3.0646 | 1.7681 | 27.8708 | 17.0382 | 66.7497 | 0 | 0 | 61.917
6275 | 51.4736 | 3.275 | 1.3773 | 32.5259 | 16.2412 | 104.893 | 0 | 0 | 100.2407
6276 | 0 | 2.4364 | 2.3299 | 26.3166 | 13.2183 | 44.3011 | 0 | 0 | 39.5349
6277 | 0 | 3.3195 | 2.3888 | 32.7094 | 8.3648 | 46.7825 | 0 | 0 | 41.0742
6278 | 0 | 2.7934 | 2.0295 | 33.5288 | 20.1225 | 58.4742 | 0 | 0 | 53.6514
6279 | 0 | 3.3714 | 1.9886 | 24.8825 | 15.3052 | 45.5478 | 0 | 0 | 40.1877
6280 | 0 | 3.5209 | 2.2272 | 24.8426 | 19.3743 | 49.965 | 0 | 0 | 44.2169
6281 | 0 | 3.3163 | 2.1199 | 32.4661 | 10.7148 | 48.6171 | 0 | 0 | 43.1809
6282 | 0 | 3.3772 | 1.5861 | 27.215 | 13.5503 | 45.7286 | 0 | 0 | 40.7652
6283 | 0 | 3.4658 | 1.239 | 35.5865 | 15.2413 | 55.5326 | 0 | 0 | 50.8278
6284 | 0 | 3.0247 | 1.0185 | 27.7718 | 0 | 31.815 | 0 | 0 | 27.7718
6285 | 0 | 3.0115 | 1.0722 | 25.7311 | 0 | 29.8148 | 0 | 0 | 25.7311
6286 | 0 | 2.9639 | 1.1947 | 36.6198 | 0 | 40.7784 | 0 | 0 | 36.6198
6287 | 0 | 3.4806 | 1.2542 | 35.0089 | 0 | 39.7437 | 0 | 0 | 35.0089
6288 | 0 | 3.3048 | 2.7569 | 28.641 | 0 | 34.7027 | 0 | 0 | 28.641
6289 | 0 | 3.3038 | 4.3028 | 28.663 | 0 | 36.2696 | 0 | 0 | 28.663
6290 | 0 | 3.3274 | 3.0702 | 30.8788 | 0 | 37.2764 | 0 | 0 | 30.8788
6291 | 0 | 3.0095 | 2.3713 | 30.172 | 0 | 35.5528 | 0 | 0 | 30.172
6292 | 0 | 3.2351 | 2.2727 | 32.5526 | 0 | 38.0604 | 0 | 0 | 32.5526
6293 | 0 | 3.1905 | 2.0277 | 31.6815 | 0 | 36.8997 | 0 | 0 | 31.6815
6294 | 0 | 3.1647 | 1.8545 | 29.6904 | 0 | 34.7096 | 0 | 0 | 29.6904
6295 | 0 | 3.259 | 1.8626 | 27.6004 | 0 | 32.722 | 0 | 0 | 27.6004
6296 | 0 | 3.3246 | 1.8002 | 34.6157 | 17.9888 | 57.7293 | 0 | 0 | 52.6045
6297 | 0 | 3.5182 | 1.7611 | 35.8373 | 21.2893 | 62.4059 | 0 | 0 | 57.1266
6298 | 0 | 2.3715 | 1.7681 | 38.3359 | 3.92 | 46.3955 | 0 | 0 | 42.2559
6299 | 0 | 3.08 | 1.3773 | 32.5266 | 12.3271 | 49.311 | 0 | 0 | 44.8537
6300 | 0 | 2.9476 | 2.3299 | 31.436 | 14.7707 | 51.4842 | 0 | 0 | 46.2067
6301 | 9.3987 | 3.6074 | 2.3888 | 33.7292 | 15.4664 | 64.5906 | 0 | 0 | 58.5944
6302 | 44.4518 | 2.9341 | 2.0295 | 29.8648 | 19.759 | 99.0392 | 0 | 0 | 94.0756
6303 | 52.6034 | 3.4581 | 1.9886 | 33.1005 | 13.626 | 104.7767 | 0 | 0 | 99.3299
6304 | 0 | 2.8998 | 2.2272 | 35.973 | 7.4341 | 48.5341 | 200 | 0 | 243.407
6305 | 0 | 3.698 | 2.1199 | 24.8717 | 7.3766 | 38.0662 | 0 | 0 | 32.2483
6306 | 0 | 3.0256 | 1.5861 | 36.4406 | 21.0377 | 62.09 | 0 | 0 | 57.4783
6307 | 0 | 3.1823 | 1.239 | 31.0669 | 7.5295 | 43.0178 | 0 | 0 | 38.5964
6308 | 0 | 3.3335 | 1.0185 | 34.6348 | 0 | 38.9868 | 0 | 0 | 34.6348
6309 | 0 | 3.137 | 1.0722 | 31.1164 | 0 | 35.3256 | 0 | 0 | 31.1164
6310 | 0 | 3.2616 | 1.1947 | 33.3049 | 0 | 37.7613 | 0 | 0 | 33.3049
6311 | 0 | 3.0108 | 1.2542 | 27.3479 | 0 | 31.6128 | 0 | 0 | 27.3479
6312 | 0 | 2.8129 | 2.7569 | 33.3103 | 0 | 38.8802 | 0 | 0 | 33.3103
6313 | 0 | 2.8338 | 4.3028 | 29.4361 | 0 | 36.5727 | 0 | 0 | 29.4361
6314 | 0 | 3.2318 | 3.0702 | 32.2949 | 0 | 38.5969 | 0 | 0 | 32.2949
6315 | 0 | 3.0468 | 2.3713 | 34.5334 | 0 | 39.9515 | 0 | 0 | 34.5334
6316 | 7.9722 | 3.0183 | 2.2727 | 21.2071 | 0 | 34.4703 | 0 | 0 | 29.1793
6317 | 43.8247 | 2.9016 | 2.3753 | 31.4019 | 0 | 80.5036 | 0 | 0 | 75.2267
6318 | 63.2115 | 3.5569 | 1.8545 | 36.8634 | 0 | 105.4863 | 0 | 0 | 100.0749
6319 | 45.6195 | 3.2461 | 2.4254 | 26.1425 | 0 | 77.4335 | 0 | 0 | 71.762
6320 | 52.1247 | 2.6328 | 2.4229 | 35.075 | 11.3892 | 103.6445 | 0 | 0 | 98.5889
6321 | 38.8715 | 2.9507 | 1.7611 | 27.6653 | 29.0617 | 100.3104 | 0 | 0 | 95.5985
6322 | 30.1149 | 3.3143 | 1.7681 | 33.7097 | 14.0333 | 82.9403 | 0 | 0 | 77.8578
6323 | 16.6363 | 3.0493 | 1.3773 | 24.3381 | 14.5502 | 59.9513 | 0 | 0 | 55.5247
6324 | 47.1985 | 3.4171 | 2.3299 | 36.5869 | 9.4107 | 98.9431 | 0 | 200 | 293.1961
6325 | 0.91818 | 2.6667 | 2.3888 | 37.6616 | 10.0216 | 53.6569 | 0 | 0 | 48.6013
6326 | 0 | 3.5826 | 2.0295 | 31.36 | 18.092 | 55.0641 | 0 | 0 | 49.452
6327 | 0.59468 | 3.2555 | 1.9886 | 37.343 | 16.6645 | 59.8464 | 0 | 0 | 54.6022
6328 | 18.7973 | 3.577 | 2.2272 | 28.9526 | 6.2056 | 59.7597 | 0 | 0 | 53.9555
6329 | 55.5519 | 2.2208 | 2.1199 | 27.3944 | 14.5866 | 101.8735 | 0 | 0 | 97.5328
6330 | 2.2414 | 3.279 | 1.9531 | 24.5243 | 16.6409 | 48.6387 | 0 | 0 | 43.4066
6331 | 0 | 3.097 | 1.5255 | 29.3856 | 13.0477 | 47.0558 | 0 | 0 | 42.4333
6332 | 0 | 2.7376 | 1.1504 | 24.3108 | 0 | 28.1988 | 0 | 0 | 24.3108
6333 | 0 | 3.2703 | 1.1994 | 29.5062 | 0 | 33.9759 | 0 | 0 | 29.5062
6334 | 0 | 3.147 | 1.0675 | 28.1853 | 0 | 32.3998 | 0 | 0 | 28.1853
6335 | 0 | 2.6263 | 1.3615 | 31.2851 | 0 | 35.273 | 0 | 0 | 31.2851
6336 | 0 | 3.5405 | 1.7973 | 23.4303 | 0 | 28.7681 | 0 | 0 | 23.4303
6337 | 0 | 3.1552 | 2.1992 | 26.4315 | 0 | 31.7859 | 0 | 0 | 26.4315
6338 | 0 | 2.7616 | 1.9945 | 26.0217 | 0 | 30.7779 | 0 | 0 | 26.0217
6339 | 0 | 3.029 | 3.6751 | 26.3304 | 0 | 33.0345 | 0 | 0 | 26.3304
6340 | 4.0215 | 3.1474 | 3.4545 | 33.6064 | 0 | 44.2298 | 0 | 0 | 37.6278
6341 | 24.8663 | 3.3082 | 4.3117 | 30.5089 | 0 | 62.9952 | 0 | 0 | 55.3752
6342 | 59.3288 | 3.1728 | 4.6515 | 45.4648 | 0 | 112.6179 | 0 | 0 | 104.7936
6343 | 59.6362 | 3.2337 | 3.1808 | 34.8282 | 0 | 100.8788 | 0 | 0 | 94.4643
6344 | 66.1593 | 3.4578 | 2.4878 | 26.4905 | 14.9216 | 113.517 | 0 | 0 | 107.5715
6345 | 46.5945 | 2.4865 | 3.5207 | 30.8276 | 1.2322 | 84.6615 | 0 | 0 | 78.6543
6346 | 0 | 2.7686 | 1.9834 | 35.1737 | 8.9041 | 48.8298 | 0 | 0 | 44.0778
6347 | 2.4677 | 2.7176 | 2.2739 | 25.3715 | 14.1473 | 46.978 | 0 | 0 | 41.9865
6348 | 23.232 | 2.7218 | 2.4752 | 26.7945 | 18.9762 | 74.1996 | 0 | 0 | 69.0027
6349 | 60.8037 | 3.4061 | 1.8702 | 24.6511 | 12.854 | 103.5851 | 0 | 0 | 98.3088
6350 | 13.2656 | 3.0358 | 2.2301 | 36.5132 | 10.8758 | 65.9205 | 0 | 0 | 60.6545
6351 | 0 | 2.9682 | 2.3118 | 31.8708 | 14.4354 | 51.5863 | 0 | 0 | 46.3062
6352 | 0 | 3.0901 | 1.9 | 44.4016 | 14.2422 | 63.6339 | 0 | 0 | 58.6439
6353 | 0 | 3.0291 | 1.9367 | 25.4832 | 10.2458 | 40.6949 | 0 | 0 | 35.7291
6354 | 0 | 3.2303 | 1.5167 | 34.0063 | 10.5755 | 49.3288 | 0 | 0 | 44.5818
6355 | 0 | 3.5736 | 1.4117 | 33.507 | 5.346 | 43.8382 | 0 | 0 | 38.8529
6356 | 0 | 2.8501 | 1.1486 | 37.0449 | 0 | 41.0436 | 0 | 0 | 37.0449
6357 | 0 | 3.0515 | 1.2344 | 31.3802 | 0 | 35.6661 | 0 | 0 | 31.3802
6358 | 0 | 3.8363 | 1.1264 | 23.7302 | 0 | 28.693 | 0 | 0 | 23.7302
6359 | 0 | 2.7711 | 1.1609 | 25.7037 | 0 | 29.6356 | 0 | 0 | 25.7037
6360 | 0 | 3.5395 | 2.0964 | 35.9368 | 0 | 41.5728 | 0 | 0 | 35.9368
6361 | 0 | 3.4191 | 2.1636 | 23.4538 | 0 | 29.0365 | 0 | 0 | 23.4538
6362 | 0 | 2.6505 | 1.767 | 38.6866 | 0 | 43.1041 | 0 | 0 | 38.6866
6363 | 0 | 2.8025 | 2.6204 | 25.1021 | 0 | 30.525 | 0 | 0 | 25.1021
6364 | 0 | 2.8887 | 4.5195 | 37.7805 | 0 | 45.1886 | 0 | 0 | 37.7805
6365 | 0 | 2.7301 | 4.7946 | 30.9258 | 0 | 38.4505 | 0 | 0 | 30.9258
6366 | 0 | 3.0052 | 4.9797 | 33.2887 | 0 | 41.2735 | 0 | 0 | 33.2887
6367 | 0 | 2.8989 | 4.9405 | 31.758 | 0 | 39.5973 | 0 | 0 | 31.758
6368 | 0 | 3.2224 | 4.6816 | 32.8223 | 15.4894 | 56.2157 | 0 | 0 | 48.3117
6369 | 0 | 3.0625 | 4.6418 | 39.4077 | 15.5273 | 62.6393 | 200 | 0 | 254.935
6370 | 0 | 3.3811 | 4.2152 | 27.9662 | 15.359 | 50.9215 | 0 | 0 | 43.3252
6371 | 0 | 2.6686 | 3.6311 | 31.5789 | 17.5236 | 55.4023 | 0 | 0 | 49.1025
6372 | 0 | 3.2669 | 3.1742 | 32.5062 | 25.2969 | 64.2441 | 0 | 0 | 57.8031
6373 | 0 | 3.3977 | 2.2196 | 30.4577 | 7.3999 | 43.4749 | 0 | 0 | 37.8575
6374 | 0 | 3.2353 | 2.2605 | 30.0094 | 9.0941 | 44.5993 | 0 | 0 | 39.1035
6375 | 0 | 3.1444 | 2.3533 | 25.7101 | 9.3945 | 40.6024 | 0 | 0 | 35.1047
6376 | 0 | 3.3842 | 2.1677 | 23.1942 | 14.6917 | 43.438 | 0 | 0 | 37.886
6377 | 0 | 2.8269 | 2.1706 | 30.6913 | 21.0453 | 56.7342 | 0 | 0 | 51.7366
6378 | 0 | 2.8633 | 1.5861 | 32.0648 | 19.7018 | 56.2161 | 0 | 0 | 51.7666
6379 | 0 | 3.247 | 1.239 | 31.6057 | 14.81 | 50.9018 | 0 | 0 | 46.4157
6380 | 0 | 3.3124 | 1.0185 | 33.2741 | 0 | 37.605 | 0 | 0 | 33.2741
6381 | 0 | 3.2557 | 1.536 | 26.2245 | 0 | 31.0163 | 0 | 0 | 26.2245
6382 | 0 | 3.0817 | 2.9101 | 30.821 | 0 | 36.8128 | 0 | 0 | 30.821
6383 | 0 | 3.381 | 4.2976 | 22.033 | 0 | 29.7116 | 0 | 0 | 22.033
6384 | 0 | 2.781 | 5.2626 | 30.603 | 0 | 38.6466 | 0 | 0 | 30.603
6385 | 0 | 3.2834 | 7.5488 | 35.4725 | 0 | 46.3048 | 0 | 0 | 35.4725
6386 | 0 | 3.567 | 4.852 | 22.9642 | 0 | 31.3832 | 0 | 0 | 22.9642
6387 | 11.7914 | 3.483 | 4.588 | 25.2724 | 0 | 45.1348 | 0 | 0 | 37.0638
6388 | 67.2247 | 3.5451 | 4.1617 | 27.7327 | 0 | 102.6642 | 0 | 0 | 94.9574
6389 | 82.4342 | 2.9944 | 3.8993 | 34.0633 | 0 | 123.3911 | 0 | 0 | 116.4975
6390 | 79.0105 | 2.9843 | 3.6485 | 30.4036 | 0 | 116.0469 | 0 | 0 | 109.4141
6391 | 51.5468 | 3.2478 | 3.3164 | 29.8119 | 0 | 87.9229 | 0 | 0 | 81.3587
6392 | 66.0496 | 3.4277 | 3.3056 | 36.2069 | 13.2453 | 122.235 | 0 | 0 | 115.5017
6393 | 77.7101 | 3.0336 | 1.7611 | 34.0007 | 21.875 | 138.3806 | 0 | 0 | 133.5859
6394 | 36.3431 | 3.2657 | 2.1203 | 27.9131 | 10.5518 | 80.1939 | 0 | 0 | 74.8079
6395 | 21.0887 | 3.1068 | 1.3773 | 32.3036 | 19.1661 | 77.0425 | 0 | 0 | 72.5583
6396 | 63.1642 | 2.7837 | 2.3299 | 30.2094 | 22.4345 | 120.9218 | 0 | 0 | 115.8082
6397 | 45.4335 | 3.2323 | 2.3888 | 21.0913 | 4.0932 | 76.2391 | 0 | 0 | 70.618
6398 | 29.5096 | 2.9881 | 3.8894 | 31.4058 | 15.7634 | 83.5562 | 0 | 200 | 276.6787
6399 | 5.9001 | 3.1282 | 3.6625 | 33.2327 | 14.341 | 60.2645 | 0 | 0 | 53.4738
6400 | 0 | 3.3878 | 4.3177 | 22.2021 | 13.0621 | 42.9696 | 0 | 0 | 35.2642
6401 | 0 | 2.6599 | 4.1422 | 26.5541 | 17.249 | 50.6052 | 0 | 0 | 43.8031
6402 | 0 | 3.4423 | 3.8487 | 35.2056 | 10.4936 | 52.9901 | 0 | 0 | 45.6992
6403 | 15.47 | 2.9449 | 2.0995 | 27.0946 | 17.7575 | 65.3665 | 0 | 0 | 60.3221
6404 | 75.0054 | 2.9231 | 2.8857 | 37.2067 | 0 | 118.0209 | 0 | 0 | 112.2121
6405 | 59.5058 | 2.8208 | 3.7868 | 25.031 | 0 | 91.1444 | 0 | 0 | 84.5368
6406 | 34.5534 | 3.287 | 4.3707 | 26.2284 | 0 | 68.4394 | 0 | 0 | 60.7817
6407 | 0 | 3.486 | 5.265 | 30.8027 | 0 | 39.5537 | 0 | 0 | 30.8027
6408 | 0 | 3.32 | 8.103 | 24.7373 | 0 | 36.1603 | 0 | 0 | 24.7373
6409 | 0 | 3.2866 | 11.0559 | 31.0281 | 0 | 45.3706 | 0 | 0 | 31.0281
6410 | 14.7614 | 3.214 | 6.7371 | 33.2378 | 0 | 57.9503 | 0 | 0 | 47.9992
6411 | 53.0384 | 3.0469 | 4.8622 | 36.7789 | 0 | 97.7264 | 0 | 0 | 89.8174
6412 | 47.2536 | 2.6946 | 3.9521 | 27.924 | 0 | 81.8243 | 0 | 0 | 75.1776
6413 | 24.7087 | 2.5091 | 2.8833 | 34.1658 | 0 | 64.2669 | 0 | 0 | 58.8746
6414 | 70.2423 | 2.6913 | 3.5012 | 34.4387 | 0 | 110.8734 | 0 | 0 | 104.681
6415 | 86.2523 | 3.1552 | 2.4254 | 26.4209 | 0 | 118.2538 | 0 | 0 | 112.6732
6416 | 56.1179 | 3.1656 | 2.1513 | 28.0181 | 11.4117 | 100.8646 | 0 | 0 | 95.5477
6417 | 45.8834 | 2.8587 | 1.7611 | 32.5218 | 7.0273 | 90.0525 | 0 | 0 | 85.4326
6418 | 64.5044 | 3.0163 | 1.7681 | 30.6435 | 16.2674 | 116.1997 | 0 | 0 | 111.4153
6419 | 70.3521 | 3.1084 | 1.3773 | 31.9505 | 9.6019 | 116.3901 | 0 | 0 | 111.9044
6420 | 52.2987 | 2.5895 | 2.3299 | 29.5221 | 9.6754 | 96.4155 | 0 | 0 | 91.4961
6421 | 14.9968 | 2.9583 | 2.3888 | 27.4747 | 15.7053 | 63.5239 | 0 | 0 | 58.1767
6422 | 0 | 3.2757 | 3.9753 | 33.9597 | 16.1899 | 57.4006 | 0 | 0 | 50.1496
6423 | 0 | 2.9735 | 2.3371 | 33.5841 | 9.6115 | 48.5061 | 0 | 0 | 43.1955
6424 | 0 | 2.8866 | 2.2272 | 30.6769 | 20.2973 | 56.088 | 0 | 0 | 50.9742
6425 | 0 | 3.2362 | 2.1199 | 27.8622 | 6.9033 | 40.1217 | 0 | 0 | 34.7655
6426 | 2.3723 | 2.903 | 2.9614 | 32.3911 | 11.7054 | 52.3331 | 0 | 0 | 46.4688
6427 | 21.4228 | 2.8501 | 2.62 | 27.2257 | 15.2298 | 69.3485 | 0 | 0 | 63.8783
6428 | 73.6515 | 3.0521 | 1.189 | 23.3557 | 0 | 101.2483 | 0 | 0 | 97.0071
6429 | 61.1069 | 3.1794 | 2.9026 | 28.9692 | 0 | 96.1581 | 0 | 0 | 90.0761
6430 | 56.2385 | 3.0669 | 3.1535 | 32.2049 | 0 | 94.6639 | 0 | 0 | 88.4434
6431 | 17.6074 | 2.7798 | 3.6526 | 34.4313 | 0 | 58.4711 | 0 | 0 | 52.0386
6432 | 0 | 3.2109 | 4.3496 | 32.7935 | 0 | 40.354 | 0 | 0 | 32.7935
6433 | 0 | 3.0178 | 7.0617 | 27.0886 | 0 | 37.1681 | 200 | 0 | 227.0886
6434 | 0 | 2.7494 | 5.9995 | 23.1164 | 0 | 31.8653 | 0 | 0 | 23.1164
6435 | 11.9467 | 3.1355 | 5.2049 | 31.1767 | 0 | 51.4638 | 0 | 0 | 43.1234
6436 | 51.5653 | 2.9351 | 4.6509 | 29.7207 | 0 | 88.872 | 0 | 0 | 81.2859
6437 | 72.9817 | 3.6657 | 3.101 | 23.8365 | 0 | 103.5849 | 0 | 0 | 96.8182
6438 | 47.143 | 3.1303 | 1.8545 | 28.0899 | 0 | 80.2178 | 0 | 0 | 75.233
6439 | 52.6983 | 3.0911 | 1.8626 | 28.2641 | 0 | 85.9161 | 0 | 0 | 80.9624
6440 | 53.1569 | 2.9443 | 1.8002 | 25.6486 | 15.6941 | 99.2441 | 0 | 0 | 94.4996
6441 | 65.9556 | 3.6078 | 1.7611 | 32.529 | 20.7499 | 124.6034 | 0 | 0 | 119.2344
6442 | 65.1713 | 2.8069 | 1.7681 | 27.582 | 22.657 | 119.9853 | 0 | 0 | 115.4103
6443 | 58.5714 | 2.952 | 1.3773 | 27.133 | 9.1438 | 99.1775 | 0 | 0 | 94.8482
6444 | 35.0964 | 2.751 | 2.3299 | 34.6144 | 18.1904 | 92.982 | 0 | 0 | 87.9011
6445 | 0 | 3.1497 | 2.3888 | 27.2957 | 5.8904 | 38.7245 | 0 | 0 | 33.186
6446 | 0 | 2.6287 | 2.0295 | 29.2198 | 16.028 | 49.906 | 0 | 0 | 45.2478
6447 | 0 | 2.9056 | 1.9886 | 32.5158 | 20.8076 | 58.2176 | 0 | 0 | 53.3233
6448 | 0 | 3.1612 | 2.2272 | 25.9388 | 3.7296 | 35.0568 | 0 | 0 | 29.6684
6449 | 0 | 3.1658 | 2.1199 | 27.7994 | 24.7566 | 57.8417 | 0 | 0 | 52.556
6450 | 10.2971 | 2.8009 | 1.5861 | 27.7661 | 8.0332 | 50.4834 | 0 | 0 | 46.0963
6451 | 41.9317 | 3.1495 | 1.239 | 35.1739 | 31.0683 | 112.5624 | 0 | 0 | 108.1739
6452 | 62.3302 | 3.0698 | 1.0185 | 29.4417 | 0 | 95.8602 | 0 | 0 | 91.7719
6453 | 56.325 | 3.0507 | 1.0722 | 31.2082 | 0 | 91.656 | 0 | 0 | 87.5332
6454 | 53.3301 | 3.0299 | 1.1947 | 23.9309 | 0 | 81.4857 | 0 | 0 | 77.261
6455 | 40.4527 | 3.3691 | 1.2542 | 23.6713 | 0 | 68.7473 | 0 | 0 | 64.124
6456 | 69.616 | 3.2115 | 2.7569 | 32.1403 | 0 | 107.7247 | 0 | 0 | 101.7563
6457 | 69.2856 | 2.9252 | 4.3028 | 29.9509 | 0 | 106.4645 | 0 | 0 | 99.2365
6458 | 90.3035 | 2.9157 | 3.0702 | 30.3687 | 0 | 126.658 | 0 | 0 | 120.6722
6459 | 52.8635 | 2.9059 | 2.3713 | 28.656 | 0 | 86.7966 | 0 | 0 | 81.5194
6460 | 28.527 | 2.7657 | 2.2727 | 35.095 | 0 | 68.6604 | 0 | 0 | 63.622
6461 | 19.3348 | 3.7702 | 2.0277 | 29.1569 | 0 | 54.2896 | 0 | 0 | 48.4917
6462 | 59.5391 | 2.9219 | 1.8545 | 29.8645 | 0 | 94.18 | 0 | 0 | 89.4036
6463 | 53.0949 | 3.119 | 1.8626 | 25.8691 | 0 | 83.9456 | 0 | 0 | 78.964
6464 | 35.897 | 3.1859 | 1.8002 | 33.7845 | 12.9005 | 87.5681 | 0 | 200 | 282.582
6465 | 53.6443 | 3.4166 | 1.7611 | 28.5012 | 15.5129 | 102.8362 | 0 | 0 | 97.6585
6466 | 71.5674 | 2.4643 | 1.7681 | 33.7525 | 7.4172 | 116.9696 | 0 | 0 | 112.7371
6467 | 50.3288 | 2.6937 | 1.3773 | 29.4549 | 8.6698 | 92.5246 | 0 | 0 | 88.4536
6468 | 49.6284 | 2.6907 | 2.3299 | 28.7191 | 3.8423 | 87.2104 | 0 | 0 | 82.1898
6469 | 46.9757 | 3.0074 | 2.3888 | 28.2555 | 13.6357 | 94.2632 | 0 | 0 | 88.867
6470 | 23.9582 | 3.163 | 2.0295 | 36.4656 | 15.237 | 80.8532 | 0 | 0 | 75.6607
6471 | 0 | 3.3826 | 1.9886 | 35.3131 | 15.4853 | 56.1696 | 0 | 0 | 50.7984
6472 | 0 | 3.165 | 3.0632 | 29.0699 | 20.7786 | 56.0766 | 0 | 0 | 49.8485
6473 | 0 | 3.5715 | 2.1199 | 25.3928 | 15.0224 | 46.1065 | 0 | 0 | 40.4151
6474 | 13.0456 | 2.9399 | 1.5861 | 31.1066 | 12.1146 | 60.7929 | 0 | 0 | 56.2668
6475 | 55.2784 | 2.9721 | 1.239 | 38.9194 | 21.0032 | 119.4122 | 0 | 0 | 115.2011
6476 | 56.5557 | 2.7341 | 1.0185 | 26.553 | 0 | 86.8613 | 0 | 0 | 83.1086
6477 | 57.6085 | 2.9537 | 1.0722 | 26.7606 | 0 | 88.3949 | 0 | 0 | 84.3691
6478 | 48.5502 | 3.1917 | 1.1947 | 28.7315 | 0 | 81.6681 | 0 | 0 | 77.2816
6479 | 57.3922 | 2.9931 | 1.2542 | 32.1317 | 0 | 93.7711 | 0 | 0 | 89.5238
6480 | 53.1484 | 3.0004 | 2.7569 | 27.0158 | 0 | 85.9214 | 0 | 0 | 80.1641
6481 | 45.2361 | 2.9872 | 4.3028 | 27.0342 | 0 | 79.5603 | 0 | 0 | 72.2703
6482 | 49.135 | 2.4524 | 3.0702 | 31.3066 | 0 | 85.9641 | 0 | 0 | 80.4416
6483 | 53.2803 | 2.8351 | 3.0801 | 29.1815 | 0 | 88.377 | 0 | 0 | 82.4618
6484 | 34.7452 | 2.861 | 3.3231 | 31.0737 | 0 | 72.003 | 0 | 0 | 65.8189
6485 | 14.4518 | 2.9116 | 2.8107 | 27.1351 | 0 | 47.3093 | 0 | 0 | 41.5869
6486 | 45.2542 | 3.3367 | 2.3223 | 23.6679 | 0 | 74.5812 | 0 | 0 | 68.9221
6487 | 50.9078 | 3.1115 | 2.4254 | 35.8834 | 0 | 92.328 | 0 | 0 | 86.7912
6488 | 62.9455 | 3.8708 | 2.4908 | 22.0515 | 14.4818 | 105.8404 | 0 | 0 | 99.4788
6489 | 42.7281 | 2.7789 | 1.7611 | 28.8484 | 7.8527 | 83.9691 | 0 | 0 | 79.4291
6490 | 42.5446 | 3.1618 | 1.7681 | 23.642 | 11.6392 | 82.7558 | 0 | 0 | 77.8258
6491 | 38.6646 | 3.4557 | 1.3773 | 24.6696 | 8.017 | 76.1841 | 0 | 0 | 71.3511
6492 | 19.0357 | 2.668 | 2.3299 | 30.544 | 18.962 | 73.5396 | 0 | 0 | 68.5417
6493 | 28.5447 | 3.4559 | 2.3888 | 35.4203 | 19.0328 | 88.8426 | 0 | 0 | 82.9979
6494 | 0.81835 | 2.4667 | 2.0295 | 32.7484 | 14.3517 | 52.4146 | 0 | 0 | 47.9185
6495 | 0 | 3.0755 | 4.988 | 32.0045 | 6.6945 | 46.7625 | 0 | 0 | 38.699
6496 | 0 | 2.7617 | 5.9143 | 32.7313 | 7.1245 | 48.5318 | 0 | 0 | 39.8558
6497 | 18.8005 | 2.8375 | 5.4786 | 29.244 | 4.6204 | 60.981 | 0 | 0 | 52.6649
6498 | 62.2639 | 3.2848 | 3.7256 | 27.6293 | 26.6575 | 123.5611 | 0 | 0 | 116.5507
6499 | 74.8715 | 3.2389 | 4.0327 | 30.4622 | 17.3492 | 129.9545 | 200 | 0 | 322.6829
6500 | 49.0494 | 2.8899 | 4.4142 | 25.6942 | 0 | 82.0477 | 0 | 0 | 74.7436
6501 | 0 | 3.37 | 4.4022 | 26.5757 | 0 | 34.3479 | 0 | 0 | 26.5757
6502 | 0 | 3.4025 | 5.2914 | 35.9259 | 0 | 44.6199 | 0 | 0 | 35.9259
6503 | 0 | 3.0304 | 5.9344 | 25.0349 | 0 | 33.9997 | 0 | 0 | 25.0349
6504 | 0 | 2.9412 | 5.8661 | 24.8055 | 0 | 33.6128 | 0 | 0 | 24.8055
6505 | 0 | 3.3079 | 2.7323 | 35.7207 | 0 | 41.7609 | 0 | 0 | 35.7207
6506 | 0 | 3.2315 | 1.9945 | 25.4596 | 0 | 30.6856 | 0 | 0 | 25.4596
6507 | 0.09098 | 3.0887 | 3.6751 | 36.3018 | 0 | 43.1566 | 0 | 0 | 36.3928
6508 | 20.3735 | 3.3669 | 4.2712 | 22.6303 | 0 | 50.6419 | 0 | 0 | 43.0038
6509 | 72.208 | 2.641 | 4.1338 | 30.6537 | 0 | 109.6366 | 0 | 0 | 102.8618
6510 | 76.794 | 2.8405 | 3.1241 | 36.792 | 0 | 119.5506 | 0 | 0 | 113.586
6511 | 87.9625 | 3.0177 | 2.8224 | 23.9064 | 0 | 117.709 | 0 | 0 | 111.8689
6512 | 71.6733 | 3.1275 | 1.9857 | 31.0341 | 11.279 | 119.0996 | 0 | 0 | 113.9863
6513 | 69.584 | 3.0834 | 1.7436 | 35.2332 | 15.9971 | 125.6413 | 0 | 0 | 120.8143
6514 | 70.2419 | 3.479 | 1.9834 | 32.2012 | 21.7078 | 129.6134 | 0 | 0 | 124.151
6515 | 77.399 | 3.154 | 2.2739 | 32.8759 | 11.2685 | 126.9713 | 0 | 0 | 121.5434
6516 | 69.3142 | 3.0409 | 2.4752 | 35.4616 | 5.4809 | 115.7728 | 0 | 0 | 110.2567
6517 | 80.722 | 3.4218 | 1.8702 | 34.8694 | 15.2784 | 136.1618 | 0 | 0 | 130.8698
6518 | 86.1218 | 3.8357 | 2.2301 | 29.5228 | 8.2649 | 129.9754 | 0 | 0 | 123.9095
6519 | 71.2939 | 3.0872 | 3.0896 | 27.7288 | 11.0524 | 116.2519 | 0 | 0 | 110.075
6520 | 63.1298 | 3.2269 | 5.2399 | 27.5079 | 6.2266 | 105.331 | 0 | 0 | 96.8643
6521 | 79.1557 | 3.5034 | 5.0034 | 29.1666 | 13.4157 | 130.2448 | 0 | 0 | 121.738
6522 | 85.6478 | 2.9719 | 5.0346 | 27.0224 | 7.4862 | 128.1629 | 0 | 0 | 120.1564
6523 | 62.8975 | 3.0517 | 4.6681 | 29.5989 | 10.0908 | 110.3071 | 0 | 0 | 102.5872
6524 | 73.5445 | 3.0347 | 5.0344 | 26.1021 | 0 | 107.7157 | 0 | 0 | 99.6466
6525 | 91.4665 | 3.1466 | 5.2238 | 28.4934 | 0 | 128.3303 | 0 | 0 | 119.9599
6526 | 47.0333 | 2.7905 | 5.8319 | 22.7713 | 0 | 78.4271 | 0 | 0 | 69.8047
6527 | 1.9849 | 3.0673 | 6.7168 | 30.6196 | 0 | 42.3887 | 0 | 200 | 232.6046
6528 | 0 | 3.1134 | 6.9116 | 30.6583 | 0 | 40.6834 | 0 | 0 | 30.6583
6529 | 0 | 3.3581 | 4.4468 | 22.2006 | 0 | 30.0056 | 0 | 0 | 22.2006
6530 | 0 | 3.0327 | 3.5554 | 34.0768 | 0 | 40.665 | 0 | 0 | 34.0768
6531 | 0 | 3.5299 | 2.6204 | 30.5159 | 0 | 36.6663 | 0 | 0 | 30.5159
6532 | 0 | 2.916 | 3.8779 | 27.0941 | 0 | 33.888 | 0 | 0 | 27.0941
6533 | 15.1414 | 3.4405 | 3.1853 | 28.4791 | 0 | 50.2464 | 0 | 0 | 43.6206
6534 | 72.2783 | 2.9793 | 2.1434 | 41.0931 | 0 | 118.4941 | 0 | 0 | 113.3714
6535 | 58.4947 | 3.4322 | 1.9431 | 33.967 | 0 | 97.8371 | 0 | 0 | 92.4617
6536 | 74.8559 | 3.0711 | 1.9321 | 34.5622 | 14.2151 | 128.6364 | 0 | 0 | 123.6332
6537 | 67.6853 | 2.8522 | 1.7582 | 34.6708 | 11.504 | 118.4706 | 0 | 0 | 113.8602
6538 | 56.3713 | 3.3879 | 1.4747 | 28.8396 | 12.3584 | 102.4319 | 0 | 0 | 97.5693
6539 | 25.7509 | 2.4878 | 1.8335 | 30.9804 | 16.8855 | 77.9381 | 0 | 0 | 73.6168
6540 | 15.0264 | 3.3866 | 2.0907 | 33.9489 | 13.5932 | 68.0458 | 0 | 0 | 62.5685
6541 | 45.0196 | 3.3573 | 2.2196 | 29.7865 | 10.0402 | 90.4233 | 0 | 0 | 84.8463
6542 | 0.88184 | 3.2476 | 2.2605 | 27.3874 | 15.5311 | 49.3084 | 0 | 0 | 43.8003
6543 | 0 | 2.8331 | 2.1706 | 29.0354 | 11.2426 | 45.2818 | 0 | 0 | 40.278
6544 | 0 | 3.0885 | 2.1677 | 28.5899 | 12.6423 | 46.4885 | 0 | 0 | 41.2322
6545 | 0 | 3.3879 | 2.1706 | 32.7786 | 12.7534 | 51.0905 | 0 | 0 | 45.5319
6546 | 0 | 3.1964 | 1.5861 | 32.0814 | 18.6365 | 55.5004 | 0 | 0 | 50.718
6547 | 0 | 2.8823 | 1.239 | 26.3542 | 13.454 | 43.9295 | 0 | 0 | 39.8082
6548 | 0 | 3.2953 | 1.2698 | 32.0125 | 0 | 36.5776 | 0 | 0 | 32.0125
6549 | 0 | 2.8143 | 1.0722 | 25.6447 | 0 | 29.5312 | 0 | 0 | 25.6447
6550 | 0 | 3.0232 | 1.1947 | 34.5652 | 0 | 38.7832 | 0 | 0 | 34.5652
6551 | 0 | 3.014 | 2.524 | 31.0793 | 0 | 36.6173 | 0 | 0 | 31.0793
6552 | 0 | 2.7877 | 3.538 | 19.3349 | 0 | 25.6607 | 0 | 0 | 19.3349
6553 | 0 | 3.0122 | 6.5746 | 28.0176 | 0 | 37.6044 | 0 | 0 | 28.0176
6554 | 0 | 2.8556 | 4.934 | 31.1271 | 0 | 38.9167 | 0 | 0 | 31.1271
6555 | 1.1953 | 3.514 | 4.9993 | 34.8259 | 0 | 44.5345 | 0 | 0 | 36.0212
6556 | 21.1368 | 3.2953 | 4.9305 | 29.127 | 0 | 58.4895 | 0 | 0 | 50.2637
6557 | 68.5903 | 3.0384 | 5.3507 | 39.5252 | 0 | 116.5045 | 0 | 0 | 108.1155
6558 | 70.1812 | 3.328 | 3.9432 | 23.0871 | 0 | 100.5395 | 0 | 0 | 93.2683
6559 | 64.177 | 3.5521 | 4.5502 | 22.4044 | 0 | 94.6837 | 0 | 0 | 86.5814
6560 | 56.2479 | 3.2919 | 6.1575 | 23.5526 | 16.4101 | 105.6599 | 0 | 0 | 96.2105
6561 | 38.684 | 2.975 | 4.1038 | 31.8372 | 18.8895 | 96.4896 | 0 | 0 | 89.4108
6562 | 27.3933 | 3.3347 | 5.1311 | 28.8389 | 1.2049 | 65.9028 | 0 | 0 | 57.4371
6563 | 25.8827 | 2.9778 | 2.5543 | 25.36 | 5.9035 | 62.6783 | 200 | 0 | 257.1462
6564 | 26.3044 | 3.2654 | 2.3299 | 22.0036 | 5.3425 | 59.2458 | 0 | 0 | 53.6505
6565 | 59.2453 | 3.3426 | 3.8673 | 25.7933 | 24.1713 | 116.4197 | 0 | 0 | 109.2098
6566 | 59.1157 | 3.9751 | 4.2329 | 36.091 | 5.9778 | 109.3925 | 0 | 0 | 101.1846
6567 | 42.0155 | 3.0507 | 4.8934 | 29.5684 | 5.5481 | 85.0761 | 0 | 0 | 77.132
6568 | 16.4362 | 3.6235 | 2.9491 | 35.348 | 6.9114 | 65.2682 | 0 | 0 | 58.6955
6569 | 0 | 2.8612 | 4.0309 | 36.0716 | 24.8558 | 67.8195 | 0 | 0 | 60.9274
6570 | 0 | 2.8887 | 1.7784 | 28.2489 | 18.7106 | 51.6266 | 0 | 0 | 46.9596
6571 | 0 | 3.0605 | 2.4465 | 29.7898 | 4.2721 | 39.5689 | 0 | 0 | 34.0619
6572 | 0 | 3.1819 | 1.8354 | 27.6825 | 0 | 32.6998 | 0 | 0 | 27.6825
6573 | 0 | 3.435 | 1.536 | 29.9527 | 0 | 34.9238 | 0 | 0 | 29.9527
6574 | 0 | 3.3876 | 1.6929 | 23.0972 | 0 | 28.1777 | 0 | 0 | 23.0972
6575 | 0 | 3.3359 | 2.2015 | 28.9359 | 0 | 34.4733 | 0 | 0 | 28.9359
6576 | 0 | 3.6688 | 3.2337 | 31.3289 | 0 | 38.2314 | 0 | 0 | 31.3289
6577 | 0 | 3.2893 | 6.2824 | 30.4567 | 0 | 40.0284 | 0 | 0 | 30.4567
6578 | 0 | 3.3472 | 5.9995 | 21.3122 | 0 | 30.6589 | 0 | 0 | 21.3122
6579 | 0 | 3.102 | 6.2331 | 27.6926 | 0 | 37.0277 | 0 | 0 | 27.6926
6580 | 0 | 3.0746 | 6.2583 | 24.7581 | 0 | 34.0911 | 0 | 0 | 24.7581
6581 | 14.281 | 3.259 | 5.4958 | 26.8626 | 0 | 49.8984 | 0 | 0 | 41.1436
6582 | 58.2348 | 3.5633 | 4.68 | 30.7339 | 0 | 97.212 | 0 | 0 | 88.9687
6583 | 81.2869 | 3.0621 | 3.4535 | 24.7908 | 0 | 112.5934 | 0 | 0 | 106.0777
6584 | 60.5083 | 2.6154 | 2.6945 | 22.3485 | 2.9244 | 91.0911 | 0 | 0 | 85.7812
6585 | 47.1663 | 4.2378 | 1.7611 | 25.3487 | 14.172 | 92.6859 | 0 | 0 | 86.687
6586 | 47.1043 | 3.6347 | 1.7681 | 30.1501 | 0.49162 | 83.1488 | 0 | 0 | 77.746
6587 | 20.6047 | 3.1525 | 1.3773 | 23.553 | 17.098 | 65.7855 | 0 | 0 | 61.2557
6588 | 5.5648 | 3.3463 | 2.3299 | 27.3779 | 14.9654 | 53.5843 | 0 | 0 | 47.9081
6589 | 22.5037 | 3.1044 | 2.3888 | 33.5567 | 8.5849 | 70.1384 | 0 | 200 | 264.6452
6590 | 12.4198 | 3.5345 | 2.0295 | 30.9009 | 12.8359 | 61.7205 | 0 | 0 | 56.1565
6591 | 0 | 3.8994 | 1.9886 | 25.8363 | 6.1023 | 37.8266 | 0 | 0 | 31.9385
6592 | 0 | 3.106 | 2.2272 | 31.4419 | 16.2923 | 53.0674 | 0 | 0 | 47.7342
6593 | 0 | 3.2593 | 2.1199 | 30.9614 | 7.9226 | 44.2631 | 0 | 0 | 38.8839
6594 | 0 | 4.0855 | 1.5861 | 29.1267 | 8.4979 | 43.2962 | 0 | 0 | 37.6246
6595 | 0 | 2.9815 | 1.239 | 24.7874 | 16.152 | 45.1599 | 0 | 0 | 40.9393
6596 | 0 | 2.9924 | 1.0185 | 25.3038 | 0 | 29.3147 | 0 | 0 | 25.3038
6597 | 0 | 3.2304 | 1.0722 | 29.722 | 0 | 34.0246 | 0 | 0 | 29.722
6598 | 0 | 3.0654 | 1.1947 | 29.0632 | 0 | 33.3233 | 0 | 0 | 29.0632
6599 | 0 | 2.6878 | 1.2542 | 26.4501 | 0 | 30.3922 | 0 | 0 | 26.4501
6600 | 0 | 3.0478 | 2.7569 | 27.53 | 0 | 33.3348 | 0 | 0 | 27.53
6601 | 0 | 3.7775 | 4.8211 | 28.6478 | 0 | 37.2463 | 0 | 0 | 28.6478
6602 | 0.026646 | 2.9207 | 4.4422 | 24.7779 | 0 | 32.1675 | 0 | 0 | 24.8045
6603 | 13.9289 | 3.0158 | 3.697 | 21.172 | 0 | 41.8137 | 0 | 0 | 35.1009
6604 | 71.7031 | 3.2757 | 3.5328 | 30.6534 | 0 | 109.165 | 0 | 0 | 102.3566
6605 | 53.8961 | 3.6981 | 3.0285 | 28.8955 | 0 | 89.5182 | 0 | 0 | 82.7916
6606 | 55.5739 | 3.0585 | 2.5434 | 27.0894 | 0 | 88.2651 | 0 | 0 | 82.6633
6607 | 46.0403 | 3.4772 | 2.9052 | 34.2125 | 0 | 86.6352 | 0 | 0 | 80.2528
6608 | 54.8367 | 3.3882 | 2.355 | 34.9061 | 20.1845 | 115.6705 | 0 | 0 | 109.9273
6609 | 66.0018 | 3.9097 | 1.9384 | 31.34 | 8.187 | 111.3769 | 0 | 0 | 105.5288
6610 | 56.5796 | 3.2039 | 1.7681 | 27.7902 | 18.3525 | 107.6943 | 0 | 0 | 102.7223
6611 | 56.9811 | 3.071 | 1.3773 | 30.9733 | 18.5424 | 110.945 | 0 | 0 | 106.4967
6612 | 25.715 | 3.6547 | 2.3299 | 21.3813 | 12.905 | 65.986 | 0 | 0 | 60.0013
6613 | 0.14256 | 3.1083 | 2.3888 | 30.0522 | -0.12648 | 35.5654 | 0 | 0 | 30.0683
6614 | 21.0929 | 2.9274 | 3.1166 | 22.7847 | 13.591 | 63.5127 | 0 | 0 | 57.4686
6615 | 67.4925 | 3.3759 | 1.9886 | 33.2432 | 23.0174 | 129.1177 | 0 | 0 | 123.7531
6616 | 23.8141 | 3.8384 | 2.2272 | 21.1483 | 16.3343 | 67.3624 | 0 | 0 | 61.2967
6617 | 0 | 3.3031 | 2.1199 | 25.9861 | 5.0458 | 36.455 | 0 | 0 | 31.032
6618 | 15.1923 | 3.4765 | 1.5861 | 32.2263 | 8.2168 | 60.698 | 0 | 0 | 55.6354
6619 | 49.0897 | 3.3415 | 1.239 | 32.0278 | 17.5141 | 103.2121 | 0 | 0 | 98.6316
6620 | 39.9105 | 3.1423 | 1.0185 | 26.7226 | 0 | 70.7939 | 0 | 0 | 66.6331
6621 | 30.5268 | 3.4084 | 1.0722 | 16.0603 | 0 | 51.0677 | 0 | 0 | 46.5871
6622 | 0 | 3.094 | 1.1947 | 35.5015 | 0 | 39.7902 | 0 | 0 | 35.5015
6623 | 0 | 3.0526 | 1.2542 | 24.579 | 0 | 28.8857 | 200 | 0 | 224.579
6624 | 0 | 3.5638 | 2.7569 | 27.1956 | 0 | 33.5163 | 0 | 0 | 27.1956
6625 | 22.8636 | 3.4757 | 4.3028 | 34.1607 | 0 | 64.8028 | 0 | 0 | 57.0243
6626 | 76.1686 | 3.936 | 3.0702 | 33.2689 | 0 | 116.4436 | 0 | 0 | 109.4374
6627 | 67.0255 | 2.9632 | 3.2171 | 27.5472 | 0 | 100.7531 | 0 | 0 | 94.5727
6628 | 32.1247 | 3.2973 | 3.4629 | 27.9157 | 0 | 66.8006 | 0 | 0 | 60.0404
6629 | 46.8958 | 3.3304 | 2.5205 | 33.5679 | 0 | 86.3146 | 0 | 0 | 80.4637
6630 | 45.2518 | 3.2813 | 1.8545 | 30.2641 | 0 | 80.6517 | 0 | 0 | 75.5159
6631 | 41.9954 | 3.724 | 1.8626 | 29.9569 | 0 | 77.539 | 0 | 0 | 71.9523
6632 | 34.6902 | 3.2322 | 1.8002 | 21.6089 | 12.4837 | 73.8153 | 0 | 0 | 68.7829
6633 | 52.9763 | 3.5386 | 1.7611 | 32.7649 | 14.3008 | 105.3417 | 0 | 0 | 100.0419
6634 | 36.0634 | 3.9206 | 1.7681 | 22.0202 | 4.08 | 67.8524 | 0 | 0 | 62.1636
6635 | 43.6277 | 3.7348 | 1.3773 | 26.5454 | 19.7706 | 95.0557 | 0 | 0 | 89.9436
6636 | 51.8132 | 2.3665 | 2.3299 | 31.5106 | 14.1262 | 102.1464 | 0 | 0 | 97.45
6637 | 43.7668 | 3.1837 | 2.3888 | 27.7433 | 16.9097 | 93.9923 | 0 | 0 | 88.4198
6638 | 42.2245 | 2.5861 | 2.0295 | 29.8966 | 17.2234 | 93.9601 | 0 | 0 | 89.3445
6639 | 36.7013 | 3.4912 | 1.9886 | 25.5716 | 4.0862 | 71.839 | 0 | 0 | 66.3591
6640 | 0 | 3.2665 | 2.2272 | 34.2909 | 10.0376 | 49.8222 | 0 | 0 | 44.3285
6641 | 0 | 2.9137 | 2.1199 | 36.1178 | 14.6727 | 55.8241 | 0 | 0 | 50.7905
6642 | 8.1844 | 3.2159 | 1.5861 | 27.9304 | 20.7426 | 61.6594 | 0 | 0 | 56.8575
6643 | 46.9629 | 3.2983 | 1.239 | 26.3783 | 8.6699 | 86.5485 | 0 | 0 | 82.0112
6644 | 65.4363 | 3.3733 | 1.0185 | 30.1838 | 0 | 100.0119 | 0 | 0 | 95.6201
6645 | 73.1774 | 3.4705 | 1.0722 | 26.8396 | 0 | 104.5597 | 0 | 0 | 100.017
6646 | 65.762 | 3.4379 | 1.1947 | 22.0608 | 0 | 92.4554 | 0 | 0 | 87.8228
6647 | 31.0162 | 3.1749 | 2.0402 | 27.3223 | 0 | 63.5536 | 0 | 0 | 58.3385
6648 | 14.5191 | 3.2776 | 3.0308 | 29.7234 | 0 | 50.551 | 0 | 0 | 44.2426
6649 | 0.054645 | 3.7731 | 6.1849 | 24.9515 | 0 | 34.9642 | 0 | 0 | 25.0061
6650 | 15.0895 | 2.8774 | 4.3602 | 32.407 | 0 | 54.7342 | 0 | 0 | 47.4966
6651 | 61.0392 | 3.4 | 3.1486 | 25.4097 | 0 | 92.9975 | 0 | 0 | 86.4489
6652 | 46.6961 | 2.4778 | 2.2727 | 25.4086 | 0 | 76.8552 | 0 | 0 | 72.1047
6653 | 14.6124 | 3.7785 | 2.0277 | 28.9697 | 0 | 49.3883 | 0 | 0 | 43.5821
6654 | 73.9857 | 3.5079 | 1.8545 | 25.8331 | 0 | 105.1812 | 0 | 0 | 99.8189
6655 | 67.9906 | 3.444 | 1.8626 | 24.6378 | 0 | 97.935 | 0 | 0 | 92.6283
6656 | 71.5728 | 3.682 | 1.8002 | 28.1434 | 16.2903 | 121.4889 | 0 | 0 | 116.0066
6657 | 83.6895 | 3.781 | 1.7611 | 32.9736 | 9.0233 | 131.2284 | 0 | 0 | 125.6863
6658 | 80.8479 | 3.259 | 1.7681 | 28.3252 | 16.8737 | 131.074 | 0 | 0 | 126.0469
6659 | 72.3567 | 3.2259 | 1.3773 | 24.4612 | 11.4795 | 112.9006 | 0 | 0 | 108.2974
6660 | 67.9253 | 3.2874 | 2.3299 | 28.7765 | 11.3098 | 113.629 | 0 | 0 | 108.0117
6661 | 52.6158 | 2.3345 | 2.3888 | 25.9134 | 21.2318 | 104.4844 | 0 | 0 | 99.761
6662 | 5.7796 | 3.1122 | 2.0295 | 22.8785 | 15.5564 | 49.3561 | 0 | 0 | 44.2145
6663 | 0 | 3.1645 | 1.9886 | 34.0496 | 12.2057 | 51.4085 | 0 | 0 | 46.2553
6664 | 0 | 3.3355 | 2.3789 | 23.9137 | 6.1436 | 35.7717 | 0 | 0 | 30.0573
6665 | 0 | 3.1577 | 2.1199 | 23.37 | 10.0972 | 38.7448 | 0 | 0 | 33.4672
6666 | 0 | 3.1185 | 1.9531 | 27.8391 | 21.8717 | 54.7824 | 0 | 0 | 49.7108
6667 | 0 | 3.4722 | 1.5255 | 31.2208 | 28.3745 | 64.593 | 0 | 0 | 59.5954
6668 | 0 | 3.0545 | 1.1504 | 22.7898 | 0 | 26.9946 | 0 | 0 | 22.7898
6669 | 0 | 2.9927 | 1.7938 | 23.2561 | 0 | 28.0426 | 0 | 0 | 23.2561
6670 | 0 | 3.5039 | 2.6391 | 21.7134 | 0 | 27.8564 | 0 | 0 | 21.7134
6671 | 0 | 2.891 | 2.7401 | 31.6697 | 0 | 37.3008 | 0 | 0 | 31.6697
6672 | 0 | 3.1246 | 1.8934 | 30.4948 | 0 | 35.5128 | 0 | 0 | 30.4948
6673 | 0 | 3.4607 | 2.1992 | 31.2823 | 0 | 36.9422 | 0 | 0 | 31.2823
6674 | 0 | 3.172 | 1.9945 | 30.8606 | 0 | 36.027 | 0 | 0 | 30.8606
6675 | 0 | 3.0206 | 3.6751 | 27.7402 | 0 | 34.4358 | 0 | 0 | 27.7402
6676 | 0 | 3.1487 | 3.2685 | 27.9693 | 0 | 34.3865 | 0 | 0 | 27.9693
6677 | 0 | 3.6684 | 2.6595 | 31.1947 | 0 | 37.5226 | 0 | 0 | 31.1947
6678 | 0 | 2.9907 | 2.1561 | 28.588 | 0 | 33.7348 | 0 | 0 | 28.588
6679 | 0 | 3.5566 | 1.9466 | 29.5781 | 0 | 35.0813 | 0 | 200 | 229.5781
6680 | 0 | 3.0121 | 1.9857 | 25.062 | 30.0677 | 60.1275 | 0 | 0 | 55.1298
6681 | 0 | 2.8649 | 1.7436 | 25.6283 | 21.6724 | 51.9092 | 0 | 0 | 47.3007
6682 | 0 | 3.2613 | 1.9834 | 25.9442 | 15.1022 | 46.2911 | 0 | 0 | 41.0464
6683 | 0 | 3.1131 | 2.2739 | 33.4252 | 10.259 | 49.0712 | 0 | 0 | 43.6842
6684 | 0 | 3.92 | 2.4752 | 38.5252 | -1.2605 | 43.6599 | 200 | 0 | 237.2647
6685 | 12.9383 | 3.6396 | 1.8702 | 33.6915 | 19.7319 | 71.8715 | 0 | 0 | 66.3617
6686 | 58.118 | 3.338 | 2.2301 | 19.6692 | 21.6028 | 104.9581 | 0 | 0 | 99.39
6687 | 63.0083 | 3.3846 | 2.3118 | 31.3921 | 12.6052 | 112.702 | 0 | 0 | 107.0056
6688 | 44.6528 | 3.739 | 1.9 | 29.1425 | 9.9248 | 89.359 | 0 | 0 | 83.7201
6689 | 0 | 3.4345 | 1.9367 | 27.3337 | 11.4136 | 44.1185 | 0 | 0 | 38.7473
6690 | 0 | 3.8312 | 1.5167 | 26.6481 | 14.6179 | 46.6139 | 0 | 0 | 41.266
6691 | 0 | 3.1933 | 1.4117 | 19.6242 | 21.8378 | 46.0671 | 0 | 0 | 41.4621
6692 | 0 | 3.3415 | 1.1486 | 30.5734 | 0 | 35.0635 | 0 | 0 | 30.5734
6693 | 0 | 3.0772 | 1.2344 | 25.8713 | 0 | 30.1829 | 0 | 0 | 25.8713
6694 | 0 | 2.9723 | 1.1264 | 28.2415 | 0 | 32.3403 | 0 | 0 | 28.2415
6695 | 0 | 3.3487 | 1.1609 | 30.5958 | 0 | 35.1053 | 0 | 0 | 30.5958
6696 | 0 | 3.254 | 2.37 | 25.812 | 0 | 31.436 | 0 | 0 | 25.812
6697 | 0 | 3.0886 | 2.1636 | 35.0601 | 0 | 40.3123 | 0 | 0 | 35.0601
6698 | 0 | 2.9213 | 1.767 | 31.8153 | 0 | 36.5036 | 0 | 0 | 31.8153
6699 | 0 | 3.5421 | 2.6204 | 28.196 | 0 | 34.3585 | 0 | 0 | 28.196
6700 | 0 | 2.9412 | 3.9766 | 30.9344 | 0 | 37.8522 | 0 | 0 | 30.9344
6701 | 0 | 3.4474 | 3.4779 | 35.4509 | 0 | 42.3762 | 0 | 0 | 35.4509
6702 | 0 | 2.9221 | 4.0524 | 30.9498 | 0 | 37.9244 | 0 | 0 | 30.9498
6703 | 5.4476 | 3.1135 | 3.5269 | 34.3564 | 0 | 46.4444 | 0 | 0 | 39.804
6704 | 38.262 | 2.9292 | 2.158 | 38.0575 | 19.6608 | 101.0674 | 0 | 0 | 95.9802
6705 | 86.8274 | 3.2075 | 2.0263 | 20.8226 | 16.4869 | 129.3708 | 0 | 0 | 124.1369
6706 | 60.9281 | 3.3582 | 1.6125 | 21.5661 | 24.0442 | 111.5091 | 0 | 0 | 106.5384
6707 | 15.9082 | 3.2525 | 1.8335 | 27.8105 | 13.603 | 62.4077 | 0 | 0 | 57.3217
6708 | 0 | 2.9672 | 3.0995 | 21.1691 | 9.1786 | 36.4144 | 0 | 0 | 30.3477
6709 | 0 | 2.8952 | 3.8293 | 25.2436 | 19.9429 | 51.911 | 0 | 0 | 45.1865
6710 | 0 | 3.1417 | 4.9465 | 35.6626 | 6.1341 | 49.8848 | 0 | 0 | 41.7967
6711 | 0 | 3.5878 | 5.4666 | 21.4737 | 18.9181 | 49.4462 | 0 | 0 | 40.3918
6712 | 0 | 3.2243 | 5.5327 | 26.798 | 14.763 | 50.318 | 0 | 0 | 41.561
6713 | 0 | 2.4463 | 4.8292 | 25.8076 | 13.3785 | 46.4617 | 0 | 0 | 39.1861
6714 | 0 | 3.6306 | 4.5388 | 27.2124 | 17.7411 | 53.1228 | 0 | 0 | 44.9535
6715 | 0 | 3.7298 | 4.4416 | 31.8783 | -0.63063 | 39.4191 | 0 | 0 | 31.2477
6716 | 0 | 3.1749 | 4.9863 | 29.2607 | 0 | 37.4219 | 0 | 0 | 29.2607
6717 | 0 | 3.2602 | 4.7515 | 30.6979 | 0 | 38.7095 | 0 | 0 | 30.6979
6718 | 0 | 2.8251 | 5.4256 | 18.6482 | 0 | 26.8988 | 0 | 0 | 18.6482
6719 | 0 | 2.5615 | 6.3937 | 23.167 | 0 | 32.1222 | 0 | 0 | 23.167
6720 | 0 | 3.247 | 8.4074 | 20.6548 | 0 | 32.3092 | 0 | 0 | 20.6548
6721 | 0 | 3.8263 | 9.4972 | 32.2396 | 0 | 45.5631 | 0 | 0 | 32.2396
6722 | 0 | 3.3808 | 7.5567 | 24.6803 | 0 | 35.6179 | 0 | 0 | 24.6803
6723 | 0 | 3.2845 | 5.9589 | 22.5225 | 0 | 31.7659 | 0 | 0 | 22.5225
6724 | 0 | 2.8652 | 4.5112 | 26.2137 | 0 | 33.59 | 0 | 0 | 26.2137
6725 | 14.6716 | 3.0405 | 2.8833 | 30.9453 | 0 | 51.5407 | 0 | 0 | 45.6169
6726 | 49.9332 | 3.3285 | 2.2486 | 31.2964 | 0 | 86.8068 | 0 | 0 | 81.2296
6727 | 77.7888 | 3.0041 | 2.0141 | 24.2089 | 0 | 107.0159 | 0 | 0 | 101.9977
6728 | 77.8599 | 3.9439 | 1.8002 | 34.7023 | 15.2408 | 133.5472 | 0 | 0 | 127.8031
6729 | 62.2495 | 3.1691 | 1.7611 | 23.7899 | 11.5079 | 102.4775 | 0 | 0 | 97.5473
6730 | 62.7808 | 3.757 | 1.7681 | 28.5737 | 17.5626 | 114.4422 | 0 | 0 | 108.9171
6731 | 78.1897 | 3.3755 | 1.3773 | 25.7534 | 18.5585 | 127.2544 | 0 | 0 | 122.5016
6732 | 88.0678 | 3.6624 | 2.3299 | 17.672 | 21.6058 | 133.3379 | 0 | 0 | 127.3455
6733 | 78.0619 | 3.5374 | 2.3888 | 29.4686 | 24.5035 | 137.9602 | 0 | 0 | 132.034
6734 | 77.4582 | 3.4271 | 3.2024 | 30.4814 | 7.072 | 121.6412 | 0 | 0 | 115.0116
6735 | 49.5413 | 3.1473 | 3.4732 | 26.8525 | 14.0455 | 97.0598 | 0 | 0 | 90.4393
6736 | 0 | 2.8882 | 2.2272 | 21.661 | 9.7105 | 36.4869 | 0 | 0 | 31.3714
6737 | 0 | 3.23 | 2.1199 | 29.1399 | 15.2543 | 49.7441 | 0 | 0 | 44.3942
6738 | 9.013 | 3.7707 | 1.5861 | 29.7513 | 19.4356 | 63.5567 | 0 | 0 | 58.1999
6739 | 45.9611 | 3.7181 | 1.239 | 30.4128 | 9.6451 | 90.9761 | 0 | 0 | 86.0189
6740 | 38.9962 | 3.441 | 1.0185 | 35.1533 | 0 | 78.609 | 0 | 0 | 74.1496
6741 | 42.7796 | 2.8705 | 1.0722 | 25.0961 | 0 | 71.8184 | 0 | 0 | 67.8757
6742 | 47.1702 | 3.2533 | 1.1947 | 31.0504 | 0 | 82.6686 | 0 | 0 | 78.2206
6743 | 42.1084 | 2.9698 | 1.879 | 31.3487 | 0 | 78.3058 | 0 | 0 | 73.4571
6744 | 41.4349 | 3.4896 | 3.2337 | 33.5706 | 0 | 81.7289 | 0 | 200 | 275.0055
6745 | 42.5584 | 3.2619 | 7.0617 | 18.744 | 0 | 71.626 | 200 | 0 | 261.3023
6746 | 48.8458 | 3.1026 | 6.1634 | 19.9914 | 0 | 78.1033 | 0 | 0 | 68.8372
6747 | 61.6884 | 2.8335 | 5.0678 | 25.4809 | 0 | 95.0706 | 0 | 0 | 87.1692
6748 | 60.7069 | 3.4245 | 3.8123 | 30.8434 | 0 | 98.7871 | 0 | 0 | 91.5503
6749 | 15.5145 | 3.0483 | 2.3753 | 26.8317 | 0 | 47.7698 | 0 | 0 | 42.3462
6750 | 45.1823 | 3.744 | 1.8545 | 27.8372 | 0 | 78.618 | 0 | 0 | 73.0195
6751 | 79.3601 | 3.9126 | 1.8626 | 27.471 | 0 | 112.6065 | 0 | 0 | 106.8312
6752 | 73.1216 | 3.1136 | 1.8002 | 22.5978 | 13.7967 | 114.43 | 0 | 0 | 109.5161
6753 | 58.5977 | 3.2063 | 1.7611 | 29.1245 | 13.5603 | 106.2499 | 0 | 0 | 101.2825
6754 | 73.1483 | 3.6011 | 1.7681 | 23.5923 | 15.5896 | 117.6994 | 0 | 0 | 112.3302
6755 | 49.845 | 3.6043 | 1.3773 | 29.027 | 3.3411 | 87.1947 | 0 | 0 | 82.2131
6756 | 62.6415 | 3.1179 | 2.3299 | 26.2042 | 8.342 | 102.6355 | 0 | 0 | 97.1877
6757 | 32.0532 | 3.1937 | 2.3888 | 26.108 | 8.6802 | 72.4239 | 0 | 0 | 66.8414
6758 | 35.1603 | 3.6527 | 3.2024 | 27.7947 | 26.302 | 96.1122 | 0 | 0 | 89.2571
6759 | 20.3347 | 3.409 | 2.8104 | 23.3614 | 14.9693 | 64.8849 | 0 | 0 | 58.6654
6760 | 0 | 3.2089 | 2.9491 | 28.5308 | 0.86423 | 35.5531 | 0 | 0 | 29.395
6761 | 5.37 | 3.6142 | 2.9172 | 35.402 | 12.394 | 59.6975 | 0 | 0 | 53.166
6762 | 25.1581 | 2.4169 | 1.877 | 28.1843 | 12.5032 | 70.1394 | 0 | 0 | 65.8455
6763 | 46.5175 | 3.3527 | 2.62 | 35.8545 | 12.0384 | 100.3831 | 0 | 0 | 94.4104
6764 | 41.964 | 3.6111 | 2.8049 | 33.2887 | 0 | 81.6687 | 0 | 0 | 75.2527
6765 | 46.3443 | 3.2036 | 3.3045 | 25.251 | 0 | 78.1035 | 0 | 0 | 71.5954
6766 | 52.0843 | 3.3509 | 3.5592 | 33.2006 | 0 | 92.195 | 0 | 0 | 85.2848
6767 | 42.122 | 3.4838 | 4.5394 | 31.1453 | 0 | 81.2906 | 0 | 0 | 73.2673
6768 | 46.3782 | 3.528 | 5.364 | 30.1277 | 0 | 85.3979 | 0 | 0 | 76.5059
6769 | 75.0076 | 3.8501 | 8.3282 | 30.8029 | 0 | 117.9887 | 0 | 0 | 105.8105
6770 | 68.2661 | 3.4607 | 5.9995 | 27.1648 | 0 | 104.891 | 0 | 0 | 95.4309
6771 | 18.5547 | 4.0075 | 3.9026 | 28.6951 | 0 | 55.1599 | 0 | 0 | 47.2498
6772 | 6.296 | 3.7122 | 2.4146 | 33.5882 | 0 | 46.011 | 0 | 0 | 39.8842
6773 | 37.5075 | 3.192 | 2.0277 | 29.996 | 0 | 72.7232 | 0 | 0 | 67.5035
6774 | 70.1108 | 3.3159 | 1.8545 | 32.1898 | 0 | 107.471 | 0 | 0 | 102.3006
6775 | 73.1164 | 3.2139 | 1.8626 | 25.5313 | 0 | 103.7241 | 0 | 0 | 98.6476
6776 | 73.0178 | 3.7827 | 1.8002 | 25.5278 | 7.9064 | 112.035 | 0 | 0 | 106.452
6777 | 37.8286 | 3.6818 | 1.7611 | 24.326 | 13.9992 | 81.5968 | 0 | 0 | 76.1539
6778 | 56.6898 | 2.9192 | 1.7681 | 29.1286 | 7.9708 | 98.4766 | 0 | 0 | 93.7893
6779 | 38.607 | 3.9266 | 1.3773 | 22.6079 | 11.5149 | 78.0337 | 0 | 0 | 72.7299
6780 | 56.8807 | 3.4281 | 2.3299 | 21.0032 | 18.3345 | 101.9765 | 0 | 0 | 96.2185
6781 | 71.7847 | 2.7837 | 2.3888 | 30.2421 | 14.7115 | 121.9109 | 0 | 0 | 116.7383
6782 | 69.0227 | 3.0134 | 2.0295 | 25.0803 | 14.4756 | 113.6215 | 0 | 0 | 108.5786
6783 | 34.0353 | 3.247 | 1.9886 | 31.6411 | 13.8662 | 84.7783 | 0 | 0 | 79.5426
6784 | 0 | 2.6249 | 2.2272 | 22.9033 | 16.9174 | 44.6728 | 0 | 0 | 39.8207
6785 | 0 | 3.456 | 2.1199 | 35.5282 | 13.8757 | 54.9798 | 0 | 0 | 49.4039
6786 | 10.6861 | 3.3426 | 1.5861 | 25.0353 | 17.59 | 58.2401 | 0 | 0 | 53.3114
6787 | 51.2702 | 2.9921 | 1.239 | 29.9061 | 16.1146 | 101.5221 | 0 | 0 | 97.2909
6788 | 77.5584 | 2.8736 | 1.0185 | 30.8819 | 0 | 112.3324 | 0 | 0 | 108.4403
6789 | 81.0045 | 2.7795 | 1.0722 | 31.8237 | 0 | 116.6799 | 0 | 0 | 112.8282
6790 | 45.6714 | 2.9336 | 1.1947 | 24.195 | 0 | 73.9948 | 0 | 0 | 69.8664
6791 | 41.1477 | 3.3869 | 1.2542 | 28.4962 | 0 | 74.285 | 0 | 0 | 69.6438
6792 | 29.3868 | 2.8586 | 2.7569 | 31.2952 | 0 | 66.2975 | 0 | 0 | 60.682
6793 | 38.3915 | 3.1939 | 5.6004 | 32.9343 | 0 | 80.1201 | 0 | 0 | 71.3258
6794 | 58.5943 | 3.1989 | 3.5406 | 29.6874 | 0 | 95.0212 | 0 | 0 | 88.2817
6795 | 86.5023 | 3.3149 | 2.3713 | 24.3673 | 0 | 116.5559 | 0 | 0 | 110.8697
6796 | 59.5701 | 3.0013 | 2.2727 | 31.7513 | 0 | 96.5955 | 0 | 0 | 91.3214
6797 | 14.9878 | 3.542 | 2.0277 | 32.7643 | 0 | 53.3217 | 0 | 0 | 47.752
6798 | 49.1886 | 2.7823 | 1.8545 | 29.0454 | 0 | 82.8708 | 0 | 0 | 78.234
6799 | 77.4424 | 3.1673 | 1.8626 | 29.9686 | 0 | 112.441 | 0 | 0 | 107.4111
6800 | 59.8783 | 3.4116 | 1.8002 | 22.2226 | 20.978 | 108.2907 | 0 | 0 | 103.0789
6801 | 49.6052 | 3.2535 | 1.7611 | 31.853 | 12.7065 | 99.1794 | 0 | 0 | 94.1647
6802 | 53.0819 | 3.213 | 1.7681 | 27.4325 | 11.827 | 97.3226 | 0 | 0 | 92.3414
6803 | 65.2788 | 2.9185 | 1.3773 | 31.1292 | 12.6928 | 113.3967 | 0 | 0 | 109.1009
6804 | 6.0356 | 3.5848 | 2.3299 | 25.4657 | 12.0505 | 49.4665 | 0 | 0 | 43.5518
6805 | 1.0884 | 3.5277 | 2.3888 | 25.1897 | 15.7917 | 47.9864 | 0 | 0 | 42.0698
6806 | 10.2101 | 2.6941 | 2.0295 | 25.9104 | 20.4094 | 61.2534 | 200 | 0 | 256.5299
6807 | 33.9473 | 2.9442 | 1.9886 | 24.8402 | 10.3505 | 74.0707 | 0 | 0 | 69.1379
6808 | 41.2326 | 3.7701 | 2.2272 | 30.8278 | 6.7956 | 84.8534 | 0 | 0 | 78.8561
6809 | 33.6526 | 3.7118 | 2.1199 | 24.0546 | 12.3518 | 75.8906 | 0 | 0 | 70.059
6810 | 7.6215 | 3.472 | 1.5861 | 29.6673 | 15.9032 | 58.2501 | 0 | 0 | 53.192
6811 | 39.9574 | 3.1597 | 1.239 | 24.1201 | 10.9906 | 79.4667 | 0 | 0 | 75.068
6812 | 38.5704 | 3.4922 | 1.0185 | 24.9073 | 0 | 67.9885 | 0 | 0 | 63.4777
6813 | 54.6545 | 2.9065 | 1.0722 | 23.3832 | 0 | 82.0164 | 0 | 0 | 78.0376
6814 | 46.4855 | 3.3702 | 1.1947 | 33.3485 | 0 | 84.3989 | 0 | 0 | 79.834
6815 | 16.0127 | 3.3944 | 1.2542 | 27.1741 | 0 | 47.8354 | 0 | 0 | 43.1868
6816 | 13.4578 | 3.4368 | 2.7569 | 34.3271 | 0 | 53.9786 | 0 | 0 | 47.7848
6817 | 52.7395 | 3.6766 | 4.3028 | 22.7119 | 0 | 83.4308 | 0 | 0 | 75.4514
6818 | 60.0954 | 3.4195 | 3.0702 | 18.8989 | 0 | 85.4841 | 0 | 0 | 78.9944
6819 | 28.8851 | 4.0146 | 2.3713 | 29.3288 | 0 | 64.5999 | 0 | 0 | 58.214
6820 | 8.9362 | 3.4521 | 2.2727 | 28.2902 | 0 | 42.9513 | 0 | 0 | 37.2265
6821 | 12.0591 | 3.6826 | 2.0277 | 27.1439 | 0 | 44.9133 | 0 | 0 | 39.203
6822 | 45.8964 | 3.0008 | 1.8545 | 27.6037 | 0 | 78.3553 | 0 | 0 | 73.5
6823 | 59.0401 | 3.5995 | 1.8626 | 30.3358 | 0 | 94.8381 | 0 | 0 | 89.3759
6824 | 54.6667 | 3.4036 | 1.8002 | 23.4649 | 15.3921 | 98.7276 | 0 | 0 | 93.5237
6825 | 57.8227 | 3.4206 | 1.7611 | 29.6666 | 13.7864 | 106.4574 | 0 | 0 | 101.2757
6826 | 66.9293 | 3.5392 | 1.7681 | 32.6394 | 21.3452 | 126.2212 | 0 | 200 | 320.9139
6827 | 46.3958 | 3.2104 | 1.3773 | 34.7836 | 16.5817 | 102.3488 | 0 | 0 | 97.761
6828 | 27.6561 | 3.2997 | 2.3299 | 34.8302 | 5.5869 | 73.7028 | 0 | 0 | 68.0732
6829 | 16.3677 | 2.7296 | 2.3888 | 28.8529 | 1.6328 | 51.9717 | 0 | 0 | 46.8534
6830 | 0 | 3.5464 | 2.0295 | 27.3116 | 28.7637 | 61.6511 | 0 | 0 | 56.0753
6831 | 0 | 3.2892 | 1.9886 | 28.4294 | 10.0107 | 43.7179 | 0 | 0 | 38.4401
6832 | 0 | 3.3211 | 2.2272 | 36.1314 | 5.5799 | 47.2596 | 0 | 0 | 41.7113
6833 | 0 | 2.4589 | 2.1199 | 25.6051 | 12.3956 | 42.5796 | 0 | 0 | 38.0008
6834 | 0.026974 | 3.6994 | 1.9531 | 33.3612 | 13.828 | 52.8686 | 0 | 0 | 47.2161
6835 | 10.6135 | 3.0225 | 1.5255 | 27.2156 | 15.5905 | 57.9675 | 0 | 0 | 53.4196
6836 | 55.9661 | 3.2215 | 1.1504 | 23.3957 | 0 | 83.7337 | 0 | 0 | 79.3618
6837 | 59.1369 | 3.0785 | 1.1994 | 32.744 | 0 | 96.1588 | 0 | 0 | 91.8809
6838 | 49.6533 | 3.0069 | 1.0675 | 33.6574 | 0 | 87.3852 | 0 | 0 | 83.3107
6839 | 0 | 3.0618 | 1.3615 | 27.8419 | 0 | 32.2652 | 0 | 0 | 27.8419
6840 | 0 | 3.3844 | 1.7973 | 27.6311 | 0 | 32.8128 | 0 | 0 | 27.6311
6841 | 5.133 | 3.3563 | 2.1992 | 24.2797 | 0 | 34.9683 | 0 | 0 | 29.4128
6842 | 19.8596 | 3.2223 | 1.9945 | 17.1815 | 0 | 42.2579 | 0 | 0 | 37.0411
6843 | 13.4085 | 3.3658 | 3.6751 | 19.1124 | 0 | 39.5618 | 0 | 0 | 32.5209
6844 | 0 | 3.7594 | 3.2685 | 19.528 | 0 | 26.5559 | 0 | 0 | 19.528
6845 | 0 | 2.7912 | 2.6595 | 25.4331 | 0 | 30.8838 | 0 | 0 | 25.4331
6846 | 0 | 3.4393 | 2.1561 | 25.9187 | 0 | 31.5141 | 0 | 0 | 25.9187
6847 | 0 | 3.2576 | 1.9466 | 24.9353 | 0 | 30.1395 | 0 | 0 | 24.9353
6848 | 0 | 3.4484 | 1.9857 | 34.688 | 14.3179 | 54.4401 | 0 | 0 | 49.0059
6849 | 0 | 3.4042 | 1.7436 | 27.4576 | 9.2013 | 41.8067 | 0 | 0 | 36.6588
6850 | 0 | 3.1591 | 1.9834 | 32.9868 | 24.3963 | 62.5255 | 0 | 0 | 57.383
6851 | 0 | 3.4437 | 2.2739 | 30.2842 | 20.659 | 56.6609 | 0 | 0 | 50.9432
6852 | 0 | 2.7099 | 2.4752 | 27.8875 | 3.773 | 36.8456 | 0 | 0 | 31.6605
6853 | 0 | 3.542 | 1.8702 | 30.9534 | 9.3785 | 45.7441 | 0 | 0 | 40.3319
6854 | 0 | 3.099 | 2.2301 | 27.8612 | 20.803 | 53.9934 | 0 | 0 | 48.6643
6855 | 0 | 3.1599 | 2.3118 | 29.0548 | 16.4447 | 50.9712 | 0 | 0 | 45.4995
6856 | 0 | 3.0327 | 1.9 | 27.3588 | 20.1257 | 52.4171 | 0 | 0 | 47.4845
6857 | 0 | 3.3378 | 1.9367 | 30.8561 | 7.1972 | 43.3279 | 0 | 0 | 38.0533
6858 | 0 | 2.9517 | 1.5167 | 26.9469 | 6.2553 | 37.6706 | 0 | 0 | 33.2022
6859 | 0 | 2.668 | 1.4117 | 31.8045 | 0.41757 | 36.3019 | 0 | 0 | 32.2221
6860 | 0 | 2.8884 | 1.1486 | 27.0654 | 0 | 31.1024 | 0 | 0 | 27.0654
6861 | 0 | 3.1221 | 1.2344 | 32.2988 | 0 | 36.6552 | 0 | 0 | 32.2988
6862 | 0 | 2.9795 | 1.1264 | 33.5457 | 0 | 37.6516 | 0 | 0 | 33.5457
6863 | 0 | 3.5281 | 1.1609 | 26.7175 | 0 | 31.4065 | 0 | 0 | 26.7175
6864 | 0 | 3.0223 | 1.1591 | 22.2721 | 0 | 26.4535 | 0 | 0 | 22.2721
6865 | 0 | 3.3878 | 2.1636 | 24.1269 | 0 | 29.6783 | 0 | 0 | 24.1269
6866 | 0 | 3.2393 | 1.767 | 29.1807 | 0 | 34.187 | 0 | 0 | 29.1807
6867 | 0 | 2.9563 | 2.6204 | 33.2477 | 0 | 38.8243 | 200 | 0 | 233.2477
6868 | 0 | 2.9859 | 2.6397 | 29.4275 | 0 | 35.0531 | 0 | 0 | 29.4275
6869 | 0 | 3.0044 | 2.3626 | 22.974 | 0 | 28.341 | 0 | 0 | 22.974
6870 | 0 | 3.2279 | 1.8189 | 24.9233 | 0 | 29.97 | 0 | 0 | 24.9233
6871 | 0 | 2.99 | 1.9431 | 27.0545 | 0 | 31.9876 | 0 | 0 | 27.0545
6872 | 0 | 3.3137 | 1.9321 | 23.9479 | 21.4631 | 50.6567 | 0 | 0 | 45.4109
6873 | 0 | 2.4683 | 1.7582 | 30.0492 | 20.659 | 54.9347 | 0 | 0 | 50.7082
6874 | 0 | 3.2068 | 1.4747 | 31.987 | 13.2109 | 49.8795 | 0 | 0 | 45.1979
6875 | 0 | 3.1304 | 1.8335 | 28.613 | 21.5016 | 55.0785 | 0 | 0 | 50.1146
6876 | 0 | 2.9608 | 2.0907 | 28.4028 | 15.9767 | 49.431 | 0 | 0 | 44.3795
6877 | 0 | 2.9488 | 2.2196 | 24.7282 | 15.2509 | 45.1475 | 0 | 0 | 39.979
6878 | 0 | 3.2086 | 2.2605 | 28.9441 | 15.6043 | 50.0175 | 0 | 0 | 44.5485
6879 | 0 | 4.0236 | 2.1706 | 22.1861 | 11.4552 | 39.8356 | 0 | 0 | 33.6414
6880 | 0 | 2.8572 | 2.1677 | 24.4692 | 15.8396 | 45.3337 | 0 | 0 | 40.3088
6881 | 0 | 3.2926 | 2.1706 | 32.672 | 5.7275 | 43.8627 | 0 | 0 | 38.3995
6882 | 0 | 3.4467 | 1.5861 | 31.2741 | 19.8384 | 56.1453 | 0 | 0 | 51.1125
6883 | 0 | 3.3854 | 1.239 | 25.7114 | 23.0508 | 53.3866 | 0 | 0 | 48.7622
6884 | 0 | 3.4494 | 1.0185 | 22.0641 | 0 | 26.532 | 0 | 0 | 22.0641
6885 | 0 | 3.0069 | 1.0722 | 26.4867 | 0 | 30.5659 | 0 | 0 | 26.4867
6886 | 0 | 3.2505 | 1.1947 | 28.6705 | 0 | 33.1157 | 0 | 0 | 28.6705
6887 | 0 | 2.9156 | 1.2542 | 26.0404 | 0 | 30.2102 | 0 | 0 | 26.0404
6888 | 0 | 3.2191 | 2.7569 | 29.8253 | 0 | 35.8013 | 0 | 0 | 29.8253
6889 | 0 | 3.3254 | 4.3028 | 30.3024 | 0 | 37.9306 | 0 | 0 | 30.3024
6890 | 0 | 3.4129 | 3.0702 | 36.0228 | 0 | 42.5058 | 0 | 0 | 36.0228
6891 | 0.013309 | 3.183 | 2.3713 | 24.7458 | 0 | 30.3134 | 0 | 0 | 24.7591
6892 | 18.5591 | 3.7138 | 2.2727 | 22.2377 | 0 | 46.7833 | 0 | 0 | 40.7969
6893 | 76.7602 | 3.5611 | 2.0277 | 34.5735 | 0 | 116.9225 | 0 | 0 | 111.3337
6894 | 47.2461 | 3.6051 | 1.8545 | 22.421 | 0 | 75.1267 | 0 | 0 | 69.6671
6895 | 7.9436 | 3.3899 | 1.8626 | 29.1834 | 0 | 42.3796 | 0 | 0 | 37.127
6896 | 21.7889 | 3.1916 | 1.8002 | 26.3141 | 19.5594 | 72.6542 | 0 | 0 | 67.6624
6897 | 0 | 2.9802 | 1.7611 | 29.2845 | 11.5965 | 45.6224 | 0 | 0 | 40.881
6898 | 0.53324 | 3.3939 | 1.7681 | 29.8609 | 14.9505 | 50.5067 | 0 | 0 | 45.3446
6899 | 15.8108 | 2.8309 | 1.3773 | 32.6546 | 13.8392 | 66.5128 | 0 | 0 | 62.3046
6900 | 54.9918 | 3.3812 | 2.3299 | 28.6066 | 20.8898 | 110.1994 | 0 | 0 | 104.4882
6901 | 0 | 4.0529 | 2.3888 | 35.2122 | 15.9177 | 57.5717 | 0 | 0 | 51.13
6902 | 0 | 3.713 | 2.0295 | 33.0565 | 12.0798 | 50.8788 | 0 | 0 | 45.1363
6903 | 0 | 3.0601 | 1.9886 | 30.5436 | 16.7231 | 52.3154 | 0 | 0 | 47.2666
6904 | 0 | 2.7104 | 2.2272 | 34.7508 | 2.5396 | 42.228 | 0 | 0 | 37.2904
6905 | 6.1262 | 3.2913 | 2.1199 | 27.16 | 11.7578 | 50.4553 | 0 | 0 | 45.044
6906 | 39.2839 | 3.1054 | 1.5861 | 28.3342 | 15.1676 | 87.4773 | 0 | 0 | 82.7858
6907 | 56.4833 | 3.4549 | 1.239 | 26.193 | 17.5649 | 104.9352 | 0 | 0 | 100.2412
6908 | 41.5388 | 3.3386 | 1.0185 | 25.7092 | 0 | 71.6052 | 0 | 0 | 67.248
6909 | 58.0684 | 3.0539 | 1.0722 | 32.2889 | 0 | 94.4834 | 0 | 0 | 90.3573
6910 | 57.4087 | 3.6444 | 1.1947 | 29.31 | 0 | 91.5579 | 0 | 0 | 86.7187
6911 | 56.2078 | 2.8256 | 1.2542 | 18.4781 | 0 | 78.7656 | 0 | 0 | 74.6858
6912 | 32.3273 | 3.4362 | 2.7569 | 30.9922 | 0 | 69.5126 | 0 | 0 | 63.3195
6913 | 80.4876 | 3.3953 | 4.3028 | 26.9786 | 0 | 115.1643 | 0 | 0 | 107.4662
6914 | 63.1877 | 3.4582 | 3.2128 | 29.1891 | 0 | 99.0479 | 0 | 0 | 92.3769
6915 | 40.1871 | 3.2402 | 2.3713 | 22.8806 | 0 | 68.6792 | 0 | 0 | 63.0677
6916 | 0 | 2.9385 | 2.2727 | 26.9963 | 0 | 32.2074 | 0 | 0 | 26.9963
6917 | 4.751 | 3.0238 | 2.0277 | 28.7113 | 0 | 38.5139 | 0 | 0 | 33.4624
6918 | 36.5721 | 3.0175 | 1.8545 | 26.3108 | 0 | 67.7548 | 0 | 0 | 62.8829
6919 | 74.0308 | 3.4686 | 1.8626 | 34.0139 | 0 | 113.3759 | 0 | 0 | 108.0447
6920 | 34.4543 | 3.3805 | 1.8002 | 28.8666 | 19.3722 | 87.8739 | 0 | 0 | 82.6931
6921 | 0 | 3.6699 | 1.7611 | 25.6153 | 11.5428 | 42.5891 | 0 | 0 | 37.1581
6922 | 2.8653 | 3.2071 | 1.7681 | 32.2639 | 7.0973 | 47.2017 | 0 | 0 | 42.2265
6923 | 32.8002 | 3.1449 | 1.3773 | 32.0127 | 12.9465 | 82.2815 | 0 | 0 | 77.7593
6924 | 62.2112 | 3.3604 | 2.3299 | 22.3313 | 12.0287 | 102.2615 | 0 | 0 | 96.5712
6925 | 3.435 | 3.3812 | 2.3888 | 32.5436 | 7.5108 | 49.2595 | 0 | 0 | 43.4895
6926 | 0 | 3.2137 | 2.0295 | 35.589 | 3.3338 | 44.1659 | 0 | 0 | 38.9228
6927 | 0 | 3.3727 | 1.9886 | 29.75 | 11.214 | 46.3253 | 0 | 0 | 40.964
6928 | 5.0835 | 3.6347 | 2.2272 | 23.7102 | 7.486 | 42.1416 | 0 | 200 | 236.2797
6929 | 27.3573 | 3.7974 | 2.1199 | 30.25 | 17.7209 | 81.2454 | 200 | 0 | 275.3281
6930 | 64.0895 | 3.3904 | 1.5861 | 30.926 | 14.9371 | 114.9291 | 0 | 0 | 109.9525
6931 | 55.2581 | 3.3657 | 1.239 | 19.7669 | 17.2307 | 96.8606 | 0 | 0 | 92.2558
6932 | 61.9042 | 3.1377 | 1.0185 | 28.5603 | 0 | 94.6207 | 0 | 0 | 90.4645
6933 | 58.356 | 2.8681 | 1.0722 | 27.4717 | 0 | 89.768 | 0 | 0 | 85.8277
6934 | 44.4863 | 3.2384 | 1.1947 | 22.0616 | 0 | 70.981 | 0 | 0 | 66.5479
6935 | 34.09 | 2.9262 | 1.2542 | 23.815 | 0 | 62.0855 | 0 | 0 | 57.905
6936 | 68.0015 | 3.476 | 2.7569 | 28.4782 | 0 | 102.7126 | 0 | 0 | 96.4796
6937 | 78.3835 | 3.2613 | 4.9185 | 35.189 | 0 | 121.7522 | 0 | 0 | 113.5725
6938 | 21.5834 | 3.475 | 5.2618 | 30.6849 | 0 | 61.0051 | 0 | 0 | 52.2683
6939 | 8.7578 | 3.4898 | 3.3542 | 28.7331 | 0 | 44.335 | 0 | 0 | 37.4909
6940 | 0 | 3.2905 | 2.2727 | 31.1444 | 0 | 36.7077 | 0 | 0 | 31.1444
6941 | 0 | 3.2553 | 2.0277 | 29.3703 | 0 | 34.6533 | 0 | 0 | 29.3703
6942 | 7.3247 | 3.0103 | 1.8545 | 22.1076 | 0 | 34.297 | 0 | 0 | 29.4322
6943 | 40.9969 | 3.2146 | 1.8626 | 30.8397 | 0 | 76.9139 | 0 | 0 | 71.8366
6944 | 50.0383 | 3.1331 | 1.8002 | 30.7907 | 12.9492 | 98.7115 | 0 | 0 | 93.7782
6945 | 57.1567 | 3.6125 | 1.7611 | 34.2471 | 19.5488 | 116.3263 | 0 | 0 | 110.9527
6946 | 54.1932 | 3.3029 | 1.7681 | 24.0925 | 4.6129 | 87.9696 | 0 | 0 | 82.8986
6947 | 0.6079 | 3.1674 | 1.3773 | 30.924 | 10.3025 | 46.3791 | 0 | 0 | 41.8344
6948 | 0 | 2.46 | 2.3299 | 36.2289 | 20.4386 | 61.4574 | 0 | 0 | 56.6674
6949 | 0 | 3.1689 | 2.3888 | 28.0118 | 16.8895 | 50.459 | 0 | 0 | 44.9013
6950 | 0 | 2.9254 | 2.0295 | 29.6985 | 6.8097 | 41.4631 | 0 | 0 | 36.5082
6951 | 0 | 3.2835 | 1.9886 | 27.2389 | 16.5558 | 49.0669 | 0 | 0 | 43.7947
6952 | 1.7905 | 3.7745 | 2.2272 | 30.0527 | 16.8164 | 54.6613 | 0 | 0 | 48.6596
6953 | 26.4875 | 3.0195 | 2.1199 | 31.8399 | 20.7003 | 84.1671 | 0 | 0 | 79.0277
6954 | 67.004 | 3.1314 | 1.5861 | 18.0366 | 8.4323 | 98.1904 | 0 | 0 | 93.4729
6955 | 74.1839 | 2.8854 | 1.239 | 27.0075 | 25.8482 | 131.1642 | 0 | 0 | 127.0397
6956 | 77.0989 | 3.0804 | 1.0185 | 26.2316 | 0 | 107.4294 | 0 | 0 | 103.3304
6957 | 62.8424 | 2.6745 | 1.0722 | 34.4626 | 0 | 101.0517 | 0 | 0 | 97.3051
6958 | 56.7699 | 2.8428 | 1.1947 | 27.2386 | 0 | 88.046 | 0 | 0 | 84.0085
6959 | 61.849 | 3.4344 | 1.2542 | 22.2395 | 0 | 88.777 | 0 | 0 | 84.0885
6960 | 66.2407 | 3.1605 | 2.7569 | 30.7604 | 0 | 102.9184 | 0 | 0 | 97.001
6961 | 96.5284 | 3.0958 | 4.3028 | 32.5215 | 0 | 136.4484 | 0 | 0 | 129.0499
6962 | 77.1114 | 3.348 | 3.0702 | 26.9806 | 0 | 110.5102 | 0 | 0 | 104.092
6963 | 38.7464 | 3.0655 | 3.0115 | 34.3667 | 0 | 79.1902 | 0 | 0 | 73.1131
6964 | 0 | 3.0832 | 3.5328 | 30.3901 | 0 | 37.0061 | 0 | 0 | 30.3901
6965 | 10.487 | 2.8277 | 2.5205 | 26.0115 | 0 | 41.8467 | 0 | 0 | 36.4985
6966 | 40.2447 | 3.5079 | 2.2486 | 19.1839 | 0 | 65.1852 | 0 | 0 | 59.4287
6967 | 62.2048 | 3.5503 | 2.0141 | 27.6882 | 0 | 95.4574 | 0 | 0 | 89.893
6968 | 47.7676 | 3.7493 | 1.8002 | 30.283 | 18.086 | 101.6861 | 0 | 0 | 96.1366
6969 | 11.7662 | 3.5175 | 1.7611 | 28.7429 | 17.4816 | 63.2692 | 0 | 0 | 57.9906
6970 | 16.1461 | 2.8643 | 1.7681 | 27.9829 | 15.3687 | 64.1301 | 0 | 0 | 59.4976
6971 | 67.6177 | 3.0144 | 1.3773 | 35.9128 | 24.235 | 132.1573 | 0 | 0 | 127.7656
6972 | 59.84 | 3.6133 | 2.3299 | 28.6106 | 21.6952 | 116.0889 | 0 | 0 | 110.1458
6973 | 30.5931 | 2.7445 | 2.3888 | 26.1977 | 14.8228 | 76.747 | 0 | 0 | 71.6136
6974 | 0 | 3.131 | 2.0295 | 24.1799 | 12.6328 | 41.9731 | 0 | 0 | 36.8127
6975 | 0 | 3.0054 | 1.9886 | 29.0714 | 11.1857 | 45.2511 | 0 | 0 | 40.2571
6976 | 6.7405 | 3.3215 | 2.721 | 32.751 | 2.4368 | 47.9709 | 0 | 0 | 41.9283
6977 | 42.8891 | 3.3534 | 2.8059 | 24.8873 | 12.3676 | 86.3032 | 0 | 0 | 80.144
6978 | 63.6399 | 3.1039 | 2.4685 | 25.8496 | 10.3523 | 105.4142 | 0 | 0 | 99.8417
6979 | 69.4075 | 3.167 | 4.3549 | 28.5838 | 20.4072 | 125.9204 | 0 | 0 | 118.3985
6980 | 56.1174 | 3.5762 | 4.5016 | 30.87 | 0 | 95.0652 | 0 | 0 | 86.9874
6981 | 67.3649 | 3.1733 | 5.073 | 30.3426 | 0 | 105.9538 | 0 | 0 | 97.7075
6982 | 61.9155 | 3.326 | 6.1558 | 26.3171 | 0 | 97.7144 | 0 | 0 | 88.2325
6983 | 63.4174 | 2.702 | 6.6355 | 28.7107 | 0 | 101.4657 | 0 | 0 | 92.1281
6984 | 45.1799 | 3.3548 | 6.7843 | 28.0728 | 0 | 83.3919 | 0 | 0 | 73.2527
6985 | 84.6353 | 3.0832 | 9.4972 | 27.2173 | 0 | 124.433 | 0 | 0 | 111.8526
6986 | 69.0774 | 2.8235 | 8.1304 | 35.8419 | 0 | 115.8733 | 0 | 0 | 104.9194
6987 | 39.5365 | 3.3569 | 7.1927 | 37.9492 | 0 | 88.0352 | 0 | 0 | 77.4857
6988 | 0 | 3.3719 | 6.3981 | 26.6706 | 0 | 36.4406 | 0 | 0 | 26.6706
6989 | 6.4137 | 3.634 | 4.625 | 26.5087 | 0 | 41.1813 | 0 | 0 | 32.9224
6990 | 30.632 | 3.24 | 3.9432 | 27.4147 | 0 | 65.23 | 0 | 0 | 58.0467
6991 | 35.671 | 3.2034 | 3.5221 | 20.7242 | 0 | 63.1207 | 200 | 0 | 256.3952
6992 | 15.647 | 3.4264 | 2.8982 | 29.4511 | 16.2423 | 67.6649 | 0 | 0 | 61.3403
6993 | 51.2414 | 3.4389 | 2.1414 | 25.0274 | 15.9997 | 97.8488 | 0 | 0 | 92.2685
6994 | 25.8293 | 2.7909 | 1.7681 | 35.0364 | 17.0103 | 82.435 | 0 | 0 | 77.8759
6995 | 0 | 3.4296 | 1.3773 | 27.3068 | 15.9875 | 48.1012 | 0 | 0 | 43.2943
6996 | 0 | 4.124 | 2.3299 | 36.7468 | 13.8529 | 57.0535 | 0 | 0 | 50.5996
6997 | 0 | 3.3697 | 4.1958 | 26.7925 | 6.7397 | 41.0978 | 0 | 200 | 233.5323
6998 | 0 | 2.7907 | 5.6927 | 28.0999 | 7.53 | 44.1132 | 0 | 0 | 35.6299
6999 | 0 | 3.7184 | 5.5561 | 29.0682 | 12.8576 | 51.2002 | 0 | 0 | 41.9257
7000 | 0 | 3.379 | 5.8003 | 29.6196 | 13.1435 | 51.9423 | 0 | 0 | 42.7631
7001 | 0 | 3.543 | 5.5899 | 24.1212 | 19.795 | 53.0492 | 0 | 0 | 43.9162
7002 | 0 | 3.1989 | 4.7683 | 29.7441 | 18.7234 | 56.4347 | 0 | 0 | 48.4675
7003 | 0 | 3.7542 | 5.0108 | 36.8017 | 11.5003 | 57.067 | 0 | 0 | 48.302
7004 | 0 | 3.3912 | 4.7628 | 22.3415 | 0 | 30.4955 | 0 | 0 | 22.3415
7005 | 0 | 3.4515 | 5.5879 | 28.8539 | 0 | 37.8932 | 0 | 0 | 28.8539
7006 | 0 | 3.5981 | 6.0282 | 26.0853 | 0 | 35.7117 | 0 | 0 | 26.0853
7007 | 0 | 3.4764 | 6.6069 | 32.3885 | 0 | 42.4718 | 0 | 0 | 32.3885
7008 | 0 | 3.5989 | 6.2633 | 30.9539 | 0 | 40.8161 | 0 | 0 | 30.9539
7009 | 0 | 2.7985 | 3.2306 | 29.4739 | 0 | 35.503 | 0 | 0 | 29.4739
7010 | 0 | 3.4136 | 4.9346 | 24.9906 | 0 | 33.3387 | 0 | 0 | 24.9906
7011 | 0 | 3.1589 | 4.5641 | 24.1783 | 0 | 31.9013 | 0 | 0 | 24.1783
7012 | 7.4207 | 3.5359 | 6.156 | 25.568 | 0 | 42.6807 | 0 | 0 | 32.9888
7013 | 28.7456 | 3.2347 | 4.3711 | 31.1035 | 0 | 67.4549 | 0 | 0 | 59.8491
7014 | 51.729 | 3.6165 | 3.0604 | 26.719 | 0 | 85.1249 | 0 | 0 | 78.448
7015 | 19.8182 | 3.1222 | 2.8224 | 39.3676 | 0 | 65.1303 | 0 | 0 | 59.1858
7016 | 0 | 2.8929 | 2.0986 | 28.0206 | 8.534 | 41.5461 | 0 | 0 | 36.5546
7017 | 0 | 3.8552 | 1.7436 | 32.1467 | 10.1112 | 47.8567 | 0 | 0 | 42.2579
7018 | 0 | 2.8849 | 1.9834 | 24.5507 | 13.0514 | 42.4704 | 0 | 0 | 37.6022
7019 | 0 | 3.5373 | 2.2739 | 19.9933 | 17.891 | 43.6954 | 0 | 0 | 37.8842
7020 | 0 | 3.7133 | 2.4752 | 27.393 | 16.837 | 50.4185 | 0 | 0 | 44.2301
7021 | 0 | 3.1664 | 1.8702 | 25.5826 | 11.7693 | 42.3885 | 0 | 0 | 37.3519
7022 | 0 | 2.7192 | 2.2301 | 28.0578 | 14.2222 | 47.2293 | 0 | 0 | 42.28
7023 | 0 | 3.3238 | 2.3118 | 26.0786 | 14.6959 | 46.4101 | 0 | 0 | 40.7745
7024 | 0 | 3.8134 | 1.9 | 26.9382 | 11.8958 | 44.5474 | 0 | 0 | 38.834
7025 | 0 | 3.0519 | 1.9367 | 24.442 | 11.8502 | 41.2808 | 0 | 0 | 36.2922
7026 | 0 | 3.3909 | 1.5167 | 29.2093 | 3.6271 | 37.744 | 0 | 0 | 32.8364
7027 | 0 | 3.5727 | 1.4117 | 37.435 | 12.9251 | 55.3445 | 0 | 0 | 50.3601
7028 | 0 | 2.4183 | 1.1486 | 31.0844 | 0 | 34.6513 | 0 | 0 | 31.0844
7029 | 0 | 2.9855 | 1.2344 | 31.0859 | 0 | 35.3058 | 0 | 0 | 31.0859
7030 | 0 | 3.3902 | 1.1264 | 28.0035 | 0 | 32.5201 | 0 | 0 | 28.0035
7031 | 0 | 3.5834 | 1.1609 | 24.2706 | 0 | 29.0149 | 0 | 0 | 24.2706
7032 | 0 | 3.6842 | 1.4945 | 24.0249 | 0 | 29.2037 | 0 | 0 | 24.0249
7033 | 0 | 3.5853 | 2.1636 | 24.115 | 0 | 29.864 | 0 | 0 | 24.115
7034 | 0 | 2.2949 | 1.767 | 26.6407 | 0 | 30.7025 | 0 | 0 | 26.6407
7035 | 0 | 3.1628 | 2.6204 | 26.0407 | 0 | 31.8239 | 0 | 0 | 26.0407
7036 | 0 | 3.0561 | 3.8285 | 32.6589 | 0 | 39.5435 | 0 | 0 | 32.6589
7037 | 0 | 2.9252 | 3.4779 | 27.2326 | 0 | 33.6356 | 0 | 0 | 27.2326
7038 | 0 | 2.8068 | 2.8525 | 26.1635 | 0 | 31.8228 | 0 | 0 | 26.1635
7039 | 0 | 3.1378 | 2.7114 | 29.5122 | 0 | 35.3614 | 0 | 0 | 29.5122
7040 | 0 | 3.5838 | 1.9321 | 25.1006 | 22.437 | 53.0535 | 0 | 0 | 47.5376
7041 | 0 | 3.1029 | 1.7582 | 24.7813 | 12.7979 | 42.4403 | 0 | 0 | 37.5792
7042 | 0 | 2.9604 | 1.4747 | 31.8209 | 9.6805 | 45.9365 | 0 | 0 | 41.5015
7043 | 0 | 3.2654 | 1.8335 | 24.4928 | 20.0596 | 49.6513 | 0 | 0 | 44.5524
7044 | 0 | 3.2038 | 2.0907 | 23.5096 | 20.7508 | 49.5549 | 0 | 0 | 44.2604
7045 | 0 | 2.5186 | 2.2196 | 27.4453 | 15.8158 | 47.9994 | 0 | 0 | 43.2611
7046 | 0 | 3.2728 | 2.2605 | 28.2622 | 20.9347 | 54.7302 | 0 | 0 | 49.197
7047 | 0 | 3.2478 | 2.1706 | 31.3014 | 5.938 | 42.6579 | 0 | 0 | 37.2394
7048 | 0 | 3.444 | 2.1677 | 26.284 | 12.6685 | 44.5642 | 0 | 0 | 38.9525
7049 | 0 | 3.1198 | 2.1706 | 25.6158 | 9.6453 | 40.5516 | 0 | 0 | 35.2611
7050 | 0 | 2.9699 | 1.5861 | 24.3815 | 6.8483 | 35.7859 | 0 | 0 | 31.2298
7051 | 0 | 3.0286 | 1.239 | 28.6036 | 13.2863 | 46.1576 | 0 | 0 | 41.8899
7052 | 0 | 3.6073 | 1.0185 | 23.2946 | 0 | 27.9205 | 200 | 0 | 223.2946
7053 | 0 | 2.8199 | 1.0722 | 26.9843 | 0 | 30.8764 | 0 | 0 | 26.9843
7054 | 0 | 3.1839 | 1.1947 | 22.5587 | 0 | 26.9373 | 0 | 0 | 22.5587
7055 | 0 | 3.0816 | 1.2542 | 30.7523 | 0 | 35.0881 | 0 | 0 | 30.7523
7056 | 0 | 2.7939 | 2.7569 | 36.2401 | 0 | 41.7909 | 0 | 0 | 36.2401
7057 | 0 | 3.0091 | 4.3028 | 34.5315 | 0 | 41.8435 | 0 | 0 | 34.5315
7058 | 10.4174 | 3.0858 | 3.9504 | 30.7439 | 0 | 48.1975 | 0 | 0 | 41.1613
7059 | 49.6818 | 2.9894 | 3.9026 | 27.396 | 0 | 83.9698 | 0 | 0 | 77.0778
7060 | 82.1448 | 2.988 | 3.8123 | 33.1707 | 0 | 122.1159 | 0 | 0 | 115.3156
7061 | 92.5947 | 3.1961 | 3.101 | 27.6835 | 0 | 126.5753 | 0 | 0 | 120.2782
7062 | 90.0687 | 2.8139 | 2.6907 | 27.6176 | 0 | 123.1909 | 0 | 0 | 117.6863
7063 | 60.1027 | 3.3611 | 2.631 | 30.2926 | 0 | 96.3874 | 0 | 0 | 90.3953
7064 | 49.7185 | 2.5068 | 2.8982 | 28.4461 | 21.8862 | 105.4558 | 0 | 0 | 100.0508
7065 | 41.2369 | 3.5257 | 2.6828 | 16.9574 | 17.6846 | 82.0874 | 0 | 200 | 275.8789
7066 | 44.0531 | 3.5021 | 2.3821 | 22.0197 | 13.4892 | 85.4461 | 0 | 0 | 79.562
7067 | 43.2462 | 3.6472 | 2.2509 | 21.0687 | 15.72 | 85.933 | 0 | 0 | 80.0349
7068 | 15.1813 | 3.8182 | 4.4931 | 24.781 | 16.4158 | 64.6894 | 0 | 0 | 56.3781
7069 | 0 | 3.0358 | 6.0849 | 30.405 | 23.3559 | 62.8817 | 0 | 0 | 53.7609
7070 | 0 | 2.9082 | 6.9807 | 29.5954 | 10.7489 | 50.2331 | 0 | 0 | 40.3442
7071 | 0 | 3.2041 | 7.8284 | 21.465 | 17.961 | 50.4585 | 0 | 0 | 39.426
7072 | 3.2585 | 3.7259 | 7.3969 | 36.0854 | 5.6212 | 56.0879 | 0 | 0 | 44.965
7073 | 22.9322 | 3.4765 | 3.8081 | 29.0027 | 15.0481 | 74.2677 | 0 | 0 | 66.983
7074 | 55.391 | 3.5125 | 2.7642 | 28.3988 | 12.5015 | 102.5681 | 0 | 0 | 96.2913
7075 | 42.7929 | 2.5824 | 2.0995 | 30.042 | 10.5603 | 88.0771 | 0 | 0 | 83.3952
7076 | 78.3515 | 3.6287 | 1.9162 | 28.5622 | 0 | 112.4585 | 0 | 0 | 106.9137
7077 | 73.9427 | 3.2287 | 1.7772 | 30.7819 | 0 | 109.7305 | 0 | 0 | 104.7247
7078 | 70.8693 | 3.4878 | 1.6929 | 22.1258 | 0 | 98.1758 | 0 | 0 | 92.9951
7079 | 84.1384 | 3.8052 | 1.5565 | 26.3318 | 0 | 115.832 | 0 | 0 | 110.4703
7080 | 78.5146 | 3.7746 | 2.7569 | 31.1987 | 0 | 116.2449 | 0 | 0 | 109.7133
7081 | 67.1327 | 3.2256 | 4.5288 | 33.4364 | 0 | 108.3235 | 0 | 0 | 100.5691
7082 | 26.5846 | 3.3817 | 3.4587 | 31.8263 | 0 | 65.2513 | 0 | 0 | 58.4109
7083 | 0 | 3.7234 | 4.0397 | 24.2775 | 0 | 32.0406 | 0 | 0 | 24.2775
7084 | 0 | 3.4439 | 4.3015 | 29.237 | 0 | 36.9824 | 0 | 0 | 29.237
7085 | 13.3424 | 3.4908 | 3.8993 | 28.6937 | 0 | 49.4262 | 0 | 0 | 42.0361
7086 | 72.5387 | 2.5326 | 3.7959 | 34.9601 | 0 | 113.8272 | 0 | 0 | 107.4987
7087 | 94.0916 | 3.6261 | 3.9333 | 31.0666 | 0 | 132.7177 | 0 | 0 | 125.1582
7088 | 82.136 | 3.3858 | 3.3056 | 33.4006 | 10.6761 | 132.9041 | 0 | 0 | 126.2127
7089 | 83.4447 | 3.5241 | 2.5474 | 31.6754 | 13.2899 | 134.4816 | 0 | 0 | 128.41
7090 | 80.2789 | 2.6776 | 1.7681 | 28.7317 | 4.072 | 117.5284 | 0 | 0 | 113.0826
7091 | 88.6841 | 3.037 | 1.3773 | 19.1847 | 6.0984 | 118.3814 | 0 | 0 | 113.9671
7092 | 55.5799 | 3.625 | 2.3299 | 32.8637 | 5.4078 | 99.8064 | 0 | 0 | 93.8515
7093 | 17.2309 | 3.4827 | 2.3888 | 30.3117 | 16.3876 | 69.8016 | 0 | 0 | 63.9301
7094 | 0 | 3.9104 | 2.0295 | 31.6508 | 20.8256 | 58.4163 | 0 | 0 | 52.4764
7095 | 0 | 3.2522 | 1.9886 | 24.5495 | 8.8471 | 38.6375 | 0 | 0 | 33.3966
7096 | 1.9558 | 2.949 | 2.2272 | 26.7964 | 23.3979 | 57.3264 | 0 | 0 | 52.1502
7097 | 27.2197 | 3.2045 | 2.1199 | 30.9993 | 14.3095 | 77.8528 | 0 | 0 | 72.5284
7098 | 64.3351 | 2.99 | 1.5861 | 25.3022 | 20.3896 | 114.603 | 0 | 0 | 110.0269
7099 | 71.1194 | 3.6244 | 1.239 | 28.656 | 13.0945 | 117.7334 | 0 | 0 | 112.8699
7100 | 75.3552 | 3.1716 | 1.0185 | 31.1872 | 0 | 110.7326 | 0 | 0 | 106.5424
7101 | 78.7303 | 3.5831 | 1.0722 | 22.4335 | 0 | 105.819 | 0 | 0 | 101.1638
7102 | 58.6919 | 3.3282 | 1.1947 | 31.3605 | 0 | 94.5753 | 0 | 0 | 90.0524
7103 | 61.0724 | 2.9542 | 1.2542 | 30.2799 | 0 | 95.5608 | 0 | 0 | 91.3523
7104 | 86.6577 | 2.7868 | 2.7569 | 31.0812 | 0 | 123.2826 | 0 | 0 | 117.7389
7105 | 85.643 | 3.238 | 4.3028 | 26.1839 | 0 | 119.3676 | 0 | 0 | 111.8269
7106 | 34.4755 | 3.2101 | 3.0702 | 25.0489 | 0 | 65.8047 | 0 | 0 | 59.5244
7107 | 0 | 3.6783 | 3.2171 | 23.2677 | 0 | 30.1632 | 0 | 0 | 23.2677
7108 | 0 | 4.0404 | 3.1833 | 27.7044 | 0 | 34.9281 | 0 | 0 | 27.7044
7109 | 10.5355 | 2.7713 | 3.0285 | 35.591 | 0 | 51.9261 | 0 | 0 | 46.1264
7110 | 44.0422 | 3.2721 | 2.6907 | 27.1289 | 0 | 77.134 | 0 | 0 | 71.1711
7111 | 72.0949 | 3.709 | 2.9737 | 25.4875 | 0 | 104.2651 | 0 | 0 | 97.5824
7112 | 60.4533 | 3.5887 | 2.7624 | 28.5954 | 12.7835 | 108.1833 | 0 | 0 | 101.8322
7113 | 65.9791 | 3.392 | 1.8708 | 30.7902 | 17.1049 | 119.137 | 200 | 0 | 313.8741
7114 | 53.5663 | 3.1909 | 1.7681 | 27.7293 | 18.1305 | 104.3852 | 0 | 0 | 99.4261
7115 | 61.3741 | 3.1998 | 1.3773 | 29.9671 | 12.2304 | 108.1487 | 0 | 0 | 103.5716
7116 | 53.9946 | 3.1755 | 2.3299 | 34.2305 | 13.7561 | 107.4867 | 0 | 0 | 101.9813
7117 | 31.3765 | 2.8548 | 2.3888 | 30.8685 | 14.5095 | 81.9981 | 0 | 0 | 76.7545
7118 | 43.5387 | 2.8407 | 2.0295 | 30.0441 | 2.5222 | 80.9751 | 0 | 0 | 76.1049
7119 | 22.8386 | 3.3096 | 1.9886 | 30.2035 | -0.87618 | 57.4643 | 0 | 0 | 52.166
7120 | 4.65 | 3.2274 | 2.2272 | 24.7609 | 13.7599 | 48.6255 | 0 | 0 | 43.1708
7121 | 34.0951 | 3.7024 | 2.1199 | 29.6727 | 11.4066 | 80.9968 | 0 | 0 | 75.1744
7122 | 82.1626 | 3.5226 | 1.5861 | 22.404 | 10.1649 | 119.8402 | 0 | 0 | 114.7315
7123 | 42.8449 | 2.9314 | 1.239 | 28.7711 | 12.3542 | 88.1407 | 0 | 0 | 83.9702
7124 | 75.0733 | 2.8223 | 1.0185 | 24.9325 | 0 | 103.8466 | 0 | 0 | 100.0058
7125 | 77.0587 | 3.5761 | 1.0722 | 26.6106 | 0 | 108.3175 | 0 | 0 | 103.6693
7126 | 81.2869 | 3.0348 | 1.1947 | 23.7231 | 0 | 109.2395 | 0 | 0 | 105.0101
7127 | 77.6376 | 3.5862 | 1.2542 | 27.8316 | 0 | 110.3096 | 0 | 0 | 105.4692
7128 | 84.5426 | 3.8989 | 2.7569 | 32.301 | 0 | 123.4994 | 0 | 0 | 116.8436
7129 | 82.2313 | 3.5612 | 4.3028 | 24.6783 | 0 | 114.7736 | 0 | 0 | 106.9096
7130 | 40.6333 | 3.501 | 3.2128 | 22.5568 | 0 | 69.9039 | 0 | 0 | 63.1901
7131 | 7.8474 | 3.9081 | 4.1082 | 25.9626 | 0 | 41.8264 | 0 | 0 | 33.81
7132 | 0.56479 | 3.4946 | 4.022 | 35.2534 | 0 | 43.3348 | 0 | 0 | 35.8182
7133 | 19.106 | 3.4377 | 3.8993 | 21.4579 | 0 | 47.9009 | 0 | 0 | 40.564
7134 | 79.5733 | 2.8304 | 4.0169 | 27.6476 | 0 | 114.0682 | 0 | 0 | 107.2209
7135 | 50.7466 | 3.1661 | 4.0704 | 30.6925 | 0 | 88.6756 | 0 | 200 | 281.4391
7136 | 47.7762 | 3.4027 | 3.9846 | 23.5735 | 8.6449 | 87.3819 | 0 | 0 | 79.9946
7137 | 64.015 | 2.1502 | 3.2241 | 32.9568 | 20.294 | 122.6402 | 0 | 0 | 117.2658
7138 | 50.7907 | 3.8001 | 2.3821 | 27.0133 | 10.6922 | 94.6785 | 0 | 0 | 88.4963
7139 | 38.5294 | 3.2011 | 1.4167 | 31.0243 | 25.9222 | 100.0938 | 0 | 0 | 95.4759
7140 | 1.2529 | 3.4745 | 2.3299 | 27.5258 | 17.1434 | 51.7266 | 0 | 0 | 45.9221
7141 | 0 | 3.5599 | 2.3888 | 31.0098 | 22.1034 | 59.0619 | 0 | 0 | 53.1132
7142 | 0 | 3.3828 | 2.0295 | 31.1454 | 20.5619 | 57.1195 | 0 | 0 | 51.7072
7143 | 0 | 2.7754 | 1.9886 | 27.4137 | 17.5894 | 49.7671 | 0 | 0 | 45.0031
7144 | 0.10282 | 3.4153 | 2.2272 | 33.9165 | 8.9004 | 48.5624 | 0 | 0 | 42.9198
7145 | 17.2788 | 3.9578 | 2.1199 | 28.5347 | 11.2974 | 63.1886 | 0 | 0 | 57.1109
7146 | 71.4088 | 3.532 | 1.5861 | 34.4404 | 20.4851 | 131.4524 | 0 | 0 | 126.3343
7147 | 80.7945 | 3.191 | 1.239 | 26.1654 | 9.4137 | 120.8037 | 0 | 0 | 116.3737
7148 | 71.0977 | 3.181 | 1.0185 | 24.9717 | 0 | 100.2689 | 0 | 0 | 96.0694
7149 | 71.3162 | 3.3703 | 1.0722 | 32.6841 | 0 | 108.4428 | 0 | 0 | 104.0003
7150 | 62.7952 | 3.4823 | 1.1947 | 32.8585 | 0 | 100.3307 | 0 | 0 | 95.6537
7151 | 77.5834 | 3.2798 | 1.2542 | 36.4932 | 0 | 118.6106 | 0 | 0 | 114.0766
7152 | 72.1624 | 3.4042 | 2.7569 | 24.7721 | 0 | 103.0955 | 0 | 0 | 96.9344
7153 | 76.4393 | 3.5284 | 4.3028 | 22.5738 | 0 | 106.8443 | 0 | 0 | 99.0131
7154 | 90.9812 | 3.8592 | 4.3602 | 25.546 | 0 | 124.7466 | 0 | 0 | 116.5272
7155 | 78.7005 | 2.5771 | 5.2049 | 32.2904 | 0 | 118.7729 | 0 | 0 | 110.9908
7156 | 27.7693 | 3.498 | 5.9788 | 26.2951 | 0 | 63.5412 | 0 | 0 | 54.0644
7157 | 20.7545 | 3.1769 | 5.4958 | 26.6243 | 0 | 56.0515 | 0 | 0 | 47.3788
7158 | 67.1139 | 2.7142 | 5.1957 | 32.2082 | 0 | 107.2319 | 0 | 0 | 99.3221
7159 | 52.7615 | 3.4971 | 4.9615 | 24.733 | 0 | 85.9531 | 0 | 0 | 77.4945
7160 | 52.1584 | 2.583 | 4.7995 | 28.7188 | 14.2591 | 102.5188 | 0 | 0 | 95.1363
7161 | 58.791 | 3.6594 | 4.6452 | 23.4039 | 18.0769 | 108.5763 | 0 | 0 | 100.2717
7162 | 52.8819 | 2.9745 | 3.9529 | 26.001 | 9.0564 | 94.8667 | 0 | 0 | 87.9393
7163 | 10.4764 | 3.1875 | 2.8576 | 31.4145 | 13.1246 | 61.0606 | 0 | 0 | 55.0155
7164 | 2.0716 | 3.5432 | 2.3299 | 25.8188 | 10.2228 | 43.9864 | 0 | 0 | 38.1132
7165 | 0 | 3.2677 | 2.3888 | 32.5266 | 5.5607 | 43.7438 | 0 | 0 | 38.0873
7166 | 0 | 3.1937 | 3.4601 | 31.5243 | 7.8777 | 46.0557 | 0 | 0 | 39.402
7167 | 0 | 3.4937 | 4.1359 | 23.9325 | 11.9287 | 43.4909 | 0 | 0 | 35.8612
7168 | 0 | 3.2393 | 3.8615 | 32.757 | 12.9777 | 52.8354 | 0 | 0 | 45.7346
7169 | 0 | 3.2383 | 3.2513 | 20.9911 | 13.6437 | 41.1244 | 0 | 0 | 34.6347
7170 | 0 | 2.976 | 1.9531 | 30.3135 | 19.5019 | 54.7445 | 0 | 0 | 49.8154
7171 | 0 | 3.3187 | 1.5255 | 27.8194 | 14.727 | 47.3906 | 0 | 0 | 42.5464
7172 | 0 | 2.977 | 1.974 | 34.5287 | 0 | 39.4797 | 0 | 0 | 34.5287
7173 | 0 | 3.2193 | 2.189 | 29.3466 | 0 | 34.7549 | 0 | 0 | 29.3466
7174 | 0 | 3.5348 | 3.0075 | 33.1363 | 0 | 39.6785 | 200 | 0 | 233.1363
7175 | 0 | 3.4638 | 2.9083 | 28.9788 | 0 | 35.3508 | 0 | 0 | 28.9788
7176 | 0 | 2.9218 | 3.1647 | 26.4533 | 0 | 32.5398 | 0 | 0 | 26.4533
7177 | 0 | 3.4522 | 2.1992 | 32.4034 | 0 | 38.0548 | 0 | 0 | 32.4034
7178 | 0 | 3.2849 | 1.9945 | 26.0941 | 0 | 31.3735 | 0 | 0 | 26.0941
7179 | 0 | 3.2392 | 4.1506 | 29.3239 | 0 | 36.7138 | 0 | 0 | 29.3239
7180 | 0 | 3.1867 | 6.91 | 26.43 | 0 | 36.5267 | 0 | 0 | 26.43
7181 | 0 | 2.8855 | 5.7949 | 28.7398 | 0 | 37.4202 | 0 | 0 | 28.7398
7182 | 0 | 3.1223 | 5.288 | 22.2975 | 0 | 30.7078 | 0 | 0 | 22.2975
7183 | 0 | 3.5644 | 5.3312 | 31.2356 | 0 | 40.1312 | 0 | 0 | 31.2356
7184 | 0 | 2.9405 | 4.1744 | 26.8219 | 13.8179 | 47.7547 | 0 | 0 | 40.6398
7185 | 0 | 3.2102 | 5.3285 | 28.3655 | 20.2116 | 57.1158 | 0 | 0 | 48.5771
7186 | 0 | 3.7738 | 3.8019 | 31.6627 | 10.4803 | 49.7187 | 0 | 0 | 42.1429
7187 | 0 | 3.3662 | 2.2739 | 18.1426 | 6.4739 | 30.2567 | 0 | 0 | 24.6166
7188 | 0 | 3.206 | 3.104 | 32.9446 | 10.395 | 49.6495 | 0 | 0 | 43.3395
7189 | 0 | 3.0517 | 2.7181 | 30.168 | 7.2149 | 43.1526 | 0 | 0 | 37.3828
7190 | 0 | 4.0464 | 3.0578 | 39.4129 | 13.2225 | 59.7395 | 0 | 0 | 52.6353
7191 | 0 | 3.1397 | 4.0997 | 19.7545 | 14.7917 | 41.7857 | 0 | 0 | 34.5462
7192 | 0 | 2.6957 | 5.3367 | 24.9341 | 8.9213 | 41.8878 | 0 | 0 | 33.8554
7193 | 0 | 2.8016 | 5.9621 | 25.5386 | 23.6472 | 57.9495 | 0 | 0 | 49.1857
7194 | 0 | 2.837 | 5.7949 | 25.9857 | 21.8717 | 56.4893 | 0 | 200 | 247.8575
7195 | 0 | 4.0455 | 5.6384 | 22.5118 | 11.1662 | 43.3619 | 0 | 0 | 33.678
7196 | 0 | 2.9725 | 5.6948 | 25.3151 | 0 | 33.9825 | 0 | 0 | 25.3151
7197 | 0 | 3.3636 | 5.6215 | 23.8891 | 0 | 32.8742 | 0 | 0 | 23.8891
7198 | 0 | 3.4983 | 5.8048 | 29.1804 | 0 | 38.4834 | 0 | 0 | 29.1804
7199 | 0 | 3.3994 | 6.3943 | 28.3537 | 0 | 38.1473 | 0 | 0 | 28.3537
7200 | 0 | 3.3285 | 7.0059 | 18.9772 | 0 | 29.3117 | 0 | 0 | 18.9772
7201 | 0 | 3.4498 | 7.5136 | 25.7376 | 0 | 36.7009 | 0 | 0 | 25.7376
7202 | 0 | 2.9304 | 5.9589 | 26.595 | 0 | 35.4843 | 0 | 0 | 26.595
7203 | 0 | 3.6578 | 4.9856 | 37.069 | 0 | 45.7123 | 0 | 0 | 37.069
7204 | 0 | 3.1045 | 4.9796 | 28.1545 | 0 | 36.2386 | 0 | 0 | 28.1545
7205 | 13.9016 | 3.1691 | 7.1351 | 20.7591 | 0 | 44.9649 | 0 | 0 | 34.6607
7206 | 51.7786 | 2.9272 | 6.9892 | 27.2009 | 0 | 88.8959 | 0 | 0 | 78.9795
7207 | 90.5717 | 3.531 | 7.4887 | 34.3898 | 0 | 135.9812 | 0 | 0 | 124.9615
7208 | 82.1088 | 3.1171 | 7.0608 | 31.3055 | 13.4667 | 137.0589 | 0 | 0 | 126.881
7209 | 86.058 | 3.085 | 7.085 | 29.5626 | 18.7324 | 144.5229 | 0 | 0 | 134.353
7210 | 64.7404 | 3.399 | 6.9007 | 19.1849 | 10.6198 | 104.8447 | 0 | 0 | 94.5451
7211 | 5.4892 | 3.3267 | 6.8179 | 33.7691 | 14.2549 | 63.6577 | 0 | 0 | 53.5131
7212 | 0.044298 | 3.2752 | 7.4358 | 26.8681 | 12.0013 | 49.6248 | 0 | 0 | 38.9138
7213 | 18.8258 | 3.0838 | 7.953 | 27.2776 | 20.0441 | 77.1842 | 0 | 0 | 66.1475
7214 | 74.9994 | 3.0311 | 7.7487 | 34.6741 | 18.5908 | 139.0441 | 0 | 0 | 128.2643
7215 | 7.886 | 3.0749 | 8.5354 | 25.5851 | 7.9266 | 53.0081 | 0 | 0 | 41.3978
7216 | 31.8648 | 3.5167 | 8.8913 | 25.1969 | 14.3654 | 83.835 | 0 | 0 | 71.427
7217 | 89.2557 | 3.0693 | 7.9975 | 19.8648 | 14.4747 | 134.6619 | 0 | 0 | 123.5952
7218 | 59.5104 | 2.9026 | 6.344 | 32.1197 | 14.6519 | 115.5286 | 0 | 0 | 106.2819
7219 | 0 | 3.4766 | 5.8204 | 22.9662 | 10.5802 | 42.8434 | 0 | 0 | 33.5464
7220 | 0 | 3.5695 | 5.8295 | 28.3862 | 0 | 37.7853 | 0 | 0 | 28.3862
7221 | 0 | 3.4687 | 5.7135 | 29.5488 | 0 | 38.731 | 0 | 0 | 29.5488
7222 | 0 | 2.7082 | 5.3945 | 39.9719 | 0 | 48.0747 | 0 | 0 | 39.9719
7223 | 0 | 3.6469 | 5.4256 | 30.5866 | 0 | 39.659 | 0 | 0 | 30.5866
7224 | 0 | 3.1697 | 5.91 | 19.792 | 0 | 28.8716 | 0 | 200 | 219.792
7225 | 0 | 3.2782 | 7.7987 | 29.838 | 0 | 40.9149 | 0 | 0 | 29.838
7226 | 0 | 2.8634 | 10.5688 | 27.1719 | 0 | 40.6042 | 0 | 0 | 27.1719
7227 | 0 | 3.2018 | 8.95 | 21.755 | 0 | 33.9068 | 0 | 0 | 21.755
7228 | 0 | 3.4195 | 8.5636 | 29.5593 | 0 | 41.5424 | 0 | 0 | 29.5593
7229 | 0 | 2.8407 | 8.9838 | 31.4505 | 0 | 43.275 | 0 | 0 | 31.4505
7230 | 0 | 3.1952 | 8.9791 | 32.4684 | 0 | 44.6427 | 0 | 0 | 32.4684
7231 | 0 | 3.2601 | 8.9533 | 18.938 | 0 | 31.1514 | 0 | 0 | 18.938
7232 | 0.24901 | 3.115 | 8.7314 | 24.4187 | 17.1953 | 53.7095 | 0 | 0 | 41.863
7233 | 11.231 | 3.2041 | 8.4662 | 27.4632 | 10.8645 | 61.229 | 0 | 0 | 49.5587
7234 | 41.8696 | 3.1494 | 8.0286 | 29.3964 | -2.2541 | 80.1898 | 0 | 0 | 69.0118
7235 | 17.9178 | 3.2695 | 7.2255 | 26.8042 | 11.7296 | 66.9467 | 0 | 0 | 56.4516
7236 | 79.7481 | 3.0203 | 6.6494 | 17.2824 | 14.1538 | 120.854 | 200 | 0 | 311.1843
7237 | 48.4054 | 3.2048 | 6.0015 | 31.3132 | 11.7557 | 100.6805 | 0 | 0 | 91.4743
7238 | 18.0634 | 3.3526 | 5.7564 | 27.1475 | 14.8212 | 69.1411 | 0 | 0 | 60.0321
7239 | 0 | 3.1725 | 6.2079 | 32.5108 | 17.6237 | 59.5149 | 0 | 0 | 50.1345
7240 | 0 | 3.0532 | 6.2188 | 20.1184 | 9.0719 | 38.4624 | 0 | 0 | 29.1904
7241 | 0 | 3.4967 | 6.0284 | 30.917 | 10.5066 | 50.9487 | 0 | 0 | 41.4236
7242 | 0 | 3.2135 | 4.9218 | 23.892 | 12.1063 | 44.1335 | 0 | 0 | 35.9983
7243 | 0 | 3.0407 | 3.9473 | 20.3951 | 17.9302 | 45.3134 | 0 | 0 | 38.3253
7244 | 0 | 3.5322 | 3.7477 | 35.4851 | 0 | 42.765 | 0 | 0 | 35.4851
7245 | 0 | 3.6499 | 3.6936 | 34.1003 | 0 | 41.4439 | 0 | 0 | 34.1003
7246 | 0 | 3.3424 | 3.8672 | 21.3491 | 0 | 28.5587 | 0 | 0 | 21.3491
7247 | 0 | 3.7665 | 4.4518 | 26.8991 | 0 | 35.1174 | 0 | 0 | 26.8991
7248 | 0 | 2.7429 | 5.265 | 20.7257 | 0 | 28.7336 | 0 | 0 | 20.7257
7249 | 0 | 2.9208 | 6.9872 | 35.9204 | 0 | 45.8283 | 0 | 0 | 35.9204
7250 | 0 | 2.8283 | 9.8869 | 19.5208 | 0 | 32.2359 | 0 | 0 | 19.5208
7251 | 0 | 2.8056 | 8.7861 | 18.6993 | 0 | 30.291 | 0 | 0 | 18.6993
7252 | 0 | 3.225 | 8.3579 | 28.5435 | 0 | 40.1263 | 0 | 0 | 28.5435
7253 | 0.13573 | 3.7625 | 8.2151 | 28.9031 | 0 | 41.0164 | 0 | 200 | 229.0389
7254 | 20.4323 | 2.7888 | 7.5277 | 31.2878 | 0 | 62.0366 | 0 | 0 | 51.7201
7255 | 88.5973 | 3.462 | 7.7744 | 31.372 | 0 | 131.2057 | 0 | 0 | 119.9693
7256 | 58.8846 | 3.786 | 8.3887 | 34.0033 | 16.6995 | 121.762 | 0 | 0 | 109.5874
7257 | 75.4203 | 3.6402 | 7.6513 | 20.3652 | 9.32 | 116.3969 | 0 | 0 | 105.1054
7258 | 86.6028 | 3.3136 | 7.4196 | 35.8754 | 11.0519 | 144.2633 | 0 | 0 | 133.5301
7259 | 81.7563 | 3.318 | 6.5055 | 26.4127 | 15.6841 | 133.6767 | 0 | 0 | 123.8531
7260 | 65.8479 | 3.4595 | 6.1944 | 29.9848 | 15.9418 | 121.4283 | 0 | 0 | 111.7745
7261 | 41.7435 | 3.186 | 6.2676 | 30.2946 | 14.244 | 95.7358 | 0 | 0 | 86.2821
7262 | 70.3878 | 3.5894 | 5.8385 | 18.5619 | 20.0693 | 118.4469 | 0 | 0 | 109.019
7263 | 59.0265 | 3.4268 | 5.1774 | 33.4162 | 10.8528 | 111.8999 | 0 | 0 | 103.2956
7264 | 39.6376 | 3.0122 | 2.3371 | 26.1276 | 10.1991 | 81.3135 | 0 | 0 | 75.9642
7265 | 0 | 3.4845 | 2.2272 | 22.0025 | 21.0154 | 48.7297 | 0 | 0 | 43.0179
7266 | 0 | 2.9938 | 2.1199 | 28.2424 | 14.0638 | 47.4199 | 0 | 0 | 42.3062
7267 | 0 | 3.5735 | 1.5861 | 19.9723 | 17.4022 | 42.5341 | 0 | 0 | 37.3745
7268 | 0 | 3.5454 | 1.239 | 27.3937 | 0 | 32.1781 | 0 | 0 | 27.3937
7269 | 0 | 3.6533 | 1.0185 | 30.8161 | 0 | 35.4879 | 0 | 0 | 30.8161
7270 | 0 | 3.7836 | 1.2145 | 33.1834 | 0 | 38.1815 | 0 | 0 | 33.1834
7271 | 0 | 3.0335 | 1.8552 | 27.3514 | 0 | 32.2401 | 0 | 0 | 27.3514
7272 | 0 | 3.3399 | 3.0077 | 31.4089 | 0 | 37.7566 | 0 | 0 | 31.4089
7273 | 0 | 3.2747 | 4.7554 | 25.3325 | 0 | 33.3626 | 0 | 0 | 25.3325
7274 | 0 | 2.9546 | 8.7178 | 25.6153 | 0 | 37.2877 | 0 | 0 | 25.6153
7275 | 0 | 3.3088 | 8.2944 | 24.1831 | 0 | 35.7863 | 0 | 0 | 24.1831
7276 | 0 | 3.8687 | 7.6725 | 25.0701 | 0 | 36.6113 | 0 | 0 | 25.0701
7277 | 1.7735 | 3.1559 | 7.1668 | 29.2895 | 0 | 41.3858 | 0 | 0 | 31.063
7278 | 18.6406 | 3.0565 | 6.1489 | 22.972 | 0 | 50.8179 | 0 | 0 | 41.6125
7279 | 78.4734 | 3.2821 | 5.3431 | 28.9717 | 0 | 116.0703 | 0 | 0 | 107.4451
7280 | 87.7984 | 3.3895 | 5.2357 | 33.7002 | 10.8418 | 140.9656 | 0 | 0 | 132.3404
7281 | 43.9711 | 3.1166 | 4.8674 | 30.7011 | 15.4569 | 98.113 | 0 | 0 | 90.1291
7282 | 14.8043 | 3.165 | 4.8482 | 19.2436 | 14.8466 | 56.9078 | 0 | 0 | 48.8946
7283 | 6.6455 | 2.9378 | 5.262 | 27.7247 | 23.3502 | 65.9202 | 0 | 0 | 57.7205
7284 | 43.2087 | 3.1695 | 3.6918 | 30.9134 | 6.2978 | 87.2812 | 0 | 0 | 80.4198
7285 | 68.9389 | 3.4755 | 2.3299 | 33.2868 | 3.6874 | 111.7185 | 0 | 0 | 105.9132
7286 | 73.4451 | 2.9601 | 2.3888 | 30.169 | 21.8107 | 130.7737 | 0 | 0 | 125.4248
7287 | 26.0053 | 3.704 | 2.7731 | 25.4554 | 20.2395 | 78.1773 | 0 | 0 | 71.7002
7288 | 0 | 3.3609 | 2.6211 | 27.5148 | 10.3089 | 43.8056 | 0 | 0 | 37.8236
7289 | 0 | 3.0781 | 4.4317 | 33.0838 | 11.0859 | 51.6795 | 0 | 0 | 44.1697
7290 | 0 | 3.7258 | 3.2513 | 32.2459 | 11.8922 | 51.1152 | 0 | 0 | 44.1381
7291 | 0 | 3.4794 | 1.5861 | 30.9716 | 18.9928 | 55.0299 | 0 | 0 | 49.9644
7292 | 0 | 2.5986 | 1.3188 | 27.544 | 0 | 31.4614 | 0 | 0 | 27.544
7293 | 0 | 3.4131 | 1.3506 | 25.7924 | 0 | 30.5561 | 0 | 0 | 25.7924
7294 | 0 | 2.7327 | 1.0722 | 32.8468 | 0 | 36.6517 | 0 | 0 | 32.8468
7295 | 0 | 3.6879 | 1.1947 | 28.7697 | 0 | 33.6523 | 0 | 0 | 28.7697
7296 | 0 | 3.5184 | 1.3953 | 35.2303 | 0 | 40.1439 | 200 | 0 | 235.2303
7297 | 0 | 3.4716 | 3.1323 | 29.9476 | 0 | 36.5514 | 0 | 0 | 29.9476
7298 | 0 | 3.7836 | 6.4772 | 29.5769 | 0 | 39.8378 | 0 | 0 | 29.5769
7299 | 0 | 3.7315 | 4.2783 | 36.1266 | 0 | 44.1364 | 0 | 0 | 36.1266
7300 | 0 | 3.4322 | 4.7937 | 30.7362 | 0 | 38.962 | 0 | 200 | 230.7362
7301 | 0 | 3.2843 | 4.6509 | 26.5849 | 0 | 34.5201 | 0 | 0 | 26.5849
7302 | 6.016 | 3.3984 | 3.8267 | 31.1952 | 0 | 44.4362 | 0 | 0 | 37.2112
7303 | 33.2035 | 3.3139 | 4.0169 | 37.031 | 0 | 77.5652 | 0 | 0 | 70.2345
7304 | 73.3569 | 3.4346 | 4.4817 | 32.7607 | 12.8766 | 126.9105 | 0 | 0 | 118.9942
7305 | 57.851 | 2.9674 | 4.5278 | 32.785 | 9.9996 | 108.1308 | 0 | 0 | 100.6356
7306 | 60.0881 | 2.8479 | 4.5775 | 31.6537 | 5.9323 | 105.0995 | 0 | 0 | 97.6741
7307 | 0 | 3.6524 | 4.2147 | 36.7757 | 11.9342 | 56.577 | 0 | 0 | 48.7099
7308 | 0 | 4.2056 | 3.0851 | 29.8786 | 20.5333 | 57.7027 | 0 | 0 | 50.4119
7309 | 0 | 2.4941 | 2.3299 | 32.4223 | 6.134 | 43.3803 | 0 | 0 | 38.5563
7310 | 0 | 3.6637 | 2.3888 | 38.4167 | 11.0326 | 55.5019 | 0 | 0 | 49.4493
7311 | 0 | 3.6011 | 2.172 | 36.8673 | 15.923 | 58.5634 | 0 | 0 | 52.7903
7312 | 0 | 3.0205 | 1.9886 | 25.7702 | 13.29 | 44.0693 | 0 | 0 | 39.0602
7313 | 0 | 3.0684 | 2.2272 | 16.4621 | 4.3027 | 26.0604 | 0 | 0 | 20.7648
7314 | 0 | 3.624 | 2.1199 | 36.6376 | 19.3054 | 61.6869 | 0 | 0 | 55.943
7315 | 0 | 3.512 | 1.5861 | 32.8393 | 27.1206 | 65.058 | 0 | 0 | 59.9599
7316 | 0 | 3.4925 | 1.239 | 32.9781 | 0 | 37.7097 | 0 | 0 | 32.9781
7317 | 0 | 3.6213 | 1.0185 | 34.1425 | 0 | 38.7824 | 0 | 0 | 34.1425
7318 | 0 | 3.6523 | 1.0722 | 30.2502 | 0 | 34.9747 | 0 | 0 | 30.2502
7319 | 0 | 3.6412 | 1.1947 | 32.3278 | 0 | 37.1637 | 0 | 0 | 32.3278
7320 | 0 | 3.3871 | 1.2542 | 32.5252 | 0 | 37.1665 | 0 | 0 | 32.5252
7321 | 0 | 3.213 | 2.7569 | 27.5971 | 0 | 33.567 | 0 | 0 | 27.5971
7322 | 0 | 3.509 | 5.6978 | 37.5691 | 0 | 46.7759 | 0 | 0 | 37.5691
7323 | 0 | 3.3725 | 5.1798 | 25.5084 | 0 | 34.0608 | 0 | 0 | 25.5084
7324 | 0 | 3.2085 | 5.9589 | 33.4642 | 0 | 42.6316 | 0 | 0 | 33.4642
7325 | 0 | 2.9742 | 5.9788 | 26.7852 | 0 | 35.7381 | 0 | 0 | 26.7852
7326 | 0 | 3.1143 | 5.0604 | 28.9048 | 0 | 37.0795 | 0 | 0 | 28.9048
7327 | 0 | 3.1408 | 5.1957 | 24.8524 | 0 | 33.1889 | 0 | 0 | 24.8524
7328 | 4.1447 | 3.4971 | 6.2638 | 34.6792 | 16.4723 | 65.0572 | 0 | 0 | 55.2962
7329 | 19.2928 | 3.2442 | 5.2069 | 22.9734 | 19.1366 | 69.8539 | 0 | 0 | 61.4029
7330 | 43.3766 | 2.7676 | 4.7805 | 25.4673 | 2.2252 | 78.6171 | 0 | 0 | 71.0691
7331 | 0 | 3.6048 | 5.7856 | 31.2558 | 13.6352 | 54.2813 | 0 | 0 | 44.8909
7332 | 0 | 3.5492 | 7.0286 | 27.8972 | 13.8051 | 52.28 | 0 | 0 | 41.7023
7333 | 0 | 3.2134 | 5.3804 | 35.0941 | 16.349 | 60.0368 | 0 | 0 | 51.443
7334 | 0 | 3.2854 | 7.3991 | 35.909 | 8.8938 | 55.4873 | 0 | 0 | 44.8028
7335 | 0 | 3.7546 | 8.4405 | 26.1659 | 14.0864 | 52.4474 | 0 | 0 | 40.2523
7336 | 0 | 3.8079 | 8.9645 | 32.3838 | 21.5011 | 66.6574 | 0 | 0 | 53.8849
7337 | 0 | 3.1583 | 9.2216 | 33.2058 | 9.9914 | 55.5771 | 0 | 0 | 43.1972
7338 | 0 | 2.9628 | 7.4831 | 27.9861 | 8.1522 | 46.5842 | 0 | 0 | 36.1383
7339 | 0 | 3.6049 | 6.6219 | 37.6507 | 12.8394 | 60.7171 | 0 | 0 | 50.4902
7340 | 0 | 3.5642 | 5.7715 | 29.4296 | 0 | 38.7654 | 0 | 0 | 29.4296
7341 | 0 | 3.0774 | 6.9417 | 21.3992 | 0 | 31.4183 | 0 | 0 | 21.3992
7342 | 0 | 3.5375 | 6.5364 | 33.3301 | 0 | 43.404 | 0 | 0 | 33.3301
7343 | 0 | 3.7064 | 6.3229 | 32.3984 | 0 | 42.4277 | 0 | 200 | 232.3984
7344 | 0 | 3.8191 | 7.6997 | 36.7762 | 0 | 48.2951 | 0 | 0 | 36.7762
7345 | 0 | 3.5422 | 6.4222 | 35.9334 | 0 | 45.8979 | 0 | 0 | 35.9334
7346 | 0.16148 | 3.5981 | 4.5592 | 35.5291 | 0 | 43.8479 | 0 | 0 | 35.6906
7347 | 10.3018 | 3.1716 | 4.7842 | 32.8598 | 0 | 51.1173 | 0 | 0 | 43.1616
7348 | 51.3362 | 3.0597 | 5.1843 | 28.6611 | 0 | 88.2413 | 0 | 0 | 79.9973
7349 | 69.7412 | 2.9701 | 7.6639 | 29.6191 | 0 | 109.9943 | 0 | 0 | 99.3603
7350 | 84.8622 | 3.1651 | 7.0408 | 30.2664 | 0 | 125.3345 | 0 | 0 | 115.1287
7351 | 59.276 | 3.5819 | 6.1153 | 33.5562 | 0 | 102.5295 | 0 | 0 | 92.8322
7352 | 56.7782 | 2.9089 | 5.8688 | 34.6673 | 14.5364 | 114.7597 | 0 | 0 | 105.9819
7353 | 62.0751 | 3.1534 | 5.5366 | 22.3066 | 12.3174 | 105.3891 | 0 | 0 | 96.6991
7354 | 65.3325 | 3.3916 | 5.2682 | 30.1577 | 15.7047 | 119.8547 | 0 | 0 | 111.1949
7355 | 64.5393 | 3.7435 | 5.0211 | 30.2705 | 19.6053 | 123.1798 | 0 | 0 | 114.4151
7356 | 64.7799 | 3.0146 | 4.8026 | 33.0129 | 10.013 | 115.6231 | 200 | 0 | 307.8058
7357 | 50.7583 | 3.2108 | 6.5472 | 34.2073 | 12.322 | 107.0456 | 0 | 0 | 97.2875
7358 | 19.9343 | 3.5102 | 4.4238 | 32.8305 | 16.6046 | 77.3033 | 0 | 0 | 69.3694
7359 | 3.4598 | 2.8182 | 5.6513 | 34.6486 | 16.4528 | 63.0308 | 0 | 0 | 54.5613
7360 | 13.4002 | 3.0316 | 6.569 | 25.6775 | 14.5642 | 63.2424 | 0 | 0 | 53.6418
7361 | 0 | 2.9616 | 7.8544 | 30.319 | 6.6676 | 47.8027 | 0 | 0 | 36.9867
7362 | 0 | 3.5636 | 8.8381 | 29.6917 | 12.3352 | 54.4286 | 0 | 0 | 42.0269
7363 | 0 | 3.5761 | 7.8855 | 26.6408 | 17.8416 | 55.944 | 0 | 0 | 44.4824
7364 | 0 | 3.131 | 7.226 | 34.6967 | 0 | 45.0538 | 0 | 0 | 34.6967
7365 | 0 | 3.6337 | 6.6489 | 31.3369 | 0 | 41.6194 | 0 | 0 | 31.3369
7366 | 0 | 3.3016 | 6.8942 | 27.2075 | 0 | 37.4033 | 0 | 0 | 27.2075
7367 | 0 | 3.2837 | 8.011 | 27.8101 | 0 | 39.1048 | 0 | 0 | 27.8101
7368 | 0 | 3.5418 | 9.0297 | 24.8407 | 0 | 37.4122 | 0 | 0 | 24.8407
7369 | 0 | 3.3705 | 8.1155 | 28.5969 | 0 | 40.0828 | 0 | 0 | 28.5969
7370 | 0 | 3.3931 | 7.5717 | 39.9679 | 0 | 50.9327 | 0 | 0 | 39.9679
7371 | 0 | 4.1611 | 6.0979 | 27.8145 | 0 | 38.0735 | 0 | 0 | 27.8145
7372 | 0 | 3.4587 | 4.6101 | 31.063 | 0 | 39.1318 | 0 | 0 | 31.063
7373 | 0 | 3.6017 | 6.2961 | 23.0629 | 0 | 32.9607 | 0 | 0 | 23.0629
7374 | 11.2036 | 2.9271 | 5.4774 | 32.7368 | 0 | 52.3449 | 0 | 200 | 243.9404
7375 | 43.7931 | 3.6818 | 5.0888 | 34.2145 | 0 | 86.7781 | 0 | 0 | 78.0076
7376 | 72.6804 | 3.5623 | 4.6143 | 40.1041 | 13.7961 | 134.7572 | 0 | 0 | 126.5806
7377 | 73.57 | 3.476 | 4.0206 | 32.7901 | 7.3819 | 121.2386 | 0 | 0 | 113.7419
7378 | 79.2606 | 3.4199 | 4.1663 | 30.5971 | 22.6714 | 140.1153 | 0 | 0 | 132.5291
7379 | 71.8252 | 3.3674 | 5.8123 | 27.5599 | 18.3753 | 126.9401 | 0 | 0 | 117.7604
7380 | 74.5374 | 3.392 | 6.8651 | 25.5004 | 16.3135 | 126.6084 | 0 | 0 | 116.3513
7381 | 52.6851 | 3.1175 | 6.7583 | 31.3596 | 26.486 | 120.4065 | 0 | 0 | 110.5307
7382 | 0 | 3.5327 | 6.4125 | 30.4968 | 4.1009 | 44.5429 | 0 | 0 | 34.5977
7383 | 0 | 3.482 | 4.9465 | 28.2052 | 12.4626 | 49.0962 | 0 | 0 | 40.6678
7384 | 0 | 3.5594 | 5.9855 | 23.8393 | 10.628 | 44.0122 | 0 | 0 | 34.4673
7385 | 0 | 3.3919 | 7.0585 | 34.165 | 6.6209 | 51.2363 | 0 | 0 | 40.7859
7386 | 0 | 3.6728 | 5.0817 | 28.3154 | 26.4397 | 63.5096 | 0 | 0 | 54.7552
7387 | 0 | 3.3373 | 4.5388 | 31.8286 | 9.4491 | 49.1538 | 0 | 0 | 41.2777
7388 | 0 | 3.232 | 5.3091 | 30.9184 | 0 | 39.4595 | 0 | 0 | 30.9184
7389 | 0 | 3.4279 | 4.7439 | 31.7379 | 0 | 39.9097 | 0 | 0 | 31.7379
7390 | 0 | 3.0636 | 4.6711 | 25.9366 | 0 | 33.6713 | 0 | 0 | 25.9366
7391 | 0 | 3.0694 | 4.8575 | 33.9189 | 0 | 41.8458 | 0 | 0 | 33.9189
7392 | 0 | 3.1961 | 4.9425 | 29.7543 | 0 | 37.8929 | 0 | 0 | 29.7543
7393 | 0 | 3.8672 | 4.5525 | 32.8132 | 0 | 41.2328 | 0 | 0 | 32.8132
7394 | 0 | 3.6082 | 7.1591 | 28.3296 | 0 | 39.0969 | 0 | 0 | 28.3296
7395 | 0 | 3.5413 | 6.4912 | 26.132 | 0 | 36.1645 | 0 | 0 | 26.132
7396 | 0 | 3.7443 | 6.5758 | 40.3223 | 0 | 50.6424 | 0 | 0 | 40.3223
7397 | 1.9169 | 3.9286 | 6.6776 | 33.6572 | 0 | 46.1803 | 0 | 0 | 35.5741
7398 | 31.1513 | 3.4061 | 6.5118 | 29.0851 | 0 | 70.1543 | 0 | 0 | 60.2364
7399 | 87.8079 | 3.0162 | 6.5219 | 24.4369 | 0 | 121.7829 | 0 | 0 | 112.2448
7400 | 82.761 | 3.0611 | 6.4009 | 40.3784 | 14.2517 | 146.8531 | 0 | 0 | 137.3911
7401 | 42.202 | 3.6123 | 5.818 | 28.2231 | 19.1921 | 99.0474 | 0 | 0 | 89.6171
7402 | 24.4355 | 3.4312 | 4.9158 | 32.8962 | -1.0759 | 64.6029 | 0 | 0 | 56.2558
7403 | 19.3946 | 3.0498 | 4.1493 | 23.5069 | 2.8251 | 52.9257 | 0 | 0 | 45.7266
7404 | 37.5093 | 3.1238 | 3.2368 | 29.3872 | 11.7454 | 85.0025 | 0 | 0 | 78.6419
7405 | 56.9497 | 3.7617 | 2.3299 | 20.5035 | 10.401 | 93.9456 | 0 | 0 | 87.8541
7406 | 52.98 | 3.3494 | 2.7995 | 38.6454 | -2.653 | 95.1213 | 0 | 0 | 88.9724
7407 | 34.8358 | 3.2533 | 3.7177 | 23.7526 | 11.8828 | 77.4422 | 0 | 0 | 70.4713
7408 | 0 | 3.0399 | 3.4732 | 35.5965 | 21.1874 | 63.2969 | 0 | 0 | 56.7838
7409 | 0 | 3.1301 | 3.0632 | 16.151 | 9.673 | 32.0173 | 0 | 0 | 25.824
7410 | 0 | 3.3915 | 3.8081 | 31.288 | 7.0774 | 45.565 | 0 | 0 | 38.3654
7411 | 0 | 3.3727 | 2.4685 | 35.0267 | 5.2639 | 46.1318 | 0 | 0 | 40.2906
7412 | 0 | 3.263 | 2.5333 | 25.9044 | 0 | 31.7007 | 0 | 0 | 25.9044
7413 | 0 | 3.6593 | 2.7241 | 35.9118 | 0 | 42.2952 | 0 | 0 | 35.9118
7414 | 0 | 3.634 | 2.581 | 28.0375 | 0 | 34.2525 | 0 | 0 | 28.0375
7415 | 0 | 3.3475 | 2.0986 | 37.2405 | 0 | 42.6866 | 200 | 0 | 237.2405
7416 | 0 | 3.209 | 3.2495 | 26.8056 | 0 | 33.2641 | 0 | 200 | 226.8056
7417 | 0 | 3.823 | 3.4366 | 36.1666 | 0 | 43.4263 | 0 | 0 | 36.1666
7418 | 0 | 3.8797 | 5.7953 | 20.8905 | 0 | 30.5655 | 0 | 0 | 20.8905
7419 | 0 | 3.8882 | 5.0979 | 33.822 | 0 | 42.8082 | 0 | 0 | 33.822
7420 | 0 | 3.6072 | 4.588 | 35.9867 | 0 | 44.1819 | 0 | 0 | 35.9867
7421 | 0 | 3.3335 | 4.0919 | 28.8914 | 0 | 36.3168 | 0 | 0 | 28.8914
7422 | 9.7263 | 3.5311 | 2.0277 | 35.5123 | 0 | 50.7975 | 0 | 0 | 45.2386
7423 | 43.3593 | 2.8247 | 1.8545 | 27.9709 | 0 | 76.0094 | 0 | 0 | 71.3303
7424 | 74.754 | 3.8725 | 1.8626 | 27.1317 | 12.9688 | 120.5897 | 0 | 0 | 114.8545
7425 | 87.9165 | 3.2819 | 1.8002 | 35.426 | 17.6333 | 146.058 | 0 | 0 | 140.9758
7426 | 53.2528 | 3.3646 | 2.8181 | 29.9256 | 8.9319 | 98.2931 | 0 | 0 | 92.1104
7427 | 49.8359 | 3.5143 | 2.6439 | 29.5045 | 13.2921 | 98.7906 | 0 | 0 | 92.6324
7428 | 69.5048 | 3.147 | 1.6442 | 34.7426 | 20.9509 | 129.9896 | 0 | 0 | 125.1983
7429 | 63.5895 | 4.0991 | 2.3299 | 32.5256 | 23.1426 | 125.6867 | 0 | 0 | 119.2577
7430 | 37.3023 | 4.1272 | 2.3888 | 38.6086 | 11.727 | 94.154 | 0 | 0 | 87.6379
7431 | 10.8569 | 3.3692 | 2.0295 | 30.245 | 10.5327 | 57.0332 | 0 | 0 | 51.6345
7432 | 0 | 3.484 | 2.1477 | 28.9756 | 4.2276 | 38.8349 | 0 | 0 | 33.2032
7433 | 0 | 3.3679 | 2.2272 | 28.7432 | 15.8885 | 50.2268 | 0 | 0 | 44.6317
7434 | 0 | 3.2761 | 2.1199 | 33.3854 | 17.8683 | 56.6497 | 0 | 0 | 51.2537
7435 | 0 | 3.5708 | 1.5861 | 34.3988 | 11.6687 | 51.2244 | 0 | 0 | 46.0675
7436 | 0 | 3.1926 | 1.239 | 33.7508 | 0 | 38.1824 | 0 | 0 | 33.7508
7437 | 0 | 3.2388 | 1.0185 | 21.9828 | 0 | 26.2401 | 0 | 0 | 21.9828
7438 | 0 | 3.3543 | 1.0722 | 29.2315 | 0 | 33.658 | 0 | 0 | 29.2315
7439 | 0 | 3.4821 | 1.1947 | 37.9827 | 0 | 42.6595 | 0 | 0 | 37.9827
7440 | 0 | 3.5558 | 1.2542 | 29.7178 | 0 | 34.5278 | 0 | 0 | 29.7178
7441 | 0 | 3.3806 | 2.7569 | 25.1595 | 0 | 31.297 | 0 | 0 | 25.1595
7442 | 0 | 3.5419 | 5.3082 | 19.3781 | 0 | 28.2281 | 0 | 0 | 19.3781
7443 | 0 | 4.0142 | 4.2783 | 34.3279 | 0 | 42.6204 | 0 | 0 | 34.3279
7444 | 0 | 3.5708 | 3.7655 | 37.2497 | 0 | 44.586 | 0 | 0 | 37.2497
7445 | 6.0263 | 3.4205 | 3.6725 | 28.4951 | 0 | 41.6143 | 0 | 0 | 34.5213
7446 | 32.9404 | 3.0497 | 3.0285 | 31.8039 | 0 | 70.8225 | 0 | 0 | 64.7443
7447 | 79.0484 | 3.7742 | 2.2486 | 39.3746 | 0 | 124.4458 | 0 | 0 | 118.423
7448 | 71.3189 | 3.5565 | 2.7681 | 29.0646 | 10.9806 | 117.6886 | 0 | 0 | 111.3641
7449 | 53.9655 | 3.6777 | 2.4908 | 35.8283 | 28.7765 | 124.7387 | 0 | 0 | 118.5702
7450 | 72.027 | 3.3649 | 2.0061 | 35.7286 | 17.5185 | 130.645 | 0 | 0 | 125.274
7451 | 99.6833 | 3.6567 | 1.7681 | 29.1969 | 20.3895 | 154.6945 | 0 | 0 | 149.2696
7452 | 44.9674 | 3.3002 | 1.3773 | 32.8627 | 11.5728 | 94.0805 | 0 | 0 | 89.4029
7453 | 43.1246 | 2.7515 | 2.3299 | 35.3009 | 15.8996 | 99.4064 | 0 | 0 | 94.3251
7454 | 48.6257 | 3.0227 | 2.3888 | 34.3193 | 11.8098 | 100.1663 | 0 | 0 | 94.7548
7455 | 20.5209 | 3.6114 | 2.0295 | 32.3644 | 17.1498 | 75.676 | 0 | 0 | 70.0352
7456 | 0 | 2.6206 | 1.9886 | 33.6908 | 21.1764 | 59.4765 | 0 | 0 | 54.8673
7457 | 0 | 2.8606 | 2.2272 | 24.302 | 14.6145 | 44.0043 | 0 | 0 | 38.9165
7458 | 0 | 3.368 | 2.1199 | 35.0672 | 9.0327 | 49.5878 | 0 | 0 | 44.0999
7459 | 0 | 3.3271 | 1.5861 | 27.3476 | 19.3343 | 51.5951 | 0 | 0 | 46.6819
7460 | 0 | 3.687 | 1.239 | 37.9768 | 0 | 42.9029 | 0 | 0 | 37.9768
7461 | 0 | 3.9671 | 1.0185 | 27.7712 | 0 | 32.7568 | 0 | 0 | 27.7712
7462 | 0 | 3.6083 | 1.0722 | 25.4629 | 0 | 30.1434 | 0 | 0 | 25.4629
7463 | 0 | 3.6077 | 1.1947 | 24.926 | 0 | 29.7284 | 0 | 0 | 24.926
7464 | 0 | 3.4709 | 1.2542 | 30.2592 | 0 | 34.9843 | 0 | 0 | 30.2592
7465 | 0 | 3.4503 | 2.7569 | 25.7509 | 0 | 31.9581 | 0 | 0 | 25.7509
7466 | 0 | 3.6964 | 4.7236 | 31.6884 | 0 | 40.1085 | 0 | 0 | 31.6884
7467 | 0 | 3.3874 | 4.77 | 26.2972 | 0 | 34.4546 | 0 | 0 | 26.2972
7468 | 0 | 3.3461 | 4.8622 | 31.6963 | 0 | 39.9046 | 0 | 0 | 31.6963
7469 | 5.3791 | 3.4051 | 5.0004 | 29.8958 | 0 | 43.6803 | 0 | 0 | 35.2749
7470 | 28.2827 | 3.3619 | 4.1896 | 34.1209 | 0 | 69.955 | 0 | 0 | 62.4036
7471 | 16.8843 | 4.0196 | 3.7222 | 23.7702 | 0 | 48.3963 | 0 | 0 | 40.6545
7472 | 0 | 3.1598 | 3.6592 | 28.1093 | 20.4798 | 55.4081 | 200 | 0 | 248.5891
7473 | 0 | 3.3924 | 3.6451 | 27.4191 | 14.5623 | 49.0189 | 0 | 0 | 41.9814
7474 | 0.86229 | 2.844 | 3.9008 | 32.2447 | 16.0459 | 55.8976 | 0 | 0 | 49.1528
7475 | 20.439 | 2.8817 | 5.7856 | 35.5521 | 14.2563 | 78.9146 | 0 | 0 | 70.2473
7476 | 65.3346 | 2.865 | 6.4219 | 29.3162 | 13.5126 | 117.4502 | 0 | 0 | 108.1633
7477 | 30.8603 | 3.7898 | 7.0662 | 28.3237 | 19.8983 | 89.9382 | 0 | 0 | 79.0823
7478 | 9.9331 | 3.4433 | 6.5777 | 29.1077 | 12.6496 | 61.7114 | 0 | 0 | 51.6903
7479 | 33.9195 | 3.3915 | 7.7535 | 26.5499 | 10.4082 | 82.0227 | 0 | 0 | 70.8776
7480 | 16.5487 | 3.1245 | 8.3964 | 28.578 | 7.7112 | 64.359 | 0 | 200 | 252.838
7481 | 0 | 3.439 | 7.739 | 30.6509 | 8.5746 | 50.4035 | 0 | 0 | 39.2255
7482 | 0 | 3.5818 | 5.8126 | 27.7043 | 9.5424 | 46.6412 | 0 | 0 | 37.2467
7483 | 0 | 3.5187 | 4.1444 | 33.4207 | 13.1264 | 54.2103 | 0 | 0 | 46.5471
7484 | 0 | 2.7383 | 2.7067 | 35.6358 | 0 | 41.0808 | 0 | 0 | 35.6358
7485 | 0 | 3.5516 | 2.7241 | 31.0768 | 0 | 37.3525 | 0 | 0 | 31.0768
7486 | 0 | 3.7044 | 2.5007 | 27.6618 | 0 | 33.8669 | 0 | 0 | 27.6618
7487 | 0 | 2.9333 | 2.2609 | 33.8777 | 0 | 39.072 | 0 | 0 | 33.8777
7488 | 0 | 3.5919 | 2.6046 | 34.4261 | 0 | 40.6226 | 0 | 0 | 34.4261
7489 | 0 | 3.481 | 3.3351 | 28.6679 | 0 | 35.484 | 0 | 0 | 28.6679
7490 | 0 | 3.1939 | 5.8927 | 39.3313 | 0 | 48.418 | 0 | 0 | 39.3313
7491 | 0 | 3.1124 | 5.0979 | 31.6504 | 0 | 39.8607 | 0 | 0 | 31.6504
7492 | 0 | 3.2554 | 4.9993 | 30.6089 | 0 | 38.8637 | 0 | 0 | 30.6089
7493 | 0 | 3.2158 | 5.21 | 31.7271 | 0 | 40.153 | 0 | 0 | 31.7271
7494 | 14.5182 | 3.6934 | 4.7701 | 29.0049 | 0 | 51.9866 | 0 | 0 | 43.5231
7495 | 65.7073 | 3.0843 | 4.459 | 28.2552 | 0 | 101.5058 | 0 | 0 | 93.9625
7496 | 77.8747 | 3.3479 | 4.5502 | 20.4251 | 21.9885 | 128.1864 | 0 | 0 | 120.2883
7497 | 50.5611 | 4.1528 | 4.392 | 35.8553 | 18.0339 | 112.9952 | 0 | 0 | 104.4503
7498 | 71.6064 | 3.4813 | 4.0362 | 29.9212 | 14.2612 | 123.3062 | 0 | 0 | 115.7888
7499 | 41.3485 | 3.1782 | 3.5602 | 24.3603 | 16.2517 | 88.6989 | 0 | 0 | 81.9605
7500 | 16.726 | 2.58 | 2.7818 | 27.9976 | 12.6768 | 62.7621 | 0 | 0 | 57.4004
7501 | 0 | 3.0653 | 2.3299 | 35.2981 | 11.6789 | 52.3722 | 0 | 0 | 46.9771
7502 | 0 | 3.5583 | 2.5531 | 32.6009 | 19.6092 | 58.3215 | 0 | 0 | 52.2101
7503 | 7.2601 | 3.4276 | 2.5155 | 35.786 | 16.4114 | 65.4006 | 0 | 0 | 59.4576
7504 | 34.7791 | 3.7417 | 1.9886 | 25.1496 | 8.9551 | 74.614 | 0 | 0 | 68.8837
7505 | 41.0705 | 3.2221 | 2.2272 | 34.3316 | 16.4718 | 97.3232 | 0 | 0 | 91.8739
7506 | 0 | 3.2557 | 2.1199 | 35.7163 | 9.9635 | 51.0554 | 0 | 0 | 45.6798
7507 | 0 | 3.6504 | 1.9531 | 28.6719 | 16.6903 | 50.9657 | 0 | 0 | 45.3623
7508 | 0 | 3.3979 | 1.5255 | 24.8606 | 0 | 29.7839 | 0 | 0 | 24.8606
7509 | 0 | 3.4028 | 1.1504 | 30.9704 | 0 | 35.5235 | 0 | 0 | 30.9704
7510 | 0 | 3.5521 | 1.1994 | 29.8339 | 0 | 34.5854 | 0 | 0 | 29.8339
7511 | 0 | 3.5331 | 1.0675 | 21.1899 | 0 | 25.7906 | 0 | 0 | 21.1899
7512 | 0 | 3.2663 | 1.3615 | 33.0359 | 0 | 37.6637 | 0 | 0 | 33.0359
7513 | 0 | 2.9926 | 1.7973 | 32.692 | 0 | 37.4819 | 0 | 0 | 32.692
7514 | 0 | 3.5378 | 2.1992 | 34.4012 | 0 | 40.1383 | 0 | 0 | 34.4012
7515 | 0 | 3.205 | 1.9945 | 27.8654 | 0 | 33.0649 | 0 | 0 | 27.8654
7516 | 0 | 2.6945 | 3.6751 | 33.547 | 0 | 39.9166 | 0 | 0 | 33.547
7517 | 0 | 3.4096 | 4.0827 | 31.7972 | 0 | 39.2895 | 0 | 0 | 31.7972
7518 | 0 | 3.0692 | 4.1338 | 29.4134 | 0 | 36.6164 | 0 | 0 | 29.4134
7519 | 0 | 3.763 | 3.6332 | 36.1598 | 0 | 43.556 | 0 | 0 | 36.1598
7520 | 18.9989 | 3.8554 | 3.7184 | 32.684 | 9.0971 | 68.3538 | 0 | 0 | 60.78
7521 | 89.8265 | 3.4132 | 3.0068 | 36.7432 | 16.9689 | 149.9586 | 0 | 0 | 143.5386
7522 | 67.8203 | 3.2564 | 2.9784 | 38.0569 | 20.1616 | 132.2736 | 0 | 0 | 126.0388
7523 | 0.77431 | 2.8128 | 1.9834 | 33.9296 | 19.0173 | 58.5175 | 0 | 0 | 53.7213
7524 | 3.26 | 3.7459 | 2.2739 | 33.9473 | 11.9736 | 55.2007 | 0 | 0 | 49.1809
7525 | 13.1249 | 3.689 | 2.4752 | 37.824 | 5.9833 | 63.0963 | 0 | 0 | 56.9321
7526 | 0 | 3.2219 | 1.8702 | 31.7777 | 17.0837 | 53.9535 | 0 | 0 | 48.8614
7527 | 0 | 3.3938 | 2.2301 | 30.302 | 15.4254 | 51.3513 | 0 | 0 | 45.7273
7528 | 0 | 3.7822 | 2.3118 | 31.659 | 20.8421 | 58.5951 | 0 | 0 | 52.5011
7529 | 0 | 3.3304 | 1.9 | 38.3274 | 22.3347 | 65.8925 | 0 | 0 | 60.6622
7530 | 0 | 3.6023 | 1.9367 | 26.614 | 11.6503 | 43.8033 | 0 | 0 | 38.2643
7531 | 0 | 2.9362 | 1.5167 | 41.5134 | 18.618 | 64.5843 | 0 | 0 | 60.1314
7532 | 0 | 3.7275 | 1.4117 | 29.6055 | 0 | 34.7447 | 200 | 0 | 229.6055
7533 | 0 | 3.3725 | 1.1486 | 36.5487 | 0 | 41.0698 | 0 | 0 | 36.5487
7534 | 0 | 3.5029 | 1.2344 | 32.3256 | 0 | 37.0629 | 0 | 0 | 32.3256
7535 | 0 | 3.4493 | 1.1264 | 24.8793 | 0 | 29.4551 | 0 | 0 | 24.8793
7536 | 0 | 3.5759 | 1.1609 | 28.6356 | 0 | 33.3724 | 0 | 0 | 28.6356
7537 | 0 | 3.7439 | 1.1591 | 32.4244 | 0 | 37.3275 | 0 | 0 | 32.4244
7538 | 0 | 4.1335 | 2.1636 | 25.7623 | 0 | 32.0595 | 0 | 0 | 25.7623
7539 | 0 | 3.2664 | 1.767 | 28.4187 | 0 | 33.4521 | 0 | 0 | 28.4187
7540 | 0 | 3.1932 | 2.6204 | 30.9751 | 0 | 36.7887 | 0 | 0 | 30.9751
7541 | 3.3952 | 3.831 | 3.8779 | 32.0153 | 0 | 43.1194 | 0 | 0 | 35.4105
7542 | 25.6214 | 2.9682 | 3.9168 | 22.1205 | 0 | 54.6269 | 0 | 0 | 47.7419
7543 | 69.1307 | 3.4426 | 3.6161 | 29.5549 | 0 | 105.7443 | 0 | 0 | 98.6856
7544 | 80.3719 | 2.7396 | 3.3638 | 30.5683 | 10.8973 | 127.9409 | 0 | 0 | 121.8375
7545 | 53.2794 | 3.2181 | 2.879 | 29.8769 | 15.2491 | 104.5025 | 0 | 0 | 98.4054
7546 | 2.4567 | 3.0677 | 2.6207 | 36.0328 | 15.6265 | 59.8045 | 0 | 0 | 54.116
7547 | 0 | 3.5219 | 2.4407 | 30.1076 | 15.8162 | 51.8863 | 0 | 0 | 45.9238
7548 | 0 | 3.4738 | 2.8068 | 45.199 | 13.8892 | 65.3688 | 0 | 0 | 59.0882
7549 | 0 | 3.0483 | 2.0907 | 31.3995 | 4.1767 | 40.7152 | 0 | 0 | 35.5762
7550 | 0 | 3.8395 | 2.2196 | 31.5773 | 14.9914 | 52.6278 | 0 | 0 | 46.5687
7551 | 0 | 3.0699 | 2.2605 | 39.7204 | 17.602 | 62.6528 | 0 | 0 | 57.3224
7552 | 0 | 3.526 | 2.1706 | 26.8194 | 22.7782 | 55.2942 | 0 | 0 | 49.5976
7553 | 0 | 3.0268 | 2.1677 | 37.1642 | 14.9055 | 57.2643 | 0 | 200 | 252.0698
7554 | 0 | 3.6538 | 2.1706 | 38.5605 | 13.9196 | 58.3045 | 0 | 0 | 52.48
7555 | 0 | 3.2952 | 1.5861 | 29.9663 | 11.4593 | 46.3069 | 0 | 0 | 41.4256
7556 | 0 | 3.6477 | 1.239 | 31.9894 | 0 | 36.8761 | 0 | 0 | 31.9894
7557 | 0 | 3.0403 | 1.0185 | 24.7666 | 0 | 28.8255 | 0 | 0 | 24.7666
7558 | 0 | 3.3602 | 1.0722 | 23.195 | 0 | 27.6274 | 0 | 0 | 23.195
7559 | 0 | 3.0332 | 1.1947 | 27.2583 | 0 | 31.4862 | 0 | 0 | 27.2583
7560 | 0 | 3.3755 | 1.2542 | 30.0595 | 0 | 34.6891 | 0 | 0 | 30.0595
7561 | 0 | 3.5456 | 2.7569 | 26.9289 | 0 | 33.2314 | 0 | 0 | 26.9289
7562 | 0 | 3.242 | 4.5288 | 29.8086 | 0 | 37.5794 | 0 | 0 | 29.8086
7563 | 0 | 2.9708 | 4.4422 | 32.087 | 0 | 39.5 | 0 | 0 | 32.087
7564 | 0 | 3.2125 | 4.9307 | 31.0886 | 0 | 39.2318 | 0 | 0 | 31.0886
7565 | 13.0828 | 3.4947 | 5.4197 | 32.0289 | 0 | 54.0261 | 0 | 0 | 45.1117
7566 | 54.7925 | 3.1172 | 5.1329 | 32.5243 | 0 | 95.5669 | 0 | 0 | 87.3167
7567 | 60.1478 | 2.8536 | 5.0484 | 26.0917 | 0 | 94.1415 | 0 | 0 | 86.2395
7568 | 0 | 3.2811 | 5.2357 | 30.7632 | 8.0788 | 47.3588 | 0 | 0 | 38.842
7569 | 12.5545 | 3.8233 | 4.6636 | 33.9236 | 18.6175 | 73.5826 | 0 | 0 | 65.0956
7570 | 52.4989 | 2.8225 | 4.1038 | 30.1163 | 20.5302 | 110.0717 | 0 | 0 | 103.1454
7571 | 33.0823 | 3.6807 | 3.6257 | 37.2648 | 13.604 | 91.2575 | 0 | 0 | 83.9511
7572 | 0 | 3.6218 | 2.5543 | 19.0227 | 20.3692 | 45.5679 | 0 | 0 | 39.3919
7573 | 0 | 3.4698 | 2.3299 | 37.2143 | 9.9372 | 52.9512 | 0 | 0 | 47.1515
7574 | 0 | 2.9703 | 2.3888 | 41.1196 | 15.5973 | 62.076 | 0 | 0 | 56.7169
7575 | 0 | 3.3342 | 2.0862 | 28.2421 | 16.048 | 49.7105 | 0 | 0 | 44.2901
7576 | 0 | 3.6853 | 2.1477 | 29.9438 | 5.8367 | 41.6135 | 0 | 0 | 35.7805
7577 | 0 | 4.0321 | 2.2272 | 31.3597 | 11.6558 | 49.2748 | 0 | 0 | 43.0155
7578 | 0 | 3.3619 | 2.1199 | 35.6157 | 15.3697 | 56.4672 | 0 | 0 | 50.9854
7579 | 0 | 3.0115 | 1.5861 | 31.5748 | 7.2681 | 43.4406 | 0 | 0 | 38.8429
7580 | 0 | 2.8937 | 1.239 | 36.5223 | 0 | 40.655 | 0 | 0 | 36.5223
7581 | 0 | 3.7564 | 1.0185 | 27.2675 | 0 | 32.0425 | 0 | 0 | 27.2675
7582 | 0 | 3.2548 | 1.0722 | 29.1051 | 0 | 33.4321 | 0 | 0 | 29.1051
7583 | 0 | 3.5269 | 1.1947 | 26.8262 | 0 | 31.5478 | 0 | 0 | 26.8262
7584 | 0 | 3.0903 | 1.6371 | 36.6188 | 0 | 41.3462 | 0 | 0 | 36.6188
7585 | 0 | 3.1483 | 2.7569 | 28.6884 | 0 | 34.5936 | 0 | 0 | 28.6884
7586 | 0 | 3.4583 | 4.6262 | 32.9564 | 0 | 41.0409 | 0 | 0 | 32.9564
7587 | 0 | 3.2239 | 4.3602 | 31.2248 | 0 | 38.809 | 0 | 0 | 31.2248
7588 | 0 | 3.7039 | 4.5195 | 33.7269 | 0 | 41.9503 | 0 | 0 | 33.7269
7589 | 0 | 3.5067 | 5.21 | 33.1125 | 0 | 41.8293 | 0 | 0 | 33.1125
7590 | 0 | 3.1241 | 4.5524 | 26.2036 | 0 | 33.8801 | 0 | 0 | 26.2036
7591 | 0 | 3.2339 | 4.2379 | 28.9945 | 0 | 36.4663 | 0 | 0 | 28.9945
7592 | 0 | 3.3786 | 4.3446 | 30.0666 | 3.3119 | 41.1017 | 200 | 0 | 233.3785
7593 | 0 | 3.0295 | 3.9846 | 24.6756 | 10.4801 | 42.1698 | 0 | 0 | 35.1557
7594 | 0 | 3.1113 | 3.4948 | 39.4038 | 17.7728 | 63.7828 | 0 | 0 | 57.1766
7595 | 0 | 3.9156 | 3.2984 | 25.9496 | 7.4808 | 40.6444 | 0 | 0 | 33.4304
7596 | 0 | 3.6859 | 2.5543 | 22.0592 | 13.6775 | 41.9769 | 0 | 0 | 35.7367
7597 | 0 | 3.1988 | 2.3299 | 30.3558 | 10.4935 | 46.3781 | 0 | 0 | 40.8494
7598 | 0.20498 | 2.8619 | 2.3888 | 33.1641 | 15.8922 | 54.512 | 0 | 0 | 49.2613
7599 | 0.67378 | 3.7918 | 2.6014 | 36.1295 | 17.2125 | 60.4089 | 0 | 0 | 54.0157
7600 | 0 | 3.2789 | 2.3371 | 33.128 | 14.5462 | 53.2902 | 0 | 0 | 47.6742
7601 | 0 | 3.2875 | 2.2272 | 29.2826 | 0.79287 | 35.5902 | 0 | 0 | 30.0754
7602 | 0 | 3.406 | 2.1199 | 35.9496 | 17.6468 | 59.1223 | 0 | 0 | 53.5964
7603 | 0 | 3.4957 | 1.5861 | 28.4873 | 13.8739 | 47.443 | 0 | 0 | 42.3611
7604 | 0 | 3.5106 | 1.239 | 23.5152 | 0 | 28.2648 | 0 | 0 | 23.5152
7605 | 0 | 2.7373 | 1.3506 | 29.9571 | 0 | 34.0451 | 0 | 0 | 29.9571
7606 | 0 | 3.4579 | 1.7772 | 35.9772 | 0 | 41.2123 | 0 | 0 | 35.9772
7607 | 0 | 3.7665 | 2.5855 | 19.0507 | 0 | 25.4028 | 0 | 0 | 19.0507
7608 | 0 | 3.1649 | 3.6526 | 29.209 | 0 | 36.0265 | 0 | 0 | 29.209
7609 | 0 | 3.0936 | 5.364 | 32.0449 | 0 | 40.5026 | 0 | 0 | 32.0449
7610 | 0 | 3.466 | 8.8153 | 30.5209 | 0 | 42.8022 | 0 | 0 | 30.5209
7611 | 0 | 3.5165 | 7.6387 | 31.2207 | 0 | 42.3758 | 0 | 0 | 31.2207
7612 | 0 | 3.5019 | 6.7129 | 30.7258 | 0 | 40.9406 | 0 | 0 | 30.7258
7613 | 12.2389 | 3.0048 | 6.5378 | 28.9157 | 0 | 50.6972 | 0 | 0 | 41.1546
7614 | 68.1239 | 3.5343 | 5.2781 | 35.3374 | 0 | 112.2736 | 0 | 200 | 303.4612
7615 | 77.3629 | 3.5085 | 4.68 | 25.6508 | 0 | 111.2022 | 0 | 0 | 103.0137
7616 | 67.6101 | 2.9054 | 4.4817 | 29.552 | 18.441 | 122.9902 | 0 | 0 | 115.6031
7617 | 38.4915 | 2.9495 | 4.1883 | 41.8025 | 10.0057 | 97.4376 | 0 | 0 | 90.2998
7618 | 15.5415 | 3.4895 | 3.9685 | 27.543 | 15.4074 | 65.95 | 0 | 0 | 58.492
7619 | 24.5233 | 4.0569 | 3.7566 | 32.2937 | 9.9561 | 74.5865 | 0 | 0 | 66.7731
7620 | 0 | 2.7486 | 3.9951 | 21.8083 | 15.8939 | 44.446 | 0 | 0 | 37.7022
7621 | 0 | 3.2776 | 5.0254 | 26.0776 | 13.3252 | 47.7059 | 0 | 0 | 39.4028
7622 | 0 | 4.1382 | 4.6886 | 27.4891 | 18.6227 | 54.9386 | 0 | 0 | 46.1118
7623 | 0 | 3.1804 | 4.7481 | 26.7258 | 13.0691 | 47.7234 | 0 | 0 | 39.7949
7624 | 0 | 2.8615 | 4.8934 | 25.2943 | 16.4721 | 49.5212 | 0 | 0 | 41.7663
7625 | 0 | 3.004 | 6.0284 | 41.4177 | 15.0215 | 65.4716 | 0 | 0 | 56.4393
7626 | 0 | 2.576 | 4.8104 | 16.247 | 20.5401 | 44.1735 | 0 | 0 | 36.7871
7627 | 0 | 3.4511 | 3.8487 | 32.9024 | 17.4639 | 57.666 | 0 | 0 | 50.3662
7628 | 0 | 3.0181 | 5.4826 | 39.3826 | 0 | 47.8833 | 0 | 0 | 39.3826
7629 | 0 | 3.7231 | 5.2287 | 38.0705 | 0 | 47.0223 | 0 | 0 | 38.0705
7630 | 0 | 3.7985 | 4.3495 | 19.2964 | 0 | 27.4444 | 0 | 0 | 19.2964
7631 | 0 | 3.7302 | 4.8575 | 24.1137 | 0 | 32.7015 | 0 | 0 | 24.1137
7632 | 0 | 3.2885 | 6.0712 | 32.51 | 0 | 41.8697 | 0 | 0 | 32.51
7633 | 0 | 3.6614 | 7.9002 | 24.575 | 0 | 36.1365 | 0 | 0 | 24.575
7634 | 0 | 3.2773 | 10.9585 | 28.0736 | 0 | 42.3095 | 0 | 0 | 28.0736
7635 | 0 | 3.7382 | 10.6712 | 29.2988 | 0 | 43.7083 | 0 | 0 | 29.2988
7636 | 0 | 2.9238 | 9.5917 | 37.505 | 0 | 50.0205 | 0 | 0 | 37.505
7637 | 4.3609 | 3.9738 | 8.4247 | 32.2711 | 0 | 49.0306 | 0 | 0 | 36.632
7638 | 28.9212 | 3.4117 | 7.0923 | 28.931 | 0 | 68.3562 | 0 | 0 | 57.8522
7639 | 59.6102 | 3.2402 | 6.3009 | 26.3232 | 0 | 95.4745 | 0 | 0 | 85.9333
7640 | 14.2383 | 3.7332 | 5.5784 | 31.67 | 9.46 | 64.6799 | 0 | 0 | 55.3683
7641 | 1.6994 | 3.09 | 5.139 | 40.1695 | 13.576 | 63.6739 | 0 | 0 | 55.445
7642 | 20.1822 | 3.9972 | 5.1865 | 30.2753 | 15.9858 | 75.627 | 0 | 0 | 66.4433
7643 | 75.7968 | 3.4245 | 6.7019 | 39.511 | 8.0162 | 133.4504 | 0 | 0 | 123.3241
7644 | 71.2316 | 3.5494 | 7.1802 | 29.5078 | 18.7119 | 130.181 | 0 | 0 | 119.4514
7645 | 31.6057 | 3.3122 | 7.776 | 28.6217 | 6.5007 | 77.8164 | 0 | 0 | 66.7282
7646 | 0 | 3.0328 | 7.317 | 34.4918 | 15.6913 | 60.5329 | 0 | 0 | 50.1831
7647 | 0 | 3.7595 | 7.6676 | 39.1406 | 15.5537 | 66.1215 | 0 | 200 | 254.6943
7648 | 0 | 3.3717 | 9.3432 | 32.8142 | 9.7316 | 55.2607 | 0 | 0 | 42.5458
7649 | 0 | 3.0605 | 11.7306 | 27.8296 | 18.0031 | 60.6237 | 0 | 0 | 45.8326
7650 | 0 | 3.4178 | 10.4898 | 34.5939 | 22.8788 | 71.3803 | 0 | 0 | 57.4727
7651 | 0 | 3.2502 | 9.1723 | 38.1564 | 20.1121 | 70.691 | 200 | 0 | 258.2685
7652 | 0 | 2.9719 | 9.2126 | 26.9247 | 0 | 39.1092 | 0 | 0 | 26.9247
7653 | 0 | 3.3621 | 9.1876 | 30.7728 | 0 | 43.3225 | 0 | 0 | 30.7728
7654 | 0 | 3.0541 | 9.4138 | 28.2423 | 0 | 40.7102 | 0 | 0 | 28.2423
7655 | 0 | 3.448 | 9.8885 | 30.9308 | 0 | 44.2672 | 0 | 0 | 30.9308
7656 | 0 | 3.32 | 10.1828 | 29.5766 | 0 | 43.0794 | 0 | 0 | 29.5766
7657 | 0 | 3.3152 | 13.7839 | 25.9963 | 0 | 43.0955 | 0 | 0 | 25.9963
7658 | 0 | 3.4005 | 16.414 | 20.7816 | 0 | 40.596 | 0 | 0 | 20.7816
7659 | 0 | 2.8961 | 14.0316 | 33.7249 | 0 | 50.6526 | 0 | 0 | 33.7249
7660 | 0 | 3.1849 | 12.0593 | 31.8284 | 0 | 47.0726 | 0 | 0 | 31.8284
7661 | 0 | 3.4855 | 10.3815 | 35.2388 | 0 | 49.1059 | 0 | 0 | 35.2388
7662 | 11.7275 | 2.9359 | 8.5437 | 26.8725 | 0 | 50.0796 | 0 | 0 | 38.6
7663 | 44.9405 | 3.1372 | 7.6271 | 25.2936 | 0 | 80.9984 | 0 | 0 | 70.2341
7664 | 30.6731 | 3.7261 | 7.292 | 35.3033 | 19.4545 | 96.4489 | 0 | 0 | 85.4308
7665 | 0.027145 | 3.6937 | 6.5649 | 29.6357 | 16.5524 | 56.4739 | 0 | 0 | 46.2153
7666 | 1.9494 | 3.4167 | 6.8782 | 30.9299 | 17.2445 | 60.4187 | 0 | 0 | 50.1238
7667 | 17.1942 | 3.2124 | 7.6182 | 32.409 | 17.0491 | 77.483 | 0 | 200 | 266.6524
7668 | 58.8699 | 3.357 | 7.1802 | 24.7342 | 12.5336 | 106.6749 | 0 | 0 | 96.1377
7669 | 86.3285 | 3.6207 | 5.9127 | 32.4736 | 17.2043 | 145.5398 | 0 | 0 | 136.0064
7670 | 41.0539 | 2.7643 | 6.2492 | 26.8261 | 9.0717 | 85.9653 | 0 | 0 | 76.9518
7671 | 4.7391 | 3.6632 | 7.3242 | 25.9105 | 14.0623 | 55.6993 | 0 | 0 | 44.7119
7672 | 0.96654 | 2.8847 | 8.8698 | 32.0549 | 11.4316 | 56.2075 | 0 | 0 | 44.453
7673 | 0 | 2.7066 | 9.3357 | 34.3758 | 10.106 | 56.524 | 0 | 0 | 44.4818
7674 | 0 | 3.0961 | 8.9308 | 37.7006 | 22.3683 | 72.0958 | 0 | 0 | 60.069
7675 | 0 | 3.3678 | 8.128 | 32.7731 | 1.8352 | 46.1041 | 0 | 0 | 34.6083
7676 | 0 | 3.2822 | 7.0757 | 24.7697 | 0 | 35.1275 | 0 | 0 | 24.7697
7677 | 0 | 3.1694 | 5.7215 | 25.8281 | 0 | 34.719 | 0 | 0 | 25.8281
7678 | 0 | 2.9916 | 7.0107 | 26.386 | 0 | 36.3883 | 0 | 0 | 26.386
7679 | 0 | 2.9077 | 6.8387 | 33.3159 | 0 | 43.0622 | 0 | 0 | 33.3159
7680 | 0 | 2.9684 | 7.4475 | 28.5631 | 0 | 38.979 | 0 | 0 | 28.5631
7681 | 0 | 3.746 | 6.6606 | 36.0936 | 0 | 46.5001 | 0 | 0 | 36.0936
7682 | 0 | 3.4095 | 3.8949 | 31.5521 | 0 | 38.8565 | 0 | 0 | 31.5521
7683 | 0 | 2.9523 | 5.6865 | 27.6437 | 0 | 36.2825 | 0 | 0 | 27.6437
7684 | 0 | 3.6688 | 7.1483 | 31.0488 | 0 | 41.8659 | 0 | 0 | 31.0488
7685 | 0 | 3.4591 | 8.9832 | 31.8122 | 0 | 44.2546 | 0 | 0 | 31.8122
7686 | 0 | 3.3833 | 8.4646 | 31.4294 | 0 | 43.2773 | 0 | 0 | 31.4294
7687 | 0 | 3.5507 | 7.5155 | 31.04 | 0 | 42.1062 | 0 | 0 | 31.04
7688 | 0 | 2.3446 | 7.1233 | 23.9153 | 7.5362 | 40.9194 | 0 | 0 | 31.4515
7689 | 0 | 3.2953 | 6.7691 | 24.9689 | 14.3385 | 49.3718 | 0 | 0 | 39.3074
7690 | 0 | 3.6767 | 6.835 | 34.8963 | 10.4096 | 55.8176 | 0 | 0 | 45.3059
7691 | 0 | 3.3463 | 5.9195 | 32.9984 | 9.0842 | 51.3484 | 0 | 0 | 42.0826
7692 | 0 | 3.4142 | 3.7194 | 24.9988 | 6.4696 | 38.6021 | 0 | 0 | 31.4685
7693 | 0 | 3.5484 | 4.5218 | 35.24 | 10.3061 | 53.6163 | 0 | 0 | 45.546
7694 | 0 | 3.3273 | 4.9255 | 45.0614 | 18.6608 | 71.9749 | 0 | 0 | 63.7221
7695 | 0 | 3.845 | 5.8769 | 28.9859 | 6.2967 | 45.0045 | 0 | 0 | 35.2826
7696 | 0 | 3.4894 | 7.2424 | 29.1981 | 18.9929 | 58.9228 | 0 | 200 | 248.191
7697 | 0 | 3.6429 | 9.4038 | 31.5462 | 11.6038 | 56.1967 | 0 | 0 | 43.15
7698 | 0 | 3.2719 | 8.6251 | 24.6643 | 8.9123 | 45.4735 | 0 | 0 | 33.5766
7699 | 0 | 3.2906 | 8.1706 | 39.6761 | 7.4154 | 58.5526 | 0 | 0 | 47.0915
7700 | 0 | 3.4236 | 7.9316 | 39.7662 | 0 | 51.1214 | 0 | 0 | 39.7662
7701 | 12.3381 | 3.1374 | 7.3093 | 27.5177 | 0 | 50.3025 | 0 | 0 | 39.8557
7702 | 50.2421 | 3.7094 | 7.4752 | 34.4189 | 0 | 95.8457 | 0 | 0 | 84.661
7703 | 76.9553 | 3.7447 | 7.519 | 32.2597 | 0 | 120.4786 | 0 | 0 | 109.2149
7704 | 66.3973 | 2.8436 | 8.3069 | 31.7793 | 0 | 109.3271 | 0 | 0 | 98.1766
7705 | 26.1977 | 3.7116 | 8.006 | 32.4344 | 0 | 70.3497 | 0 | 0 | 58.6321
7706 | 0 | 3.5193 | 7.9749 | 35.0815 | 0 | 46.5758 | 0 | 0 | 35.0815
7707 | 0 | 3.667 | 7.2897 | 28.1672 | 0 | 39.1239 | 0 | 0 | 28.1672
7708 | 0 | 3.5909 | 7.4187 | 27.4681 | 0 | 38.4777 | 0 | 0 | 27.4681
7709 | 0 | 2.924 | 9.2572 | 26.002 | 0 | 38.1832 | 0 | 0 | 26.002
7710 | 4.9436 | 3.4072 | 8.4035 | 39.7497 | 0 | 56.504 | 0 | 0 | 44.6933
7711 | 22.9871 | 3.1071 | 8.1432 | 34.5585 | 0 | 68.7959 | 200 | 0 | 257.5457
7712 | 18.5195 | 3.1004 | 7.9851 | 30.2201 | 12.5855 | 72.4106 | 0 | 0 | 61.3251
7713 | 0 | 3.5487 | 7.6858 | 29.0268 | 19.8345 | 60.0958 | 0 | 0 | 48.8612
7714 | 0 | 3.5226 | 7.6734 | 28.9277 | 16.76 | 56.8837 | 0 | 0 | 45.6877
7715 | 0 | 3.9748 | 8.2375 | 26.2657 | 25.9206 | 64.3986 | 0 | 0 | 52.1863
7716 | 0 | 3.4943 | 8.4503 | 31.7582 | 15.4514 | 59.1542 | 0 | 0 | 47.2096
7717 | 0 | 3.0552 | 9.073 | 30.9427 | 17.9603 | 61.0312 | 0 | 0 | 48.903
7718 | 0 | 3.2239 | 7.3924 | 36.1181 | 6.5558 | 53.2902 | 0 | 0 | 42.6739
7719 | 0 | 2.9199 | 6.6465 | 23.6716 | 23.4174 | 56.6555 | 0 | 0 | 47.0891
7720 | 0 | 3.7669 | 6.2969 | 32.3499 | 17.2207 | 59.6344 | 0 | 0 | 49.5706
7721 | 0 | 3.1002 | 5.8848 | 27.84 | 11.9709 | 48.796 | 0 | 0 | 39.811
7722 | 0 | 3.4925 | 4.5767 | 24.4629 | 16.9444 | 49.4765 | 0 | 0 | 41.4073
7723 | 0 | 3.2552 | 5.0317 | 26.2661 | 17.038 | 51.591 | 0 | 200 | 243.3041
7724 | 0 | 2.9765 | 4.7019 | 30.1671 | 0 | 37.8455 | 0 | 0 | 30.1671
7725 | 0 | 3.6046 | 4.0976 | 25.1202 | 0 | 32.8224 | 0 | 0 | 25.1202
7726 | 0 | 3.8175 | 3.4653 | 24.6219 | 0 | 31.9048 | 0 | 0 | 24.6219
7727 | 0 | 3.7064 | 3.8838 | 28.6463 | 0 | 36.2366 | 0 | 0 | 28.6463
7728 | 0 | 3.5253 | 4.5394 | 34.8741 | 0 | 42.9388 | 0 | 0 | 34.8741
7729 | 0 | 3.6805 | 5.9727 | 26.0877 | 0 | 35.7409 | 0 | 0 | 26.0877
7730 | 0 | 3.2265 | 8.9127 | 30.9787 | 0 | 43.1179 | 0 | 0 | 30.9787
7731 | 0 | 3.1795 | 8.2944 | 31.8299 | 0 | 43.3038 | 0 | 0 | 31.8299
7732 | 0 | 3.8036 | 8.3579 | 32.2773 | 0 | 44.4388 | 0 | 0 | 32.2773
7733 | 1.6924 | 2.8723 | 8.7742 | 39.8012 | 0 | 53.14 | 0 | 0 | 41.4936
7734 | 15.3977 | 3.603 | 8.6162 | 29.5221 | 0 | 57.139 | 0 | 0 | 44.9198
7735 | 36.6374 | 3.9279 | 8.2902 | 33.991 | 0 | 82.8465 | 0 | 0 | 70.6285
7736 | 55.258 | 3.4179 | 8.3201 | 24.0127 | 10.8391 | 101.8478 | 0 | 0 | 90.1098
7737 | 25.3974 | 3.3695 | 8.4662 | 30.2241 | 16.7974 | 84.2546 | 0 | 0 | 72.4189
7738 | 0 | 3.2602 | 7.9609 | 28.8623 | 14.3911 | 54.4745 | 0 | 0 | 43.2534
7739 | 0 | 3.595 | 7.291 | 34.2398 | 9.6527 | 54.7784 | 0 | 0 | 43.8925
7740 | 0 | 3.4834 | 6.8011 | 21.5155 | 16.7723 | 48.5723 | 0 | 0 | 38.2879
7741 | 0 | 2.9593 | 6.1789 | 37.6277 | 13.4416 | 60.2075 | 0 | 0 | 51.0693
7742 | 0 | 2.6578 | 6.1671 | 26.5842 | 7.3915 | 42.8005 | 0 | 0 | 33.9756
7743 | 0 | 3.3579 | 7.0666 | 36.7469 | 15.6002 | 62.7715 | 0 | 0 | 52.3471
7744 | 0 | 3.587 | 6.5976 | 35.7378 | 15.5387 | 61.4612 | 0 | 0 | 51.2766
7745 | 0 | 3.4213 | 6.2564 | 33.0035 | 8.4334 | 51.1146 | 0 | 0 | 41.4369
7746 | 0 | 3.5196 | 5.2558 | 29.3702 | 24.5157 | 62.6614 | 0 | 0 | 53.8859
7747 | 0 | 3.3823 | 5.2289 | 30.9334 | 18.4345 | 57.9792 | 0 | 0 | 49.368
7748 | 0 | 3.1932 | 4.6151 | 37.9111 | 0 | 45.7194 | 0 | 0 | 37.9111
7749 | 9.5028 | 3.6194 | 4.34 | 25.6193 | 0 | 43.0815 | 0 | 0 | 35.122
7750 | 41.6027 | 3.4319 | 4.2691 | 30.7397 | 0 | 80.0434 | 0 | 0 | 72.3424
7751 | 73.1391 | 2.6575 | 4.8575 | 24.7972 | 0 | 105.4513 | 0 | 0 | 97.9363
7752 | 68.4692 | 3.2223 | 5.7487 | 29.2629 | 0 | 106.7031 | 0 | 0 | 97.7321
7753 | 69.3967 | 3.5136 | 7.5958 | 38.2184 | 0 | 118.7246 | 0 | 200 | 307.6152
7754 | 56.3231 | 3.4363 | 10.5688 | 30.8348 | 0 | 101.163 | 0 | 0 | 87.1579
7755 | 67.9457 | 3.1016 | 9.6877 | 33.5706 | 0 | 114.3056 | 0 | 0 | 101.5163
7756 | 45.658 | 3.0593 | 9.7973 | 31.5937 | 0 | 90.1084 | 0 | 0 | 77.2517
7757 | 3.9073 | 3.5228 | 10.5912 | 33.4047 | 0 | 51.426 | 0 | 0 | 37.3121
7758 | 3.6925 | 3.54 | 10.7207 | 29.2411 | 0 | 47.1943 | 0 | 0 | 32.9336
7759 | 0 | 2.9666 | 10.7215 | 31.2511 | 0 | 44.9392 | 0 | 0 | 31.2511
7760 | 0 | 3.5763 | 10.6506 | 28.0896 | 12.7826 | 55.099 | 0 | 0 | 40.8721
7761 | 0 | 3.3321 | 10.1637 | 32.2905 | 12.0914 | 57.8778 | 0 | 0 | 44.382
7762 | 0 | 3.1866 | 9.4496 | 27.0403 | 9.5154 | 49.1919 | 0 | 0 | 36.5557
7763 | 0 | 3.5314 | 8.4037 | 26.7033 | 19.6641 | 58.3024 | 0 | 0 | 46.3674
7764 | 0 | 3.8909 | 8.2419 | 25.408 | 10.3322 | 47.873 | 0 | 0 | 35.7402
7765 | 0 | 2.772 | 8.6633 | 36.7612 | 20.7064 | 68.9029 | 0 | 0 | 57.4677
7766 | 0 | 3.5471 | 8.6311 | 26.968 | 24.8427 | 63.9889 | 0 | 0 | 51.8107
7767 | 0 | 3.5571 | 8.4405 | 29.4686 | 19.5124 | 60.9786 | 0 | 0 | 48.981
7768 | 0 | 3.6819 | 8.3018 | 23.6526 | 11.1864 | 46.8226 | 0 | 0 | 34.839
7769 | 0 | 3.1534 | 8.4233 | 33.9741 | 21.8596 | 67.4103 | 0 | 0 | 55.8336
7770 | 0 | 3.4206 | 7.149 | 29.372 | 16.0148 | 55.9563 | 0 | 0 | 45.3868
7771 | 0 | 3.6966 | 6.4119 | 32.1179 | 11.0985 | 53.3249 | 200 | 0 | 243.2164
7772 | 0 | 3.5301 | 6.0898 | 25.9534 | 0 | 35.5733 | 0 | 0 | 25.9534
7773 | 10.4705 | 3.4147 | 6.1174 | 24.6332 | 0 | 44.6359 | 0 | 0 | 35.1038
7774 | 43.8347 | 3.2956 | 6.6003 | 33.6587 | 0 | 87.3893 | 0 | 0 | 77.4934
7775 | 67.3314 | 3.6109 | 7.5353 | 34.515 | 0 | 112.9926 | 0 | 0 | 101.8464
7776 | 31.123 | 3.7644 | 8.9735 | 31.8078 | 0 | 75.6688 | 0 | 200 | 262.9308
7777 | 0 | 3.4028 | 11.5522 | 27.0296 | 0 | 41.9845 | 0 | 0 | 27.0296
7778 | 11.5319 | 3.4619 | 14.7579 | 29.3086 | 0 | 59.0603 | 0 | 0 | 40.8405
7779 | 59.4707 | 3.4477 | 12.2285 | 27.7112 | 0 | 102.8581 | 0 | 0 | 87.1819
7780 | 64.7016 | 3.543 | 10.6199 | 34.7095 | 0 | 113.5739 | 0 | 0 | 99.4111
7781 | 71.1076 | 3.5878 | 10.4514 | 20.6638 | 0 | 105.8106 | 0 | 0 | 91.7714
7782 | 22.3061 | 3.3284 | 10.0676 | 31.8247 | 0 | 67.5269 | 0 | 0 | 54.1309
7783 | 0 | 2.9425 | 10.2795 | 23.3644 | 0 | 36.5864 | 0 | 0 | 23.3644
7784 | 0 | 3.1394 | 9.8966 | 34.8672 | 22.3147 | 70.218 | 0 | 0 | 57.1819
7785 | 0 | 2.9833 | 9.6205 | 30.0934 | 9.3703 | 52.0676 | 0 | 0 | 39.4637
7786 | 12.7548 | 3.3528 | 8.9083 | 34.2558 | 18.344 | 77.6156 | 0 | 0 | 65.3546
7787 | 53.1474 | 3.6031 | 8.0764 | 32.797 | 16.8716 | 114.4955 | 0 | 0 | 102.816
7788 | 38.6742 | 3.4175 | 7.4836 | 30.7337 | 14.4996 | 94.8085 | 0 | 0 | 83.9074
7789 | 0 | 3.2566 | 7.3324 | 29.2949 | 17.6024 | 57.4864 | 0 | 0 | 46.8974
7790 | 0 | 3.3572 | 6.9884 | 29.7944 | 9.4721 | 49.6122 | 0 | 0 | 39.2666
7791 | 0 | 3.67 | 9.2133 | 29.019 | 17.5033 | 59.4056 | 0 | 0 | 46.5223
7792 | 0 | 3.5967 | 10.29 | 33.7534 | 15.4801 | 63.1202 | 0 | 0 | 49.2335
7793 | 0 | 3.7787 | 9.3357 | 30.365 | 18.0648 | 61.5442 | 0 | 0 | 48.4298
7794 | 0 | 3.0963 | 7.7058 | 28.7067 | 13.4501 | 52.9589 | 0 | 0 | 42.1568
7795 | 0 | 2.8871 | 6.0176 | 28.8927 | 8.6303 | 46.4277 | 0 | 0 | 37.523
7796 | 18.1265 | 2.9833 | 5.7428 | 27.7421 | 0 | 54.5948 | 0 | 0 | 45.8686
7797 | 81.99 | 3.0906 | 5.8751 | 26.7769 | 0 | 117.7327 | 0 | 0 | 108.767
7798 | 75.1996 | 3.4132 | 6.1984 | 31.4309 | 0 | 116.242 | 0 | 0 | 106.6305
7799 | 46.195 | 2.8403 | 6.4804 | 22.5213 | 0 | 78.037 | 0 | 200 | 268.7163
7800 | 0.55806 | 3.8142 | 7.3611 | 25.733 | 0 | 37.4663 | 0 | 0 | 26.291
7801 | 19.2178 | 3.7658 | 9.4218 | 44.0308 | 0 | 76.4363 | 0 | 0 | 63.2486
7802 | 62.8815 | 3.2969 | 12.4198 | 26.4119 | 0 | 105.0101 | 0 | 0 | 89.2934
7803 | 19.099 | 3.0429 | 11.081 | 38.0716 | 0 | 71.2945 | 0 | 0 | 57.1706
7804 | 2.7225 | 3.323 | 10.4828 | 33.0919 | 0 | 49.6202 | 0 | 0 | 35.8144
7805 | 8.116 | 3.0915 | 11.0804 | 27.2024 | 0 | 49.4904 | 0 | 0 | 35.3185
7806 | 0 | 3.5618 | 11.1562 | 27.2263 | 0 | 41.9442 | 0 | 0 | 27.2263
7807 | 0 | 3.358 | 11.0899 | 27.5208 | 0 | 41.9687 | 0 | 0 | 27.5208
7808 | 0 | 3.3084 | 10.7192 | 28.0452 | 21.7233 | 63.796 | 0 | 0 | 49.7684
7809 | 0 | 3.8791 | 10.2995 | 29.7002 | 7.2305 | 51.1093 | 0 | 0 | 36.9307
7810 | 0 | 2.9607 | 9.6527 | 38.5087 | 13.5108 | 64.6328 | 0 | 0 | 52.0194
7811 | 0 | 3.6409 | 8.7309 | 29.9454 | 14.2822 | 56.5994 | 0 | 0 | 44.2276
7812 | 0 | 2.8832 | 8.2419 | 26.3208 | 6.9368 | 44.3827 | 0 | 0 | 33.2576
7813 | 0 | 3.8236 | 7.776 | 32.8137 | 1.7894 | 46.2027 | 0 | 0 | 34.6031
7814 | 0 | 3.4467 | 7.1527 | 35.761 | 15.0456 | 61.4059 | 0 | 0 | 50.8065
7815 | 0 | 3.4222 | 7.5818 | 37.0594 | 15.6478 | 63.7112 | 0 | 0 | 52.7072
7816 | 0 | 3.6114 | 7.639 | 30.1629 | 11.131 | 52.5443 | 0 | 0 | 41.294
7817 | 0 | 4.045 | 7.739 | 20.2843 | 14.4223 | 46.4905 | 0 | 0 | 34.7065
7818 | 0 | 3.6324 | 6.4808 | 31.9465 | 4.4659 | 46.5256 | 0 | 0 | 36.4124
7819 | 0 | 2.6595 | 7.595 | 28.0937 | 15.9671 | 54.3153 | 0 | 0 | 44.0608
7820 | 0 | 3.1949 | 6.9572 | 27.889 | 0 | 38.0411 | 0 | 0 | 27.889
7821 | 0 | 3.8381 | 6.1174 | 21.448 | 0 | 31.4035 | 0 | 0 | 21.448
7822 | 0 | 2.918 | 5.7965 | 29.2915 | 0 | 38.006 | 0 | 200 | 229.2915
7823 | 0 | 3.2761 | 7.1296 | 27.3676 | 0 | 37.7732 | 0 | 0 | 27.3676
7824 | 0 | 4.207 | 9.1347 | 26.7612 | 0 | 40.1029 | 0 | 0 | 26.7612
7825 | 0 | 3.609 | 12.1608 | 29.8994 | 0 | 45.6693 | 0 | 0 | 29.8994
7826 | 0 | 3.059 | 14.4656 | 26.1769 | 0 | 43.7015 | 0 | 0 | 26.1769
7827 | 0 | 3.0266 | 13.6218 | 34.1428 | 0 | 50.7912 | 0 | 0 | 34.1428
7828 | 0 | 2.9208 | 11.4424 | 34.6804 | 0 | 49.0436 | 0 | 0 | 34.6804
7829 | 0 | 3.5177 | 10.8008 | 31.6646 | 0 | 45.9831 | 0 | 0 | 31.6646
7830 | 0 | 3.313 | 10.7207 | 27.634 | 0 | 41.6677 | 200 | 0 | 227.634
7831 | 0 | 3.2151 | 9.9847 | 30.2594 | 0 | 43.4592 | 0 | 0 | 30.2594
7832 | 0 | 3.2559 | 9.0741 | 28.6346 | 7.0551 | 48.0198 | 0 | 0 | 35.6897
7833 | 0 | 3.4903 | 8.8057 | 22.097 | 14.2418 | 48.6347 | 0 | 0 | 36.3388
7834 | 0 | 3.6494 | 9.2466 | 34.2679 | 5.649 | 52.813 | 0 | 0 | 39.9169
7835 | 0 | 3.362 | 7.4219 | 34.2761 | 18.0301 | 63.0901 | 0 | 0 | 52.3062
7836 | 0 | 3.5925 | 6.7252 | 34.4949 | 11.287 | 56.0996 | 0 | 0 | 45.7819
7837 | 0 | 2.6178 | 6.2676 | 36.4948 | 6.0671 | 51.4474 | 0 | 0 | 42.5619
7838 | 0 | 3.1428 | 6.3313 | 35.3353 | 17.7839 | 62.5934 | 0 | 0 | 53.1192
7839 | 0 | 3.4775 | 8.3546 | 33.4543 | 9.5931 | 54.8795 | 0 | 0 | 43.0474
7840 | 0 | 3.2469 | 8.6805 | 29.5945 | 15.2569 | 56.7788 | 0 | 0 | 44.8514
7841 | 0 | 3.4251 | 9.5637 | 32.1039 | 6.5785 | 51.6712 | 0 | 0 | 38.6824
7842 | 0 | 3.632 | 8.374 | 30.6158 | 4.473 | 47.0948 | 0 | 0 | 35.0889
7843 | 0 | 2.6367 | 5.6951 | 28.5962 | 14.3265 | 51.2545 | 0 | 0 | 42.9227
7844 | 0 | 3.1001 | 4.9021 | 26.8924 | 0 | 34.8945 | 0 | 200 | 226.8924
7845 | 0 | 3.6789 | 4.85 | 27.729 | 0 | 36.2579 | 0 | 0 | 27.729
7846 | 0 | 3.3114 | 4.8765 | 33.866 | 0 | 42.0539 | 0 | 0 | 33.866
7847 | 0 | 2.6019 | 5.2178 | 34.9543 | 0 | 42.774 | 0 | 0 | 34.9543
7848 | 0 | 3.8492 | 5.9344 | 22.8426 | 0 | 32.6263 | 0 | 0 | 22.8426
7849 | 0 | 3.3262 | 5.8661 | 33.1975 | 0 | 42.3898 | 0 | 0 | 33.1975
7850 | 0 | 3.3984 | 2.7323 | 38.8726 | 0 | 45.0033 | 0 | 0 | 38.8726
7851 | 0 | 3.632 | 5.5361 | 32.9414 | 0 | 42.1095 | 0 | 0 | 32.9414
7852 | 0 | 3.013 | 8.0787 | 36.7806 | 0 | 47.8723 | 0 | 0 | 36.7806
7853 | 0 | 3.4773 | 10.6796 | 30.9469 | 0 | 45.1037 | 0 | 0 | 30.9469
7854 | 0 | 3.5854 | 10.6004 | 30.6113 | 0 | 44.797 | 0 | 0 | 30.6113
7855 | 0 | 3.4395 | 10.5067 | 30.7641 | 0 | 44.7103 | 0 | 0 | 30.7641
7856 | 0 | 3.3843 | 10.2295 | 35.3855 | 14.1914 | 63.1906 | 0 | 0 | 49.5769
7857 | 0 | 3.3016 | 9.818 | 36.9667 | 17.2266 | 67.3128 | 0 | 0 | 54.1933
7858 | 0 | 3.3258 | 9.0044 | 33.6901 | 13.1057 | 59.1259 | 0 | 0 | 46.7958
7859 | 0 | 3.5534 | 7.5237 | 27.0435 | 15.0788 | 53.1993 | 0 | 0 | 42.1222
7860 | 0 | 3.4214 | 5.9842 | 28.971 | 16.0784 | 54.4551 | 0 | 0 | 45.0494
7861 | 0 | 3.1693 | 6.0409 | 29.3346 | 7.1667 | 45.7115 | 0 | 0 | 36.5013
7862 | 0 | 2.8606 | 5.5275 | 24.4907 | 16.5982 | 49.4769 | 0 | 0 | 41.0888
7863 | 0 | 3.5371 | 5.5386 | 35.658 | 25.5251 | 70.2588 | 0 | 0 | 61.1831
7864 | 0 | 3.1112 | 5.8955 | 23.0418 | 10.5959 | 42.6445 | 0 | 0 | 33.6377
7865 | 0 | 3.3858 | 6.8861 | 22.4747 | 15.8751 | 48.6217 | 0 | 0 | 38.3498
7866 | 0 | 3.4511 | 6.3882 | 29.6408 | 19.9651 | 59.4452 | 0 | 0 | 49.6059
7867 | 0 | 3.7999 | 5.7949 | 26.3342 | 1.7615 | 37.6905 | 0 | 0 | 28.0957
7868 | 0 | 3.2889 | 5.3738 | 38.6519 | 0 | 47.3145 | 0 | 0 | 38.6519
7869 | 0 | 3.5573 | 5.1812 | 36.7002 | 0 | 45.4386 | 0 | 0 | 36.7002
7870 | 0 | 3.1061 | 4.788 | 31.31 | 0 | 39.2041 | 0 | 0 | 31.31
7871 | 0 | 3.6286 | 4.9181 | 29.9526 | 0 | 38.4994 | 0 | 0 | 29.9526
7872 | 0 | 3.7121 | 5.5604 | 38.3635 | 0 | 47.636 | 0 | 0 | 38.3635
7873 | 0 | 3.4012 | 5.7078 | 28.0026 | 0 | 37.1117 | 0 | 0 | 28.0026
7874 | 0 | 3.2467 | 2.7332 | 28.5372 | 0 | 34.517 | 0 | 0 | 28.5372
7875 | 0 | 3.2005 | 4.1911 | 38.1225 | 0 | 45.5141 | 0 | 200 | 238.1225
7876 | 0 | 3.1742 | 5.8666 | 33.8072 | 0 | 42.848 | 0 | 0 | 33.8072
7877 | 0 | 2.9829 | 8.3689 | 34.899 | 0 | 46.2508 | 0 | 0 | 34.899
7878 | 0 | 2.8599 | 8.4522 | 28.6953 | 0 | 40.0074 | 0 | 0 | 28.6953
7879 | 0 | 3.3624 | 9.0159 | 31.7043 | 0 | 44.0826 | 0 | 0 | 31.7043
7880 | 0 | 3.6025 | 8.8006 | 24.778 | 12.9648 | 50.1458 | 0 | 0 | 37.7427
7881 | 0 | 3.0729 | 8.7073 | 35.7392 | 16.0457 | 63.5651 | 0 | 0 | 51.7849
7882 | 0 | 3.0003 | 8.2679 | 29.3364 | 12.7409 | 53.3455 | 0 | 0 | 42.0773
7883 | 0 | 2.7937 | 7.7052 | 30.7694 | 11.5384 | 52.8067 | 0 | 0 | 42.3079
7884 | 0 | 3.1063 | 7.1821 | 27.7313 | 18.7039 | 56.7237 | 0 | 0 | 46.4353
7885 | 0 | 3.3856 | 6.9076 | 35.0705 | 5.5959 | 50.9596 | 0 | 0 | 40.6664
7886 | 0 | 3.2715 | 6.2344 | 28.6991 | 16.7048 | 54.9098 | 0 | 0 | 45.4039
7887 | 0 | 3.3895 | 5.9854 | 23.66 | -0.86422 | 32.1706 | 0 | 0 | 22.7957
7888 | 0 | 3.0274 | 6.2969 | 24.3167 | 11.0847 | 44.7257 | 0 | 0 | 35.4015
7889 | 0 | 3.8372 | 6.237 | 27.0713 | 13.385 | 50.5305 | 0 | 0 | 40.4563
7890 | 0 | 3.5779 | 4.703 | 23.7447 | 10.0935 | 42.1191 | 200 | 0 | 233.8382
7891 | 0 | 3.3753 | 3.9473 | 26.1286 | 10.8246 | 44.2757 | 0 | 0 | 36.9531
7892 | 0 | 3.6402 | 3.4874 | 29.643 | 0 | 36.7707 | 0 | 0 | 29.643
7893 | 0 | 3.5407 | 3.3704 | 31.0298 | 0 | 37.941 | 0 | 0 | 31.0298
7894 | 0 | 3.4531 | 3.4653 | 33.9101 | 0 | 40.8285 | 0 | 0 | 33.9101
7895 | 0 | 3.5016 | 3.965 | 32.9192 | 0 | 40.3858 | 0 | 0 | 32.9192
7896 | 0 | 2.8369 | 4.7813 | 26.615 | 0 | 34.2331 | 0 | 0 | 26.615
7897 | 0 | 3.3234 | 6.4799 | 31.599 | 0 | 41.4023 | 0 | 0 | 31.599
7898 | 0 | 3.6609 | 9.5946 | 23.6654 | 0 | 36.921 | 0 | 0 | 23.6654
7899 | 0 | 3.0243 | 8.95 | 35.2585 | 0 | 47.2328 | 0 | 0 | 35.2585
7900 | 0 | 3.2534 | 8.9748 | 29.261 | 0 | 41.4892 | 0 | 0 | 29.261
7901 | 9.4659 | 3.3734 | 9.5429 | 29.4977 | 0 | 51.8799 | 0 | 0 | 38.9636
7902 | 54.9795 | 3.7102 | 9.7048 | 25.0984 | 0 | 93.493 | 0 | 0 | 80.078
7903 | 83.3239 | 3.5586 | 9.6164 | 20.3787 | 0 | 116.8776 | 0 | 0 | 103.7026
7904 | 72.769 | 2.9462 | 9.6225 | 27.5427 | 16.6782 | 129.5586 | 0 | 200 | 316.9899
7905 | 77.0515 | 3.222 | 9.5526 | 22.5644 | 10.8595 | 123.25 | 0 | 0 | 110.4754
7906 | 76.8812 | 3.7759 | 8.976 | 32.1895 | 14.7332 | 136.5557 | 0 | 0 | 123.8039
7907 | 56.5687 | 2.8715 | 8.0764 | 31.5193 | 12.752 | 111.7879 | 0 | 0 | 100.84
7908 | 56.5287 | 3.794 | 8.3936 | 33.1983 | 13.7431 | 115.6576 | 0 | 0 | 103.4701
7909 | 65.0595 | 3.5415 | 8.2196 | 33.4595 | 12.9487 | 123.2288 | 0 | 0 | 111.4677
7910 | 41.4971 | 3.2135 | 8.0562 | 25.9282 | 13.0579 | 91.753 | 0 | 0 | 80.4832
7911 | 23.8441 | 3.5304 | 7.9253 | 25.5703 | 11.3327 | 72.2028 | 0 | 0 | 60.7471
7912 | 0 | 3.7851 | 8.5858 | 32.1999 | 7.4907 | 52.0615 | 0 | 0 | 39.6906
7913 | 0 | 3.3018 | 9.7918 | 28.8696 | 20.2526 | 62.2159 | 0 | 0 | 49.1222
7914 | 0 | 3.0038 | 9.5989 | 26.3203 | 13.5534 | 52.4765 | 0 | 0 | 39.8737
7915 | 0 | 3.4185 | 7.7921 | 39.0401 | 7.6392 | 57.89 | 0 | 0 | 46.6794
7916 | 0 | 3.6052 | 6.003 | 25.0972 | 0 | 34.7054 | 0 | 0 | 25.0972
7917 | 0 | 3.3149 | 4.7439 | 40.8663 | 0 | 48.9251 | 0 | 0 | 40.8663
7918 | 0 | 3.6726 | 4.6711 | 35.8207 | 0 | 44.1643 | 0 | 0 | 35.8207
7919 | 0 | 3.4768 | 5.3444 | 27.2684 | 0 | 36.0896 | 0 | 0 | 27.2684
7920 | 0 | 3.5644 | 6.2324 | 25.8486 | 0 | 35.6455 | 0 | 0 | 25.8486
7921 | 0 | 3.8557 | 8.3059 | 24.9965 | 0 | 37.1581 | 0 | 0 | 24.9965
7922 | 0 | 3.549 | 11.3482 | 31.1324 | 0 | 46.0296 | 0 | 0 | 31.1324
7923 | 0 | 3.7831 | 10.5073 | 25.0338 | 0 | 39.3242 | 0 | 0 | 25.0338
7924 | 0 | 3.8176 | 10.2771 | 31.3079 | 0 | 45.4027 | 0 | 0 | 31.3079
7925 | 0 | 3.7221 | 10.8707 | 33.5983 | 0 | 48.1911 | 0 | 0 | 33.5983
7926 | 0 | 3.8369 | 10.7207 | 22.4201 | 0 | 36.9778 | 0 | 0 | 22.4201
7927 | 18.8583 | 3.0717 | 10.6478 | 25.3501 | 0 | 57.928 | 0 | 200 | 244.2084
7928 | 67.3746 | 3.2152 | 10.0337 | 27.2719 | 15.9537 | 123.8491 | 0 | 0 | 110.6002
7929 | 63.2001 | 2.4804 | 9.4847 | 22.8424 | 4.4108 | 102.4183 | 0 | 0 | 90.4532
7930 | 52.4341 | 3.5299 | 8.976 | 29.6902 | 2.6616 | 97.2918 | 0 | 0 | 84.7859
7931 | 50.0803 | 2.8897 | 7.9455 | 32.7336 | 11.9032 | 105.5523 | 0 | 0 | 94.7171
7932 | 12.6111 | 3.5235 | 7.2561 | 30.7628 | 18.9671 | 73.1206 | 0 | 0 | 62.3411
7933 | 0 | 3.3741 | 6.8 | 30.333 | 14.4203 | 54.9275 | 0 | 0 | 44.7534
7934 | 0 | 3.6226 | 6.9063 | 28.2447 | 14.0289 | 52.8025 | 0 | 0 | 42.2736
7935 | 0 | 3.7673 | 9.0416 | 31.6249 | 15.5442 | 59.978 | 0 | 0 | 47.1691
7936 | 0 | 3.5082 | 9.5326 | 28.5773 | 14.7481 | 56.3661 | 0 | 0 | 43.3254
7937 | 0 | 4.0694 | 10.7042 | 34.231 | 19.8879 | 68.8925 | 0 | 0 | 54.1189
7938 | 0 | 3.3162 | 9.5989 | 34.9669 | 24.6979 | 72.58 | 0 | 0 | 59.6648
7939 | 0 | 3.6167 | 7.8907 | 33.1466 | 29.5811 | 74.2352 | 0 | 0 | 62.7277
7940 | 0 | 3.5686 | 7.044 | 27.6988 | 0 | 38.3114 | 0 | 0 | 27.6988
7941 | 0 | 3.8249 | 6.8446 | 27.0133 | 0 | 37.6828 | 0 | 0 | 27.0133
7942 | 0 | 2.6074 | 6.9219 | 24.853 | 0 | 34.3823 | 0 | 0 | 24.853
7943 | 0 | 3.5217 | 7.5353 | 32.3343 | 0 | 43.3912 | 0 | 0 | 32.3343
7944 | 0 | 3.842 | 7.9254 | 29.0225 | 0 | 40.79 | 0 | 0 | 29.0225
7945 | 0 | 3.8211 | 10.2334 | 29.0298 | 0 | 43.0842 | 0 | 0 | 29.0298
7946 | 0 | 2.7193 | 12.8095 | 29.3035 | 0 | 44.8322 | 0 | 0 | 29.3035
7947 | 0 | 3.1494 | 10.7532 | 27.619 | 0 | 41.5216 | 0 | 0 | 27.619
7948 | 0 | 2.7783 | 9.3861 | 38.7478 | 0 | 50.9122 | 200 | 0 | 238.7478
7949 | 0 | 3.4134 | 9.9622 | 35.7435 | 0 | 49.1191 | 0 | 0 | 35.7435
7950 | 0 | 2.9649 | 9.4145 | 29.089 | 0 | 41.4684 | 0 | 200 | 229.089
7951 | 0 | 2.8419 | 8.8059 | 29.8057 | 0 | 41.4536 | 0 | 0 | 29.8057
7952 | 0 | 3.363 | 8.3887 | 37.0577 | 21.3359 | 70.1453 | 0 | 0 | 58.3936
7953 | 0 | 3.9386 | 7.9229 | 32.7898 | 7.2357 | 51.887 | 0 | 0 | 40.0255
7954 | 11.2309 | 3.1474 | 7.0812 | 34.0894 | 17.0839 | 72.6329 | 0 | 0 | 62.4043
7955 | 44.6518 | 3.9691 | 6.3746 | 34.2305 | 12.5701 | 101.7962 | 0 | 0 | 91.4524
7956 | 61.7305 | 3.4049 | 5.6635 | 36.1993 | 10.6389 | 117.6371 | 0 | 0 | 108.5687
7957 | 41.2691 | 3.541 | 4.7593 | 28.9415 | 11.773 | 90.2838 | 0 | 0 | 81.9836
7958 | 15.9383 | 3.3528 | 4.1958 | 26.5244 | 11.367 | 61.3783 | 0 | 0 | 53.8297
7959 | 0 | 3.5392 | 4.2329 | 29.9243 | 12.7153 | 50.4117 | 0 | 0 | 42.6396
7960 | 0 | 3.3585 | 4.0413 | 26.2716 | 15.0665 | 48.7378 | 0 | 0 | 41.3381
7961 | 0 | 2.9234 | 3.1772 | 26.2379 | 9.3354 | 41.6739 | 0 | 0 | 35.5733
7962 | 0 | 3.0188 | 2.1199 | 26.3762 | 11.7154 | 43.2303 | 0 | 0 | 38.0915
7963 | 0 | 2.8045 | 1.5861 | 23.2248 | 9.8542 | 37.4697 | 0 | 0 | 33.079
7964 | 0 | 4.001 | 1.239 | 32.106 | 0 | 37.3461 | 0 | 0 | 32.106
7965 | 0 | 4.0105 | 1.0274 | 28.0532 | 0 | 33.0911 | 0 | 0 | 28.0532
7966 | 0 | 3.7447 | 1.0722 | 25.8465 | 0 | 30.6633 | 0 | 0 | 25.8465
7967 | 0 | 3.0601 | 1.1947 | 30.5977 | 0 | 34.8524 | 0 | 0 | 30.5977
7968 | 0 | 3.1875 | 1.7984 | 33.8666 | 0 | 38.8525 | 0 | 0 | 33.8666
7969 | 0 | 3.0034 | 2.7569 | 22.6988 | 0 | 28.4591 | 0 | 0 | 22.6988
7970 | 0 | 3.0662 | 5.6978 | 28.3818 | 0 | 37.1458 | 0 | 0 | 28.3818
7971 | 0 | 3.2904 | 5.5077 | 26.5517 | 0 | 35.3498 | 0 | 0 | 26.5517
7972 | 0 | 3.2845 | 6.3016 | 25.3069 | 0 | 34.893 | 0 | 0 | 25.3069
7973 | 0 | 3.2762 | 6.8873 | 32.1122 | 0 | 42.2757 | 0 | 0 | 32.1122
7974 | 0 | 3.7442 | 6.7295 | 34.6043 | 0 | 45.0779 | 0 | 0 | 34.6043
7975 | 0 | 3.1864 | 6.4482 | 36.7169 | 0 | 46.3516 | 0 | 0 | 36.7169
7976 | 0 | 3.9914 | 6.4695 | 33.1203 | 13.8631 | 57.4442 | 0 | 0 | 46.9833
7977 | 13.8595 | 3.0449 | 5.7501 | 31.0232 | 15.1887 | 68.8664 | 0 | 0 | 60.0715
7978 | 50.5972 | 3.2728 | 4.9835 | 29.6127 | 19.3675 | 107.8337 | 0 | 0 | 99.5774
7979 | 20.917 | 2.9897 | 4.1493 | 32.302 | 19.2345 | 79.5924 | 0 | 0 | 72.4534
7980 | 0 | 3.0714 | 3.2368 | 30.0842 | 12.9637 | 49.356 | 0 | 0 | 43.0479
7981 | 0 | 3.862 | 2.3299 | 32.2781 | 13.9687 | 52.4388 | 0 | 0 | 46.2468
7982 | 0 | 3.419 | 2.3888 | 28.6042 | 8.5727 | 42.9847 | 0 | 0 | 37.1769
7983 | 0 | 3.3573 | 2.0295 | 33.2 | 13.1824 | 51.7692 | 0 | 0 | 46.3824
7984 | 0 | 3.5467 | 1.9886 | 32.7973 | 6.875 | 45.2077 | 0 | 0 | 39.6724
7985 | 0 | 2.9368 | 2.2272 | 35.4175 | 14.0419 | 54.6234 | 0 | 0 | 49.4594
7986 | 0 | 3.0634 | 2.1199 | 32.0161 | 10.26 | 47.4594 | 0 | 0 | 42.2761
7987 | 0 | 3.2725 | 1.5861 | 30.6759 | 14.3809 | 49.9154 | 0 | 0 | 45.0568
7988 | 0 | 3.0346 | 1.239 | 29.4885 | 0 | 33.7621 | 0 | 0 | 29.4885
7989 | 0 | 3.3529 | 1.0185 | 31.2603 | 0 | 35.6317 | 0 | 0 | 31.2603
7990 | 0 | 3.6689 | 1.0722 | 31.954 | 0 | 36.6951 | 0 | 0 | 31.954
7991 | 0 | 3.2996 | 1.1947 | 28.1556 | 0 | 32.6499 | 0 | 0 | 28.1556
7992 | 0 | 3.3367 | 1.2542 | 30.5478 | 0 | 35.1387 | 0 | 0 | 30.5478
7993 | 0 | 3.7338 | 2.7569 | 38.8641 | 0 | 45.3548 | 0 | 0 | 38.8641
7994 | 0 | 2.5983 | 5.2107 | 35.1662 | 0 | 42.9752 | 0 | 0 | 35.1662
7995 | 0 | 3.4955 | 4.77 | 30.6817 | 0 | 38.9473 | 0 | 0 | 30.6817
7996 | 0 | 3.6417 | 5.5476 | 23.762 | 0 | 32.9513 | 0 | 0 | 23.762
7997 | 3.9259 | 3.6324 | 5.6992 | 30.6287 | 0 | 43.8862 | 0 | 0 | 34.5546
7998 | 33.1034 | 3.5367 | 5.2781 | 24.2096 | 0 | 66.1279 | 0 | 0 | 57.3131
7999 | 61.7507 | 3.5157 | 4.901 | 31.1704 | 0 | 101.3378 | 0 | 0 | 92.921
8000 | 35.8993 | 3.3381 | 5.3042 | 36.7678 | 21.5595 | 102.869 | 0 | 200 | 294.2266
8001 | 7.0076 | 3.2862 | 4.8674 | 26.9373 | 21.3531 | 63.4515 | 0 | 0 | 55.2979
8002 | 17.1543 | 3.3978 | 4.4422 | 25.8456 | 17.6396 | 68.4795 | 0 | 0 | 60.6396
8003 | 0.042297 | 3.154 | 3.6911 | 33.4766 | 10.3464 | 50.7103 | 0 | 0 | 43.8652
8004 | 0 | 3.5661 | 2.8576 | 28.3258 | 8.3372 | 43.0867 | 0 | 0 | 36.663
8005 | 0 | 3.4605 | 2.3299 | 32.2253 | 19.8079 | 57.8236 | 0 | 0 | 52.0332
8006 | 0 | 3.7664 | 2.3888 | 30.8978 | 11.1063 | 48.1593 | 0 | 0 | 42.0041
8007 | 0 | 3.0918 | 2.859 | 26.9984 | 14.6582 | 47.6074 | 0 | 0 | 41.6567
8008 | 0 | 3.782 | 2.9998 | 32.7576 | 17.0611 | 56.6004 | 200 | 0 | 249.8187
8009 | 0 | 3.1707 | 2.8351 | 40.9476 | 12.3771 | 59.3305 | 0 | 0 | 53.3247
8010 | 0 | 3.2781 | 2.4718 | 26.8174 | 11.208 | 43.7754 | 0 | 0 | 38.0254
8011 | 0 | 3.7578 | 1.9531 | 31.9857 | 15.936 | 53.6325 | 0 | 0 | 47.9217
8012 | 0 | 3.1949 | 1.5255 | 34.2123 | 0 | 38.9327 | 0 | 0 | 34.2123
8013 | 0 | 2.5588 | 1.3639 | 31.2418 | 0 | 35.1645 | 0 | 0 | 31.2418
8014 | 0 | 3.0285 | 1.9519 | 29.7912 | 0 | 34.7716 | 0 | 0 | 29.7912
8015 | 0 | 3.4706 | 2.6391 | 30.3659 | 0 | 36.4756 | 0 | 0 | 30.3659
8016 | 0 | 3.6249 | 2.6561 | 29.6777 | 0 | 35.9587 | 0 | 0 | 29.6777
8017 | 0 | 2.5723 | 2.9263 | 28.2908 | 0 | 33.7894 | 0 | 0 | 28.2908
8018 | 0 | 2.3219 | 2.1992 | 24.5351 | 0 | 29.0563 | 0 | 0 | 24.5351
8019 | 0 | 2.5642 | 1.9945 | 33.687 | 0 | 38.2457 | 0 | 0 | 33.687
8020 | 0 | 2.7861 | 3.6751 | 24.7622 | 0 | 31.2233 | 0 | 0 | 24.7622
8021 | 0 | 2.1777 | 7.4126 | 27.1313 | 0 | 36.7216 | 0 | 0 | 27.1313
8022 | 0 | 2.3883 | 7.2781 | 28.1201 | 0 | 37.7864 | 0 | 0 | 28.1201
8023 | 0 | 2.7277 | 6.6881 | 27.1903 | 0 | 36.6062 | 0 | 0 | 27.1903
8024 | 0 | 2.5842 | 6.6454 | 32.1572 | 19.1142 | 60.501 | 0 | 0 | 51.2714
8025 | 0 | 2.6998 | 5.9907 | 35.7917 | 13.1243 | 57.6065 | 0 | 0 | 48.916
8026 | 0 | 2.6837 | 5.2682 | 25.6246 | 20.7661 | 54.3426 | 0 | 0 | 46.3907
8027 | 0 | 2.3541 | 3.4169 | 28.2413 | 3.1811 | 37.1933 | 0 | 0 | 31.4223
8028 | 0 | 2.6333 | 2.2739 | 28.7395 | 10.9593 | 44.606 | 0 | 0 | 39.6988
8029 | 0 | 2.739 | 2.4752 | 25.4766 | 17.146 | 47.8367 | 0 | 0 | 42.6225
8030 | 0 | 2.4747 | 1.8702 | 30.5281 | 12.702 | 47.575 | 0 | 0 | 43.2301
8031 | 0 | 2.3775 | 2.2301 | 25.1881 | 14.8738 | 44.6695 | 0 | 0 | 40.0618
8032 | 0 | 2.4379 | 2.3118 | 29.0554 | 18.5901 | 52.3952 | 0 | 0 | 47.6455
8033 | 0 | 2.4767 | 1.9 | 36.4568 | 19.7214 | 60.5549 | 0 | 0 | 56.1782
8034 | 0 | 2.6753 | 1.9367 | 18.5365 | 19.7085 | 42.857 | 0 | 0 | 38.245
8035 | 0 | 3.2293 | 1.5167 | 29.5665 | 22.579 | 56.8915 | 0 | 0 | 52.1455
8036 | 0 | 2.8524 | 1.4117 | 30.3934 | 0 | 34.6575 | 0 | 0 | 30.3934
8037 | 0 | 2.5605 | 1.1486 | 33.0622 | 0 | 36.7713 | 0 | 0 | 33.0622
8038 | 0 | 2.456 | 1.2344 | 22.7403 | 0 | 26.4307 | 0 | 0 | 22.7403
8039 | 0 | 2.6024 | 1.1264 | 27.8354 | 0 | 31.5642 | 0 | 0 | 27.8354
8040 | 0 | 2.8142 | 1.1609 | 31.6087 | 0 | 35.5838 | 0 | 0 | 31.6087
8041 | 0 | 2.6008 | 1.7134 | 22.9288 | 0 | 27.2431 | 0 | 0 | 22.9288
8042 | 0 | 2.2873 | 2.1636 | 31.6874 | 0 | 36.1383 | 0 | 0 | 31.6874
8043 | 0 | 2.3117 | 1.767 | 29.4703 | 0 | 33.5489 | 0 | 0 | 29.4703
8044 | 0 | 2.1651 | 2.6204 | 28.5082 | 0 | 33.2937 | 0 | 0 | 28.5082
8045 | 0 | 2.8154 | 4.2233 | 28.4166 | 0 | 35.4553 | 0 | 0 | 28.4166
8046 | 0 | 3.1011 | 4.0631 | 27.2532 | 0 | 34.4173 | 0 | 0 | 27.2532
8047 | 0 | 2.5579 | 3.8343 | 27.8336 | 0 | 34.2258 | 0 | 0 | 27.8336
8048 | 0 | 2.6341 | 3.5269 | 26.1628 | 15.214 | 47.5379 | 0 | 0 | 41.3769
8049 | 0 | 2.3216 | 2.9992 | 26.3894 | 10.068 | 41.7782 | 0 | 0 | 36.4575
8050 | 0 | 2.7286 | 2.9774 | 24.799 | 18.8991 | 49.404 | 0 | 0 | 43.6981
8051 | 0 | 2.3306 | 2.559 | 26.7641 | 12.8169 | 44.4705 | 0 | 0 | 39.581
8052 | 0 | 2.5492 | 1.8335 | 33.3613 | 20.6641 | 58.4081 | 0 | 0 | 54.0255
8053 | 0 | 2.7325 | 2.0907 | 30.3872 | 19.0372 | 54.2476 | 0 | 0 | 49.4244
8054 | 0 | 2.8398 | 2.2196 | 31.1289 | 9.3513 | 45.5397 | 0 | 0 | 40.4802
8055 | 0 | 2.7119 | 2.2605 | 36.1483 | 5.7577 | 46.8785 | 0 | 0 | 41.9061
8056 | 0 | 2.2987 | 2.1706 | 31.715 | 17.0057 | 53.19 | 0 | 0 | 48.7207
8057 | 0 | 2.864 | 2.1677 | 30.3696 | 21.6002 | 57.0015 | 0 | 0 | 51.9698
8058 | 0 | 2.3747 | 2.1706 | 29.5302 | 13.6722 | 47.7478 | 0 | 0 | 43.2024
8059 | 0 | 2.3734 | 1.5861 | 26.4051 | 18.9306 | 49.2953 | 0 | 0 | 45.3357
8060 | 0 | 2.6194 | 1.239 | 32.606 | 0 | 36.4644 | 0 | 0 | 32.606
8061 | 0 | 2.5748 | 1.0185 | 27.6226 | 0 | 31.2159 | 0 | 0 | 27.6226
8062 | 0 | 2.4952 | 1.0722 | 27.8942 | 0 | 31.4617 | 0 | 0 | 27.8942
8063 | 0 | 2.8911 | 1.1947 | 31.9871 | 0 | 36.073 | 0 | 0 | 31.9871
8064 | 0 | 2.1878 | 1.2542 | 19.9958 | 0 | 23.4378 | 0 | 0 | 19.9958
8065 | 0 | 2.4582 | 2.7569 | 32.9392 | 0 | 38.1544 | 0 | 0 | 32.9392
8066 | 0 | 2.6874 | 4.3028 | 31.1069 | 0 | 38.0971 | 0 | 0 | 31.1069
8067 | 0 | 2.8084 | 3.1308 | 33.9164 | 0 | 39.8556 | 0 | 0 | 33.9164
8068 | 0 | 2.4143 | 3.9711 | 23.4937 | 0 | 29.8791 | 0 | 0 | 23.4937
8069 | 15.8367 | 2.6579 | 4.7907 | 29.7228 | 0 | 53.008 | 0 | 0 | 45.5594
8070 | 70.9345 | 3.0174 | 4.0444 | 30.46 | 0 | 108.4564 | 0 | 0 | 101.3945
8071 | 88.032 | 2.6436 | 3.9432 | 28.6404 | 0 | 123.2592 | 0 | 200 | 316.6724
8072 | 85.4668 | 2.88 | 4.4817 | 24.847 | 15.8615 | 133.537 | 0 | 0 | 126.1754
8073 | 78.8881 | 2.5756 | 4.392 | 25.3079 | 19.1429 | 130.3066 | 0 | 0 | 123.3389
8074 | 33.5229 | 2.7379 | 3.7655 | 38.2781 | 14.8946 | 93.1991 | 0 | 0 | 86.6956
8075 | 11.6789 | 2.5249 | 2.9711 | 26.1908 | 13.79 | 57.1558 | 0 | 0 | 51.6597
8076 | 55.3551 | 2.8482 | 1.5684 | 34.5035 | 13.0296 | 107.3048 | 0 | 0 | 102.8882
8077 | 95.3124 | 2.659 | 2.3299 | 27.348 | 13.4811 | 141.1304 | 0 | 0 | 136.1415
8078 | 65.7464 | 2.4624 | 2.3888 | 26.4969 | 19.7289 | 116.8234 | 0 | 0 | 111.9721
8079 | 36.6577 | 2.6144 | 2.0295 | 24.8702 | 21.204 | 87.3759 | 0 | 0 | 82.732
8080 | 0 | 2.2627 | 2.9998 | 30.9886 | 12.477 | 48.728 | 0 | 0 | 43.4655
8081 | 0 | 2.6201 | 2.3789 | 21.3818 | 9.9888 | 36.3695 | 0 | 0 | 31.3706
8082 | 0 | 2.7642 | 2.1199 | 31.7462 | 18.5757 | 55.206 | 0 | 0 | 50.3219
8083 | 0 | 3.0475 | 1.5861 | 30.9247 | 15.6554 | 51.2137 | 200 | 0 | 246.5801
8084 | 0 | 2.2091 | 1.4923 | 34.3077 | 0 | 38.0091 | 0 | 0 | 34.3077
8085 | 0 | 2.4663 | 3.6936 | 36.6758 | 0 | 42.8357 | 0 | 0 | 36.6758
8086 | 0 | 2.6912 | 3.4653 | 32.0411 | 0 | 38.1976 | 0 | 0 | 32.0411
8087 | 0 | 2.8832 | 4.2084 | 27.3272 | 0 | 34.4188 | 0 | 0 | 27.3272
8088 | 0 | 2.862 | 5.1844 | 24.5054 | 0 | 32.5518 | 0 | 0 | 24.5054
8089 | 0 | 2.6207 | 8.0016 | 30.1717 | 0 | 40.794 | 0 | 0 | 30.1717
8090 | 0 | 2.5884 | 10.7637 | 33.3525 | 0 | 46.7046 | 0 | 0 | 33.3525
8091 | 0 | 2.3643 | 10.5073 | 29.8805 | 0 | 42.7521 | 0 | 0 | 29.8805
8092 | 0 | 2.7369 | 8.9063 | 26.9201 | 0 | 38.5633 | 0 | 0 | 26.9201
8093 | 3.9682 | 2.6092 | 8.5645 | 29.6916 | 0 | 44.8335 | 0 | 0 | 33.6598
8094 | 23.8371 | 2.6778 | 7.4551 | 25.5065 | 0 | 59.4765 | 0 | 0 | 49.3436
8095 | 63.7867 | 2.9277 | 7.185 | 35.4471 | 0 | 109.3465 | 0 | 0 | 99.2338
8096 | 53.0309 | 2.5005 | 7.2234 | 29.3621 | 10.0724 | 102.1894 | 0 | 0 | 92.4654
8097 | 22.4917 | 2.391 | 7.2439 | 35.3776 | 8.7415 | 76.2457 | 0 | 0 | 66.6108
8098 | 33.7691 | 2.5227 | 8.2316 | 29.4349 | 14.3065 | 88.2649 | 0 | 0 | 77.5106
8099 | 87.0394 | 2.7403 | 8.6 | 26.3936 | 10.4355 | 135.2087 | 0 | 0 | 123.8684
8100 | 52.4339 | 2.5095 | 9.2278 | 26.3767 | 1.156 | 91.7039 | 0 | 0 | 79.9666
8101 | 5.885 | 2.2545 | 9.3731 | 30.1968 | 5.5538 | 53.2632 | 0 | 0 | 41.6356
8102 | 16.4897 | 2.1994 | 9.5346 | 31.1872 | 19.5 | 78.9109 | 0 | 0 | 67.1768
8103 | 0 | 2.2046 | 10.6731 | 29.9227 | 14.8086 | 57.609 | 0 | 0 | 44.7313
8104 | 0.32316 | 2.6949 | 10.6687 | 26.6365 | 22.4043 | 62.7276 | 0 | 200 | 249.364
8105 | 17.1254 | 2.3399 | 11.8446 | 32.8868 | 12.6402 | 76.8369 | 0 | 0 | 62.6523
8106 | 45.7922 | 2.337 | 11.3807 | 26.0283 | 6.6772 | 92.2154 | 0 | 0 | 78.4977
8107 | 0 | 2.5802 | 6.2148 | 25.8843 | 6.1747 | 40.8538 | 0 | 0 | 32.0589
8108 | 0 | 2.6144 | 6.2633 | 33.1959 | 0 | 42.0736 | 0 | 0 | 33.1959
8109 | 0 | 2.6518 | 6.683 | 31.5501 | 0 | 40.8848 | 0 | 0 | 31.5501
8110 | 0 | 2.4623 | 6.6807 | 30.6926 | 0 | 39.8356 | 0 | 0 | 30.6926
8111 | 0 | 2.8507 | 7.5353 | 29.1855 | 0 | 39.5715 | 0 | 0 | 29.1855
8112 | 0 | 2.5145 | 7.5223 | 32.5775 | 0 | 42.6144 | 0 | 0 | 32.5775
8113 | 0 | 2.4728 | 9.8276 | 29.318 | 0 | 41.6184 | 0 | 0 | 29.318
8114 | 0 | 2.8119 | 12.4198 | 34.4811 | 0 | 49.7129 | 0 | 0 | 34.4811
8115 | 0 | 2.3356 | 10.7532 | 31.2504 | 0 | 44.3392 | 0 | 0 | 31.2504
8116 | 0 | 2.5225 | 10.1401 | 29.9184 | 0 | 42.5809 | 0 | 0 | 29.9184
8117 | 0 | 2.944 | 10.0321 | 26.1197 | 0 | 39.0958 | 0 | 0 | 26.1197
8118 | 0 | 2.299 | 9.4871 | 30.329 | 0 | 42.1151 | 0 | 0 | 30.329
8119 | 0 | 2.214 | 9.1743 | 27.0454 | 0 | 38.4336 | 0 | 0 | 27.0454
8120 | 0 | 2.5765 | 8.937 | 22.1121 | 16.2045 | 49.8301 | 0 | 0 | 38.3166
8121 | 0 | 2.39 | 8.3983 | 31.9739 | 20.0573 | 62.8195 | 0 | 0 | 52.0312
8122 | 0 | 2.7343 | 7.6226 | 36.7983 | 16.7892 | 63.9445 | 0 | 0 | 53.5876
8123 | 14.4613 | 2.5629 | 6.5055 | 32.1732 | 8.6648 | 64.3677 | 0 | 0 | 55.2992
8124 | 61.3298 | 2.3997 | 5.5118 | 34.0292 | 10.5519 | 113.8224 | 0 | 0 | 105.9109
8125 | 79.4153 | 2.8456 | 4.4044 | 29.3744 | 21.4504 | 137.4901 | 0 | 0 | 130.2401
8126 | 65.3983 | 2.3666 | 4.1137 | 34.3023 | 22.9955 | 129.1764 | 0 | 0 | 122.6961
8127 | 39.4235 | 2.2968 | 4.2329 | 24.1767 | 7.718 | 77.8479 | 0 | 0 | 71.3182
8128 | 0 | 2.5541 | 3.6625 | 33.3867 | 3.9805 | 43.5838 | 0 | 0 | 37.3672
8129 | 0 | 2.9991 | 2.607 | 29.8959 | 8.2785 | 43.7806 | 0 | 0 | 38.1744
8130 | 0 | 2.3603 | 2.1199 | 36.5773 | 10.6631 | 51.7206 | 0 | 0 | 47.2404
8131 | 0 | 2.6109 | 1.5861 | 31.6575 | 7.3813 | 43.2359 | 0 | 0 | 39.0389
8132 | 0 | 2.8406 | 1.239 | 31.5322 | 0 | 35.6119 | 0 | 0 | 31.5322
8133 | 0 | 2.1222 | 1.0185 | 30.3893 | 0 | 33.5301 | 0 | 0 | 30.3893
8134 | 0 | 2.3751 | 1.1341 | 33.1121 | 0 | 36.6214 | 0 | 0 | 33.1121
8135 | 0 | 2.6947 | 1.2872 | 31.7411 | 0 | 35.7229 | 0 | 0 | 31.7411
8136 | 0 | 2.5922 | 1.7178 | 29.3927 | 0 | 33.7026 | 0 | 0 | 29.3927
8137 | 0 | 3.0964 | 2.7569 | 32.2018 | 0 | 38.0551 | 0 | 200 | 232.2018
8138 | 0 | 2.2444 | 4.6262 | 23.0173 | 0 | 29.8879 | 0 | 0 | 23.0173
8139 | 0 | 2.3045 | 4.1963 | 33.434 | 0 | 39.9348 | 0 | 0 | 33.434
8140 | 0 | 2.6134 | 4.7251 | 30.2474 | 0 | 37.5859 | 0 | 0 | 30.2474
8141 | 8.0769 | 2.6952 | 5.1401 | 26.1994 | 0 | 42.1117 | 0 | 0 | 34.2763
8142 | 31.2139 | 2.287 | 4.7701 | 33.1163 | 0 | 71.3872 | 0 | 0 | 64.3302
8143 | 39.9834 | 2.4809 | 4.6063 | 16.9557 | 0 | 64.0263 | 0 | 0 | 56.9391
8144 | 18.7161 | 2.7075 | 4.9615 | 35.0957 | 14.2038 | 75.6846 | 0 | 0 | 68.0157
8145 | 72.6479 | 2.7352 | 4.6636 | 23.936 | 13.4494 | 117.4322 | 0 | 0 | 110.0333
8146 | 61.3002 | 2.5659 | 4.0362 | 31.9997 | 10.1864 | 110.0884 | 0 | 0 | 103.4863
8147 | 42.9404 | 2.6362 | 3.1675 | 28.6737 | 18.0522 | 95.47 | 0 | 0 | 89.6663
8148 | 2.6165 | 2.6264 | 1.4926 | 32.4996 | 14.6167 | 53.8519 | 0 | 0 | 49.7329
8149 | 31.8072 | 3.268 | 2.3299 | 27.1267 | 14.2319 | 78.7636 | 0 | 0 | 73.1657
8150 | 67.3333 | 2.393 | 2.3888 | 32.3055 | 15.1893 | 119.6099 | 0 | 0 | 114.8281
8151 | 35.5098 | 2.4641 | 2.0295 | 37.0323 | 9.8514 | 86.8871 | 0 | 0 | 82.3935
8152 | 10.8825 | 2.0741 | 1.9886 | 26.9045 | 2.9228 | 44.7725 | 0 | 0 | 40.7098
8153 | 1.167 | 2.4603 | 2.2272 | 28.7252 | 6.6922 | 41.272 | 0 | 0 | 36.5845
8154 | 3.0633 | 2.5356 | 2.1199 | 24.8706 | 7.5928 | 40.1821 | 0 | 0 | 35.5267
8155 | 0 | 2.6681 | 1.5861 | 33.2877 | 7.2367 | 44.7786 | 0 | 0 | 40.5244
8156 | 0 | 2.2682 | 1.239 | 33.7389 | 0 | 37.2461 | 0 | 0 | 33.7389
8157 | 0 | 2.6271 | 1.0185 | 29.2295 | 0 | 32.8751 | 0 | 0 | 29.2295
8158 | 0 | 2.7454 | 1.0722 | 31.4255 | 0 | 35.2431 | 0 | 0 | 31.4255
8159 | 0 | 2.5819 | 1.1947 | 28.8397 | 0 | 32.6163 | 0 | 0 | 28.8397
8160 | 0 | 2.6726 | 1.2542 | 22.4818 | 0 | 26.4085 | 0 | 0 | 22.4818
8161 | 0 | 2.5898 | 2.7569 | 28.4167 | 0 | 33.7634 | 200 | 0 | 228.4167
8162 | 0 | 2.5774 | 4.3028 | 24.629 | 0 | 31.5093 | 0 | 0 | 24.629
8163 | 0 | 2.1693 | 3.5406 | 31.2314 | 0 | 36.9413 | 0 | 0 | 31.2314
8164 | 0 | 2.4698 | 4.4509 | 28.3642 | 0 | 35.2849 | 0 | 0 | 28.3642
8165 | 3.6736 | 2.2478 | 4.9305 | 22.2886 | 0 | 33.1405 | 0 | 0 | 25.9622
8166 | 25.4613 | 2.1639 | 4.6975 | 30.6943 | 0 | 63.017 | 0 | 0 | 56.1556
8167 | 46.7546 | 2.9204 | 4.8273 | 22.0264 | 0 | 76.5287 | 0 | 0 | 68.781
8168 | 0.4205 | 2.5961 | 4.9615 | 31.3712 | 8.8861 | 48.2353 | 0 | 0 | 40.6777
8169 | 22.9083 | 2.3176 | 4.7315 | 32.779 | 21.2566 | 83.9931 | 0 | 0 | 76.9439
8170 | 52.3166 | 2.7226 | 3.9685 | 31.1325 | 15.3275 | 105.4676 | 0 | 0 | 98.7766
8171 | 29.221 | 2.5077 | 3.5602 | 23.8281 | 20.0518 | 79.1689 | 0 | 0 | 73.1009
8172 | 0 | 2.1725 | 4.071 | 25.8631 | 18.5572 | 50.6638 | 0 | 0 | 44.4203
8173 | 0 | 2.7427 | 3.6058 | 26.2036 | 19.7856 | 52.3377 | 0 | 0 | 45.9892
8174 | 0 | 2.2665 | 3.7851 | 26.0577 | 23.5619 | 55.6711 | 0 | 0 | 49.6195
8175 | 0 | 2.561 | 3.9753 | 29.9998 | 17.3055 | 53.8416 | 0 | 0 | 47.3053
8176 | 0 | 2.6436 | 4.3253 | 31.848 | 13.5272 | 52.3441 | 0 | 0 | 45.3752
8177 | 0 | 2.5525 | 4.2036 | 27.9726 | 4.2929 | 39.0217 | 0 | 0 | 32.2655
8178 | 0 | 2.567 | 3.8081 | 31.6876 | 15.4253 | 53.4881 | 0 | 0 | 47.1129
8179 | 0 | 2.5458 | 1.9531 | 24.8089 | 20.9571 | 50.2648 | 0 | 0 | 45.766
8180 | 0 | 2.5057 | 1.5255 | 27.1511 | 0 | 31.1822 | 0 | 0 | 27.1511
8181 | 0 | 2.5581 | 1.1896 | 29.3748 | 0 | 33.1225 | 0 | 0 | 29.3748
8182 | 0 | 2.417 | 1.3195 | 29.2252 | 0 | 32.9618 | 0 | 0 | 29.2252
8183 | 0 | 2.8811 | 1.6813 | 24.4113 | 0 | 28.9737 | 0 | 0 | 24.4113
8184 | 0 | 2.2998 | 1.3952 | 32.989 | 0 | 36.684 | 0 | 0 | 32.989
8185 | 0 | 2.7312 | 1.7973 | 33.56 | 0 | 38.0884 | 0 | 0 | 33.56
8186 | 0 | 2.2409 | 2.1992 | 28.4302 | 0 | 32.8704 | 0 | 0 | 28.4302
8187 | 0 | 2.5648 | 1.9945 | 28.8917 | 0 | 33.451 | 0 | 0 | 28.8917
8188 | 0 | 2.3161 | 3.6751 | 28.4869 | 0 | 34.4781 | 0 | 0 | 28.4869
8189 | 0 | 2.3072 | 6.5958 | 36.3331 | 0 | 45.2362 | 0 | 0 | 36.3331
8190 | 0 | 2.5371 | 6.6255 | 23.9321 | 0 | 33.0947 | 0 | 0 | 23.9321
8191 | 0 | 2.9375 | 5.9244 | 29.2262 | 0 | 38.0881 | 0 | 0 | 29.2262
8192 | 0 | 2.6867 | 6.1078 | 34.0678 | 17.0491 | 59.9114 | 0 | 0 | 51.1169
8193 | 0 | 2.93 | 5.342 | 31.4417 | 19.1804 | 58.8942 | 0 | 0 | 50.6221
8194 | 0 | 2.369 | 5.0272 | 27.5904 | 5.5891 | 40.5756 | 0 | 0 | 33.1795
8195 | 0 | 2.3205 | 2.9036 | 22.5081 | 11.8694 | 39.6015 | 0 | 0 | 34.3774
8196 | 0 | 2.4792 | 2.2739 | 33.8027 | 12.4154 | 50.9712 | 0 | 0 | 46.2181
8197 | 0 | 2.333 | 2.4752 | 24.1127 | 4.9161 | 33.8369 | 0 | 200 | 229.0288
8198 | 0 | 2.2697 | 1.8702 | 33.8693 | 7.1225 | 45.1317 | 0 | 0 | 40.9918
8199 | 0 | 2.33 | 2.2301 | 26.9942 | 14.3926 | 45.9469 | 0 | 0 | 41.3867
8200 | 0 | 3.2712 | 2.3118 | 36.0124 | 10.5615 | 52.1569 | 0 | 0 | 46.5739
8201 | 0 | 2.5584 | 1.9 | 23.0885 | 15.7959 | 43.3427 | 0 | 0 | 38.8844
8202 | 0 | 2.6198 | 1.9367 | 22.111 | 14.8498 | 41.5174 | 0 | 0 | 36.9608
8203 | 0 | 2.5579 | 1.5167 | 26.4767 | 16.2238 | 46.7751 | 0 | 0 | 42.7004
8204 | 0 | 2.3387 | 1.4117 | 21.037 | 0 | 24.7874 | 0 | 0 | 21.037
8205 | 0 | 2.3645 | 1.1486 | 24.9416 | 0 | 28.4547 | 0 | 0 | 24.9416
8206 | 0 | 2.5632 | 1.2344 | 27.6453 | 0 | 31.4429 | 0 | 0 | 27.6453
8207 | 0 | 2.5735 | 1.1264 | 24.7286 | 0 | 28.4285 | 0 | 0 | 24.7286
8208 | 0 | 2.2146 | 1.1609 | 28.167 | 0 | 31.5425 | 0 | 0 | 28.167
8209 | 0 | 3.0057 | 2.3153 | 26.1845 | 0 | 31.5055 | 0 | 0 | 26.1845
8210 | 0 | 2.9873 | 2.1636 | 23.5792 | 0 | 28.7301 | 0 | 0 | 23.5792
8211 | 0 | 2.4222 | 1.767 | 33.0241 | 0 | 37.2133 | 0 | 0 | 33.0241
8212 | 0 | 2.6685 | 2.7623 | 30.2973 | 0 | 35.7281 | 0 | 0 | 30.2973
8213 | 0 | 2.555 | 6.1481 | 31.6869 | 0 | 40.3899 | 0 | 0 | 31.6869
8214 | 0 | 2.597 | 5.8675 | 31.3366 | 0 | 39.8011 | 0 | 0 | 31.3366
8215 | 0 | 2.7484 | 5.9614 | 25.2587 | 0 | 33.9685 | 0 | 0 | 25.2587
8216 | 0 | 2.5648 | 5.9191 | 34.4223 | 7.773 | 50.6791 | 0 | 0 | 42.1952
8217 | 0 | 2.6609 | 5.703 | 28.5247 | 13.7684 | 50.657 | 0 | 0 | 42.2931
8218 | 0 | 2.4523 | 5.8307 | 37.4146 | 7.0908 | 52.7884 | 0 | 0 | 44.5054
8219 | 0 | 2.5035 | 5.4574 | 25.4792 | 13.4828 | 46.9229 | 0 | 0 | 38.962
8220 | 0 | 2.7725 | 5.2798 | 27.4982 | 1.6026 | 37.1532 | 0 | 0 | 29.1008
8221 | 0 | 2.6812 | 4.5929 | 29.4174 | 22.0524 | 58.7438 | 0 | 0 | 51.4698
8222 | 0 | 2.5836 | 4.8091 | 34.3363 | 11.4756 | 53.2046 | 0 | 0 | 45.8119
8223 | 0 | 3.1994 | 3.9076 | 27.994 | 7.4508 | 42.5518 | 0 | 0 | 35.4448
8224 | 0 | 2.2236 | 4.5326 | 20.4654 | 8.6672 | 35.8888 | 0 | 0 | 29.1325
8225 | 0 | 2.4349 | 4.1243 | 24.8728 | 11.1244 | 42.5564 | 0 | 0 | 35.9972
8226 | 0 | 2.7494 | 4.0718 | 33.2276 | 1.1561 | 41.2048 | 0 | 0 | 34.3837
8227 | 0 | 2.5756 | 3.4543 | 29.7659 | 14.1801 | 49.976 | 0 | 0 | 43.9461
8228 | 0 | 2.7369 | 3.1405 | 29.23 | 0 | 35.1074 | 0 | 0 | 29.23
8229 | 0 | 2.5532 | 3.2897 | 27.0872 | 0 | 32.93 | 0 | 0 | 27.0872
8230 | 0 | 2.1888 | 4.1084 | 31.7995 | 0 | 38.0967 | 0 | 0 | 31.7995
8231 | 0 | 2.9498 | 4.0461 | 27.4459 | 0 | 34.4419 | 0 | 0 | 27.4459
8232 | 0 | 2.6983 | 4.5394 | 27.9838 | 0 | 35.2215 | 0 | 0 | 27.9838
8233 | 0 | 2.9151 | 7.2915 | 32.9931 | 0 | 43.1997 | 0 | 0 | 32.9931
8234 | 0 | 2.2409 | 10.5688 | 31.492 | 0 | 44.3018 | 0 | 0 | 31.492
8235 | 0 | 2.7145 | 9.2779 | 24.0464 | 0 | 36.0388 | 0 | 0 | 24.0464
8236 | 0 | 1.9595 | 8.9063 | 26.1831 | 0 | 37.0489 | 0 | 0 | 26.1831
8237 | 9.3095 | 2.3004 | 9.0537 | 37.4727 | 0 | 58.1363 | 0 | 0 | 46.7822
8238 | 46.4992 | 2.6518 | 8.4711 | 29.1244 | 0 | 86.7465 | 0 | 0 | 75.6236
8239 | 98.4921 | 2.6695 | 8.1428 | 25.4533 | 0 | 134.7577 | 0 | 0 | 123.9454
8240 | 68.7434 | 2.6475 | 9.1427 | 28.5683 | 10.1434 | 119.2453 | 200 | 200 | 507.4551
8241 | 70.2168 | 2.7692 | 8.2625 | 21.7545 | 19.8798 | 122.8828 | 0 | 0 | 111.8511
8242 | 49.2154 | 2.1777 | 7.8256 | 23.8232 | 7.9569 | 90.9987 | 0 | 0 | 80.9954
8243 | 83.7441 | 2.4898 | 7.1601 | 33.5556 | 11.4528 | 138.4024 | 0 | 0 | 128.7525
8244 | 31.7641 | 2.3331 | 6.1944 | 32.6592 | 11.7328 | 84.6836 | 0 | 0 | 76.1561
8245 | 19.2447 | 2.8481 | 5.824 | 27.9062 | 14.0579 | 69.8809 | 0 | 0 | 61.2088
8246 | 81.0422 | 2.656 | 5.4278 | 21.8455 | 15.4602 | 126.4316 | 0 | 0 | 118.3478
8247 | 36.9454 | 3.2548 | 6.5513 | 30.9508 | 16.0621 | 93.7644 | 0 | 0 | 83.9583
8248 | 0 | 2.488 | 5.9348 | 27.5868 | 13.13 | 49.1396 | 0 | 0 | 40.7168
8249 | 0 | 2.8215 | 5.9143 | 33.3616 | 10.7669 | 52.8643 | 0 | 0 | 44.1286
8250 | 0 | 3.1062 | 4.8104 | 30.901 | 24.7946 | 63.6123 | 0 | 0 | 55.6957
8251 | 0 | 2.2285 | 4.243 | 24.5349 | 9.7667 | 40.773 | 0 | 0 | 34.3015
8252 | 0 | 2.3104 | 3.4874 | 35.6065 | 0 | 41.4043 | 0 | 0 | 35.6065
8253 | 0 | 2.5967 | 3.2897 | 26.5942 | 0 | 32.4805 | 0 | 0 | 26.5942
8254 | 0 | 2.5562 | 3.5457 | 30.761 | 0 | 36.8628 | 0 | 0 | 30.761
8255 | 0 | 2.7303 | 4.0461 | 23.7392 | 0 | 30.5156 | 0 | 0 | 23.7392
8256 | 0 | 2.538 | 5.9906 | 26.0438 | 0 | 34.5724 | 0 | 0 | 26.0438
8257 | 0 | 2.4658 | 8.6103 | 23.3794 | 0 | 34.4555 | 0 | 0 | 23.3794
8258 | 0 | 2.9003 | 12.1275 | 27.8011 | 0 | 42.8289 | 0 | 0 | 27.8011
8259 | 0 | 2.4789 | 11.2449 | 27.7697 | 0 | 41.4935 | 0 | 0 | 27.7697
8260 | 0 | 2.3385 | 9.8659 | 32.0897 | 0 | 44.2941 | 0 | 0 | 32.0897
8261 | 0 | 2.0828 | 9.3333 | 32.5094 | 0 | 43.9255 | 0 | 0 | 32.5094
8262 | 14.4484 | 2.514 | 8.2534 | 21.2999 | 0 | 46.5157 | 0 | 0 | 35.7483
8263 | 62.898 | 2.6175 | 8.2165 | 31.8837 | 0 | 105.6157 | 0 | 0 | 94.7816
8264 | 60.4035 | 2.5259 | 8.1145 | 29.0531 | 14.7903 | 114.8873 | 0 | 0 | 104.2469
8265 | 36.3258 | 2.5151 | 8.7378 | 27.606 | 8.4643 | 83.649 | 0 | 0 | 72.3961
8266 | 20.8775 | 2.5107 | 8.8406 | 31.0932 | 16.5717 | 79.8937 | 0 | 0 | 68.5425
8267 | 62.0398 | 2.6539 | 7.3564 | 26.3348 | 4.3137 | 102.6987 | 0 | 0 | 92.6883
8268 | 15.6878 | 3.2375 | 7.5594 | 27.0683 | 16.7898 | 70.3428 | 0 | 0 | 59.5459
8269 | 47.1159 | 2.6691 | 6.9775 | 33.5234 | 18.6928 | 108.9787 | 0 | 200 | 299.3321
8270 | 16.0818 | 2.7213 | 9.0418 | 26.8646 | 4.3181 | 59.0277 | 0 | 0 | 47.2646
8271 | 0 | 2.4381 | 9.9861 | 35.3748 | 12.4284 | 60.2274 | 0 | 0 | 47.8032
8272 | 0 | 2.3589 | 11.0474 | 31.7214 | 28.4703 | 73.5981 | 0 | 0 | 60.1917
8273 | 0 | 2.5672 | 12.0727 | 32.1828 | 18.444 | 65.2667 | 0 | 0 | 50.6268
8274 | 0 | 2.8093 | 10.7126 | 29.5558 | 15.0128 | 58.0905 | 0 | 0 | 44.5687
8275 | 0 | 2.2175 | 9.8624 | 23.4192 | 15.0904 | 50.5895 | 0 | 0 | 38.5096
8276 | 0 | 2.7424 | 8.1716 | 25.3493 | 0 | 36.2634 | 0 | 0 | 25.3493
8277 | 0 | 2.0631 | 7.5717 | 32.606 | 0 | 42.2408 | 0 | 0 | 32.606
8278 | 0 | 2.277 | 7.4042 | 23.6054 | 0 | 33.2866 | 0 | 0 | 23.6054
8279 | 0 | 2.9452 | 8.4279 | 29.3469 | 0 | 40.7199 | 0 | 0 | 29.3469
8280 | 0 | 2.5194 | 8.9735 | 24.3486 | 0 | 35.8415 | 0 | 0 | 24.3486
8281 | 0 | 2.455 | 11.1464 | 22.4066 | 0 | 36.008 | 0 | 0 | 22.4066
8282 | 0 | 2.4986 | 13.394 | 30.7442 | 0 | 46.6368 | 0 | 0 | 30.7442
8283 | 0 | 2.212 | 12.6383 | 26.9075 | 0 | 41.7578 | 0 | 0 | 26.9075
8284 | 0 | 2.0492 | 11.648 | 26.7397 | 0 | 40.437 | 0 | 0 | 26.7397
8285 | 0 | 2.8807 | 11.0804 | 25.3055 | 0 | 39.2666 | 0 | 0 | 25.3055
8286 | 0 | 2.6151 | 10.6482 | 29.818 | 0 | 43.0813 | 0 | 0 | 29.818
8287 | 0 | 2.9637 | 10.4268 | 24.0943 | 0 | 37.4848 | 0 | 0 | 24.0943
8288 | 0 | 2.685 | 9.9652 | 27.3425 | 12.4603 | 52.4529 | 0 | 0 | 39.8028
8289 | 0 | 2.8722 | 9.5526 | 24.2347 | 24.2353 | 60.8948 | 0 | 200 | 248.47
8290 | 0 | 3.1775 | 9.2466 | 26.6213 | 15.5873 | 54.6327 | 0 | 0 | 42.2085
8291 | 0 | 2.2622 | 9.909 | 28.0619 | 6.7398 | 46.973 | 0 | 0 | 34.8017
8292 | 0 | 2.1567 | 10.2137 | 36.8466 | 17.7049 | 66.9218 | 0 | 0 | 54.5515
8293 | 0 | 2.6072 | 10.7927 | 35.8241 | 11.9191 | 61.1431 | 0 | 0 | 47.7432
8294 | 0 | 2.5901 | 9.2061 | 21.4284 | 16.5776 | 49.8021 | 0 | 0 | 38.006
8295 | 0 | 2.4635 | 9.4709 | 34.3578 | 15.4031 | 61.6953 | 0 | 0 | 49.7609
8296 | 0 | 2.9147 | 9.4379 | 31.3421 | 14.5751 | 58.2698 | 0 | 0 | 45.9172
8297 | 0 | 2.9272 | 12.4149 | 22.6791 | 15.1716 | 53.1927 | 0 | 0 | 37.8507
8298 | 11.3343 | 3.086 | 11.9375 | 31.47 | 13.908 | 71.7358 | 0 | 0 | 56.7122
8299 | 31.137 | 2.2434 | 8.9752 | 24.4309 | 16.1875 | 82.9739 | 0 | 0 | 71.7553
8300 | 20.529 | 2.5001 | 7.7379 | 26.4482 | 0 | 57.2152 | 0 | 0 | 46.9771
8301 | 66.2242 | 2.2903 | 8.3797 | 26.371 | 0 | 103.2652 | 0 | 0 | 92.5952
8302 | 38.4311 | 2.2864 | 7.0826 | 29.3475 | 0 | 77.1476 | 0 | 0 | 67.7786
8303 | 52.0418 | 2.5743 | 7.6164 | 26.3802 | 0 | 88.6127 | 0 | 0 | 78.4219
8304 | 63.1417 | 2.8692 | 8.7316 | 29.52 | 0 | 104.2625 | 0 | 0 | 92.6617
8305 | 37.8208 | 2.6043 | 11.6536 | 32.3104 | 0 | 84.3891 | 0 | 0 | 70.1312
8306 | 9.2958 | 2.536 | 15.0501 | 32.205 | 0 | 59.0869 | 0 | 0 | 41.5008
8307 | 0 | 2.3253 | 13.212 | 22.3141 | 0 | 37.8513 | 0 | 0 | 22.3141
8308 | 0 | 2.3594 | 12.1964 | 34.6422 | 0 | 49.1979 | 0 | 200 | 234.6422
8309 | 7.1149 | 2.5017 | 12.3383 | 28.8009 | 0 | 50.7558 | 0 | 0 | 35.9158
8310 | 29.6461 | 2.5122 | 11.8093 | 26.6597 | 0 | 70.6273 | 0 | 0 | 56.3058
8311 | 46.8352 | 2.57 | 11.3109 | 27.2113 | 0 | 87.9274 | 0 | 0 | 74.0464
8312 | 40.3807 | 2.4623 | 10.7877 | 36.2818 | 15.4834 | 105.3959 | 0 | 0 | 92.1459
8313 | 47.0879 | 2.7172 | 10.5711 | 28.3336 | 14.3857 | 103.0955 | 0 | 0 | 89.8072
8314 | 0 | 2.8221 | 10.194 | 28.7458 | 18.9666 | 60.7284 | 0 | 0 | 47.7123
8315 | 0 | 2.6046 | 9.32 | 26.0053 | 3.5319 | 41.4618 | 0 | 0 | 29.5372
8316 | 0 | 2.4923 | 8.8486 | 28.4209 | 20.2343 | 59.9961 | 0 | 0 | 48.6551
8317 | 0 | 2.6407 | 8.6633 | 25.7832 | 20.3649 | 57.4521 | 200 | 0 | 246.1481
8318 | 0 | 2.8466 | 8.1383 | 26.5007 | 12.0039 | 49.4896 | 0 | 0 | 38.5047
8319 | 0 | 2.8948 | 9.0416 | 28.5386 | 13.5704 | 54.0453 | 0 | 0 | 42.1089
8320 | 0 | 2.5621 | 9.1539 | 26.5724 | 11.4581 | 49.7465 | 0 | 0 | 38.0305
8321 | 0.27901 | 2.6104 | 9.9059 | 31.5857 | 10.2784 | 54.6594 | 0 | 0 | 42.1431
8322 | 0.77094 | 2.4422 | 8.9308 | 25.6268 | 6.9596 | 44.7303 | 0 | 0 | 33.3574
8323 | 14.4069 | 2.2896 | 7.3978 | 28.7929 | 17.3677 | 70.255 | 0 | 0 | 60.5675
8324 | 42.4448 | 2.5406 | 6.35 | 32.9082 | 0 | 84.2436 | 0 | 0 | 75.353
8325 | 19.6782 | 2.6595 | 6.1174 | 25.7246 | 0 | 54.1797 | 0 | 0 | 45.4028
8326 | 53.8149 | 2.6078 | 6.2788 | 38.5356 | 0 | 101.2371 | 0 | 0 | 92.3505
8327 | 13.2483 | 2.3562 | 6.7239 | 27.7005 | 0 | 50.0289 | 0 | 0 | 40.9489
8328 | 74.4055 | 2.3846 | 7.603 | 30.5417 | 0 | 114.9347 | 0 | 0 | 104.9472
8329 | 52.5297 | 2.6866 | 10.3348 | 23.9717 | 0 | 89.5229 | 0 | 0 | 76.5014
8330 | 65.0205 | 2.7241 | 14.2708 | 31.2196 | 0 | 113.2349 | 0 | 200 | 296.2401
8331 | 28.5389 | 2.8295 | 12.7202 | 38.0468 | 0 | 82.1354 | 0 | 0 | 66.5857
8332 | 0 | 2.4241 | 11.5795 | 20.859 | 0 | 34.8626 | 0 | 0 | 20.859
8333 | 0 | 2.6142 | 11.919 | 22.7528 | 0 | 37.286 | 0 | 0 | 22.7528
8334 | 13.388 | 1.9615 | 11.5916 | 21.0225 | 0 | 47.9636 | 0 | 0 | 34.4105
8335 | 45.9507 | 2.3064 | 11.6056 | 24.9008 | 0 | 84.7636 | 0 | 0 | 70.8516
8336 | 0 | 2.0749 | 11.6102 | 30.8363 | 14.2973 | 58.8189 | 0 | 0 | 45.1337
8337 | 22.8496 | 2.3211 | 11.0464 | 34.6725 | 11.8366 | 82.7262 | 0 | 0 | 69.3587
8338 | 49.2604 | 2.4461 | 11.412 | 31.9508 | 11.2248 | 106.2941 | 0 | 0 | 92.436
8339 | 4.231 | 2.1209 | 10.1709 | 33.7073 | 21.1763 | 71.4064 | 0 | 0 | 59.1146
8340 | 0 | 2.3429 | 9.4553 | 26.0698 | 21.854 | 59.7219 | 0 | 0 | 47.9237
8341 | 0 | 2.2472 | 9.3731 | 31.3168 | 16.5477 | 59.4848 | 0 | 0 | 47.8645
8342 | 0 | 2.3704 | 8.8775 | 18.0625 | 28.009 | 57.3194 | 0 | 0 | 46.0715
8343 | 0 | 2.3935 | 9.5568 | 35.8186 | 13.9709 | 61.7397 | 0 | 0 | 49.7895
8344 | 0 | 2.3803 | 10.006 | 30.5018 | 14.8312 | 57.7193 | 0 | 0 | 45.333
8345 | 0 | 2.4897 | 10.5902 | 28.6914 | 2.9934 | 44.7646 | 0 | 0 | 31.6848
8346 | 0 | 2.2431 | 9.7103 | 31.5801 | 20.2374 | 63.7709 | 0 | 0 | 51.8175
8347 | 0 | 2.6578 | 7.8963 | 25.0605 | 9.7807 | 45.3954 | 0 | 0 | 34.8412
8348 | 0 | 2.8617 | 6.967 | 34.0304 | 0 | 43.8591 | 0 | 0 | 34.0304
8349 | 0 | 2.0445 | 6.593 | 28.7348 | 0 | 37.3723 | 0 | 0 | 28.7348
8350 | 0 | 2.2983 | 6.4574 | 21.4133 | 0 | 30.169 | 0 | 200 | 221.4133
8351 | 0 | 2.8496 | 6.6176 | 29.0594 | 0 | 38.5266 | 0 | 0 | 29.0594
8352 | 0 | 2.7872 | 7.2794 | 34.0048 | 0 | 44.0714 | 0 | 0 | 34.0048
8353 | 0 | 2.7869 | 6.9784 | 24.2617 | 0 | 34.027 | 0 | 0 | 24.2617
8354 | 0 | 2.4881 | 4.8914 | 27.2138 | 0 | 34.5933 | 0 | 0 | 27.2138
8355 | 0 | 2.8223 | 7.3408 | 30.0893 | 0 | 40.2524 | 0 | 0 | 30.0893
8356 | 0 | 2.7211 | 9.3191 | 25.1933 | 0 | 37.2335 | 0 | 0 | 25.1933
8357 | 0 | 2.9536 | 11.622 | 35.9141 | 0 | 50.4896 | 0 | 0 | 35.9141
8358 | 0 | 2.5752 | 11.431 | 24.8427 | 0 | 38.8488 | 0 | 0 | 24.8427
8359 | 0 | 2.208 | 11.3977 | 35.7937 | 0 | 49.3995 | 0 | 0 | 35.7937
8360 | 0 | 2.5026 | 11.245 | 26.8102 | 5.5363 | 46.0942 | 0 | 0 | 32.3465
8361 | 0 | 2.7227 | 11.1153 | 27.5454 | 8.5849 | 49.9683 | 0 | 0 | 36.1303
8362 | 0 | 2.8225 | 10.2698 | 27.1639 | 17.0332 | 57.2894 | 0 | 0 | 44.1971
8363 | 0 | 2.8539 | 8.8712 | 34.0472 | 26.3144 | 72.0867 | 0 | 0 | 60.3616
8364 | 0 | 2.2422 | 8.0521 | 21.8417 | 21.5253 | 53.6612 | 0 | 0 | 43.367
8365 | 0 | 2.6456 | 8.2688 | 25.6193 | 8.2279 | 44.7615 | 0 | 0 | 33.8472
8366 | 0 | 2.832 | 8.6379 | 23.5862 | 6.2446 | 41.3008 | 0 | 0 | 29.8309
8367 | 0 | 2.5968 | 9.8235 | 31.5994 | 17.4774 | 61.497 | 0 | 0 | 49.0767
8368 | 0 | 2.8472 | 10.385 | 21.4733 | 10.4423 | 45.1478 | 0 | 0 | 31.9156
8369 | 0 | 2.7186 | 10.8564 | 30.6349 | 17.7446 | 61.9545 | 0 | 0 | 48.3795
8370 | 0 | 2.9932 | 10.3294 | 25.3011 | 13.7926 | 52.4164 | 0 | 0 | 39.0937
8371 | 0 | 2.4795 | 8.8358 | 28.4771 | 7.3753 | 47.1677 | 0 | 0 | 35.8524
8372 | 0 | 2.2147 | 7.8434 | 30.2328 | 0 | 40.2909 | 0 | 200 | 230.2328
8373 | 0 | 2.5889 | 7.3827 | 36.0743 | 0 | 46.0458 | 0 | 0 | 36.0743
8374 | 0 | 2.4375 | 7.4752 | 32.9147 | 0 | 42.8274 | 0 | 0 | 32.9147
8375 | 0 | 2.479 | 7.7298 | 31.3635 | 0 | 41.5723 | 0 | 0 | 31.3635
8376 | 0 | 2.4087 | 8.3069 | 27.0581 | 0 | 37.7738 | 0 | 0 | 27.0581
8377 | 0 | 2.6332 | 7.7324 | 23.002 | 0 | 33.3677 | 0 | 0 | 23.002
8378 | 0 | 2.2646 | 6.4629 | 31.3266 | 0 | 40.0541 | 0 | 0 | 31.3266
8379 | 0 | 2.505 | 7.1308 | 33.0835 | 0 | 42.7193 | 0 | 0 | 33.0835
8380 | 0 | 2.5568 | 8.5273 | 39.5893 | 0 | 50.6734 | 0 | 0 | 39.5893
8381 | 0 | 2.6008 | 10.1455 | 31.1118 | 0 | 43.8581 | 0 | 0 | 31.1118
8382 | 0 | 2.0142 | 10.1591 | 24.6647 | 0 | 36.8381 | 0 | 0 | 24.6647
8383 | 0 | 2.5645 | 10.8158 | 26.877 | 0 | 40.2573 | 0 | 0 | 26.877
8384 | 0 | 2.2687 | 10.486 | 31.6575 | 12.8988 | 57.311 | 0 | 0 | 44.5563
8385 | 0 | 3.1664 | 10.4497 | 23.5873 | 18.3163 | 55.5197 | 0 | 0 | 41.9036
8386 | 0 | 2.4813 | 9.8134 | 31.5091 | 24.8125 | 68.6164 | 0 | 0 | 56.3217
8387 | 0 | 2.682 | 9.2431 | 25.593 | 21.6459 | 59.164 | 0 | 0 | 47.2389
8388 | 0 | 2.4762 | 8.8308 | 29.5629 | 13.2082 | 54.0781 | 0 | 0 | 42.7711
8389 | 0 | 2.9689 | 8.849 | 32.7854 | 17.2513 | 61.8547 | 0 | 0 | 50.0367
8390 | 0 | 2.4525 | 8.3722 | 32.4796 | 22.5809 | 65.8852 | 0 | 0 | 55.0605
8391 | 0 | 2.7217 | 8.1576 | 21.2968 | 9.6119 | 41.7879 | 0 | 0 | 30.9086
8392 | 0 | 2.567 | 8.4762 | 27.0644 | 15.1295 | 53.2371 | 0 | 0 | 42.1939
8393 | 0 | 2.2727 | 8.5844 | 30.0551 | 14.4883 | 55.4004 | 0 | 0 | 44.5434
8394 | 0 | 2.7074 | 7.6064 | 24.6562 | 19.9068 | 54.8769 | 0 | 0 | 44.5631
8395 | 0 | 2.7904 | 6.4119 | 35.0389 | 14.8926 | 59.1338 | 0 | 200 | 249.9315
8396 | 0 | 2.7469 | 5.7428 | 25.6579 | 0 | 34.1476 | 200 | 0 | 225.6579
8397 | 0 | 2.2912 | 5.3903 | 24.3545 | 0 | 32.036 | 0 | 0 | 24.3545
8398 | 0 | 2.4542 | 5.3945 | 27.479 | 0 | 35.3277 | 0 | 0 | 27.479
8399 | 0 | 2.2661 | 5.5878 | 32.3054 | 0 | 40.1593 | 0 | 0 | 32.3054
8400 | 0 | 2.6005 | 6.1518 | 22.1729 | 0 | 30.9252 | 0 | 0 | 22.1729
8401 | 0 | 2.5232 | 7.6973 | 33.5682 | 0 | 43.7886 | 0 | 0 | 33.5682
8402 | 0 | 2.9828 | 10.2766 | 31.6343 | 0 | 44.8937 | 0 | 0 | 31.6343
8403 | 0 | 2.6408 | 9.2779 | 27.7329 | 0 | 39.6515 | 0 | 0 | 27.7329
8404 | 0 | 2.6858 | 9.0434 | 29.0675 | 0 | 40.7966 | 0 | 0 | 29.0675
8405 | 0 | 2.6908 | 9.3333 | 24.8192 | 0 | 36.8433 | 0 | 0 | 24.8192
8406 | 0 | 2.3531 | 8.834 | 18.7299 | 0 | 29.9169 | 0 | 0 | 18.7299
8407 | 0 | 2.7297 | 8.2165 | 34.2367 | 0 | 45.1828 | 0 | 0 | 34.2367
8408 | 0 | 1.9221 | 7.8403 | 23.8985 | 15.8753 | 49.5362 | 0 | 0 | 39.7738
8409 | 0 | 2.69 | 7.3797 | 34.1867 | 13.634 | 57.8904 | 0 | 0 | 47.8207
8410 | 0 | 2.6803 | 6.6752 | 25.9311 | 20.9456 | 56.2322 | 0 | 0 | 46.8767
8411 | 0 | 2.7147 | 5.9165 | 28.3146 | 18.4965 | 55.4422 | 0 | 0 | 46.8111
8412 | 0 | 2.9204 | 4.981 | 23.8369 | 21.1629 | 52.9013 | 0 | 0 | 44.9998
8413 | 0 | 2.3309 | 4.2269 | 25.2401 | 17.1335 | 48.9314 | 0 | 0 | 42.3736
8414 | 0 | 2.6849 | 4.935 | 20.6762 | 15.7386 | 44.0347 | 0 | 0 | 36.4147
8415 | 0 | 2.3931 | 6.122 | 26.0407 | 18.8535 | 53.4094 | 0 | 0 | 44.8942
8416 | 0 | 2.6974 | 6.0295 | 32.2986 | 9.4316 | 50.4571 | 0 | 0 | 41.7302
8417 | 0 | 3.0633 | 6.0284 | 31.124 | 10.9399 | 51.1556 | 0 | 0 | 42.064
8418 | 0 | 2.0457 | 3.8081 | 25.8262 | 10.7555 | 42.4355 | 0 | 0 | 36.5816
8419 | 0 | 2.1477 | 2.2713 | 30.5051 | 16.1328 | 51.0569 | 0 | 0 | 46.6379
8420 | 0 | 2.809 | 1.9261 | 25.4059 | 0 | 30.1409 | 0 | 0 | 25.4059
8421 | 0 | 2.63 | 2.2393 | 28.2553 | 0 | 33.1246 | 0 | 0 | 28.2553
8422 | 0 | 2.924 | 2.7418 | 27.3932 | 0 | 33.059 | 0 | 0 | 27.3932
8423 | 0 | 3.225 | 3.1535 | 22.0562 | 0 | 28.4347 | 0 | 0 | 22.0562
8424 | 0 | 2.6994 | 3.6526 | 28.5045 | 0 | 34.8565 | 0 | 0 | 28.5045
8425 | 0 | 2.4909 | 5.1612 | 30.391 | 0 | 38.043 | 0 | 0 | 30.391
8426 | 0 | 2.6986 | 8.4256 | 25.2601 | 0 | 36.3842 | 0 | 0 | 25.2601
8427 | 0 | 2.4452 | 7.6387 | 34.7213 | 0 | 44.8052 | 0 | 0 | 34.7213
8428 | 0 | 2.9303 | 7.8781 | 29.1656 | 0 | 39.974 | 0 | 200 | 229.1656
8429 | 0 | 2.6783 | 8.7742 | 31.2092 | 0 | 42.6617 | 0 | 0 | 31.2092
8430 | 0 | 2.3415 | 8.1808 | 22.4246 | 0 | 32.947 | 0 | 0 | 22.4246
8431 | 0 | 2.6227 | 8.2165 | 25.3983 | 0 | 36.2375 | 0 | 0 | 25.3983
8432 | 0 | 2.5333 | 8.1145 | 22.437 | 19.9186 | 53.0035 | 0 | 0 | 42.3557
8433 | 0 | 2.2417 | 7.7871 | 29.1391 | 14.6262 | 53.7941 | 0 | 0 | 43.7652
8434 | 0 | 3.3197 | 7.4196 | 31.7038 | 19.4299 | 61.873 | 0 | 0 | 51.1337
8435 | 0 | 2.2572 | 6.7019 | 19.8781 | 16.7101 | 45.5473 | 0 | 0 | 36.5882
8436 | 0 | 2.4689 | 5.6635 | 22.6907 | 19.1169 | 49.94 | 0 | 0 | 41.8076
8437 | 0 | 2.4734 | 5.1142 | 24.2037 | 12.5738 | 44.3651 | 0 | 0 | 36.7775
8438 | 0 | 2.7863 | 4.8529 | 30.205 | 6.1689 | 44.013 | 0 | 0 | 36.3739
8439 | 0 | 2.5527 | 5.5209 | 31.8809 | 16.7846 | 56.7391 | 0 | 0 | 48.6655
8440 | 0 | 2.302 | 5.3667 | 29.8366 | 10.0472 | 47.5525 | 0 | 0 | 39.8838
8441 | 0 | 2.5599 | 4.8879 | 31.8336 | 18.6337 | 57.9152 | 0 | 0 | 50.4673
8442 | 0 | 2.498 | 3.8081 | 30.2821 | 20.4866 | 57.0748 | 0 | 0 | 50.7687
8443 | 0 | 2.5739 | 2.9614 | 29.9865 | 24.9524 | 60.4742 | 0 | 0 | 54.9389
8444 | 0 | 2.8158 | 2.967 | 28.1306 | 0 | 33.9135 | 0 | 0 | 28.1306
8445 | 0 | 2.4545 | 2.8049 | 32.5704 | 0 | 37.8297 | 0 | 0 | 32.5704
8446 | 0 | 2.2688 | 2.0183 | 24.8277 | 0 | 29.1149 | 0 | 0 | 24.8277
8447 | 0 | 2.7741 | 2.5855 | 31.2916 | 0 | 36.6512 | 0 | 0 | 31.2916
8448 | 0 | 2.1688 | 3.4108 | 22.9259 | 0 | 28.5055 | 0 | 0 | 22.9259
8449 | 0 | 2.4248 | 5.4655 | 23.5626 | 0 | 31.4529 | 0 | 0 | 23.5626
8450 | 0 | 2.8404 | 8.7178 | 20.4631 | 0 | 32.0213 | 0 | 0 | 20.4631
8451 | 0 | 2.3662 | 7.8026 | 16.6457 | 0 | 26.8146 | 0 | 0 | 16.6457
8452 | 0 | 2.091 | 7.6039 | 28.1539 | 0 | 37.8489 | 0 | 0 | 28.1539
8453 | 0 | 2.4799 | 7.7259 | 29.6454 | 0 | 39.8512 | 0 | 0 | 29.6454
8454 | 0 | 2.257 | 7.1649 | 30.6985 | 0 | 40.1204 | 0 | 0 | 30.6985
8455 | 0 | 2.4346 | 6.4482 | 28.7949 | 0 | 37.6778 | 0 | 0 | 28.7949
8456 | 0 | 2.6705 | 6.6065 | 31.2593 | 19.4325 | 59.9688 | 0 | 0 | 50.6918
8457 | 0 | 2.4462 | 6.2254 | 23.3983 | 9.7533 | 41.8232 | 0 | 0 | 33.1516
8458 | 0 | 2.4798 | 5.5249 | 26.9278 | 12.9749 | 47.9074 | 0 | 0 | 39.9027
8459 | 0 | 2.3616 | 4.6729 | 32.4272 | 13.6675 | 53.1291 | 0 | 0 | 46.0946
8460 | 0 | 2.7561 | 3.616 | 25.3183 | 17.0022 | 48.6926 | 0 | 0 | 42.3205
8461 | 0 | 2.4974 | 2.3636 | 37.4545 | 6.8124 | 49.1278 | 0 | 0 | 44.2668
8462 | 0 | 2.4533 | 2.3888 | 27.1821 | 9.8967 | 41.9209 | 0 | 0 | 37.0788
8463 | 0 | 2.4561 | 2.859 | 19.4338 | 12.2885 | 37.0374 | 0 | 0 | 31.7223
8464 | 0 | 2.2636 | 3.2838 | 28.3018 | 8.1716 | 42.0209 | 0 | 0 | 36.4735
8465 | 0 | 2.4086 | 3.5194 | 23.4421 | 13.2147 | 42.5847 | 0 | 0 | 36.6568
8466 | 0 | 2.049 | 3.9195 | 25.4361 | 24.6648 | 56.0694 | 0 | 200 | 250.1009
8467 | 0 | 2.5674 | 3.2572 | 30.1259 | 25.843 | 61.7935 | 0 | 0 | 55.969
8468 | 0 | 2.4117 | 2.967 | 28.5456 | 0 | 33.9243 | 0 | 0 | 28.5456
8469 | 0 | 2.7972 | 3.0473 | 28.9498 | 0 | 34.7943 | 0 | 0 | 28.9498
8470 | 0 | 3.2073 | 2.4203 | 30.2361 | 0 | 35.8636 | 0 | 0 | 30.2361
8471 | 0 | 2.4838 | 2.1798 | 24.6219 | 0 | 29.2855 | 0 | 0 | 24.6219
8472 | 0 | 2.6654 | 2.927 | 34.991 | 0 | 40.5835 | 0 | 0 | 34.991
8473 | 0 | 2.8008 | 4.8568 | 31.5389 | 0 | 39.1966 | 0 | 0 | 31.5389
8474 | 0 | 2.6263 | 7.7437 | 20.376 | 0 | 30.746 | 200 | 0 | 220.376
8475 | 0 | 2.174 | 6.901 | 37.4758 | 0 | 46.5508 | 0 | 0 | 37.4758
8476 | 0 | 2.6521 | 7.0556 | 28.1803 | 0 | 37.888 | 0 | 0 | 28.1803
8477 | 0 | 2.7135 | 7.5861 | 29.4713 | 0 | 39.7709 | 0 | 0 | 29.4713
8478 | 0 | 2.6988 | 7.1649 | 30.8986 | 0 | 40.7623 | 0 | 0 | 30.8986
8479 | 0 | 2.5927 | 7.2587 | 31.3883 | 0 | 41.2397 | 0 | 0 | 31.3883
8480 | 0 | 2.6989 | 7.4291 | 26.9565 | 14.849 | 51.9334 | 0 | 0 | 41.8055
8481 | 0 | 2.723 | 7.176 | 25.3939 | 20.5776 | 55.8705 | 0 | 0 | 45.9715
8482 | 0 | 2.8762 | 6.7429 | 34.2633 | 14.8692 | 58.7517 | 0 | 0 | 49.1325
8483 | 0 | 2.477 | 5.7856 | 22.8729 | 18.0378 | 49.1733 | 0 | 0 | 40.9107
8484 | 0 | 2.673 | 4.6777 | 28.3783 | 16.8775 | 52.6064 | 0 | 0 | 45.2558
8485 | 0 | 2.3021 | 3.3396 | 23.8076 | 16.6006 | 46.0499 | 0 | 0 | 40.4082
8486 | 0 | 2.1479 | 2.7995 | 29.7671 | 12.657 | 47.3715 | 0 | 0 | 42.4241
8487 | 0 | 2.2051 | 3.0307 | 29.8056 | 11.5111 | 46.5525 | 0 | 0 | 41.3167
8488 | 0 | 2.722 | 3.7572 | 22.4229 | 12.9432 | 41.8453 | 0 | 0 | 35.3661
8489 | 0 | 2.6789 | 2.2272 | 32.805 | 5.3385 | 43.0496 | 0 | 0 | 38.1434
8490 | 0 | 2.2139 | 2.1199 | 25.6826 | 14.0186 | 44.0349 | 0 | 0 | 39.7012
8491 | 0 | 2.2136 | 1.5861 | 23.6559 | 0.62396 | 28.0796 | 0 | 0 | 24.2799
8492 | 0 | 2.523 | 1.239 | 26.1027 | 0 | 29.8647 | 0 | 0 | 26.1027
8493 | 0 | 2.4346 | 1.0185 | 35.8309 | 0 | 39.284 | 0 | 0 | 35.8309
8494 | 0 | 2.3164 | 1.2949 | 25.6945 | 0 | 29.3057 | 0 | 0 | 25.6945
8495 | 0 | 2.6963 | 1.9364 | 35.7209 | 0 | 40.3535 | 0 | 0 | 35.7209
8496 | 0 | 2.4612 | 2.6852 | 24.6707 | 0 | 29.8172 | 0 | 0 | 24.6707
8497 | 0 | 2.5241 | 3.4366 | 35.8777 | 0 | 41.8384 | 0 | 0 | 35.8777
8498 | 0 | 2.9517 | 6.5746 | 22.2563 | 0 | 31.7827 | 0 | 0 | 22.2563
8499 | 0 | 1.994 | 6.2453 | 23.4637 | 0 | 31.7031 | 0 | 0 | 23.4637
8500 | 0 | 2.3626 | 6.3702 | 30.9654 | 0 | 39.6982 | 0 | 0 | 30.9654
8501 | 0 | 2.8765 | 6.5378 | 29.2584 | 0 | 38.6727 | 0 | 0 | 29.2584
8502 | 0 | 2.4162 | 5.8586 | 30.9499 | 0 | 39.2247 | 0 | 0 | 30.9499
8503 | 0 | 2.431 | 4.7537 | 31.3643 | 0 | 38.549 | 0 | 0 | 31.3643
8504 | 0 | 2.5113 | 4.5502 | 33.3482 | 14.5828 | 54.9925 | 0 | 0 | 47.931
8505 | 0 | 2.939 | 4.3241 | 21.8884 | 17.032 | 46.1836 | 0 | 0 | 38.9205
8506 | 0 | 2.283 | 3.8331 | 32.1891 | 19.722 | 58.0272 | 0 | 0 | 51.9111
8507 | 0 | 2.1879 | 4.0838 | 27.161 | 14.2074 | 47.6402 | 0 | 0 | 41.3684
8508 | 0 | 2.463 | 3.0851 | 26.4905 | 18.5262 | 50.5648 | 0 | 0 | 45.0167
8509 | 0 | 2.6962 | 2.3299 | 26.4606 | 11.8601 | 43.3467 | 0 | 0 | 38.3206
8510 | 0 | 2.7515 | 2.3888 | 25.7273 | 17.0373 | 47.905 | 0 | 0 | 42.7647
8511 | 0 | 2.685 | 2.3438 | 24.6996 | 17.5365 | 47.2649 | 0 | 0 | 42.2361
8512 | 0 | 2.6216 | 2.6211 | 22.2265 | 12.2844 | 39.7535 | 0 | 0 | 34.5109
8513 | 0 | 2.5674 | 2.2272 | 27.7156 | 20.8441 | 53.3544 | 0 | 0 | 48.5598
8514 | 0 | 2.2777 | 2.1199 | 28.693 | 13.8751 | 46.9657 | 0 | 0 | 42.5681
8515 | 0 | 2.2601 | 1.9531 | 37.5304 | 16.2588 | 58.0024 | 0 | 0 | 53.7892
8516 | 0 | 2.8464 | 1.5255 | 27.2957 | 0 | 31.6676 | 0 | 200 | 227.2957
8517 | 0 | 2.2924 | 1.1504 | 23.9718 | 0 | 27.4145 | 0 | 0 | 23.9718
8518 | 0 | 2.2954 | 1.1994 | 31.336 | 0 | 34.8307 | 0 | 0 | 31.336
8519 | 0 | 2.7983 | 1.0675 | 33.1202 | 0 | 36.986 | 0 | 0 | 33.1202
8520 | 0 | 2.6215 | 1.3615 | 22.7966 | 0 | 26.7796 | 0 | 0 | 22.7966
8521 | 0 | 2.8124 | 1.7973 | 32.804 | 0 | 37.4138 | 0 | 0 | 32.804
8522 | 0 | 2.6117 | 2.1992 | 34.0441 | 0 | 38.8551 | 0 | 0 | 34.0441
8523 | 0 | 2.5883 | 1.9945 | 25.5485 | 0 | 30.1313 | 0 | 0 | 25.5485
8524 | 0 | 2.525 | 3.6751 | 34.7565 | 0 | 40.9566 | 0 | 0 | 34.7565
8525 | 0 | 2.7736 | 6.2189 | 32.7634 | 0 | 41.7558 | 0 | 0 | 32.7634
8526 | 0 | 2.781 | 6.5068 | 31.8909 | 0 | 41.1788 | 0 | 0 | 31.8909
8527 | 0 | 2.5122 | 5.988 | 35.1234 | 0 | 43.6236 | 0 | 0 | 35.1234
8528 | 0 | 2.3628 | 6.3467 | 30.9413 | 11.7397 | 51.3905 | 0 | 0 | 42.681
8529 | 0 | 2.4505 | 5.7312 | 28.0463 | 26.6626 | 62.8906 | 0 | 0 | 54.7089
8530 | 0 | 2.8601 | 5.2682 | 35.0539 | 11.1215 | 54.3037 | 0 | 0 | 46.1754
8531 | 0 | 1.9307 | 3.7378 | 34.5721 | 7.4852 | 47.7257 | 0 | 0 | 42.0573
8532 | 0 | 2.3977 | 2.2739 | 30.2991 | 11.5364 | 46.5071 | 0 | 0 | 41.8355
8533 | 0 | 2.2962 | 2.4752 | 26.2804 | 11.669 | 42.7208 | 0 | 0 | 37.9495
8534 | 0 | 2.6301 | 1.8702 | 23.0649 | 14.5799 | 42.1451 | 0 | 0 | 37.6448
8535 | 0 | 2.2297 | 2.2301 | 26.8758 | 10.4368 | 41.7725 | 0 | 0 | 37.3127
8536 | 0 | 2.405 | 2.3118 | 33.5778 | 10.8937 | 49.1883 | 0 | 0 | 44.4715
8537 | 0 | 2.6205 | 2.0443 | 31.0671 | 19.7277 | 55.4595 | 0 | 0 | 50.7947
8538 | 0 | 3.0236 | 1.9367 | 30.8505 | 6.7435 | 42.5543 | 0 | 0 | 37.594
8539 | 0 | 2.7567 | 1.5167 | 27.3313 | 11.5804 | 43.1852 | 0 | 0 | 38.9118
8540 | 0 | 2.6775 | 1.4117 | 24.9614 | 0 | 29.0506 | 0 | 0 | 24.9614
8541 | 0 | 2.3416 | 2.2457 | 29.2321 | 0 | 33.8195 | 0 | 0 | 29.2321
8542 | 0 | 2.7411 | 1.665 | 28.2424 | 0 | 32.6486 | 0 | 0 | 28.2424
8543 | 0 | 2.3487 | 2.4578 | 23.2191 | 0 | 28.0256 | 0 | 0 | 23.2191
8544 | 0 | 2.625 | 2.9584 | 39.1023 | 0 | 44.6857 | 0 | 0 | 39.1023
8545 | 0 | 2.4378 | 3.6833 | 41.3942 | 0 | 47.5152 | 0 | 0 | 41.3942
8546 | 0 | 2.6674 | 2.1636 | 29.3625 | 0 | 34.1935 | 0 | 0 | 29.3625
8547 | 0 | 2.2854 | 1.767 | 32.2566 | 0 | 36.3089 | 0 | 0 | 32.2566
8548 | 0 | 2.9102 | 2.7623 | 35.0146 | 0 | 40.687 | 0 | 0 | 35.0146
8549 | 0 | 2.129 | 6.2468 | 28.9906 | 0 | 37.3663 | 0 | 0 | 28.9906
8550 | 0 | 2.5894 | 6.3552 | 31.9485 | 0 | 40.893 | 0 | 0 | 31.9485
8551 | 0 | 2.0154 | 6.7251 | 25.4984 | 0 | 34.2388 | 0 | 0 | 25.4984
8552 | 0 | 2.3316 | 6.6259 | 36.685 | 11.5874 | 57.2299 | 0 | 0 | 48.2724
8553 | 0 | 2.8424 | 6.424 | 29.1056 | 12.6783 | 51.0503 | 200 | 0 | 241.7839
8554 | 0 | 2.6995 | 6.2468 | 28.799 | 21.0427 | 58.788 | 0 | 0 | 49.8417
8555 | 0 | 2.2615 | 5.9898 | 26.1256 | 16.0475 | 50.4243 | 0 | 0 | 42.173
8556 | 0 | 2.7036 | 5.5969 | 30.0307 | 4.1527 | 42.4839 | 0 | 0 | 34.1835
8557 | 0 | 2.4776 | 5.4889 | 31.4094 | 18.9478 | 58.3237 | 0 | 0 | 50.3572
8558 | 0 | 2.8253 | 4.5419 | 22.7387 | 6.4764 | 36.5823 | 0 | 0 | 29.2151
8559 | 0 | 2.5728 | 4.5687 | 29.3714 | 15.5795 | 52.0924 | 0 | 0 | 44.9509
8560 | 0 | 2.7007 | 5.0515 | 24.5603 | 11.7355 | 44.0481 | 0 | 0 | 36.2958
8561 | 0 | 2.3999 | 4.8285 | 30.8024 | 21.857 | 59.8878 | 0 | 0 | 52.6594
8562 | 0 | 2.7155 | 3.0619 | 25.1407 | 3.9164 | 34.8346 | 0 | 0 | 29.0572
8563 | 0 | 2.3474 | 2.5671 | 25.8549 | 12.7546 | 43.524 | 0 | 0 | 38.6096
8564 | 0 | 2.8883 | 2.273 | 25.8059 | 0 | 30.9672 | 0 | 0 | 25.8059
8565 | 0 | 2.6098 | 2.8049 | 32.2146 | 0 | 37.6293 | 0 | 0 | 32.2146
8566 | 0 | 2.5724 | 3.0634 | 26.827 | 0 | 32.4628 | 0 | 0 | 26.827
8567 | 0 | 2.2708 | 3.965 | 28.7483 | 0 | 34.9841 | 0 | 0 | 28.7483
8568 | 0 | 2.6378 | 4.9425 | 32.1541 | 0 | 39.7344 | 0 | 0 | 32.1541
8569 | 0 | 2.5408 | 6.277 | 25.5404 | 0 | 34.3582 | 0 | 200 | 225.5404
8570 | 0 | 2.4041 | 10.2766 | 27.5207 | 0 | 40.2014 | 0 | 0 | 27.5207
8571 | 0 | 2.6281 | 11.4089 | 22.594 | 0 | 36.6309 | 0 | 0 | 22.594
8572 | 0 | 2.939 | 10.4828 | 30.6044 | 0 | 44.0262 | 0 | 0 | 30.6044
8573 | 0 | 2.5444 | 9.8225 | 23.3474 | 0 | 35.7143 | 0 | 0 | 23.3474
8574 | 0 | 2.5125 | 8.834 | 25.9066 | 0 | 37.253 | 0 | 0 | 25.9066
8575 | 0 | 2.5488 | 8.2902 | 23.1477 | 0 | 33.9867 | 0 | 0 | 23.1477
8576 | 0 | 2.4896 | 8.046 | 26.3237 | 13.112 | 49.9713 | 0 | 0 | 39.4357
8577 | 0 | 2.9917 | 7.4476 | 28.2923 | 22.7187 | 61.4503 | 0 | 0 | 51.011
8578 | 0 | 2.5178 | 8.2316 | 30.0784 | 9.7541 | 50.5819 | 0 | 0 | 39.8325
8579 | 0 | 2.5144 | 9.0582 | 27.6316 | 19.2885 | 58.4926 | 0 | 0 | 46.9201
8580 | 0 | 2.3576 | 7.7869 | 35.6595 | 0.78509 | 46.5891 | 0 | 0 | 36.4446
8581 | 0 | 2.7322 | 6.3564 | 29.131 | 20.4866 | 58.7062 | 0 | 0 | 49.6177
8582 | 0 | 3.2146 | 5.9207 | 18.9877 | 21.9526 | 50.0755 | 0 | 0 | 40.9403
8583 | 0 | 2.4108 | 5.6068 | 27.3868 | 25.8947 | 61.2991 | 0 | 0 | 53.2815
8584 | 0 | 2.3416 | 7.1656 | 28.9066 | 8.3536 | 46.7675 | 0 | 0 | 37.2602
8585 | 0 | 2.4439 | 6.7126 | 25.8707 | 11.285 | 46.3122 | 0 | 0 | 37.1557
8586 | 0 | 2.3609 | 5.8126 | 31.0407 | 22.6676 | 61.8819 | 0 | 0 | 53.7084
8587 | 0 | 2.4641 | 3.8943 | 31.1921 | -0.39877 | 37.1518 | 0 | 0 | 30.7933
8588 | 0 | 2.807 | 3.1687 | 33.0721 | 0 | 39.0478 | 0 | 0 | 33.0721
8589 | 0 | 2.1548 | 3.1264 | 18.7849 | 0 | 24.0661 | 0 | 0 | 18.7849
8590 | 0 | 2.189 | 2.4639 | 27.6093 | 0 | 32.2622 | 0 | 0 | 27.6093
8591 | 0 | 2.7555 | 2.8796 | 25.6449 | 0 | 31.2799 | 0 | 0 | 25.6449
8592 | 0 | 2.3233 | 3.4643 | 27.8111 | 0 | 33.5988 | 0 | 0 | 27.8111
8593 | 0 | 2.5235 | 4.3399 | 20.5884 | 0 | 27.4518 | 0 | 0 | 20.5884
8594 | 0 | 2.4671 | 2.1636 | 25.4483 | 0 | 30.0791 | 0 | 0 | 25.4483
8595 | 0 | 2.7745 | 2.3637 | 26.1744 | 0 | 31.3126 | 0 | 0 | 26.1744
8596 | 0 | 2.8689 | 4.2405 | 24.7669 | 0 | 31.8763 | 0 | 0 | 24.7669
8597 | 0 | 3.0336 | 7.1844 | 31.3287 | 0 | 41.5467 | 0 | 0 | 31.3287
8598 | 0 | 2.5177 | 6.7941 | 30.7598 | 0 | 40.0716 | 0 | 0 | 30.7598
8599 | 0 | 2.4386 | 7.3796 | 32.7575 | 0 | 42.5757 | 0 | 0 | 32.7575
8600 | 0 | 2.5132 | 6.8977 | 34.424 | 15.5353 | 59.3702 | 0 | 0 | 49.9593
8601 | 0 | 2.0296 | 6.9648 | 25.3607 | 6.173 | 40.528 | 0 | 200 | 231.5336
8602 | 0 | 2.7982 | 6.4846 | 35.479 | 16.0853 | 60.8472 | 0 | 0 | 51.5644
8603 | 0 | 2.741 | 6.4038 | 30.9199 | 19.173 | 59.2377 | 0 | 0 | 50.0929
8604 | 0 | 2.1947 | 6.6114 | 25.9517 | 9.1652 | 43.923 | 0 | 0 | 35.1169
8605 | 0 | 2.9203 | 6.1609 | 33.5173 | 19.263 | 61.8616 | 0 | 0 | 52.7803
8606 | 0 | 2.8509 | 6.0562 | 22.277 | 7.8148 | 38.9989 | 0 | 0 | 30.0918
8607 | 0 | 2.7618 | 6.552 | 34.3364 | 19.2152 | 62.8654 | 0 | 0 | 53.5516
8608 | 0 | 2.2723 | 7.2309 | 26.0098 | 6.5096 | 42.0225 | 0 | 0 | 32.5194
8609 | 0 | 2.1838 | 7.4107 | 30.326 | 17.95 | 57.8705 | 0 | 0 | 48.276
8610 | 0 | 2.3516 | 6.344 | 31.2353 | 11.5767 | 51.5076 | 0 | 0 | 42.812
8611 | 0 | 2.8494 | 4.9396 | 30.7098 | 13.8473 | 52.3461 | 0 | 0 | 44.5571
8612 | 0 | 2.3093 | 4.5799 | 31.7671 | 0 | 38.6564 | 0 | 0 | 31.7671
8613 | 0 | 2.7689 | 4.6675 | 31.0298 | 0 | 38.4662 | 0 | 0 | 31.0298
8614 | 0 | 2.1743 | 4.2796 | 30.604 | 0 | 37.058 | 0 | 0 | 30.604
8615 | 0 | 2.1874 | 4.4963 | 24.9789 | 0 | 31.6627 | 0 | 0 | 24.9789
8616 | 0 | 2.2487 | 4.6931 | 28.7148 | 0 | 35.6565 | 0 | 0 | 28.7148
8617 | 0 | 2.0292 | 4.9418 | 28.4794 | 0 | 35.4504 | 0 | 0 | 28.4794
8618 | 0 | 2.6448 | 2.1636 | 25.4953 | 0 | 30.3038 | 0 | 0 | 25.4953
8619 | 0 | 2.2749 | 2.8404 | 30.4608 | 0 | 35.576 | 0 | 0 | 30.4608
8620 | 0 | 2.4195 | 4.7579 | 22.3577 | 0 | 29.5351 | 0 | 0 | 22.3577
8621 | 0 | 2.4987 | 7.5299 | 30.5587 | 0 | 40.5872 | 0 | 0 | 30.5587
8622 | 0 | 2.3819 | 7.4769 | 33.2031 | 0 | 43.0619 | 0 | 0 | 33.2031
8623 | 0 | 2.7092 | 7.925 | 26.4644 | 0 | 37.0987 | 0 | 0 | 26.4644
8624 | 0 | 2.1903 | 7.6589 | 28.1362 | 0.94987 | 38.9352 | 0 | 0 | 29.0861
8625 | 0 | 2.5448 | 7.5656 | 27.1324 | 13.2924 | 50.5353 | 0 | 0 | 40.4249
8626 | 0 | 2.5746 | 7.1979 | 33.1946 | 17.4155 | 60.3826 | 0 | 0 | 50.6101
8627 | 0 | 2.6731 | 6.877 | 33.7566 | 12.3369 | 55.6436 | 0 | 0 | 46.0935
8628 | 0 | 3.2151 | 6.6114 | 27.7087 | 18.9208 | 56.4561 | 0 | 0 | 46.6295
8629 | 0 | 2.45 | 6.4596 | 26.4021 | 12.3538 | 47.6656 | 0 | 0 | 38.7559
8630 | 0 | 2.7535 | 5.9671 | 24.9859 | 12.3566 | 46.0632 | 0 | 0 | 37.3425
8631 | 0 | 2.2395 | 5.9854 | 35.4156 | 10.681 | 54.3215 | 0 | 0 | 46.0966
8632 | 0 | 2.4943 | 6.5044 | 27.5881 | 2.9661 | 39.5529 | 200 | 0 | 230.5542
8633 | 0 | 2.3016 | 6.7064 | 26.1943 | 7.3415 | 42.5438 | 0 | 0 | 33.5357
8634 | 0 | 2.5778 | 5.7129 | 25.5232 | 22.5851 | 56.399 | 0 | 200 | 248.1083
8635 | 0 | 2.5983 | 4.8345 | 27.7681 | 11.4989 | 46.6998 | 0 | 0 | 39.267
8636 | 0 | 2.299 | 4.5284 | 30.535 | 0 | 37.3624 | 0 | 0 | 30.535
8637 | 0 | 2.4804 | 4.5824 | 20.609 | 0 | 27.6718 | 0 | 0 | 20.609
8638 | 0 | 2.7546 | 5.1534 | 29.7363 | 0 | 37.6443 | 0 | 0 | 29.7363
8639 | 0 | 2.2102 | 5.8313 | 27.6914 | 0 | 35.7329 | 0 | 0 | 27.6914
8640 | 0 | 2.2227 | 6.8774 | 24.8046 | 0 | 33.9048 | 0 | 0 | 24.8046
8641 | 0 | 2.2332 | 9.1175 | 34.4501 | 0 | 45.8008 | 0 | 0 | 34.4501
8642 | 0 | 2.3518 | 11.8353 | 32.4558 | 0 | 46.6429 | 0 | 0 | 32.4558
8643 | 0 | 2.6363 | 10.7532 | 31.4839 | 0 | 44.8734 | 0 | 0 | 31.4839
8644 | 0 | 1.8899 | 10.5513 | 32.5246 | 0 | 44.9658 | 0 | 0 | 32.5246
8645 | 0 | 2.7206 | 11.1503 | 23.0222 | 0 | 36.8931 | 0 | 0 | 23.0222
8646 | 0 | 2.4267 | 10.7933 | 25.2573 | 0 | 38.4774 | 0 | 0 | 25.2573
8647 | 0 | 2.1179 | 10.0584 | 37.344 | 0 | 49.5204 | 0 | 0 | 37.344
8648 | 0 | 2.2144 | 9.3483 | 21.7482 | 23.9434 | 57.2543 | 0 | 0 | 45.6916
8649 | 0 | 2.8809 | 8.8057 | 26.4872 | 21.156 | 59.3297 | 0 | 0 | 47.6431
8650 | 0 | 2.4466 | 8.5023 | 23.4536 | 17.8588 | 52.2613 | 0 | 0 | 41.3124
8651 | 0 | 2.6878 | 8.1418 | 23.4528 | 14.2447 | 48.5271 | 0 | 0 | 37.6975
8652 | 0 | 2.539 | 8.2419 | 22.8607 | 14.9692 | 48.6108 | 0 | 0 | 37.8299
8653 | 0 | 2.718 | 7.8647 | 25.9786 | 6.2212 | 42.7825 | 0 | 0 | 32.1998
8654 | 0 | 2.2028 | 7.6455 | 34.1788 | 11.4506 | 55.4777 | 0 | 0 | 45.6294
8655 | 0 | 2.5717 | 9.385 | 24.3405 | 24.9652 | 61.2625 | 0 | 0 | 49.3057
8656 | 0 | 2.2155 | 10.4793 | 33.0992 | 7.0603 | 52.8543 | 0 | 0 | 40.1594
8657 | 0 | 2.4541 | 12.3008 | 23.3166 | 19.6394 | 57.7109 | 0 | 200 | 242.956
8658 | 0 | 2.6427 | 10.2671 | 26.8349 | 12.3859 | 52.1307 | 0 | 0 | 39.2208
8659 | 0 | 2.5295 | 9.2709 | 33.981 | 13.6516 | 59.4331 | 0 | 0 | 47.6326
8660 | 0 | 1.8648 | 7.9981 | 25.6242 | 0 | 35.4872 | 0 | 0 | 25.6242
8661 | 0 | 2.0457 | 7.1678 | 24.2632 | 0 | 33.4767 | 0 | 0 | 24.2632
8662 | 0 | 2.4507 | 6.6807 | 31.9416 | 0 | 41.0729 | 0 | 0 | 31.9416
8663 | 0 | 2.7271 | 6.6427 | 27.5865 | 0 | 36.9563 | 0 | 0 | 27.5865
8664 | 0 | 2.7472 | 7.1999 | 33.0859 | 0 | 43.0329 | 0 | 0 | 33.0859
8665 | 0 | 2.9739 | 9.4218 | 29.74 | 0 | 42.1357 | 0 | 0 | 29.74
8666 | 0 | 2.2318 | 12.0301 | 23.0083 | 0 | 37.2702 | 0 | 0 | 23.0083
8667 | 0 | 2.7176 | 10.7532 | 33.7736 | 0 | 47.2444 | 0 | 0 | 33.7736
8668 | 0 | 3.0194 | 10.2771 | 34.8254 | 0 | 48.1219 | 0 | 0 | 34.8254
8669 | 0 | 2.2025 | 10.6611 | 32.4075 | 0 | 45.271 | 0 | 0 | 32.4075
8670 | 0 | 2.5675 | 10.3579 | 22.4871 | 0 | 35.4125 | 0 | 0 | 22.4871
8671 | 0 | 2.3941 | 9.9847 | 31.6149 | 0 | 43.9938 | 0 | 0 | 31.6149
8672 | 0 | 2.8718 | 9.5539 | 31.8154 | 17.0504 | 61.2914 | 0 | 0 | 48.8657
8673 | 0 | 2.5553 | 9.0094 | 24.3062 | 21.4005 | 57.2714 | 0 | 0 | 45.7068
8674 | 0 | 2.9808 | 8.4346 | 28.5538 | 18.449 | 58.4182 | 0 | 0 | 47.0028
8675 | 0 | 2.563 | 7.5528 | 37.9927 | 22.5738 | 70.6822 | 0 | 0 | 60.5665
8676 | 0 | 2.4228 | 6.7252 | 32.9134 | 6.0686 | 48.13 | 0 | 0 | 38.982
8677 | 0 | 2.2853 | 6.0902 | 28.9524 | 16.0728 | 53.4006 | 0 | 0 | 45.0252
8678 | 0 | 2.7463 | 5.7564 | 24.3479 | 16.5234 | 49.3741 | 0 | 0 | 40.8714
8679 | 0 | 2.2569 | 6.122 | 21.7027 | 16.8394 | 46.9211 | 0 | 0 | 38.5422
8680 | 0 | 2.9917 | 6.0295 | 30.0474 | 13.4759 | 52.5445 | 0 | 0 | 43.5233
8681 | 0 | 2.7758 | 5.5722 | 26.3548 | 8.4181 | 43.1209 | 0 | 0 | 34.7729
8682 | 0 | 2.0315 | 4.3649 | 33.0483 | 8.2732 | 47.718 | 0 | 0 | 41.3215
8683 | 0 | 2.7484 | 1.9531 | 29.5584 | 12.0445 | 46.3043 | 0 | 200 | 241.6028
8684 | 0 | 2.583 | 1.5255 | 31.5194 | 0 | 35.6279 | 0 | 0 | 31.5194
8685 | 0 | 2.7377 | 1.7125 | 24.3489 | 0 | 28.7991 | 0 | 0 | 24.3489
8686 | 0 | 2.4636 | 1.6357 | 25.1146 | 0 | 29.2139 | 0 | 0 | 25.1146
8687 | 0 | 2.8228 | 2.1233 | 21.4543 | 0 | 26.4004 | 0 | 0 | 21.4543
8688 | 0 | 2.8466 | 2.0677 | 25.3157 | 0 | 30.2299 | 0 | 0 | 25.3157
8689 | 0 | 2.6346 | 1.814 | 31.854 | 0 | 36.3025 | 0 | 0 | 31.854
8690 | 0 | 2.3678 | 2.1992 | 35.0358 | 0 | 39.6028 | 0 | 0 | 35.0358
8691 | 0 | 2.3956 | 1.9945 | 34.1222 | 0 | 38.5123 | 0 | 0 | 34.1222
8692 | 0 | 2.8454 | 3.6751 | 28.3253 | 0 | 34.8458 | 0 | 0 | 28.3253
8693 | 0 | 2.7635 | 7.4126 | 37.0006 | 0 | 47.1766 | 0 | 0 | 37.0006
8694 | 0 | 2.6311 | 7.4561 | 27.1322 | 0 | 37.2194 | 0 | 0 | 27.1322
8695 | 0 | 2.3328 | 7.0063 | 37.2157 | 0 | 46.5548 | 0 | 0 | 37.2157
8696 | 0 | 2.3054 | 7.183 | 27.5675 | 13.6225 | 50.6784 | 0 | 0 | 41.19
8697 | 0 | 2.8132 | 6.4448 | 30.0215 | 6.7325 | 46.0119 | 0 | 0 | 36.754
8698 | 0 | 2.5894 | 5.7503 | 32.9548 | 14.7807 | 56.0752 | 0 | 0 | 47.7355
8699 | 0 | 2.7475 | 3.6094 | 27.5701 | 10.2079 | 44.1349 | 0 | 0 | 37.778
8700 | 0 | 2.329 | 2.2739 | 23.6254 | 8.8034 | 37.0317 | 0 | 0 | 32.4288
8701 | 0 | 2.5535 | 2.4752 | 35.7385 | 16.5301 | 57.2972 | 0 | 0 | 52.2685
8702 | 0 | 2.1701 | 1.8702 | 25.3136 | 7.7169 | 37.0709 | 0 | 0 | 33.0305
8703 | 0 | 2.5713 | 2.2301 | 32.0461 | 10.3453 | 47.1928 | 0 | 0 | 42.3914
8704 | 0 | 2.4366 | 2.3118 | 24.4095 | 12.0496 | 41.2075 | 0 | 0 | 36.4591
8705 | 0 | 2.3765 | 1.9 | 23.7864 | 7.6765 | 35.7393 | 0 | 0 | 31.4629
8706 | 0 | 2.2203 | 1.9367 | 29.6218 | 9.7839 | 43.5627 | 0 | 0 | 39.4057
8707 | 0 | 2.7233 | 1.5167 | 29.2048 | 13.5128 | 46.9575 | 0 | 0 | 42.7176
8708 | 0 | 2.3305 | 1.4117 | 29.5816 | 0 | 33.3238 | 0 | 0 | 29.5816
8709 | 0 | 2.2966 | 1.2183 | 24.9764 | 0 | 28.4913 | 0 | 0 | 24.9764
8710 | 0 | 2.3056 | 1.2344 | 25.945 | 0 | 29.4849 | 0 | 0 | 25.945
8711 | 0 | 2.7794 | 1.544 | 27.6922 | 0 | 32.0155 | 0 | 0 | 27.6922
8712 | 0 | 2.5182 | 1.9465 | 23.9111 | 0 | 28.3758 | 200 | 0 | 223.9111
8713 | 0 | 2.6045 | 2.9719 | 25.2247 | 0 | 30.8011 | 0 | 0 | 25.2247
8714 | 0 | 2.6832 | 2.1636 | 22.5521 | 0 | 27.3989 | 0 | 0 | 22.5521
8715 | 0 | 2.0982 | 1.767 | 29.4063 | 0 | 33.2715 | 0 | 0 | 29.4063
8716 | 0 | 2.3969 | 2.6204 | 30.213 | 0 | 35.2303 | 0 | 0 | 30.213
8717 | 0 | 2.4574 | 6.1974 | 39.4439 | 0 | 48.0987 | 0 | 0 | 39.4439
8718 | 0 | 2.1801 | 6.1114 | 18.7759 | 0 | 27.0673 | 0 | 0 | 18.7759
8719 | 0 | 2.5453 | 6.1796 | 29.6025 | 0 | 38.3275 | 0 | 0 | 29.6025
8720 | 0 | 3.0168 | 5.8647 | 25.733 | 10.3242 | 44.9388 | 0 | 0 | 36.0572
8721 | 0 | 2.8457 | 6.0635 | 22.7502 | 17.7714 | 49.4308 | 0 | 0 | 40.5216
8722 | 0 | 2.575 | 5.8901 | 28.1785 | 21.7277 | 58.3713 | 0 | 0 | 49.9062
8723 | 0 | 2.3663 | 5.3982 | 28.6104 | 20.043 | 56.4179 | 0 | 0 | 48.6534
8724 | 0 | 2.7487 | 4.8359 | 30.8135 | 9.3754 | 47.7735 | 0 | 0 | 40.1889
8725 | 0 | 2.8185 | 4.2942 | 31.4785 | 19.684 | 58.2752 | 0 | 0 | 51.1625
8726 | 0 | 2.8969 | 2.9385 | 31.6108 | 9.6851 | 47.1313 | 0 | 0 | 41.2959
8727 | 0 | 2.0603 | 2.2605 | 33.8041 | 10.1768 | 48.3016 | 0 | 0 | 43.9809
8728 | 0 | 2.3919 | 2.1706 | 22.7907 | 16.9617 | 44.3149 | 0 | 0 | 39.7524
8729 | 0 | 2.4676 | 2.1677 | 29.5569 | 11.3907 | 45.5829 | 0 | 0 | 40.9476
8730 | 0 | 2.6492 | 2.1706 | 26.6863 | 9.698 | 41.2042 | 0 | 0 | 36.3843
8731 | 0 | 2.8072 | 1.5861 | 36.0917 | 16.1478 | 56.6329 | 0 | 0 | 52.2395
8732 | 0 | 2.3804 | 1.239 | 34.0235 | 0 | 37.6429 | 0 | 0 | 34.0235
8733 | 0 | 2.4163 | 1.0185 | 25.2958 | 0 | 28.7307 | 0 | 0 | 25.2958
8734 | 0 | 2.8207 | 1.0722 | 29.7686 | 0 | 33.6615 | 0 | 0 | 29.7686
8735 | 0 | 2.243 | 1.1947 | 24.3498 | 0 | 27.7875 | 0 | 0 | 24.3498
8736 | 0 | 2.5336 | 1.5565 | 30.777 | 0 | 34.8671 | 0 | 0 | 30.777
8737 | 0 | 2.6515 | 2.7569 | 30.6664 | 0 | 36.0748 | 0 | 0 | 30.6664
8738 | 0 | 2.8567 | 5.7953 | 35.3252 | 0 | 43.9771 | 0 | 0 | 35.3252
8739 | 0 | 2.4002 | 5.8355 | 35.1235 | 0 | 43.3592 | 0 | 0 | 35.1235
8740 | 0 | 2.8368 | 6.2331 | 29.872 | 0 | 38.9418 | 0 | 0 | 29.872
8741 | 0 | 2.611 | 6.5378 | 29.9948 | 0 | 39.1436 | 0 | 200 | 229.9948
8742 | 0 | 2.6019 | 6.294 | 25.1175 | 0 | 34.0134 | 0 | 0 | 25.1175
8743 | 0 | 2.3483 | 6.1535 | 24.5004 | 0 | 33.0022 | 0 | 0 | 24.5004
8744 | 0 | 2.4408 | 6.1267 | 31.6643 | 9.271 | 49.5028 | 0 | 0 | 40.9353
8745 | 0 | 2.1696 | 6.0896 | 35.9742 | 15.2103 | 59.4437 | 0 | 0 | 51.1845
8746 | 0 | 2.5426 | 5.3219 | 18.3335 | 9.1309 | 35.3289 | 0 | 0 | 27.4644
8747 | 0 | 2.461 | 4.4765 | 25.5473 | 15.6509 | 48.1358 | 0 | 0 | 41.1982
8748 | 0 | 1.7385 | 3.7676 | 29.9075 | 17.5346 | 52.9482 | 0 | 0 | 47.442
8749 | 0 | 2.3648 | 2.3636 | 26.9384 | 16.6088 | 48.2756 | 0 | 0 | 43.5471
8750 | 0 | 2.9479 | 2.3888 | 32.5983 | 20.7162 | 58.6512 | 0 | 0 | 53.3145
8751 | 0 | 2.5363 | 2.7731 | 27.2787 | 5.0954 | 37.6835 | 0 | 0 | 32.3741
8752 | 0 | 2.3386 | 2.7158 | 33.2788 | 8.8376 | 47.1708 | 0 | 0 | 42.1164
8753 | 0 | 2.4912 | 2.2649 | 36.6493 | 19.4308 | 60.8361 | 0 | 0 | 56.08
8754 | 0 | 2.5368 | 2.1199 | 16.2806 | 13.2839 | 34.2212 | 0 | 0 | 29.5645
8755 | 0 | 2.3047 | 1.5167 | 36.0049 | 10.1706 | 49.9969 | 0 | 0 | 46.1755
8756 | 0 | 2.6269 | 1.4117 | 36.7694 | 0 | 40.8081 | 0 | 0 | 36.7694
8757 | 0 | 2.539 | 1.1486 | 31.655 | 0 | 35.3426 | 0 | 0 | 31.655
8758 | 0 | 2.6201 | 1.2344 | 30.5553 | 0 | 34.4097 | 0 | 0 | 30.5553
8759 | 0 | 2.5231 | 1.1264 | 27.3242 | 0 | 30.9738 | 0 | 0 | 27.3242
8760 | 0 | 1.9795 | 1.3683 | 26.9002 | 0 | 30.248 | 0 | 0 | 26.9002